## Contents
SHEPD Network Scenario Headroom Report 2026 Summary
Our Network Scenario Headroom Report (NSHR) is published to enable customers, developers, generators, local authorities and other interested third parties to view the possible headroom capacity at our Primary Substations and Bulk Supply Points (BSP) up to 2050. SSEN have used the latest Distribution Future Energy Scenarios (DFES) data to inform four scenarios of demand and generation forecasts. SSEN's best view of the future demand and generation needs on our network is aligned to the Holistic Transition scenario. Although the NSHR provides a view of the future in terms of our potential available capacity and constraints on our network, we would encourage any party using this information in their decision-making process to engage with us ahead of making an application to connect or offer flexible services.
Network Headroom Report Contents
Tab | Description
Key Information | This tab provides some additional detail to assist users with how to read the data presented within this report.
Primary Headroom Dem | This tab provides the demand headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Primary Headroom Gen | This tab provides the generation headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Local Authority Reference | This tab provides information on the local authorities and the Primaries that support those areas
EISD | To indicate potential transmission constraints by 'Earliest in Service Date' per Grid Supply Point (GSP)
Apr 2026 Version 1.1

## Key Information
SHEPD Network Scenario Headroom Report 2026 Key Information
Our Network Scenario Headroom Report (NSHR) has been developed to be used in conjunction with our other documents that combine to make the full Network Development Plan; the other documents to reference are the Network Development Plan Methodology & Assumptions and Network Development Report. The capacity that demand and generation growth is measured against is the firm capacity of the primary substation as per our Load Indices submission to Ofgem and as indicated by our Long Term Development Statement. Firm capacity means the available capacity on the network with a single feed on outage; for instance a twin transformer sites firm capacity would be the lowest capacity available on a single transformer. For single transformer sites, the firm capacity is based on the backfeed supply available to restore supplies; this may be limited by the backfeed circuit capacity rather than the transformer providing the backfeed. In order to identify future overloaded network assets, forecasts are created which combine our long term DFES projections with the estimated contribution from our connections pipeline after appropriate diversity factors have been applied. The DFES incorporates transitional Regional Energy Strategic Plan (tRESP) insights to ensure alignment and consistency with National Energy System Operator (NESO)'s energy infrastructure needs. Forecast headroom and outstanding contracted generation capacity are indicative and subject to external policy drivers. Actual outcomes will be influenced by Clean Power 2030 (CP2030) programme and Connections Reform, which may materially affect connection queue management. When reviewing the headroom reports for demand and generation the following applies: GREEN and POSTIVE VALUES = Capacity is forecast to be available RED and NEGATIVE VALUES = There are constraints forecast It must be noted that forecasts in RED do not mean that connections cannot be made; there are opportunities through flexible services that can enable connections without triggering network reinforcement. We would encourage any developer, generator or customer to contact us to discuss their connection and available opportunities to connect. The data shown within this NSHR is used by us to identify long term investment opportunities where there are constraints highlighted. As the forecast is scenario based, these constraints are subject to change and will be reviewed and published annually by SHEPD. Please note that our DFES scenario naming convention has been updated yearly to align with the updated NESO Future Energy Scenario (FES) pathways framework. Published annually, the FES framework outlines different scenarios for the future of the whole energy system. SSEN's DFES builds on the FES scenarios by engaging a diverse and expert range of stakeholders, undertaking detailed investigations into the pipeline of projects seeking to connect, and reflecting extensive industry and local area insight to forecast future load on SSEN’s network.
New DFES Scenario | Previous DFES Scenario | FES Pathway Description
Electric Engagement (EE) | Electric Engagement (formerly Consumer Transformation) | Net zero met through mainly electrified demand. Consumers are highly engaged in the energy transition through smart technologies that reduce energy demands, utilising technologies such as electric heat pumps and electric vehicles.
Holistic Transition (HT) | Holistic Transition (formerly Leading the Way) | Net zero met through a mix of electrification and hydrogen, with hydrogen mainly around industrial clusters. Consumer engagement in the transition is very strong with demand shifting, with smart homes and electric vehicles providing flexibility to the grid.
Hydrogen Evolution (HE) | Hydrogen Evolution (formerly System Transformation) | Net zero met through fast progress for hydrogen in industry and heat. Some consumers will have hydrogen boilers, although most heat is electrified. There are low levels of consumer engagement. Hydrogen will be prevalent for heavy goods vehicles but electric car uptake is strong.
Falling Behind (FB) | Falling Behind (formerly Counterfactual (formerly Falling Short)) | Net zero missed, though some progress is made for decarbonisation compared to today. There is still a heavy reliance on unabated fossil fuel.
`
Apr 2026
Version 1.1

## Primary Headroom Dem
#VALUE! | Grid Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Demand (MVA) | Demand Headroom Winter (MVA) | [12 empty] | Demand Headroom Summer (MVA) | [12 empty] | Demand Headroom Spring/Autumn (MVA)
[8 empty] | 2027 | 2028 | 2028 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2040 | 2045 | 2050 | 2027 | 2028 | 2028 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2040 | 2045 | 2050 | 2027 | 2028 | 2028 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2040 | 2045 | 2050
| FORT AUGUSTUS | ABERCHALDER | MINIMUM HEADROOM | NH 33843 03575 | YES | YES | 0.13 | 0.099837 | 0.1029 | 0.1029 | 0.093714 | 0.090653 | 0.08351 | 0.077388 | 0.074327 | 0.068204 | 0.067184 | 0.055959 | 0.042694 | 0.038612 | 0.097143 | 0.10122 | 0.099184 | 0.094082 | 0.094082 | 0.09 | 0.085918 | 0.084898 | 0.079796 | 0.079796 | 0.068571 | 0.068571 | 0.067551 | 0.10308 | 0.10716 | 0.10614 | 0.096959 | 0.094918 | 0.089816 | 0.083694 | 0.081653 | 0.075531 | 0.07451 | 0.065327 | 0.057163 | 0.054102
|  | ABERCHALDER | EE |  |  |  |  | 0.099837 | 0.10392 | 0.1029 | 0.095755 | 0.091673 | 0.084531 | 0.079429 | 0.075347 | 0.069224 | 0.068204 | 0.055959 | 0.042694 | 0.039633 | 0.097143 | 0.10122 | 0.1002 | 0.095102 | 0.094082 | 0.09 | 0.085918 | 0.084898 | 0.079796 | 0.079796 | 0.070612 | 0.068571 | 0.071633 | 0.10308 | 0.10716 | 0.10716 | 0.099 | 0.094918 | 0.090837 | 0.084714 | 0.081653 | 0.076551 | 0.07451 | 0.065327 | 0.057163 | 0.055122
|  | ABERCHALDER | HT |  |  |  |  | 0.099837 | 0.1029 | 0.1029 | 0.094735 | 0.091673 | 0.085551 | 0.080449 | 0.077388 | 0.070245 | 0.069224 | 0.05902 | 0.047796 | 0.038612 | 0.097143 | 0.10122 | 0.099184 | 0.095102 | 0.094082 | 0.09 | 0.086939 | 0.084898 | 0.080816 | 0.080816 | 0.068571 | 0.068571 | 0.070612 | 0.10308 | 0.10716 | 0.10614 | 0.099 | 0.094918 | 0.090837 | 0.085735 | 0.083694 | 0.077571 | 0.075531 | 0.068388 | 0.060224 | 0.054102
|  | ABERCHALDER | HE |  |  |  |  | 0.10494 | 0.1029 | 0.1029 | 0.093714 | 0.090653 | 0.08351 | 0.077388 | 0.074327 | 0.068204 | 0.067184 | 0.058 | 0.047796 | 0.038612 | 0.10327 | 0.10122 | 0.099184 | 0.094082 | 0.095102 | 0.09 | 0.085918 | 0.084898 | 0.079796 | 0.079796 | 0.071633 | 0.071633 | 0.067551 | 0.10818 | 0.10716 | 0.10614 | 0.096959 | 0.095939 | 0.089816 | 0.083694 | 0.081653 | 0.075531 | 0.07451 | 0.068388 | 0.060224 | 0.054102
|  | ABERCHALDER | FB |  |  |  |  | 0.11004 | 0.10392 | 0.10494 | 0.10494 | 0.1029 | 0.10494 | 0.10086 | 0.098816 | 0.091673 | 0.090653 | 0.081469 | 0.074327 | 0.072286 | 0.10837 | 0.10122 | 0.10122 | 0.10224 | 0.1002 | 0.10122 | 0.097143 | 0.095102 | 0.09 | 0.09 | 0.081837 | 0.073673 | 0.070612 | 0.11329 | 0.10716 | 0.1092 | 0.11022 | 0.10716 | 0.10818 | 0.1041 | 0.10206 | 0.093898 | 0.092878 | 0.086755 | 0.078592 | 0.076551
| TUMMEL BRIDGE | ABERFELDY | MINIMUM HEADROOM | NN 84889 48876 | NO | YES | 0.326 | 4.012 | 3.7773 | 3.6876 | 3.4488 | 3.2702 | 2.9284 | 2.558 | 2.1835 | 1.8182 | 1.6222 | 0.38449 | -0.57673 | -0.95837 | 4.9324 | 4.7967 | 4.7212 | 4.5182 | 4.3192 | 4.0345 | 3.7549 | 3.5141 | 3.3008 | 3.1773 | 2.3324 | 1.7763 | 1.6876 | 4.5314 | 4.2192 | 4.1222 | 3.8927 | 3.6835 | 3.3508 | 3.0151 | 2.6763 | 2.3733 | 2.1906 | 1.0692 | 0.26612 | 0.0079592
|  | ABERFELDY | EE |  |  |  |  | 4.0161 | 3.7835 | 3.7151 | 3.5243 | 3.3427 | 2.9906 | 2.608 | 2.2845 | 1.9498 | 1.8406 | 0.38449 | -0.57673 | -0.79204 | 4.9345 | 4.7978 | 4.7345 | 4.5396 | 4.3427 | 4.0549 | 3.7549 | 3.5345 | 3.3151 | 3.2437 | 2.3396 | 1.7763 | 1.7906 | 4.5355 | 4.2222 | 4.1539 | 3.9253 | 3.7314 | 3.3876 | 3.0273 | 2.7376 | 2.4447 | 2.3365 | 1.0692 | 0.26612 | 0.16918
|  | ABERFELDY | HT |  |  |  |  | 4.012 | 3.7773 | 3.6876 | 3.4488 | 3.2702 | 2.9284 | 2.5784 | 2.2243 | 1.8182 | 1.6222 | 0.46612 | -0.47776 | -0.95837 | 4.9324 | 4.7978 | 4.7212 | 4.5182 | 4.3192 | 4.0559 | 3.8212 | 3.5876 | 3.3355 | 3.1773 | 2.3324 | 1.8018 | 1.6876 | 4.5314 | 4.2192 | 4.1222 | 3.8927 | 3.6835 | 3.3508 | 3.0447 | 2.7324 | 2.3824 | 2.1906 | 1.1263 | 0.33959 | 0.0079592
|  | ABERFELDY | HE |  |  |  |  | 4.0161 | 3.7845 | 3.6988 | 3.4947 | 3.309 | 2.9457 | 2.558 | 2.1835 | 1.8294 | 1.7049 | 0.63755 | 0.14265 | -0.20122 | 4.9335 | 4.7967 | 4.7294 | 4.5335 | 4.3345 | 4.0345 | 3.7784 | 3.5141 | 3.3008 | 3.209 | 2.5529 | 2.411 | 2.2314 | 4.5365 | 4.2222 | 4.1427 | 3.9049 | 3.712 | 3.3518 | 3.0151 | 2.6763 | 2.3733 | 2.2467 | 1.3345 | 0.98143 | 0.7151
|  | ABERFELDY | FB |  |  |  |  | 4.0957 | 4.0794 | 3.8467 | 3.8018 | 3.7335 | 3.6386 | 3.5386 | 3.3192 | 3.162 | 3.0335 | 2.2508 | 1.3978 | 0.90082 | 4.9733 | 4.9467 | 4.7651 | 4.7304 | 4.6478 | 4.5498 | 4.4641 | 4.2539 | 4.1049 | 3.9559 | 3.3876 | 2.6365 | 2.0284 | 4.6182 | 4.5845 | 4.2253 | 4.1835 | 4.1008 | 4.0018 | 3.911 | 3.7008 | 3.5314 | 3.3845 | 2.6865 | 1.7233 | 1.362
| STRATHLEVEN | ABERFOYLE | MINIMUM HEADROOM | NS 53215 99705 | YES | YES | 0.383 | 3.7031 | 3.7163 | 3.7082 | 3.6765 | 3.6602 | 3.598 | 3.5265 | 3.4612 | 3.3837 | 3.3398 | 3.0898 | 2.7918 | 2.5082 | 4.2173 | 4.2224 | 4.2224 | 4.2112 | 4.1949 | 4.1694 | 4.1224 | 4.0908 | 4.0316 | 4.002 | 3.8439 | 3.7704 | 3.6245 | 4.0362 | 4.0454 | 4.0342 | 4.0036 | 3.9719 | 3.9291 | 3.8485 | 3.7913 | 3.7128 | 3.6689 | 3.4444 | 3.2597 | 3.1097
|  | ABERFOYLE | EE |  |  |  |  | 3.7051 | 3.7194 | 3.7082 | 3.6827 | 3.6653 | 3.6122 | 3.5439 | 3.4816 | 3.4224 | 3.3694 | 3.1204 | 2.8663 | 2.6582 | 4.2194 | 4.2235 | 4.2235 | 4.2143 | 4.1949 | 4.1755 | 4.1276 | 4.099 | 4.05 | 4.0153 | 3.8847 | 3.8337 | 3.7898 | 4.0393 | 4.0474 | 4.0342 | 4.0097 | 3.9719 | 3.9403 | 3.8648 | 3.8107 | 3.7393 | 3.6923 | 3.4801 | 3.3219 | 3.2107
|  | ABERFOYLE | HT |  |  |  |  | 3.7031 | 3.7163 | 3.7082 | 3.6765 | 3.6602 | 3.598 | 3.5265 | 3.4612 | 3.3837 | 3.3398 | 3.0898 | 2.7918 | 2.5082 | 4.2173 | 4.2224 | 4.2224 | 4.2112 | 4.198 | 4.1694 | 4.1224 | 4.0908 | 4.0316 | 4.002 | 3.8439 | 3.8051 | 3.8051 | 4.0362 | 4.0454 | 4.0342 | 4.0036 | 3.975 | 3.9291 | 3.8485 | 3.7913 | 3.7128 | 3.6689 | 3.4444 | 3.2597 | 3.1097
|  | ABERFOYLE | HE |  |  |  |  | 3.7051 | 3.7194 | 3.7092 | 3.6867 | 3.6694 | 3.6163 | 3.548 | 3.4867 | 3.4122 | 3.3704 | 3.1745 | 2.8908 | 2.6827 | 4.2194 | 4.2235 | 4.2235 | 4.2133 | 4.1949 | 4.1755 | 4.1296 | 4.101 | 4.0449 | 4.0163 | 3.8929 | 3.8214 | 3.7571 | 4.0393 | 4.0474 | 4.0362 | 4.0097 | 3.977 | 3.9434 | 3.8658 | 3.8138 | 3.7362 | 3.6913 | 3.5117 | 3.324 | 3.1883
|  | ABERFOYLE | FB |  |  |  |  | 3.7296 | 3.7469 | 3.7622 | 3.7551 | 3.75 | 3.7378 | 3.7378 | 3.7112 | 3.6878 | 3.6735 | 3.5357 | 3.3 | 3.1653 | 4.2337 | 4.2388 | 4.2459 | 4.2429 | 4.2429 | 4.2337 | 4.2276 | 4.2061 | 4.1755 | 4.1612 | 4.0082 | 3.7704 | 3.6245 | 4.0719 | 4.0811 | 4.0934 | 4.0811 | 4.0801 | 4.0638 | 4.0454 | 4.0117 | 3.977 | 3.9587 | 3.8026 | 3.5291 | 3.4648
| KEITH 2 | ABERLOUR | MINIMUM HEADROOM | NJ 24809 40878 | NO | YES | 2.923 | -0.089796 | -0.090816 | -0.1102 | -0.20204 | -0.23776 | -0.39694 | -0.52857 | -0.63776 | -0.76224 | -0.92041 | -1.5071 | -1.8541 | -2.0837 | 0.81837 | 0.81837 | 0.80816 | 0.76837 | 0.75102 | 0.65306 | 0.58673 | 0.5551 | 0.45816 | 0.3398 | 0.022449 | -0.057143 | -0.079592 | 0.39184 | 0.38673 | 0.36939 | 0.28163 | 0.2449 | 0.12041 | 0.019388 | -0.065306 | -0.17143 | -0.32143 | -0.78163 | -1.0418 | -1.2265
|  | ABERLOUR | EE |  |  |  |  | -0.089796 | -0.090816 | -0.1102 | -0.20204 | -0.23776 | -0.39184 | -0.51837 | -0.61939 | -0.74796 | -0.85918 | -1.5071 | -1.8541 | -2.0837 | 0.81837 | 0.81837 | 0.80816 | 0.76837 | 0.75204 | 0.65306 | 0.60306 | 0.55816 | 0.49388 | 0.44286 | 0.022449 | -0.045918 | -0.079592 | 0.39286 | 0.38776 | 0.36939 | 0.28163 | 0.2449 | 0.12347 | 0.02551 | -0.05102 | -0.1551 | -0.24592 | -0.78163 | -1.0418 | -1.2265
|  | ABERLOUR | HT |  |  |  |  | -0.089796 | -0.089796 | -0.10306 | -0.18367 | -0.23265 | -0.37959 | -0.51429 | -0.5898 | -0.74898 | -0.92041 | -1.4235 | -1.799 | -2.0796 | 0.81837 | 0.81837 | 0.80816 | 0.77755 | 0.75102 | 0.65714 | 0.58673 | 0.56122 | 0.45816 | 0.3398 | 0.028571 | -0.057143 | -0.044898 | 0.39184 | 0.38776 | 0.37245 | 0.29796 | 0.25 | 0.13265 | 0.019388 | -0.035714 | -0.17143 | -0.32143 | -0.74082 | -0.98469 | -1.1398
|  | ABERLOUR | HE |  |  |  |  | -0.089796 | -0.090816 | -0.10714 | -0.19898 | -0.23776 | -0.39694 | -0.52857 | -0.63776 | -0.76224 | -0.86531 | -1.4102 | -1.7031 | -1.8776 | 0.81837 | 0.81837 | 0.80816 | 0.76837 | 0.75204 | 0.65306 | 0.59898 | 0.5551 | 0.49592 | 0.45102 | 0.066327 | 0.043878 | 0.040816 | 0.39286 | 0.38673 | 0.37041 | 0.28367 | 0.24694 | 0.12041 | 0.019388 | -0.065306 | -0.16327 | -0.24388 | -0.71735 | -0.87347 | -0.98469
|  | ABERLOUR | FB |  |  |  |  | -0.063265 | -0.059184 | -0.056122 | -0.11429 | -0.12653 | -0.14388 | -0.17347 | -0.38673 | -0.4051 | -0.4398 | -0.62347 | -0.87143 | -1.0714 | 0.83571 | 0.83673 | 0.83673 | 0.81224 | 0.80612 | 0.79694 | 0.77347 | 0.57347 | 0.56224 | 0.53571 | 0.42551 | 0.25714 | 0.11224 | 0.41531 | 0.41735 | 0.41429 | 0.35816 | 0.3449 | 0.32653 | 0.29796 | 0.084694 | 0.064286 | 0.053061 | -0.1051 | -0.33367 | -0.50408
| ABERNETHY | ABERNETHY | MINIMUM HEADROOM | NO 20094 17132 | YES | YES | 0.119 | 1.0531 | 1.0276 | 0.99184 | 0.94082 | 0.87755 | 0.82041 | 0.73571 | 0.65918 | 0.57449 | 0.53163 | 0.23367 | 0.026531 | -0.14592 | 1.7633 | 1.7459 | 1.7255 | 1.698 | 1.6622 | 1.6214 | 1.5612 | 1.5224 | 1.4582 | 1.4071 | 1.1857 | 1.1704 | 1.1 | 1.6143 | 1.5898 | 1.5622 | 1.5224 | 1.4745 | 1.4092 | 1.3296 | 1.2949 | 1.2184 | 1.1694 | 0.91429 | 0.78061 | 0.68367
|  | ABERNETHY | EE |  |  |  |  | 1.0531 | 1.0306 | 0.99184 | 0.94184 | 0.87959 | 0.83265 | 0.75102 | 0.68163 | 0.60204 | 0.56633 | 0.23367 | 0.026531 | -0.13265 | 1.7643 | 1.7469 | 1.7255 | 1.699 | 1.6633 | 1.6255 | 1.5643 | 1.5255 | 1.4653 | 1.4357 | 1.2204 | 1.1908 | 1.1653 | 1.6173 | 1.5898 | 1.5622 | 1.5224 | 1.4755 | 1.4184 | 1.3408 | 1.3071 | 1.2347 | 1.1918 | 0.91429 | 0.7949 | 0.71122
|  | ABERNETHY | HT |  |  |  |  | 1.0541 | 1.0286 | 0.99898 | 0.94796 | 0.9 | 0.84286 | 0.76531 | 0.69694 | 0.6102 | 0.54898 | 0.30102 | 0.065306 | -0.14592 | 1.7633 | 1.7459 | 1.7255 | 1.699 | 1.6776 | 1.6255 | 1.5622 | 1.5265 | 1.4582 | 1.4071 | 1.1857 | 1.1704 | 1.1857 | 1.6143 | 1.5908 | 1.5643 | 1.5265 | 1.4939 | 1.4255 | 1.351 | 1.3153 | 1.2347 | 1.1714 | 0.93776 | 0.80612 | 0.70306
|  | ABERNETHY | HE |  |  |  |  | 1.0551 | 1.0276 | 0.99592 | 0.94082 | 0.87755 | 0.82041 | 0.73571 | 0.65918 | 0.57449 | 0.53163 | 0.27245 | 0.032653 | -0.11735 | 1.7633 | 1.7459 | 1.7255 | 1.698 | 1.6622 | 1.6214 | 1.5612 | 1.5224 | 1.4643 | 1.4276 | 1.2184 | 1.1796 | 1.1296 | 1.6153 | 1.5908 | 1.5633 | 1.5224 | 1.4745 | 1.4092 | 1.3296 | 1.2949 | 1.2184 | 1.1694 | 0.93061 | 0.78061 | 0.68367
|  | ABERNETHY | FB |  |  |  |  | 1.0796 | 1.0602 | 1.0459 | 1.0153 | 0.98776 | 0.95918 | 0.92959 | 0.9 | 0.86735 | 0.83163 | 0.66327 | 0.4551 | 0.39184 | 1.7867 | 1.7694 | 1.751 | 1.7337 | 1.7214 | 1.6969 | 1.6653 | 1.6418 | 1.6041 | 1.5633 | 1.3959 | 1.1949 | 1.1 | 1.65 | 1.6306 | 1.6143 | 1.5918 | 1.5776 | 1.548 | 1.5153 | 1.4908 | 1.4531 | 1.4122 | 1.2286 | 1.0378 | 1.0133
| TARLAND | ABOYNE | MINIMUM HEADROOM | NO 52048 98716 | NO | NO | 1.645 | 7.9513 | 7.9074 | 7.786 | 7.5074 | 7.2594 | 6.7268 | 6.2217 | 5.8104 | 5.4492 | 5.1431 | 4.2543 | 3.3911 | 2.6757 | 9.5809 | 9.5451 | 9.4962 | 9.4237 | 9.3441 | 9.0788 | 8.8349 | 8.6482 | 8.4778 | 8.2809 | 7.5431 | 7.3819 | 7.2839 | 8.8722 | 8.8436 | 8.8018 | 8.6793 | 8.4905 | 8.0579 | 7.6671 | 7.3528 | 7.0691 | 6.8161 | 6.0916 | 5.5324 | 5.1314
|  | ABOYNE | EE |  |  |  |  | 7.9513 | 7.9084 | 7.786 | 7.538 | 7.3257 | 6.8349 | 6.3727 | 5.9931 | 5.6757 | 5.3676 | 4.2543 | 3.3911 | 2.7298 | 9.5839 | 9.5513 | 9.5013 | 9.4288 | 9.3553 | 9.0788 | 8.8349 | 8.6482 | 8.4819 | 8.289 | 7.5839 | 7.3819 | 7.2839 | 8.8722 | 8.8477 | 8.8018 | 8.6977 | 8.5324 | 8.1303 | 7.7671 | 7.4681 | 7.2171 | 6.963 | 6.0916 | 5.5324 | 5.1344
|  | ABOYNE | HT |  |  |  |  | 7.9564 | 7.9074 | 7.7992 | 7.5523 | 7.3543 | 6.9492 | 6.5574 | 6.186 | 5.8676 | 5.5013 | 4.5329 | 3.5319 | 2.6757 | 9.5819 | 9.5451 | 9.4962 | 9.4237 | 9.3441 | 9.14 | 8.9441 | 8.7533 | 8.5584 | 8.3074 | 7.5431 | 7.4309 | 7.5309 | 8.8722 | 8.8436 | 8.8048 | 8.7007 | 8.5518 | 8.2232 | 7.9181 | 7.6232 | 7.364 | 7.0548 | 6.2569 | 5.6242 | 5.1314
|  | ABOYNE | HE |  |  |  |  | 7.9543 | 7.9155 | 7.7982 | 7.5074 | 7.2594 | 6.7268 | 6.2217 | 5.8104 | 5.4492 | 5.1431 | 4.4217 | 3.5676 | 2.989 | 9.5809 | 9.5513 | 9.5033 | 9.4298 | 9.3543 | 9.0798 | 8.8411 | 8.6533 | 8.4778 | 8.2809 | 7.6747 | 7.5809 | 7.4462 | 8.8722 | 8.8518 | 8.8089 | 8.6793 | 8.4905 | 8.0579 | 7.6671 | 7.3528 | 7.0691 | 6.8161 | 6.213 | 5.6599 | 5.2814
|  | ABOYNE | FB |  |  |  |  | 8.0615 | 8.0655 | 8.036 | 7.84 | 7.7972 | 7.6145 | 7.3727 | 7.2288 | 7.1482 | 7.0574 | 6.486 | 5.8849 | 5.6013 | 9.6655 | 9.6625 | 9.6288 | 9.5186 | 9.4921 | 9.3819 | 9.2288 | 9.1737 | 9.1043 | 9.0298 | 8.6492 | 8.1043 | 7.5911 | 8.9661 | 8.9885 | 8.9701 | 8.8905 | 8.8671 | 8.7252 | 8.5354 | 8.4161 | 8.3446 | 8.2691 | 7.7997 | 7.2334 | 7.0661
| GRUDIE BRIDGE | ACHILTIBUIE | MINIMUM HEADROOM | NC 01618 09557 | YES | NO | 0.304 | -0.096927 | -0.10305 | -0.11019 | -0.12244 | -0.14182 | -0.17856 | -0.20203 | -0.22856 | -0.26325 | -0.27244 | -0.33672 | -0.38468 | -0.42142 | -0.067335 | -0.070396 | -0.075498 | -0.0806 | -0.087743 | -0.10407 | -0.11631 | -0.1306 | -0.14693 | -0.16325 | -0.19897 | -0.19999 | -0.19284 | 0.038788 | 0.032665 | 0.022461 | 0.0040939 | -0.018355 | -0.053049 | -0.072437 | -0.099988 | -0.1306 | -0.16223 | -0.22754 | -0.2357 | -0.24387
|  | ACHILTIBUIE | EE |  |  |  |  | -0.096927 | -0.10305 | -0.10917 | -0.11938 | -0.13876 | -0.17652 | -0.19591 | -0.22346 | -0.25815 | -0.26733 | -0.33672 | -0.38468 | -0.41529 | -0.067335 | -0.070396 | -0.074478 | -0.0806 | -0.087743 | -0.10305 | -0.11631 | -0.12958 | -0.14693 | -0.16325 | -0.19387 | -0.19489 | -0.18468 | 0.038788 | 0.032665 | 0.023482 | 0.0051143 | -0.017335 | -0.053049 | -0.071416 | -0.098967 | -0.12958 | -0.16223 | -0.22448 | -0.22958 | -0.2306
|  | ACHILTIBUIE | HT |  |  |  |  | -0.096927 | -0.10305 | -0.10917 | -0.11938 | -0.13876 | -0.16938 | -0.19284 | -0.22142 | -0.25713 | -0.26427 | -0.32142 | -0.37754 | -0.42142 | -0.067335 | -0.069376 | -0.074478 | -0.0806 | -0.087743 | -0.10305 | -0.11631 | -0.1306 | -0.14693 | -0.16325 | -0.19897 | -0.19999 | -0.19182 | 0.038788 | 0.032665 | 0.023482 | 0.0051143 | -0.017335 | -0.049988 | -0.070396 | -0.097947 | -0.12856 | -0.16121 | -0.22754 | -0.2357 | -0.24387
|  | ACHILTIBUIE | HE |  |  |  |  | -0.096927 | -0.10305 | -0.11019 | -0.12244 | -0.14182 | -0.17856 | -0.20203 | -0.22856 | -0.26325 | -0.27244 | -0.32142 | -0.38162 | -0.4204 | -0.067335 | -0.069376 | -0.075498 | -0.0806 | -0.087743 | -0.10407 | -0.11631 | -0.1306 | -0.14693 | -0.16325 | -0.1908 | -0.19182 | -0.19284 | 0.038788 | 0.032665 | 0.022461 | 0.0040939 | -0.018355 | -0.053049 | -0.072437 | -0.099988 | -0.1306 | -0.16223 | -0.21938 | -0.22856 | -0.23774
|  | ACHILTIBUIE | FB |  |  |  |  | -0.074478 | -0.07958 | -0.0806 | -0.08162 | -0.087743 | -0.092845 | -0.10815 | -0.11529 | -0.13264 | -0.13366 | -0.19591 | -0.24999 | -0.26836 | -0.05611 | -0.057131 | -0.058151 | -0.060192 | -0.065294 | -0.067335 | -0.075498 | -0.07958 | -0.090804 | -0.093865 | -0.12856 | -0.16223 | -0.17142 | 0.057155 | 0.054094 | 0.047971 | 0.039808 | 0.028584 | 0.0194 | 0.0030735 | -0.008151 | -0.027539 | -0.02958 | -0.10101 | -0.16325 | -0.17142
| BEAULY | AIGAS | MINIMUM HEADROOM | NH 45362 40529 | YES | NO | 0.023 | 0.48184 | 0.48082 | 0.47571 | 0.46755 | 0.46245 | 0.45122 | 0.44102 | 0.42878 | 0.42265 | 0.40939 | 0.3849 | 0.37367 | 0.36449 | 0.4848 | 0.47969 | 0.47663 | 0.47051 | 0.46745 | 0.46031 | 0.45214 | 0.43684 | 0.43582 | 0.42153 | 0.39296 | 0.39398 | 0.40214 | 0.48281 | 0.47668 | 0.47464 | 0.46648 | 0.46036 | 0.45117 | 0.44301 | 0.42872 | 0.42668 | 0.41648 | 0.39505 | 0.38689 | 0.38077
|  | AIGAS | EE |  |  |  |  | 0.48184 | 0.48082 | 0.47673 | 0.46959 | 0.46347 | 0.45327 | 0.44408 | 0.43184 | 0.42571 | 0.41245 | 0.38694 | 0.37367 | 0.36755 | 0.4848 | 0.47969 | 0.47663 | 0.47051 | 0.46745 | 0.46031 | 0.45316 | 0.43684 | 0.43582 | 0.42153 | 0.39806 | 0.4001 | 0.41031 | 0.48281 | 0.47668 | 0.47464 | 0.46852 | 0.46138 | 0.45219 | 0.44505 | 0.43077 | 0.42872 | 0.4175 | 0.39505 | 0.38791 | 0.38485
|  | AIGAS | HT |  |  |  |  | 0.48184 | 0.48082 | 0.47571 | 0.46857 | 0.46245 | 0.45429 | 0.4451 | 0.43184 | 0.42571 | 0.41347 | 0.3849 | 0.37673 | 0.36449 | 0.4848 | 0.47969 | 0.47663 | 0.47051 | 0.46745 | 0.46031 | 0.45214 | 0.43684 | 0.43582 | 0.42153 | 0.39296 | 0.39398 | 0.40214 | 0.48281 | 0.47668 | 0.47464 | 0.4675 | 0.46138 | 0.45423 | 0.44607 | 0.43077 | 0.42872 | 0.41852 | 0.39505 | 0.38689 | 0.38179
|  | AIGAS | HE |  |  |  |  | 0.48184 | 0.48082 | 0.47571 | 0.46755 | 0.46245 | 0.45122 | 0.44102 | 0.42878 | 0.42265 | 0.40939 | 0.39 | 0.37673 | 0.36551 | 0.4848 | 0.47969 | 0.47663 | 0.47051 | 0.46745 | 0.46031 | 0.45214 | 0.43684 | 0.43582 | 0.42153 | 0.39908 | 0.39908 | 0.40214 | 0.48281 | 0.47668 | 0.47464 | 0.46648 | 0.46036 | 0.45117 | 0.44301 | 0.42872 | 0.42668 | 0.41648 | 0.39811 | 0.38791 | 0.38077
|  | AIGAS | FB |  |  |  |  | 0.49 | 0.49102 | 0.48694 | 0.48796 | 0.4849 | 0.48184 | 0.48082 | 0.47163 | 0.46959 | 0.46653 | 0.44816 | 0.42571 | 0.41755 | 0.49296 | 0.49194 | 0.48582 | 0.48276 | 0.47969 | 0.47765 | 0.47459 | 0.46643 | 0.46337 | 0.46031 | 0.4399 | 0.41847 | 0.41133 | 0.49199 | 0.49199 | 0.48689 | 0.48587 | 0.48281 | 0.4777 | 0.4777 | 0.4675 | 0.46546 | 0.46138 | 0.44301 | 0.4226 | 0.42158
| ARDMORE | AIRD | MINIMUM HEADROOM | NF 79163 53853 | NO | YES | 0.693 | 4.4939 | 4.5051 | 4.5031 | 4.4745 | 4.3704 | 4.302 | 4.2327 | 4.1714 | 4.1 | 4.0714 | 3.9306 | 3.7724 | 3.6133 | 4.9845 | 4.9978 | 4.9998 | 4.9957 | 4.8937 | 4.8743 | 4.8437 | 4.8253 | 4.7967 | 4.8008 | 4.7396 | 4.7345 | 4.7427 | 4.7753 | 4.7896 | 4.7916 | 4.7743 | 4.6661 | 4.6222 | 4.5876 | 4.5467 | 4.4967 | 4.4845 | 4.3529 | 4.2467 | 4.159
|  | AIRD | EE |  |  |  |  | 4.4959 | 4.5051 | 4.5031 | 4.4765 | 4.4571 | 4.3031 | 4.2347 | 4.1714 | 4.102 | 4.0765 | 3.9306 | 3.7724 | 3.6184 | 4.9845 | 4.9978 | 4.9998 | 4.9957 | 4.9794 | 4.8743 | 4.8447 | 4.8253 | 4.7978 | 4.8018 | 4.7518 | 4.7386 | 4.758 | 4.7753 | 4.7896 | 4.7916 | 4.7753 | 4.7478 | 4.6376 | 4.5906 | 4.5467 | 4.4967 | 4.4845 | 4.3529 | 4.2478 | 4.1631
|  | AIRD | HT |  |  |  |  | 4.4959 | 4.5051 | 4.5051 | 4.4776 | 4.3704 | 4.3122 | 4.2439 | 4.1857 | 4.1163 | 4.0929 | 3.9867 | 3.8184 | 3.6133 | 4.9845 | 4.9988 | 5.0008 | 4.9967 | 4.8937 | 4.8773 | 4.8467 | 4.8304 | 4.8008 | 4.8039 | 4.7396 | 4.7365 | 4.7478 | 4.7763 | 4.7906 | 4.7937 | 4.7763 | 4.6661 | 4.6222 | 4.5947 | 4.5559 | 4.5059 | 4.4957 | 4.3814 | 4.2692 | 4.159
|  | AIRD | HE |  |  |  |  | 4.4939 | 4.5051 | 4.5051 | 4.4745 | 4.4541 | 4.302 | 4.2327 | 4.1714 | 4.1 | 4.0714 | 3.9837 | 3.7939 | 3.652 | 4.9845 | 4.9978 | 5.0008 | 4.9957 | 4.9804 | 4.8743 | 4.8437 | 4.8263 | 4.7967 | 4.8008 | 4.7498 | 4.7345 | 4.7427 | 4.7753 | 4.7906 | 4.7927 | 4.7743 | 4.7467 | 4.6365 | 4.5876 | 4.5467 | 4.4967 | 4.4845 | 4.3855 | 4.2467 | 4.1671
|  | AIRD | FB |  |  |  |  | 4.5214 | 4.5449 | 4.5633 | 4.5684 | 4.5714 | 4.5714 | 4.4755 | 4.4724 | 4.4592 | 4.452 | 4.3969 | 4.2959 | 4.2592 | 5.0029 | 5.0212 | 5.0335 | 5.0386 | 5.0437 | 5.0447 | 4.9508 | 4.9467 | 4.9365 | 4.9284 | 4.8967 | 4.8263 | 4.8018 | 4.7998 | 4.8222 | 4.8406 | 4.8467 | 4.8539 | 4.8549 | 4.7631 | 4.761 | 4.7488 | 4.7427 | 4.6896 | 4.5978 | 4.5773
| PORT ANN | AIRIGH-NA-BRODAIG | MINIMUM HEADROOM | NR 85849 74792 | YES | YES | 0 | 0.34517 | 0.33292 | 0.33292 | 0.33088 | 0.3268 | 0.32272 | 0.31966 | 0.31354 | 0.31252 | 0.30946 | 0.30231 | 0.29415 | 0.29109 | 0.32498 | 0.31376 | 0.31274 | 0.31376 | 0.30866 | 0.30764 | 0.30457 | 0.30049 | 0.29947 | 0.29743 | 0.28927 | 0.28621 | 0.28723 | 0.33814 | 0.32691 | 0.32589 | 0.32487 | 0.31977 | 0.31773 | 0.31467 | 0.31059 | 0.30855 | 0.30548 | 0.30038 | 0.29324 | 0.29426
|  | AIRIGH-NA-BRODAIG | EE |  |  |  |  | 0.34517 | 0.33394 | 0.33292 | 0.33088 | 0.32782 | 0.32272 | 0.31966 | 0.31354 | 0.31252 | 0.31048 | 0.30231 | 0.29415 | 0.29211 | 0.32498 | 0.31376 | 0.31274 | 0.31376 | 0.3107 | 0.30764 | 0.30457 | 0.30049 | 0.29947 | 0.29743 | 0.29029 | 0.28723 | 0.29131 | 0.33814 | 0.32691 | 0.32589 | 0.32487 | 0.32181 | 0.31875 | 0.31467 | 0.31059 | 0.30855 | 0.30548 | 0.30038 | 0.29528 | 0.2963
|  | AIRIGH-NA-BRODAIG | HT |  |  |  |  | 0.34517 | 0.33394 | 0.33292 | 0.3319 | 0.3268 | 0.32272 | 0.31966 | 0.31558 | 0.31354 | 0.31048 | 0.30231 | 0.29517 | 0.29313 | 0.32498 | 0.31376 | 0.31274 | 0.31478 | 0.30866 | 0.30764 | 0.30457 | 0.30151 | 0.29947 | 0.29743 | 0.28927 | 0.28621 | 0.28927 | 0.33814 | 0.32691 | 0.32589 | 0.32589 | 0.31977 | 0.31773 | 0.31467 | 0.31161 | 0.30957 | 0.3065 | 0.30038 | 0.29324 | 0.29426
|  | AIRIGH-NA-BRODAIG | HE |  |  |  |  | 0.34517 | 0.33292 | 0.33292 | 0.33088 | 0.32782 | 0.32272 | 0.31966 | 0.31354 | 0.31252 | 0.30946 | 0.30231 | 0.29517 | 0.29109 | 0.32498 | 0.31376 | 0.31274 | 0.31376 | 0.30968 | 0.30764 | 0.30457 | 0.30049 | 0.29947 | 0.29743 | 0.29029 | 0.28723 | 0.28927 | 0.33814 | 0.32691 | 0.32589 | 0.32487 | 0.32079 | 0.31773 | 0.31467 | 0.31059 | 0.30855 | 0.30548 | 0.30038 | 0.2963 | 0.29426
|  | AIRIGH-NA-BRODAIG | FB |  |  |  |  | 0.34517 | 0.34619 | 0.33803 | 0.34007 | 0.33599 | 0.33803 | 0.33497 | 0.33292 | 0.32578 | 0.3268 | 0.31966 | 0.30843 | 0.30639 | 0.32498 | 0.326 | 0.3158 | 0.31886 | 0.3158 | 0.31682 | 0.31274 | 0.3107 | 0.30355 | 0.30559 | 0.29845 | 0.28927 | 0.28723 | 0.33814 | 0.33916 | 0.32997 | 0.33201 | 0.33099 | 0.33099 | 0.32793 | 0.32589 | 0.31773 | 0.31977 | 0.31467 | 0.30548 | 0.30344
| COUPAR ANGUS | ALYTH | MINIMUM HEADROOM | NO 23579 48311 | NO | NO | 1.219 | 3.0353 | 2.8363 | 2.7251 | 2.5802 | 2.37 | 2.1088 | 1.8424 | 1.5659 | 1.3149 | 1.1363 | 0.24245 | -0.25755 | -0.52388 | 3.9322 | 3.7169 | 3.6027 | 3.5037 | 3.1904 | 2.8812 | 2.622 | 2.3312 | 2.0894 | 1.8986 | 1.0598 | 0.69143 | 0.48735 | 3.4843 | 3.272 | 3.1741 | 3.0567 | 2.7873 | 2.4761 | 2.2057 | 1.9098 | 1.6557 | 1.4669 | 0.58327 | 0.12204 | -0.11469
|  | ALYTH | EE |  |  |  |  | 3.0424 | 2.8404 | 2.7506 | 2.6404 | 2.4292 | 2.1506 | 1.9149 | 1.6078 | 1.368 | 1.2322 | 0.24245 | -0.25755 | -0.52388 | 3.9384 | 3.72 | 3.6353 | 3.5394 | 3.2261 | 2.9098 | 2.6649 | 2.3557 | 2.1057 | 1.9598 | 1.071 | 0.69143 | 0.48735 | 3.4894 | 3.2751 | 3.1924 | 3.0965 | 2.8312 | 2.5139 | 2.2639 | 1.9506 | 1.6904 | 1.5455 | 0.58327 | 0.12204 | -0.11469
|  | ALYTH | HT |  |  |  |  | 3.0353 | 2.8363 | 2.7251 | 2.5802 | 2.37 | 2.1343 | 1.87 | 1.5792 | 1.3516 | 1.1363 | 0.28633 | -0.15857 | -0.39531 | 3.9322 | 3.7169 | 3.621 | 3.5037 | 3.1904 | 2.9373 | 2.67 | 2.3761 | 2.1282 | 1.8986 | 1.0598 | 0.73633 | 0.62102 | 3.4843 | 3.272 | 3.1741 | 3.0567 | 2.7873 | 2.521 | 2.2455 | 1.9465 | 1.6965 | 1.4669 | 0.61694 | 0.21286 | 0.010816
|  | ALYTH | HE |  |  |  |  | 3.0363 | 2.8394 | 2.7424 | 2.6169 | 2.4057 | 2.1088 | 1.8424 | 1.5659 | 1.3149 | 1.1843 | 0.5251 | 0.36388 | 0.25571 | 3.9322 | 3.719 | 3.6312 | 3.5282 | 3.2149 | 2.8812 | 2.622 | 2.3312 | 2.0894 | 1.9516 | 1.3292 | 1.2792 | 1.2261 | 3.4843 | 3.2731 | 3.1853 | 3.0812 | 2.8149 | 2.4761 | 2.2057 | 1.9098 | 1.6557 | 1.5159 | 0.86388 | 0.73327 | 0.64959
|  | ALYTH | FB |  |  |  |  | 3.1231 | 3.068 | 2.8241 | 2.7598 | 2.6996 | 2.5853 | 2.4812 | 2.372 | 2.2067 | 2.1118 | 1.6414 | 0.97408 | 0.46898 | 3.9945 | 3.9455 | 3.6027 | 3.5445 | 3.472 | 3.3486 | 3.2363 | 3.1333 | 2.9445 | 2.7955 | 2.3047 | 1.6118 | 1.0057 | 3.5659 | 3.5149 | 3.2312 | 3.172 | 3.1047 | 2.9873 | 2.8802 | 2.7812 | 2.5914 | 2.4578 | 1.9649 | 1.2435 | 0.7598
| FORT WILLIAM | ANNAT | MINIMUM HEADROOM | NN 08452 76751 | YES | NO | 0.224 | 3.8724 | 3.8704 | 3.8602 | 3.8173 | 3.7541 | 2.5653 | 1.2194 | -0.15408 | -0.87959 | -1.1296 | -1.8163 | -2.1255 | -2.3429 | 4.7041 | 4.7071 | 4.7102 | 4.6867 | 4.6684 | 3.501 | 2.1133 | 0.66633 | -0.073469 | -0.26735 | -0.80714 | -0.81429 | -0.88878 | 4.3571 | 4.3541 | 4.3551 | 4.3214 | 4.2959 | 3.151 | 1.8347 | 0.48571 | -0.20612 | -0.41224 | -0.9898 | -1.1245 | -1.2092
|  | ANNAT | EE |  |  |  |  | 3.8745 | 3.8704 | 3.8602 | 3.8173 | 3.7551 | 3.6153 | 3.5235 | 2.3969 | 1.0582 | -0.34796 | -1.7847 | -2.1255 | -2.3102 | 4.7041 | 4.7071 | 4.7102 | 4.6867 | 4.6694 | 4.6408 | 4.5847 | 3.499 | 2.102 | 0.60714 | -0.68163 | -0.8102 | -0.83571 | 4.3571 | 4.3541 | 4.3551 | 4.3214 | 4.2959 | 4.2 | 4.1286 | 3.0827 | 1.7653 | 0.37959 | -0.91735 | -1.1245 | -1.2092
|  | ANNAT | HT |  |  |  |  | 3.8724 | 3.8724 | 3.8643 | 3.8184 | 3.7541 | 2.5653 | 1.2194 | -0.15408 | -0.87959 | -1.1296 | -1.8163 | -2.0949 | -2.3429 | 4.7041 | 4.7071 | 4.7112 | 4.6867 | 4.6684 | 3.501 | 2.1133 | 0.66633 | -0.073469 | -0.26735 | -0.80714 | -0.81429 | -0.80306 | 4.3571 | 4.3551 | 4.3561 | 4.3214 | 4.2959 | 3.151 | 1.8347 | 0.48571 | -0.20612 | -0.41224 | -0.9898 | -1.1071 | -1.198
|  | ANNAT | HE |  |  |  |  | 3.8724 | 3.8724 | 3.8643 | 3.8173 | 3.7551 | 3.6265 | 3.5061 | 2.248 | 0.75612 | -0.81939 | -1.7408 | -2.1 | -2.2663 | 4.7041 | 4.7071 | 4.7112 | 4.6867 | 4.6684 | 4.6429 | 4.5837 | 3.3663 | 1.8041 | 0.13265 | -0.67755 | -0.80816 | -0.83673 | 4.3571 | 4.3551 | 4.3561 | 4.3214 | 4.2969 | 4.2061 | 4.1184 | 2.9439 | 1.4776 | -0.071429 | -0.89694 | -1.1143 | -1.1949
|  | ANNAT | FB |  |  |  |  | 3.9102 | 3.9316 | 3.9459 | 3.9408 | 3.9255 | 3.9041 | 3.9112 | 3.8867 | 3.0184 | 2.0235 | -0.88265 | -1.2776 | -1.3398 | 4.7245 | 4.7408 | 4.75 | 4.7582 | 4.7561 | 4.7337 | 4.7214 | 4.6898 | 3.8 | 2.7143 | -0.39592 | -0.81224 | -0.88878 | 4.3827 | 4.3959 | 4.4092 | 4.4102 | 4.4041 | 4.3888 | 4.3816 | 4.3643 | 3.4806 | 2.4765 | -0.39898 | -0.79388 | -0.80918
| KILLIN | ARDCHYLE | MINIMUM HEADROOM | NN 52734 29223 | YES | YES | 0 | 0.11902 | 0.11902 | 0.11902 | 0.11902 | 0.10576 | 0.10576 | 0.10473 | 0.10473 | 0.10269 | 0.10269 | 0.09351 | 0.09351 | 0.09249 | 0.109 | 0.109 | 0.109 | 0.109 | 0.095735 | 0.095735 | 0.094714 | 0.094714 | 0.092673 | 0.092673 | 0.085531 | 0.087571 | 0.087571 | 0.1135 | 0.1135 | 0.1135 | 0.1135 | 0.10023 | 0.10023 | 0.099214 | 0.099214 | 0.096153 | 0.096153 | 0.08799 | 0.08799 | 0.08799
|  | ARDCHYLE | EE |  |  |  |  | 0.11902 | 0.11902 | 0.11902 | 0.11902 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10269 | 0.10269 | 0.09351 | 0.095551 | 0.09351 | 0.109 | 0.109 | 0.109 | 0.109 | 0.095735 | 0.095735 | 0.096755 | 0.096755 | 0.092673 | 0.092673 | 0.086551 | 0.089612 | 0.089612 | 0.1135 | 0.1135 | 0.1135 | 0.1135 | 0.10023 | 0.10023 | 0.10126 | 0.10126 | 0.096153 | 0.096153 | 0.08799 | 0.090031 | 0.08901
|  | ARDCHYLE | HT |  |  |  |  | 0.11902 | 0.11902 | 0.11902 | 0.11902 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10269 | 0.10269 | 0.09351 | 0.09351 | 0.09249 | 0.109 | 0.109 | 0.109 | 0.109 | 0.095735 | 0.095735 | 0.096755 | 0.096755 | 0.092673 | 0.092673 | 0.085531 | 0.087571 | 0.087571 | 0.1135 | 0.1135 | 0.1135 | 0.1135 | 0.10023 | 0.10023 | 0.10126 | 0.10126 | 0.097173 | 0.096153 | 0.08799 | 0.08799 | 0.08799
|  | ARDCHYLE | HE |  |  |  |  | 0.11902 | 0.11902 | 0.11902 | 0.11902 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10269 | 0.10269 | 0.094531 | 0.09351 | 0.094531 | 0.109 | 0.109 | 0.109 | 0.109 | 0.095735 | 0.095735 | 0.096755 | 0.096755 | 0.092673 | 0.092673 | 0.086551 | 0.087571 | 0.089612 | 0.1135 | 0.1135 | 0.1135 | 0.1135 | 0.10023 | 0.10023 | 0.10126 | 0.10126 | 0.096153 | 0.096153 | 0.08901 | 0.08799 | 0.090031
|  | ARDCHYLE | FB |  |  |  |  | 0.11902 | 0.11902 | 0.11902 | 0.11902 | 0.12004 | 0.12004 | 0.10473 | 0.10473 | 0.10576 | 0.10984 | 0.10678 | 0.10167 | 0.10167 | 0.109 | 0.109 | 0.109 | 0.109 | 0.109 | 0.11002 | 0.094714 | 0.094714 | 0.094714 | 0.098796 | 0.095735 | 0.091653 | 0.091653 | 0.1135 | 0.1135 | 0.1135 | 0.1135 | 0.1135 | 0.11452 | 0.099214 | 0.099214 | 0.099214 | 0.1033 | 0.10126 | 0.096153 | 0.095133
| NAIRN | ARDERSIER | MINIMUM HEADROOM | NH 80475 55905 | NO | YES | 0.315 | 4.2214 | 4.2245 | 4.2327 | 4.1888 | 4.1643 | 3.9245 | 3.5296 | 2.9449 | 2.1673 | 1.6265 | 0.76224 | 0.53163 | 0.3449 | 5.2357 | 5.2255 | 5.2276 | 5.2031 | 5.1878 | 4.9429 | 4.5214 | 3.8857 | 3.1122 | 2.5867 | 1.9245 | 1.9122 | 1.9061 | 4.8347 | 4.8224 | 4.8245 | 4.7857 | 4.7469 | 4.4724 | 4.0837 | 3.4969 | 2.7224 | 2.1929 | 1.4265 | 1.3102 | 1.2245
|  | ARDERSIER | EE |  |  |  |  | 4.2214 | 4.2245 | 4.2327 | 4.1949 | 4.1643 | 4.0847 | 4.0276 | 3.7939 | 3.3367 | 2.749 | 0.76224 | 0.53163 | 0.36633 | 5.2367 | 5.2255 | 5.2276 | 5.2031 | 5.1888 | 5.1367 | 5.101 | 4.8918 | 4.4622 | 3.8092 | 1.9245 | 1.9122 | 1.9153 | 4.8347 | 4.8224 | 4.8245 | 4.7908 | 4.7571 | 4.6745 | 4.6459 | 4.4041 | 3.9582 | 3.3418 | 1.4265 | 1.3102 | 1.2398
|  | ARDERSIER | HT |  |  |  |  | 4.2224 | 4.2255 | 4.2357 | 4.1959 | 4.1827 | 3.9245 | 3.5296 | 2.9449 | 2.1673 | 1.6265 | 0.83878 | 0.57653 | 0.3449 | 5.2357 | 5.2255 | 5.2286 | 5.2041 | 5.1888 | 4.9429 | 4.5214 | 3.8857 | 3.1122 | 2.5867 | 1.9276 | 1.9224 | 1.9357 | 4.8347 | 4.8235 | 4.8265 | 4.7918 | 4.7561 | 4.4724 | 4.0837 | 3.4969 | 2.7224 | 2.1929 | 1.4602 | 1.3316 | 1.2245
|  | ARDERSIER | HE |  |  |  |  | 4.2224 | 4.2255 | 4.2357 | 4.1888 | 4.1745 | 4.0827 | 4.0143 | 3.7531 | 3.2398 | 2.5429 | 0.81429 | 0.5602 | 0.41224 | 5.2357 | 5.2255 | 5.2286 | 5.2031 | 5.1878 | 5.1367 | 5.1 | 4.8745 | 4.3806 | 3.6092 | 1.9296 | 1.9122 | 1.9184 | 4.8347 | 4.8235 | 4.8265 | 4.7857 | 4.7469 | 4.6724 | 4.6378 | 4.3673 | 3.8673 | 3.1408 | 1.4541 | 1.3255 | 1.2602
|  | ARDERSIER | FB |  |  |  |  | 4.2673 | 4.2939 | 4.3092 | 4.3133 | 4.3122 | 4.2878 | 4.2765 | 4.2439 | 4.0643 | 3.8 | 1.3827 | 1.1306 | 1.0847 | 5.2704 | 5.2786 | 5.2796 | 5.2816 | 5.2816 | 5.2551 | 5.2418 | 5.2102 | 5.0235 | 4.7143 | 2.2061 | 1.9714 | 1.9061 | 4.8694 | 4.8796 | 4.8837 | 4.8847 | 4.8745 | 4.8541 | 4.8388 | 4.8133 | 4.5969 | 4.3112 | 1.9153 | 1.6531 | 1.6245
| FORT AUGUSTUS | ARDOCHY | MINIMUM HEADROOM | NH 47714 12561 | YES | YES | 0 | 0.118 | 0.11902 | 0.10576 | 0.10678 | 0.10576 | 0.098612 | 0.095551 | 0.094531 | 0.087388 | 0.084327 | 0.080245 | 0.078204 | 0.078204 | 0.109 | 0.109 | 0.096755 | 0.097776 | 0.096755 | 0.091653 | 0.089612 | 0.089612 | 0.08349 | 0.081449 | 0.075327 | 0.075327 | 0.075327 | 0.1135 | 0.11452 | 0.10126 | 0.10228 | 0.10228 | 0.095133 | 0.092071 | 0.091051 | 0.082888 | 0.080847 | 0.076765 | 0.075745 | 0.075745
|  | ARDOCHY | EE |  |  |  |  | 0.118 | 0.11902 | 0.10576 | 0.10678 | 0.10576 | 0.098612 | 0.096571 | 0.094531 | 0.088408 | 0.085347 | 0.080245 | 0.078204 | 0.078204 | 0.109 | 0.109 | 0.096755 | 0.097776 | 0.096755 | 0.091653 | 0.089612 | 0.089612 | 0.08451 | 0.081449 | 0.076347 | 0.075327 | 0.076347 | 0.1135 | 0.11452 | 0.10126 | 0.10228 | 0.10228 | 0.095133 | 0.092071 | 0.091051 | 0.084929 | 0.082888 | 0.076765 | 0.075745 | 0.075745
|  | ARDOCHY | HT |  |  |  |  | 0.118 | 0.11902 | 0.10576 | 0.10678 | 0.10576 | 0.10167 | 0.096571 | 0.095551 | 0.087388 | 0.084327 | 0.080245 | 0.081265 | 0.079224 | 0.109 | 0.109 | 0.096755 | 0.097776 | 0.096755 | 0.092673 | 0.089612 | 0.089612 | 0.08349 | 0.081449 | 0.075327 | 0.078388 | 0.077367 | 0.1135 | 0.11452 | 0.10126 | 0.10228 | 0.10228 | 0.097173 | 0.093092 | 0.091051 | 0.083908 | 0.080847 | 0.076765 | 0.078806 | 0.076765
|  | ARDOCHY | HE |  |  |  |  | 0.118 | 0.11902 | 0.10576 | 0.10678 | 0.10576 | 0.098612 | 0.095551 | 0.094531 | 0.087388 | 0.085347 | 0.081265 | 0.079224 | 0.081265 | 0.109 | 0.109 | 0.096755 | 0.097776 | 0.096755 | 0.091653 | 0.089612 | 0.089612 | 0.08349 | 0.081449 | 0.076347 | 0.076347 | 0.078388 | 0.1135 | 0.11452 | 0.10126 | 0.10228 | 0.10228 | 0.095133 | 0.092071 | 0.091051 | 0.082888 | 0.082888 | 0.077786 | 0.076765 | 0.077786
|  | ARDOCHY | FB |  |  |  |  | 0.118 | 0.11902 | 0.10882 | 0.10882 | 0.1078 | 0.10473 | 0.10473 | 0.10371 | 0.10167 | 0.10167 | 0.09351 | 0.085347 | 0.083306 | 0.109 | 0.109 | 0.099816 | 0.098796 | 0.097776 | 0.094714 | 0.094714 | 0.094714 | 0.092673 | 0.092673 | 0.08451 | 0.077367 | 0.075327 | 0.1135 | 0.11452 | 0.10432 | 0.1033 | 0.1033 | 0.10023 | 0.10023 | 0.099214 | 0.097173 | 0.097173 | 0.090031 | 0.079827 | 0.078806
| FORT WILLIAM | ARISAIG | MINIMUM HEADROOM | NM 66564 86619 | YES | NO | 0.128 | 2.2735 | 2.2714 | 2.2612 | 2.2469 | 2.2265 | 2.1898 | 2.1673 | 2.1378 | 2.102 | 2.0857 | 2.0102 | 1.9633 | 1.9214 | 2.0403 | 2.0372 | 2.0311 | 2.0281 | 2.0209 | 2.0107 | 1.9913 | 1.9668 | 1.9423 | 1.9362 | 1.8781 | 1.8852 | 1.8342 | 2.161 | 2.1569 | 2.1487 | 2.1375 | 2.1242 | 2.0967 | 2.0712 | 2.0365 | 2.0089 | 1.9946 | 1.9518 | 1.9263 | 1.9099
|  | ARISAIG | EE |  |  |  |  | 2.2735 | 2.2714 | 2.2633 | 2.249 | 2.2316 | 2.1898 | 2.1806 | 2.1388 | 2.1041 | 2.0898 | 2.0102 | 1.9633 | 1.9265 | 2.0403 | 2.0372 | 2.0321 | 2.0281 | 2.0219 | 2.0107 | 1.9944 | 1.9679 | 1.9434 | 1.9393 | 1.8883 | 1.8893 | 1.8913 | 2.161 | 2.1569 | 2.1508 | 2.1385 | 2.1273 | 2.0967 | 2.0742 | 2.0375 | 2.0099 | 1.9987 | 1.9528 | 1.9283 | 1.9263
|  | ARISAIG | HT |  |  |  |  | 2.2745 | 2.2714 | 2.2612 | 2.249 | 2.2306 | 2.2041 | 2.1673 | 2.1449 | 2.1071 | 2.0949 | 2.0184 | 1.9724 | 1.9214 | 2.0403 | 2.0383 | 2.0311 | 2.0281 | 2.0219 | 2.0128 | 1.9923 | 1.9679 | 1.9434 | 1.9362 | 1.8781 | 1.8852 | 1.8985 | 2.161 | 2.1569 | 2.1487 | 2.1385 | 2.1273 | 2.1069 | 2.0793 | 2.0426 | 2.013 | 2.0018 | 1.9518 | 1.9304 | 1.9181
|  | ARISAIG | HE |  |  |  |  | 2.2745 | 2.2714 | 2.2612 | 2.2469 | 2.2265 | 2.1929 | 2.1765 | 2.1378 | 2.102 | 2.0857 | 2.0245 | 1.9633 | 1.9327 | 2.0403 | 2.0383 | 2.0311 | 2.0281 | 2.0209 | 2.0107 | 1.9913 | 1.9668 | 1.9423 | 1.9372 | 1.8903 | 1.8893 | 1.877 | 2.161 | 2.1569 | 2.1487 | 2.1375 | 2.1242 | 2.0987 | 2.0712 | 2.0365 | 2.0089 | 1.9946 | 1.961 | 1.9263 | 1.9099
|  | ARISAIG | FB |  |  |  |  | 2.2969 | 2.299 | 2.3041 | 2.301 | 2.301 | 2.2867 | 2.2816 | 2.2673 | 2.2653 | 2.251 | 2.2031 | 2.1367 | 2.1153 | 2.0577 | 2.0546 | 2.0577 | 2.0566 | 2.0587 | 2.0464 | 2.0403 | 2.023 | 2.023 | 2.0046 | 1.9617 | 1.8852 | 1.8342 | 2.1814 | 2.1804 | 2.1844 | 2.1824 | 2.1844 | 2.1712 | 2.1661 | 2.1508 | 2.1508 | 2.1375 | 2.0946 | 2.0263 | 2.0161
| ELGIN | ASHGROVE | MINIMUM HEADROOM | NJ 22458 62130 | YES | YES | 4.628 | 0.61761 | 26.0666 | 25.3472 | 24.8809 | 24.2686 | 23.7115 | 22.737 | 22.1492 | 21.3309 | 19.8135 | 12.9217 | 10.787 | 9.8584 | 1.6278 | 26.7329 | 26.1707 | 25.9003 | 25.3972 | 25.2401 | 24.5819 | 24.3686 | 24.0258 | 22.8615 | 17.786 | 17.3829 | 16.7227 | 1.2462 | 26.9115 | 26.3003 | 25.9503 | 25.4074 | 25.0003 | 24.1605 | 23.7054 | 23.1299 | 21.7901 | 15.9635 | 14.3982 | 13.7237
|  | ASHGROVE | EE |  |  |  |  | 0.66863 | 26.0666 | 25.3472 | 24.8809 | 24.2686 | 23.7115 | 22.737 | 22.1492 | 21.5421 | 20.9554 | 13.7472 | 10.787 | 9.8584 | 1.6778 | 26.7329 | 26.1707 | 25.9003 | 25.4043 | 25.2401 | 24.5819 | 24.3686 | 24.1268 | 23.8064 | 18.4809 | 17.3829 | 17.0594 | 1.2962 | 26.9115 | 26.3003 | 25.9503 | 25.4074 | 25.0003 | 24.1605 | 23.7054 | 23.2523 | 22.7839 | 16.5962 | 14.3982 | 13.7237
|  | ASHGROVE | HT |  |  |  |  | 0.64006 | 26.0758 | 25.3635 | 24.9084 | 24.285 | 23.8064 | 23.1737 | 22.4196 | 21.3309 | 19.8135 | 12.9217 | 11.1288 | 10.1074 | 1.6492 | 26.7421 | 26.1717 | 25.9003 | 25.3972 | 25.2594 | 25.0145 | 24.6666 | 24.0258 | 22.8615 | 17.786 | 17.5503 | 17.4452 | 1.2676 | 26.9196 | 26.3105 | 25.9656 | 25.4176 | 25.0543 | 24.5707 | 23.9941 | 23.1299 | 21.7901 | 15.9635 | 14.7013 | 13.9921
|  | ASHGROVE | HE |  |  |  |  | 0.61761 | 26.0676 | 25.3543 | 24.9135 | 24.3115 | 23.8584 | 22.8911 | 22.3094 | 21.6594 | 21.088 | 14.2329 | 11.4829 | 10.7605 | 1.6278 | 26.7329 | 26.1717 | 25.9033 | 25.4043 | 25.2768 | 24.6105 | 24.3992 | 24.1513 | 23.8492 | 18.5656 | 17.6431 | 17.3533 | 1.2462 | 26.9115 | 26.3043 | 25.9686 | 25.4339 | 25.0982 | 24.2605 | 23.8186 | 23.3319 | 22.886 | 16.9809 | 14.9799 | 14.4543
|  | ASHGROVE | FB |  |  |  |  | 0.84006 | 26.386 | 25.5972 | 25.3013 | 25.0054 | 24.6013 | 24.0829 | 23.8156 | 23.5799 | 23.3421 | 20.1319 | 14.1972 | 13.5727 | 1.8237 | 26.9778 | 26.3217 | 26.1309 | 25.8574 | 25.5696 | 25.1258 | 24.9329 | 24.7921 | 24.6329 | 22.1737 | 17.5166 | 16.7227 | 1.4676 | 27.1931 | 26.5288 | 26.3156 | 26.0431 | 25.7268 | 25.2554 | 24.9839 | 24.8115 | 24.637 | 21.8564 | 16.6656 | 16.2625
| MILTON OF CRAIGIE | ASHLUDIE | MINIMUM HEADROOM | NO 49222 33584 | NO | NO | 1.063 | 3.6624 | 3.6032 | 19.644 | 19.493 | 19.3246 | 18.8154 | 18.2246 | 17.6654 | 17.095 | 16.5317 | 14.7848 | 13.7532 | 13.0899 | 6.8868 | 6.8266 | 21.3511 | 21.2736 | 21.1756 | 20.8348 | 20.5379 | 20.2266 | 19.8848 | 19.5685 | 18.5858 | 18.4654 | 18.0807 | 5.2542 | 5.1817 | 20.4389 | 20.3256 | 20.1756 | 19.7236 | 19.244 | 18.7756 | 18.2889 | 17.8052 | 16.3113 | 15.5848 | 15.1552
|  | ASHLUDIE | EE |  |  |  |  | 3.6624 | 3.6032 | 19.644 | 19.5195 | 19.3838 | 18.8573 | 18.2246 | 17.6654 | 17.095 | 16.5317 | 14.7848 | 13.7532 | 13.0899 | 6.8879 | 6.8287 | 21.3532 | 21.2797 | 21.1838 | 20.9052 | 20.5379 | 20.2481 | 19.9236 | 19.5685 | 18.644 | 18.4654 | 18.3368 | 5.2542 | 5.1817 | 20.4389 | 20.344 | 20.2175 | 19.7797 | 19.244 | 18.7766 | 18.293 | 17.8052 | 16.3113 | 15.5848 | 15.1552
|  | ASHLUDIE | HT |  |  |  |  | 3.6644 | 3.6083 | 19.6593 | 19.5348 | 19.3868 | 18.8154 | 18.3042 | 17.7532 | 17.1583 | 16.6256 | 14.9113 | 13.8685 | 13.2787 | 6.8868 | 6.8266 | 21.3511 | 21.2736 | 21.1807 | 20.8348 | 20.5593 | 20.2552 | 19.894 | 19.5685 | 18.5858 | 18.6471 | 18.7624 | 5.2552 | 5.1838 | 20.4491 | 20.3501 | 20.2144 | 19.7236 | 19.2991 | 18.8338 | 18.3256 | 17.8654 | 16.3634 | 15.6379 | 15.3001
|  | ASHLUDIE | HE |  |  |  |  | 3.6685 | 3.6083 | 19.6562 | 19.493 | 19.3246 | 18.8215 | 18.2338 | 17.6736 | 17.1042 | 16.6593 | 15.3113 | 14.3154 | 13.7522 | 6.8879 | 6.8266 | 21.3511 | 21.2736 | 21.1756 | 20.894 | 20.545 | 20.2266 | 19.8848 | 19.6052 | 18.8624 | 18.6409 | 18.4062 | 5.2583 | 5.1858 | 20.446 | 20.3256 | 20.1756 | 19.7532 | 19.2542 | 18.7756 | 18.2889 | 17.9011 | 16.7399 | 16.0522 | 15.6603
|  | ASHLUDIE | FB |  |  |  |  | 3.8317 | 3.842 | 19.9624 | 19.9787 | 19.7042 | 19.7215 | 19.6236 | 19.5113 | 19.3787 | 19.242 | 18.4603 | 17.4042 | 16.8583 | 7.0042 | 6.9715 | 21.5532 | 21.546 | 21.2624 | 21.2583 | 21.145 | 21.0144 | 20.8644 | 20.7103 | 19.9664 | 18.9144 | 18.0807 | 5.4144 | 5.4022 | 20.7501 | 20.7358 | 20.4471 | 20.4838 | 20.3817 | 20.2654 | 20.1307 | 19.9889 | 19.2471 | 18.1175 | 17.7726
| GRUDIE BRIDGE | AULTBEA | MINIMUM HEADROOM | NG 87458 88885 | YES | NO | 0.212 | -0.46939 | -0.47347 | -0.48265 | -0.53878 | -0.58673 | -0.74388 | -0.8551 | -0.98163 | -1.0806 | -1.149 | -1.3724 | -1.5622 | -1.7582 | -0.10306 | -0.1102 | -0.11735 | -0.13367 | -0.14388 | -0.26939 | -0.34184 | -0.43061 | -0.48469 | -0.5102 | -0.62959 | -0.62041 | -0.7051 | -0.37551 | -0.38776 | -0.39388 | -0.42347 | -0.45 | -0.59286 | -0.66531 | -0.77245 | -0.85204 | -0.90816 | -1.0765 | -1.1796 | -1.2592
|  | AULTBEA | EE |  |  |  |  | -0.46939 | -0.47347 | -0.48265 | -0.53776 | -0.58163 | -0.69082 | -0.74388 | -0.91224 | -1.049 | -1.1337 | -1.3724 | -1.5622 | -1.7296 | -0.10306 | -0.1102 | -0.11735 | -0.13367 | -0.14388 | -0.1898 | -0.21735 | -0.34694 | -0.44082 | -0.49796 | -0.60816 | -0.60918 | -0.59388 | -0.37551 | -0.38776 | -0.39388 | -0.42245 | -0.44694 | -0.5398 | -0.55 | -0.70204 | -0.81531 | -0.8898 | -1.0765 | -1.1796 | -1.2327
|  | AULTBEA | HT |  |  |  |  | -0.46735 | -0.47245 | -0.48163 | -0.53673 | -0.58163 | -0.74388 | -0.8551 | -0.98163 | -1.0806 | -1.1337 | -1.3429 | -1.5214 | -1.7582 | -0.10204 | -0.1102 | -0.11735 | -0.13163 | -0.14286 | -0.26939 | -0.34184 | -0.43061 | -0.48469 | -0.5102 | -0.62959 | -0.62041 | -0.5898 | -0.37347 | -0.38571 | -0.39388 | -0.42245 | -0.4449 | -0.59286 | -0.66531 | -0.77245 | -0.85204 | -0.89388 | -1.0449 | -1.1633 | -1.2592
|  | AULTBEA | HE |  |  |  |  | -0.46735 | -0.47143 | -0.48163 | -0.53878 | -0.58673 | -0.68673 | -0.74898 | -0.92449 | -1.0622 | -1.149 | -1.3306 | -1.5378 | -1.6888 | -0.10204 | -0.10918 | -0.11735 | -0.13163 | -0.14388 | -0.18776 | -0.21531 | -0.35306 | -0.45408 | -0.50918 | -0.60714 | -0.61735 | -0.62755 | -0.37347 | -0.38367 | -0.39286 | -0.42347 | -0.45 | -0.53469 | -0.55408 | -0.71429 | -0.83367 | -0.90816 | -1.0408 | -1.1796 | -1.2541
|  | AULTBEA | FB |  |  |  |  | -0.44592 | -0.4398 | -0.42551 | -0.44796 | -0.47041 | -0.4949 | -0.52857 | -0.54796 | -0.6449 | -0.69898 | -0.90816 | -1.0745 | -1.1286 | -0.07551 | -0.080612 | -0.070408 | -0.078571 | -0.080612 | -0.092857 | -0.11939 | -0.13469 | -0.22653 | -0.27755 | -0.45816 | -0.61327 | -0.7051 | -0.34184 | -0.34184 | -0.32653 | -0.33571 | -0.33469 | -0.35204 | -0.37449 | -0.38776 | -0.47857 | -0.52551 | -0.72245 | -0.8602 | -0.87347
| BOAT OF GARTEN | AVIEMORE | MINIMUM HEADROOM | NH 89856 11394 | NO | YES | 5.98 | 1.867 | 1.8802 | 1.8986 | 1.8955 | 1.8568 | 1.5945 | 1.5282 | 1.2792 | 1.1159 | 0.87104 | 0.29961 | -0.1361 | -0.60855 | 5.821 | 5.8108 | 5.8057 | 5.7904 | 5.7415 | 5.5231 | 5.5098 | 5.3068 | 5.1874 | 4.9761 | 4.4894 | 4.5221 | 4.5302 | 4.2333 | 4.2129 | 4.2047 | 4.1568 | 4.1078 | 3.8639 | 3.818 | 3.5843 | 3.4394 | 3.2037 | 2.6557 | 2.4496 | 2.3159
|  | AVIEMORE | EE |  |  |  |  | 1.867 | 1.8802 | 1.8986 | 1.9057 | 1.8751 | 1.72 | 1.5976 | 1.4017 | 1.2119 | 0.98533 | 0.30574 | -0.1361 | -0.47896 | 5.821 | 5.8108 | 5.8057 | 5.7915 | 5.7425 | 5.6761 | 5.6159 | 5.5057 | 5.4017 | 5.1435 | 4.6537 | 4.6159 | 4.6108 | 4.2333 | 4.2129 | 4.2047 | 4.1629 | 4.1159 | 4.0037 | 3.9282 | 3.7812 | 3.6363 | 3.3527 | 2.72 | 2.5098 | 2.4384
|  | AVIEMORE | HT |  |  |  |  | 1.869 | 1.8833 | 1.9057 | 1.9078 | 1.8772 | 1.5945 | 1.5282 | 1.2792 | 1.1159 | 0.87104 | 0.29961 | -0.12386 | -0.60855 | 5.8221 | 5.8119 | 5.8068 | 5.7915 | 5.7425 | 5.5231 | 5.5098 | 5.3068 | 5.1874 | 4.9761 | 4.4894 | 4.5221 | 4.6221 | 4.2353 | 4.2149 | 4.2078 | 4.1639 | 4.117 | 3.8639 | 3.818 | 3.5843 | 3.4394 | 3.2037 | 2.6557 | 2.4496 | 2.3159
|  | AVIEMORE | HE |  |  |  |  | 1.869 | 1.8843 | 1.9047 | 1.8955 | 1.8568 | 1.7098 | 1.5547 | 1.3425 | 1.1374 | 0.95982 | 0.54757 | -0.014671 | -0.34732 | 5.8221 | 5.8119 | 5.8068 | 5.7904 | 5.7415 | 5.6772 | 5.6149 | 5.5017 | 5.4037 | 5.3017 | 5.0445 | 4.9812 | 4.8904 | 4.2353 | 4.2149 | 4.2078 | 4.1568 | 4.1078 | 3.9996 | 3.9139 | 3.7527 | 3.6017 | 3.4619 | 3.119 | 2.821 | 2.6506
|  | AVIEMORE | FB |  |  |  |  | 1.9659 | 2.018 | 2.0721 | 2.0945 | 2.1455 | 2.1608 | 2.1466 | 2.1353 | 2.1088 | 2.1374 | 1.8455 | 1.4221 | 1.2915 | 5.8823 | 5.8976 | 5.9108 | 5.9078 | 5.9098 | 5.9088 | 5.8792 | 5.8221 | 5.7517 | 5.7935 | 5.4384 | 4.8904 | 4.5302 | 4.3037 | 4.3159 | 4.3282 | 4.319 | 4.321 | 4.3108 | 4.2915 | 4.2578 | 4.2221 | 4.2353 | 4.0078 | 3.5251 | 3.4659
| ALNESS | BALALDIE | MINIMUM HEADROOM | NH 87017 79720 | YES | NO | 0.122 | -1.749 | -1.749 | -1.7714 | -1.801 | -1.848 | -2.1041 | -2.3704 | -2.652 | -2.8469 | -2.9959 | -3.3724 | -3.7388 | -4.0827 | -0.62551 | -0.61837 | -0.62347 | -0.63163 | -0.63367 | -0.8398 | -1.0622 | -1.2612 | -1.3765 | -1.4367 | -1.5255 | -1.6592 | -1.8888 | -1.1939 | -1.1929 | -1.2112 | -1.248 | -1.2571 | -1.5 | -1.7602 | -1.9929 | -2.1571 | -2.2714 | -2.4908 | -2.7276 | -2.9316
|  | BALALDIE | EE |  |  |  |  | -1.749 | -1.748 | -1.7714 | -1.7959 | -1.8429 | -2.0061 | -2.099 | -2.3571 | -2.6408 | -2.9092 | -3.3724 | -3.7388 | -4.0092 | -0.62449 | -0.61837 | -0.62347 | -0.63061 | -0.63367 | -0.6949 | -0.75612 | -0.9551 | -1.1878 | -1.3786 | -1.502 | -1.5367 | -1.6 | -1.1929 | -1.1929 | -1.2112 | -1.2439 | -1.2531 | -1.3796 | -1.4633 | -1.7112 | -1.9867 | -2.2041 | -2.4908 | -2.7255 | -2.8908
|  | BALALDIE | HT |  |  |  |  | -1.748 | -1.749 | -1.7663 | -1.7959 | -1.8418 | -2.1041 | -2.3704 | -2.652 | -2.8469 | -2.9673 | -3.2816 | -3.7061 | -4.0827 | -0.62551 | -0.61837 | -0.62245 | -0.63061 | -0.63265 | -0.8398 | -1.0622 | -1.2612 | -1.3765 | -1.4367 | -1.5255 | -1.5469 | -1.549 | -1.1918 | -1.1918 | -1.2071 | -1.2429 | -1.2531 | -1.5 | -1.7602 | -1.9929 | -2.1571 | -2.2561 | -2.45 | -2.701 | -2.9316
|  | BALALDIE | HE |  |  |  |  | -1.749 | -1.749 | -1.7663 | -1.801 | -1.848 | -2.002 | -2.1173 | -2.3949 | -2.7082 | -2.9959 | -3.2918 | -3.7031 | -3.9469 | -0.62551 | -0.61837 | -0.62245 | -0.63163 | -0.63367 | -0.69388 | -0.75918 | -0.97449 | -1.2306 | -1.4286 | -1.498 | -1.5469 | -1.6378 | -1.1939 | -1.1918 | -1.2082 | -1.248 | -1.2571 | -1.3786 | -1.4765 | -1.7439 | -2.0418 | -2.2714 | -2.451 | -2.7276 | -2.8929
|  | BALALDIE | FB |  |  |  |  | -1.7 | -1.6714 | -1.652 | -1.6541 | -1.6633 | -1.6827 | -1.7286 | -1.7531 | -1.9082 | -2.052 | -2.5806 | -2.7857 | -2.8929 | -0.59082 | -0.56939 | -0.5551 | -0.55 | -0.55 | -0.57653 | -0.61837 | -0.63673 | -0.79898 | -0.96122 | -1.4276 | -1.6592 | -1.8888 | -1.1439 | -1.1184 | -1.1 | -1.098 | -1.1031 | -1.1337 | -1.1776 | -1.198 | -1.3612 | -1.4898 | -1.9929 | -2.2051 | -2.2633
| ABERNETHY | BALBEGGIE | MINIMUM HEADROOM | NO 17499 29606 | YES | YES | 0.745 | 1.7697 | 1.7717 | 1.7299 | 1.6748 | 1.4983 | 1.1177 | 0.58398 | 0.18908 | -0.79459 | -1.1477 | -2.5772 | -4.3181 | -5.7711 | 3.1105 | 3.1034 | 3.0564 | 2.8911 | 2.7697 | 2.4626 | 2.036 | 1.6809 | 0.65235 | 0.35847 | -0.97622 | -2.5079 | -3.9895 | 2.4574 | 2.4585 | 2.4197 | 2.3279 | 2.1228 | 1.8085 | 1.3217 | 0.90337 | -0.18439 | -0.52622 | -2.0038 | -3.8426 | -5.4772
|  | BALBEGGIE | EE |  |  |  |  | 1.7697 | 1.7728 | 1.7319 | 1.6911 | 1.5228 | 1.1615 | 0.65031 | 0.32684 | -0.28643 | -0.58643 | -1.9272 | -3.7956 | -4.6038 | 3.1115 | 3.1054 | 3.0636 | 3.0299 | 2.783 | 2.5136 | 2.0779 | 1.8268 | 1.2503 | 1.0187 | 0.0054082 | -1.666 | -2.263 | 2.4585 | 2.4605 | 2.4217 | 2.3738 | 2.1299 | 1.8411 | 1.3768 | 1.0615 | 0.43398 | 0.16867 | -1.0426 | -2.9619 | -3.7456
|  | BALBEGGIE | HT |  |  |  |  | 1.7697 | 1.7717 | 1.7299 | 1.6819 | 1.5136 | 1.1177 | 0.65949 | 0.22888 | -0.44663 | -0.76296 | -2.0732 | -4.1436 | -5.6374 | 3.1105 | 3.1034 | 3.0564 | 3.0187 | 2.7697 | 2.4626 | 2.0554 | 1.6809 | 1.0054 | 0.75949 | -0.34255 | -2.2017 | -3.5058 | 2.4585 | 2.4585 | 2.4197 | 2.3687 | 2.1228 | 1.8085 | 1.3523 | 0.93704 | 0.21459 | -0.060918 | -1.3028 | -3.4507 | -5.0568
|  | BALBEGGIE | HE |  |  |  |  | 1.7697 | 1.7738 | 1.7319 | 1.6748 | 1.4983 | 1.1197 | 0.58398 | 0.18908 | -0.79459 | -1.1477 | -2.5772 | -4.3181 | -5.7711 | 3.1115 | 3.1044 | 3.0574 | 3.0248 | 2.7738 | 2.4932 | 2.036 | 1.6921 | 0.65235 | 0.35847 | -0.97622 | -2.5079 | -3.9895 | 2.4574 | 2.4605 | 2.4217 | 2.3626 | 2.137 | 1.8095 | 1.3217 | 0.90337 | -0.18439 | -0.52622 | -2.0038 | -3.8426 | -5.4772
|  | BALBEGGIE | FB |  |  |  |  | 1.8452 | 1.8656 | 1.8707 | 1.7381 | 1.7064 | 1.683 | 1.5401 | 1.386 | 0.96051 | 0.81867 | 0.23806 | -0.62622 | -1.2436 | 3.1738 | 3.1799 | 3.1626 | 2.8911 | 2.8626 | 2.8187 | 2.6523 | 2.4789 | 2.0023 | 1.8452 | 1.3289 | 0.47582 | -0.22622 | 2.5095 | 2.5248 | 2.5238 | 2.3279 | 2.2993 | 2.2544 | 2.0891 | 1.9115 | 1.4472 | 1.3177 | 0.785 | -0.19765 | -0.61092
| MILTON OF CRAIGIE | BALDOVIE | MINIMUM HEADROOM | NO 45279 32147 | NO | NO | 0.947 | 10.8086 | 10.1484 | 9.6188 | 8.68 | 7.6616 | 6.379 | 5.0065 | 4.5188 | 4.0994 | 3.6769 | 0.39633 | -0.92204 | -1.8445 | 13.3157 | 12.6504 | 12.0698 | 11.1127 | 10.1127 | 9.0545 | 7.9076 | 7.729 | 7.582 | 7.4127 | 4.9392 | 4.5331 | 4.1198 | 12.0739 | 11.4351 | 10.8984 | 10.0371 | 9.0922 | 7.9371 | 6.7024 | 6.3545 | 6.0616 | 5.7545 | 2.8514 | 1.4749 | 0.60449
|  | BALDOVIE | EE |  |  |  |  | 10.9433 | 10.1484 | 9.6188 | 8.6831 | 7.679 | 6.379 | 5.0065 | 4.5188 | 4.0994 | 3.6769 | 0.51776 | -0.80367 | -1.8445 | 13.4698 | 12.6504 | 12.0698 | 11.1127 | 10.1137 | 9.0545 | 7.9076 | 7.729 | 7.582 | 7.4127 | 4.9392 | 4.5331 | 4.1198 | 12.2096 | 11.4351 | 10.8984 | 10.0371 | 9.1035 | 7.9371 | 6.7024 | 6.3545 | 6.0616 | 5.7545 | 2.8514 | 1.4749 | 0.60449
|  | BALDOVIE | HT |  |  |  |  | 10.8647 | 10.1841 | 9.6198 | 8.7055 | 7.6922 | 7.3106 | 6.8688 | 6.3994 | 5.5769 | 4.1096 | 0.39633 | -0.92204 | -1.5924 | 13.379 | 12.681 | 12.0698 | 11.1157 | 10.1137 | 10.0249 | 9.8718 | 9.6963 | 9.1106 | 7.8086 | 4.9902 | 4.7943 | 4.7331 | 12.13 | 11.4698 | 10.9127 | 10.0494 | 9.1055 | 8.8555 | 8.5453 | 8.2096 | 7.5055 | 6.1586 | 2.9014 | 1.6412 | 1.0616
|  | BALDOVIE | HE |  |  |  |  | 10.8086 | 10.1586 | 9.6361 | 8.68 | 7.6616 | 6.4035 | 5.0861 | 4.6555 | 4.2647 | 3.9035 | 0.97388 | 0.11878 | -0.41592 | 13.3157 | 12.6514 | 12.0708 | 11.1137 | 10.1127 | 9.0565 | 7.9167 | 7.7504 | 7.6055 | 7.4494 | 5.1014 | 4.8606 | 4.6024 | 12.0739 | 11.4433 | 10.9116 | 10.0382 | 9.0922 | 7.9463 | 6.7453 | 6.4331 | 6.1596 | 5.8892 | 3.3229 | 2.6198 | 2.0116
|  | BALDOVIE | FB |  |  |  |  | 11.3055 | 10.881 | 10.2494 | 9.7729 | 8.9729 | 7.9953 | 6.88 | 5.932 | 5.8218 | 5.6902 | 4.4412 | 2.679 | 2.1229 | 13.83 | 13.3382 | 12.6729 | 12.1729 | 11.2718 | 10.2116 | 9.0178 | 8.0178 | 7.9392 | 7.8402 | 6.6831 | 4.8841 | 4.1749 | 12.5637 | 12.1361 | 11.5127 | 11.0596 | 10.2667 | 9.3269 | 8.2351 | 7.3106 | 7.2208 | 7.1106 | 5.9739 | 4.2167 | 3.5953
| TARLAND | BALLATER | MINIMUM HEADROOM | NO 37542 97131 | NO | NO | 0.941 | 6.2255 | 6.2153 | 6.1806 | 6.0827 | 6.0265 | 5.5694 | 5.2245 | 4.9347 | 4.5837 | 4.3133 | 3.5184 | 2.9418 | 2.5918 | 8.4755 | 8.4653 | 8.4357 | 8.401 | 8.3765 | 8.1194 | 7.8939 | 7.7684 | 7.5541 | 7.3378 | 6.7449 | 6.6143 | 6.5929 | 7.6173 | 7.6153 | 7.5816 | 7.5184 | 7.4755 | 7.0092 | 6.7173 | 6.4898 | 6.1969 | 5.949 | 5.2439 | 4.8551 | 4.6643
|  | BALLATER | EE |  |  |  |  | 6.2255 | 6.2153 | 6.2 | 6.1571 | 6.098 | 5.6796 | 5.3724 | 5.1408 | 4.8276 | 4.5776 | 3.5184 | 2.9418 | 2.5918 | 8.4755 | 8.4673 | 8.448 | 8.4224 | 8.399 | 8.1378 | 7.9265 | 7.8153 | 7.6235 | 7.4245 | 6.7673 | 6.6143 | 6.5929 | 7.6184 | 7.6153 | 7.6071 | 7.549 | 7.5235 | 7.0806 | 6.8133 | 6.6316 | 6.3694 | 6.1408 | 5.2439 | 4.8551 | 4.6643
|  | BALLATER | HT |  |  |  |  | 6.2265 | 6.2173 | 6.1806 | 6.0827 | 6.0316 | 5.5694 | 5.2327 | 5.0439 | 4.7316 | 4.45 | 3.6827 | 3.0684 | 2.648 | 8.4765 | 8.4653 | 8.4357 | 8.401 | 8.3765 | 8.1214 | 7.8939 | 7.7949 | 7.5643 | 7.3378 | 6.7449 | 6.6449 | 6.7347 | 7.6173 | 7.6173 | 7.5816 | 7.5184 | 7.4786 | 7.0092 | 6.7173 | 6.5673 | 6.2878 | 6.0296 | 5.3286 | 4.9306 | 4.7286
|  | BALLATER | HE |  |  |  |  | 6.2296 | 6.2194 | 6.199 | 6.102 | 6.0265 | 5.5724 | 5.2245 | 4.9347 | 4.5837 | 4.3133 | 3.7816 | 3.2051 | 2.8939 | 8.4776 | 8.4684 | 8.4418 | 8.4122 | 8.3867 | 8.1194 | 7.9133 | 7.7684 | 7.5541 | 7.35 | 6.9643 | 6.8255 | 6.8122 | 7.6184 | 7.6173 | 7.5959 | 7.5327 | 7.4755 | 7.0112 | 6.7204 | 6.4898 | 6.1969 | 5.949 | 5.4806 | 5.0959 | 4.9235
|  | BALLATER | FB |  |  |  |  | 6.2949 | 6.3276 | 6.349 | 6.351 | 6.2296 | 6.1857 | 6.0592 | 5.9673 | 5.8592 | 5.8051 | 5.3337 | 4.6378 | 4.4571 | 8.5214 | 8.5276 | 8.5316 | 8.5337 | 8.4582 | 8.4316 | 8.3102 | 8.2398 | 8.1755 | 8.1163 | 7.8194 | 7.2153 | 6.9684 | 7.6786 | 7.7051 | 7.7286 | 7.7296 | 7.5347 | 7.4888 | 7.3633 | 7.301 | 7.2143 | 7.1612 | 6.7643 | 6.0929 | 5.9837
| CARRADALE 1 | BALLIEKINE | MINIMUM HEADROOM | NR 87179 38819 | YES | YES | 0 | 0.50612 | 0.5 | 0.49388 | 0.46429 | 0.44184 | 0.41531 | 0.39082 | 0.35714 | 0.34694 | 0.32347 | 0.27245 | 0.24388 | 0.22449 | 0.63367 | 0.63265 | 0.62755 | 0.60816 | 0.59184 | 0.57551 | 0.56327 | 0.53776 | 0.52347 | 0.5 | 0.45 | 0.45408 | 0.46429 | 0.48265 | 0.48265 | 0.48367 | 0.47041 | 0.46531 | 0.44796 | 0.43163 | 0.4051 | 0.38673 | 0.35918 | 0.30918 | 0.30612 | 0.30102
|  | BALLIEKINE | EE |  |  |  |  | 0.50612 | 0.5 | 0.4949 | 0.46531 | 0.44388 | 0.41633 | 0.39082 | 0.36939 | 0.34694 | 0.32347 | 0.27245 | 0.24796 | 0.23571 | 0.63469 | 0.63265 | 0.62959 | 0.60816 | 0.59184 | 0.57653 | 0.56327 | 0.53776 | 0.52347 | 0.5 | 0.46224 | 0.46633 | 0.48061 | 0.48367 | 0.48265 | 0.48469 | 0.47041 | 0.46633 | 0.44796 | 0.43163 | 0.4051 | 0.38673 | 0.35918 | 0.31122 | 0.31429 | 0.31429
|  | BALLIEKINE | HT |  |  |  |  | 0.50612 | 0.50204 | 0.49592 | 0.46633 | 0.4449 | 0.42041 | 0.39898 | 0.36327 | 0.35612 | 0.33265 | 0.27449 | 0.24388 | 0.22449 | 0.63469 | 0.63367 | 0.62959 | 0.60816 | 0.59184 | 0.57551 | 0.56429 | 0.53776 | 0.52449 | 0.50102 | 0.45 | 0.45408 | 0.47245 | 0.48367 | 0.48367 | 0.48571 | 0.47245 | 0.46735 | 0.45204 | 0.43776 | 0.4102 | 0.39082 | 0.36633 | 0.30918 | 0.30612 | 0.3051
|  | BALLIEKINE | HE |  |  |  |  | 0.50612 | 0.5 | 0.49388 | 0.46429 | 0.44184 | 0.41531 | 0.39286 | 0.35714 | 0.35204 | 0.32653 | 0.28163 | 0.24796 | 0.22551 | 0.63367 | 0.63367 | 0.62755 | 0.60816 | 0.59184 | 0.57551 | 0.56429 | 0.53776 | 0.52347 | 0.50102 | 0.46327 | 0.46224 | 0.46429 | 0.48265 | 0.48265 | 0.48367 | 0.47143 | 0.46531 | 0.44796 | 0.43367 | 0.40612 | 0.38776 | 0.36224 | 0.31837 | 0.31224 | 0.30102
|  | BALLIEKINE | FB |  |  |  |  | 0.51633 | 0.51837 | 0.51531 | 0.51122 | 0.50612 | 0.49388 | 0.49184 | 0.48367 | 0.46939 | 0.45612 | 0.41531 | 0.36531 | 0.35204 | 0.64388 | 0.64796 | 0.64694 | 0.63776 | 0.63061 | 0.61429 | 0.61122 | 0.60306 | 0.58673 | 0.57041 | 0.52959 | 0.48469 | 0.47143 | 0.49694 | 0.50306 | 0.50408 | 0.50816 | 0.51429 | 0.50612 | 0.50816 | 0.50204 | 0.49286 | 0.47653 | 0.43469 | 0.37653 | 0.37143
| BOAT OF GARTEN | BALLINDALLOCH | MINIMUM HEADROOM | NJ 19279 34652 | NO | YES | 1.465 | 6.8442 | 6.835 | 6.8217 | 6.8095 | 6.7789 | 6.4646 | 6.2666 | 6.1299 | 5.9544 | 5.9146 | 5.5095 | 5.3646 | 5.4319 | 7.4182 | 7.4049 | 7.3896 | 7.3712 | 7.3365 | 7.2233 | 7.0906 | 6.9427 | 6.7631 | 6.7243 | 6.2906 | 6.1661 | 6.2508 | 7.497 | 7.4827 | 7.4674 | 7.4552 | 7.4225 | 7.1317 | 6.9276 | 6.7847 | 6.6052 | 6.5623 | 6.1307 | 5.9878 | 6.0643
|  | BALLINDALLOCH | EE |  |  |  |  | 6.8442 | 6.835 | 6.8248 | 6.8115 | 6.7819 | 6.4738 | 6.2809 | 6.1758 | 5.9962 | 5.9146 | 5.6013 | 5.3646 | 5.4319 | 7.4182 | 7.4049 | 7.3906 | 7.3712 | 7.3386 | 7.2273 | 7.0967 | 6.9927 | 6.8069 | 6.7243 | 6.3876 | 6.1661 | 6.2508 | 7.498 | 7.4837 | 7.4684 | 7.4552 | 7.4256 | 7.1409 | 6.9378 | 6.8358 | 6.649 | 6.5623 | 6.2215 | 5.9878 | 6.0705
|  | BALLINDALLOCH | HT |  |  |  |  | 6.8442 | 6.835 | 6.8228 | 6.8115 | 6.7819 | 6.4932 | 6.3003 | 6.1299 | 5.9544 | 5.9432 | 5.5095 | 5.4044 | 5.436 | 7.4182 | 7.4049 | 7.3906 | 7.3712 | 7.3386 | 7.2314 | 7.1151 | 6.9427 | 6.7631 | 6.7518 | 6.2906 | 6.2008 | 6.2682 | 7.498 | 7.4847 | 7.4674 | 7.4562 | 7.4256 | 7.1572 | 6.9582 | 6.7847 | 6.6052 | 6.5919 | 6.1307 | 6.0225 | 6.0643
|  | BALLINDALLOCH | HE |  |  |  |  | 6.8442 | 6.835 | 6.8217 | 6.8095 | 6.7789 | 6.4646 | 6.2666 | 6.1432 | 6.0248 | 5.9391 | 5.6952 | 5.687 | 5.6626 | 7.4182 | 7.4049 | 7.3896 | 7.3712 | 7.3365 | 7.2233 | 7.0906 | 6.9671 | 6.8518 | 6.7631 | 6.5059 | 6.5171 | 6.5141 | 7.497 | 7.4827 | 7.4674 | 7.4552 | 7.4225 | 7.1317 | 6.9276 | 6.8052 | 6.6858 | 6.5929 | 6.3358 | 6.3215 | 6.3052
|  | BALLINDALLOCH | FB |  |  |  |  | 6.885 | 6.8921 | 6.8942 | 6.9003 | 6.8881 | 6.8779 | 6.8523 | 6.8228 | 6.8146 | 6.7819 | 6.6748 | 6.535 | 5.9942 | 7.4427 | 7.4416 | 7.4365 | 7.4324 | 7.4182 | 7.408 | 7.3845 | 7.3661 | 7.3518 | 7.3243 | 7.259 | 7.1518 | 6.6467 | 7.5358 | 7.5409 | 7.5358 | 7.5347 | 7.5245 | 7.5133 | 7.4898 | 7.4592 | 7.448 | 7.4154 | 7.3052 | 7.1429 | 6.6184
| CARRADALE 1 | BALLURE | MINIMUM HEADROOM | NR 71425 49944 | YES | YES | 0.155 | 1.6827 | 1.2663 | 1.1398 | 0.9949 | 0.96327 | 0.91531 | 0.8551 | 0.80918 | 0.75714 | 0.71224 | 0.63469 | 0.55918 | 0.46327 | 1.875 | 1.4566 | 1.2872 | 1.125 | 1.1138 | 1.0923 | 1.0658 | 1.0495 | 1.024 | 0.9852 | 0.91582 | 0.92296 | 0.89235 | 1.9171 | 1.4651 | 1.3304 | 1.1793 | 1.161 | 1.114 | 1.062 | 1.0222 | 1.0059 | 0.97423 | 0.91199 | 0.87934 | 0.79872
|  | BALLURE | EE |  |  |  |  | 1.6827 | 1.5031 | 1.2643 | 1.1061 | 0.96633 | 0.91939 | 0.85918 | 0.81939 | 0.77041 | 0.72449 | 0.63469 | 0.55918 | 0.46327 | 1.875 | 1.6913 | 1.4536 | 1.2781 | 1.1138 | 1.0944 | 1.0668 | 1.0546 | 1.0291 | 0.99541 | 0.9301 | 0.93724 | 0.89235 | 1.9181 | 1.7375 | 1.462 | 1.3069 | 1.162 | 1.1171 | 1.0681 | 1.0344 | 1.0232 | 0.99056 | 0.91199 | 0.87934 | 0.79872
|  | BALLURE | HT |  |  |  |  | 1.6837 | 1.2663 | 1.1398 | 0.9949 | 0.97245 | 0.94184 | 0.88571 | 0.84592 | 0.79286 | 0.74592 | 0.65102 | 0.59184 | 0.4898 | 1.875 | 1.4566 | 1.2872 | 1.125 | 1.1168 | 1.1015 | 1.075 | 1.0607 | 1.0352 | 1.0036 | 0.91582 | 0.92296 | 0.94541 | 1.9181 | 1.4651 | 1.3304 | 1.1793 | 1.1671 | 1.1395 | 1.0916 | 1.0599 | 1.0426 | 1.0069 | 0.91403 | 0.88342 | 0.8375
|  | BALLURE | HE |  |  |  |  | 1.6827 | 1.501 | 1.2653 | 1.1061 | 0.96327 | 0.91531 | 0.8551 | 0.80918 | 0.75714 | 0.71224 | 0.64796 | 0.57347 | 0.55204 | 1.875 | 1.6893 | 1.4536 | 1.277 | 1.1138 | 1.0923 | 1.0658 | 1.0495 | 1.024 | 0.9852 | 0.92602 | 0.92602 | 1.0148 | 1.9171 | 1.7344 | 1.462 | 1.3059 | 1.161 | 1.114 | 1.062 | 1.0222 | 1.0059 | 0.97423 | 0.91709 | 0.88036 | 0.89158
|  | BALLURE | FB |  |  |  |  | 1.702 | 1.699 | 1.6857 | 1.4561 | 1.298 | 1.1327 | 1.1276 | 1.1133 | 1.1031 | 1.0939 | 1.0224 | 0.95918 | 0.92857 | 1.8883 | 1.8883 | 1.8801 | 1.523 | 1.3526 | 1.1893 | 1.1862 | 1.175 | 1.1668 | 1.1556 | 1.1097 | 1.0617 | 1.0474 | 1.9314 | 1.9344 | 1.9212 | 1.5804 | 1.4099 | 1.2457 | 1.2457 | 1.2365 | 1.2314 | 1.2202 | 1.1753 | 1.1151 | 1.1018
| DYCE | BALMEDIE | MINIMUM HEADROOM | NJ 95546 18627 | NO | YES | 1.02 | 3.4804 | 2.9866 | 2.2539 | 1.3345 | 0.59982 | -0.55732 | -1.6339 | -2.241 | -2.8349 | -3.4226 | -5.5981 | -6.5471 | -7.1226 | 3.9957 | 3.661 | 3.2764 | 2.8559 | 2.1457 | 1.4855 | 0.69982 | 0.48553 | 0.27941 | 0.12839 | -1.5155 | -1.642 | -1.6818 | 3.7519 | 3.3478 | 2.8376 | 2.1886 | 1.5233 | 0.68043 | -0.32263 | -0.75324 | -1.2236 | -1.7481 | -3.5951 | -4.3522 | -4.7604
|  | BALMEDIE | EE |  |  |  |  | 3.5294 | 3.1559 | 2.5539 | 1.8008 | 1.059 | -0.33283 | -1.6339 | -2.241 | -2.8349 | -3.1165 | -5.5981 | -6.5471 | -7.1226 | 4.0549 | 3.7039 | 3.358 | 2.9835 | 2.2876 | 1.4855 | 0.69982 | 0.48553 | 0.27941 | 0.12941 | -1.4522 | -1.6063 | -1.6818 | 3.8019 | 3.4672 | 3.0223 | 2.4712 | 1.8029 | 0.74472 | -0.32263 | -0.75324 | -1.2236 | -1.5226 | -3.5951 | -4.3522 | -4.7604
|  | BALMEDIE | HT |  |  |  |  | 3.5008 | 2.9866 | 2.2539 | 1.3345 | 0.59982 | -0.55732 | -1.2226 | -1.7573 | -2.5777 | -3.4226 | -5.5369 | -6.4818 | -7.0624 | 4.0202 | 3.661 | 3.2764 | 2.8559 | 2.1457 | 1.8304 | 1.6019 | 1.408 | 0.88656 | 0.12839 | -1.5155 | -1.642 | -1.643 | 3.7723 | 3.3478 | 2.8376 | 2.1886 | 1.5233 | 0.68043 | 0.15594 | -0.27875 | -1.0134 | -1.7481 | -3.592 | -4.3318 | -4.7022
|  | BALMEDIE | HE |  |  |  |  | 3.4804 | 3.1559 | 2.6304 | 1.9192 | 1.1672 | 0.052882 | -1.2471 | -2.0665 | -2.8022 | -3.2002 | -5.59 | -6.2543 | -6.6553 | 3.9957 | 3.7019 | 3.3743 | 3.01 | 2.3121 | 1.5866 | 0.8039 | 0.53553 | 0.31207 | 0.14166 | -1.4257 | -1.4604 | -1.493 | 3.7519 | 3.4641 | 3.0672 | 2.5447 | 1.8702 | 0.96411 | -0.10732 | -0.66855 | -1.193 | -1.5563 | -3.5298 | -3.9369 | -4.192
|  | BALMEDIE | FB |  |  |  |  | 3.7427 | 3.5366 | 3.2468 | 2.8284 | 2.4845 | 1.7539 | 0.90492 | 0.003902 | -0.39406 | -0.65018 | -2.5022 | -3.8328 | -4.1553 | 4.2315 | 4.0029 | 3.7243 | 3.4743 | 3.0621 | 2.4692 | 1.7539 | 0.9539 | 0.8488 | 0.75696 | -0.13487 | -1.0196 | -1.2441 | 3.9957 | 3.8019 | 3.5304 | 3.2355 | 2.9049 | 2.2937 | 1.5498 | 0.73656 | 0.48656 | 0.28043 | -1.0573 | -2.3665 | -2.6104
| CLAYHILLS | BALNAGASK | MINIMUM HEADROOM | NJ 96055 05234 | YES | NO | 0.003 | 9.5414 | 9.5404 | 9.5394 | 9.268 | 9.1955 | 9.02 | 8.8904 | 8.7159 | 8.5435 | 8.4078 | 7.6782 | 6.7935 | 6.3343 | 9.3309 | 9.3279 | 9.3197 | 9.0054 | 8.9564 | 8.786 | 8.6666 | 8.5064 | 8.3697 | 8.2554 | 7.8585 | 7.3656 | 7.0952 | 9.4647 | 9.4637 | 9.4637 | 9.2219 | 9.1505 | 8.9852 | 8.8688 | 8.7158 | 8.5535 | 8.4178 | 7.7229 | 6.9219 | 6.5137
|  | BALNAGASK | EE |  |  |  |  | 9.5414 | 9.5424 | 9.5394 | 9.5159 | 9.2006 | 9.02 | 8.8904 | 8.718 | 8.5598 | 8.4271 | 7.6782 | 6.7935 | 6.3343 | 9.3309 | 9.3289 | 9.3289 | 9.3105 | 8.9636 | 8.786 | 8.6666 | 8.5177 | 8.386 | 8.2707 | 7.8717 | 7.3656 | 7.0952 | 9.4647 | 9.4637 | 9.4637 | 9.4474 | 9.1556 | 8.9852 | 8.8688 | 8.7239 | 8.5678 | 8.4331 | 7.7229 | 6.9219 | 6.5137
|  | BALNAGASK | HT |  |  |  |  | 9.5486 | 9.5547 | 9.5537 | 9.5424 | 9.22 | 9.0629 | 8.8914 | 8.7894 | 8.5435 | 8.4078 | 7.7598 | 7.019 | 6.7414 | 9.3319 | 9.3279 | 9.3197 | 9.3146 | 8.9677 | 8.8177 | 8.6738 | 8.5921 | 8.3697 | 8.2554 | 7.8585 | 7.4942 | 7.3738 | 9.4739 | 9.4739 | 9.4709 | 9.4678 | 9.1739 | 9.0249 | 8.8882 | 8.7943 | 8.5535 | 8.4178 | 7.8096 | 7.1586 | 6.9249
|  | BALNAGASK | HE |  |  |  |  | 9.5424 | 9.5404 | 9.5404 | 9.5139 | 9.1955 | 9.0312 | 8.9343 | 8.7159 | 8.6047 | 8.5282 | 8.0618 | 7.7424 | 7.5608 | 9.3319 | 9.3299 | 9.3309 | 9.3136 | 8.9564 | 8.7891 | 8.7217 | 8.5064 | 8.4248 | 8.3687 | 8.0615 | 7.9503 | 7.9421 | 9.4709 | 9.4658 | 9.4698 | 9.4566 | 9.1505 | 8.9984 | 8.926 | 8.7158 | 8.6107 | 8.527 | 8.0821 | 7.8158 | 7.6872
|  | BALNAGASK | FB |  |  |  |  | 9.5669 | 9.5812 | 9.5873 | 9.268 | 9.269 | 9.2598 | 9.2465 | 9.221 | 9.171 | 9.0894 | 8.6465 | 8.1343 | 7.4945 | 9.3523 | 9.3595 | 9.3472 | 9.0054 | 8.9962 | 8.984 | 8.9605 | 8.9462 | 8.9146 | 8.8513 | 8.433 | 7.9595 | 7.3911 | 9.5005 | 9.5158 | 9.5127 | 9.2219 | 9.2239 | 9.2137 | 9.1933 | 9.1811 | 9.1525 | 9.0933 | 8.6433 | 7.9852 | 7.5127
| KINTORE | BANCHORY | MINIMUM HEADROOM | NO 69262 96297 | NO | YES | 4.121 | 2.1649 | 1.9915 | 26.1972 | 25.8931 | 25.3502 | 24.3992 | 23.3564 | 22.2554 | 20.7737 | 19.9431 | 16.8482 | 13.7543 | 10.9829 | 4.5762 | 4.5047 | 28.3094 | 28.186 | 27.7349 | 27.2625 | 26.6176 | 25.9074 | 24.6145 | 23.9768 | 21.6207 | 19.8329 | 18.0941 | 3.1517 | 3.0354 | 27.3686 | 27.0798 | 26.587 | 25.8584 | 24.9696 | 24.0176 | 22.5809 | 21.9166 | 19.0258 | 16.3298 | 14.0696
|  | BANCHORY | EE |  |  |  |  | 2.219 | 2.0078 | 26.2707 | 25.989 | 25.4707 | 24.5492 | 23.4809 | 22.5217 | 21.4298 | 20.7298 | 17.5543 | 14.2564 | 12.4186 | 4.6364 | 4.5119 | 28.339 | 28.2298 | 27.7829 | 27.3084 | 26.6472 | 26.0931 | 25.286 | 24.7819 | 22.8002 | 20.7227 | 19.8268 | 3.2058 | 3.0456 | 27.4115 | 27.1472 | 26.6533 | 25.9451 | 25.0543 | 24.2554 | 23.2941 | 22.7747 | 20.0747 | 17.09 | 15.6411
|  | BANCHORY | HT |  |  |  |  | 2.1854 | 1.9915 | 26.1972 | 25.8931 | 25.3502 | 24.5339 | 23.5594 | 22.6125 | 21.2972 | 20.4635 | 17.338 | 13.7543 | 10.9829 | 4.5976 | 4.5047 | 28.3094 | 28.186 | 27.7349 | 27.4125 | 26.8492 | 26.2309 | 25.0951 | 24.5054 | 22.2819 | 20.1054 | 18.5615 | 3.17 | 3.0354 | 27.3686 | 27.0798 | 26.587 | 26.0125 | 25.1962 | 24.386 | 23.2115 | 22.5033 | 19.7166 | 16.4625 | 14.0696
|  | BANCHORY | HE |  |  |  |  | 2.1649 | 2.0088 | 26.2554 | 25.9615 | 25.4237 | 24.3992 | 23.3564 | 22.2554 | 20.7737 | 19.9431 | 16.8482 | 13.7839 | 11.4788 | 4.5762 | 4.5119 | 28.3309 | 28.2217 | 27.7717 | 27.2625 | 26.6176 | 25.9074 | 24.6145 | 23.9768 | 21.6207 | 19.8329 | 18.0941 | 3.1517 | 3.0466 | 27.4013 | 27.1278 | 26.6247 | 25.8584 | 24.9696 | 24.0176 | 22.5809 | 21.9166 | 19.0258 | 16.3298 | 14.1962
|  | BANCHORY | FB |  |  |  |  | 2.5231 | 2.367 | 26.6849 | 26.5513 | 26.437 | 26.1482 | 25.6809 | 25.2002 | 24.7186 | 24.4227 | 22.9921 | 21.2717 | 20.4166 | 4.9456 | 4.7864 | 28.539 | 28.4594 | 28.3309 | 28.0921 | 27.6421 | 27.1656 | 26.7013 | 26.4502 | 25.339 | 23.6258 | 22.3982 | 3.5282 | 3.3588 | 27.7441 | 27.6176 | 27.4819 | 27.1982 | 26.7135 | 26.2064 | 25.6788 | 25.3982 | 24.1758 | 22.637 | 22.0686
| TAYNUILT | BARCALDINE | MINIMUM HEADROOM | NM 96356 42181 | YES | YES | 2.006 | -4.0602 | -4.2602 | -4.3827 | -4.5082 | -4.8673 | -5.252 | -5.5051 | -5.8204 | -6.0367 | -6.2265 | -6.7959 | -7.0061 | -7.0949 | -3.7255 | -4.0245 | -4.1643 | -4.301 | -4.5184 | -4.7592 | -4.9439 | -5.1653 | -5.3051 | -5.4673 | -5.9622 | -6.0245 | -5.9755 | -3.7684 | -4.0439 | -4.1949 | -4.3418 | -4.7163 | -5.101 | -5.3449 | -5.649 | -5.8429 | -6.0337 | -6.5918 | -6.7378 | -6.7724
|  | BARCALDINE | EE |  |  |  |  | -4.0602 | -4.0867 | -4.3082 | -4.4255 | -4.8051 | -5.1541 | -5.4612 | -5.7827 | -6.0153 | -6.2041 | -6.7959 | -7.0061 | -7.0898 | -3.7255 | -3.7245 | -4.0388 | -4.1704 | -4.3898 | -4.6561 | -4.8959 | -5.1276 | -5.2847 | -5.45 | -5.951 | -6.0102 | -5.9755 | -3.7684 | -3.7776 | -4.0847 | -4.2306 | -4.6051 | -4.9663 | -5.2878 | -5.6061 | -5.8173 | -6.0122 | -6.5918 | -6.7378 | -6.7612
|  | BARCALDINE | HT |  |  |  |  | -4.0602 | -4.2602 | -4.3827 | -4.5082 | -4.8673 | -5.252 | -5.5051 | -5.8112 | -6.0051 | -6.2102 | -6.702 | -6.95 | -7.0949 | -3.7255 | -4.0245 | -4.1643 | -4.301 | -4.5184 | -4.7592 | -4.9439 | -5.151 | -5.2704 | -5.451 | -5.9622 | -6.0245 | -5.9724 | -3.7684 | -4.0439 | -4.1949 | -4.3418 | -4.7163 | -5.101 | -5.3449 | -5.6337 | -5.801 | -6.0133 | -6.5378 | -6.7051 | -6.7724
|  | BARCALDINE | HE |  |  |  |  | -4.0602 | -4.0867 | -4.3235 | -4.4276 | -4.7908 | -5.1765 | -5.4796 | -5.8204 | -6.0367 | -6.2265 | -6.5418 | -6.7265 | -6.8184 | -3.7245 | -3.7245 | -4.0367 | -4.1704 | -4.3786 | -4.6643 | -4.9071 | -5.1653 | -5.3051 | -5.4673 | -5.7357 | -5.7184 | -5.698 | -3.7684 | -3.7755 | -4.0796 | -4.2316 | -4.5867 | -4.9827 | -5.3041 | -5.649 | -5.8429 | -6.0337 | -6.3418 | -6.4367 | -6.4704
|  | BARCALDINE | FB |  |  |  |  | -4 | -4.002 | -4.002 | -4.4459 | -4.5316 | -4.6276 | -4.802 | -4.8918 | -4.9684 | -4.9786 | -5.2041 | -5.3122 | -5.5143 | -3.6929 | -3.6888 | -3.6867 | -4.0888 | -4.2082 | -4.3378 | -4.5214 | -4.6571 | -4.7367 | -4.7439 | -4.9204 | -5.0459 | -5.3388 | -3.7265 | -3.7143 | -3.7082 | -4.2296 | -4.3571 | -4.4745 | -4.7214 | -4.8459 | -4.9367 | -4.95 | -5.1357 | -5.249 | -5.45
| STORNOWAY | BARVAS | MINIMUM HEADROOM | NB 35613 48891 | NO | YES | 0.148 | 0.75612 | 5.6676 | 5.6604 | 5.5645 | 5.4788 | 5.2798 | 5.0573 | 4.8441 | 4.6145 | 4.4941 | 3.8502 | 3.2298 | 2.7471 | 1.6765 | 6.5951 | 6.5931 | 6.5665 | 6.542 | 6.5145 | 6.4533 | 6.3839 | 6.3298 | 6.3124 | 6.0349 | 6.0033 | 5.9349 | 1.2469 | 6.1655 | 6.138 | 6.0767 | 6.0145 | 5.8676 | 5.6818 | 5.5104 | 5.3461 | 5.3073 | 4.6869 | 4.3757 | 4.1441
|  | BARVAS | EE |  |  |  |  | 0.75612 | 5.6951 | 5.6604 | 5.5706 | 5.49 | 5.2859 | 5.0778 | 4.8624 | 4.6298 | 4.5186 | 3.8502 | 3.2298 | 2.7471 | 1.6765 | 6.6298 | 6.5931 | 6.5676 | 6.5441 | 6.5145 | 6.4563 | 6.388 | 6.3329 | 6.3155 | 6.0349 | 6.0033 | 5.9349 | 1.2469 | 6.1869 | 6.138 | 6.0808 | 6.0227 | 5.8706 | 5.6951 | 5.5247 | 5.3614 | 5.3257 | 4.6869 | 4.3757 | 4.1441
|  | BARVAS | HT |  |  |  |  | 0.75612 | 5.6676 | 5.6665 | 5.5757 | 5.5002 | 5.3155 | 5.1033 | 4.8982 | 4.6757 | 4.5757 | 4.2165 | 3.5267 | 2.8676 | 1.6776 | 6.5951 | 6.5941 | 6.5686 | 6.5451 | 6.5186 | 6.4584 | 6.39 | 6.3339 | 6.3176 | 6.1716 | 6.1502 | 6.1492 | 1.248 | 6.1655 | 6.141 | 6.0859 | 6.0288 | 5.89 | 5.7114 | 5.5461 | 5.3849 | 5.3604 | 5.088 | 4.6604 | 4.2645
|  | BARVAS | HE |  |  |  |  | 0.75612 | 5.6961 | 5.6645 | 5.5645 | 5.4788 | 5.2798 | 5.0573 | 4.8441 | 4.6145 | 4.4941 | 4.1624 | 3.4124 | 2.9849 | 1.6765 | 6.6298 | 6.5931 | 6.5665 | 6.542 | 6.5145 | 6.4533 | 6.3839 | 6.3298 | 6.3124 | 6.2002 | 6.1624 | 6.1594 | 1.248 | 6.1859 | 6.138 | 6.0767 | 6.0145 | 5.8676 | 5.6818 | 5.5104 | 5.3461 | 5.3073 | 5.0614 | 4.589 | 4.3267
|  | BARVAS | FB |  |  |  |  | 0.82755 | 5.791 | 5.8206 | 5.7931 | 5.7849 | 5.7818 | 5.7706 | 5.7308 | 5.7114 | 5.6696 | 5.4257 | 5.1818 | 5.0614 | 1.7143 | 6.6747 | 6.692 | 6.6614 | 6.6645 | 6.6512 | 6.6431 | 6.6165 | 6.6237 | 6.5961 | 6.4727 | 6.2431 | 6.0216 | 1.3194 | 6.2778 | 6.2971 | 6.2635 | 6.2522 | 6.2278 | 6.2104 | 6.1676 | 6.14 | 6.1186 | 5.8767 | 5.6482 | 5.6033
| STORNOWAY | BATTERY POINT | MINIMUM HEADROOM | NB 43147 32182 | NO | YES | 5.152 | 0.46029 | 13.7995 | 13.6076 | 13.2423 | 12.977 | 12.4301 | 11.3597 | 10.1015 | 8.0352 | 6.8964 | 2.1158 | -1.7811 | -4.9658 | 2.6419 | 15.2678 | 15.0811 | 14.8372 | 14.6831 | 14.4219 | 13.6617 | 12.8689 | 11.0811 | 10.2372 | 5.7658 | 2.7474 | -0.25665 | 1.8072 | 14.8046 | 14.6301 | 14.327 | 14.1178 | 13.6862 | 12.6576 | 11.4862 | 9.4321 | 8.4587 | 3.4933 | -0.68931 | -4.2893
|  | BATTERY POINT | EE |  |  |  |  | 0.46743 | 14.0719 | 13.8199 | 13.4056 | 13.1219 | 12.5352 | 11.7648 | 10.6678 | 9.2719 | 8.7209 | 3.576 | -0.018898 | -1.9393 | 2.646 | 15.5831 | 15.325 | 15.0219 | 14.8433 | 14.578 | 14.0382 | 13.3311 | 12.2719 | 11.9097 | 8.074 | 5.2189 | 3.9505 | 1.8133 | 15.078 | 14.8352 | 14.4852 | 14.2525 | 13.7893 | 13.0954 | 12.0607 | 10.6719 | 10.0495 | 5.378 | 1.4484 | -0.40257
|  | BATTERY POINT | HT |  |  |  |  | 0.46029 | 13.7995 | 13.6076 | 13.2423 | 12.977 | 12.4301 | 11.3597 | 10.1015 | 8.0352 | 6.8964 | 3.2464 | -0.69237 | -4.1842 | 2.6419 | 15.2678 | 15.0811 | 14.8372 | 14.6831 | 14.4219 | 13.6617 | 12.8689 | 11.2076 | 10.2372 | 7.375 | 4.1362 | 1.3831 | 1.8072 | 14.8046 | 14.6301 | 14.327 | 14.1178 | 13.6862 | 12.6576 | 11.4862 | 9.4821 | 8.4587 | 4.9046 | 0.65967 | -2.9362
|  | BATTERY POINT | HE |  |  |  |  | 0.46335 | 14.0699 | 13.8056 | 13.3923 | 13.1056 | 12.5291 | 11.7076 | 10.424 | 8.3076 | 7.5536 | 2.1158 | -1.7811 | -4.9658 | 2.644 | 15.5821 | 15.3209 | 15.0168 | 14.8372 | 14.5658 | 13.9933 | 13.0372 | 11.0811 | 10.4954 | 5.7658 | 2.7474 | -0.25665 | 1.8113 | 15.077 | 14.827 | 14.476 | 14.2423 | 13.7801 | 13.0209 | 11.7587 | 9.4321 | 8.6066 | 3.4933 | -0.68931 | -4.2893
|  | BATTERY POINT | FB |  |  |  |  | 0.60722 | 14.3025 | 14.4321 | 14.1342 | 13.9597 | 13.8015 | 13.527 | 12.6678 | 11.9719 | 11.6627 | 9.7178 | 6.9005 | 6.0076 | 2.7297 | 15.6995 | 15.7801 | 15.4505 | 15.2495 | 15.0668 | 14.725 | 13.776 | 12.9729 | 12.6087 | 10.9607 | 8.5546 | 7.1209 | 1.9276 | 15.2525 | 15.3454 | 15.0627 | 14.8933 | 14.7362 | 14.4158 | 13.5138 | 12.7178 | 12.377 | 10.5658 | 7.3944 | 6.524
| DOUNREAY | BETTYHILL | MINIMUM HEADROOM | NC 70763 61645 | YES | NO | 0.132 | 0.1898 | 0.18265 | 0.17245 | 0.1449 | 0.11939 | 0.069388 | 0.033673 | -0.010204 | -0.062245 | -0.11224 | -0.23673 | -0.38061 | -0.50714 | 0.34592 | 0.34082 | 0.33367 | 0.32245 | 0.31633 | 0.29592 | 0.26531 | 0.24286 | 0.21429 | 0.18265 | 0.12245 | 0.12143 | 0.088776 | 0.26633 | 0.2602 | 0.25204 | 0.23163 | 0.21122 | 0.17755 | 0.12755 | 0.093878 | 0.045918 | 0.027551 | -0.062245 | -0.13878 | -0.19796
|  | BETTYHILL | EE |  |  |  |  | 0.19082 | 0.18571 | 0.17551 | 0.14898 | 0.12959 | 0.077551 | 0.042857 | -0.0030612 | -0.057143 | -0.1051 | -0.23673 | -0.38061 | -0.50204 | 0.34694 | 0.34286 | 0.33469 | 0.32449 | 0.31939 | 0.29592 | 0.26531 | 0.24388 | 0.21531 | 0.18571 | 0.13673 | 0.13163 | 0.13673 | 0.26837 | 0.26224 | 0.25408 | 0.23571 | 0.21633 | 0.18061 | 0.13571 | 0.1 | 0.053061 | 0.033673 | -0.062245 | -0.13878 | -0.18163
|  | BETTYHILL | HT |  |  |  |  | 0.19082 | 0.18469 | 0.17347 | 0.15 | 0.12857 | 0.076531 | 0.039796 | -0.0030612 | -0.056122 | -0.10102 | -0.20204 | -0.34388 | -0.50714 | 0.34694 | 0.34286 | 0.33469 | 0.32551 | 0.31837 | 0.29592 | 0.26531 | 0.24286 | 0.21531 | 0.18469 | 0.12245 | 0.12143 | 0.13776 | 0.26837 | 0.26224 | 0.25204 | 0.23469 | 0.21633 | 0.18265 | 0.13367 | 0.09898 | 0.053061 | 0.034694 | -0.045918 | -0.12551 | -0.19592
|  | BETTYHILL | HE |  |  |  |  | 0.1898 | 0.18265 | 0.17245 | 0.1449 | 0.11939 | 0.069388 | 0.033673 | -0.010204 | -0.062245 | -0.11224 | -0.19898 | -0.34796 | -0.47959 | 0.34592 | 0.34082 | 0.33367 | 0.32245 | 0.31633 | 0.29592 | 0.26531 | 0.24286 | 0.21429 | 0.18265 | 0.1398 | 0.12755 | 0.11429 | 0.26633 | 0.2602 | 0.25204 | 0.23163 | 0.21122 | 0.17755 | 0.12755 | 0.093878 | 0.045918 | 0.027551 | -0.039796 | -0.13367 | -0.19796
|  | BETTYHILL | FB |  |  |  |  | 0.21633 | 0.21429 | 0.21633 | 0.20816 | 0.20714 | 0.19592 | 0.18469 | 0.16327 | 0.15 | 0.13061 | 0.047959 | -0.033673 | -0.062245 | 0.36837 | 0.36633 | 0.36531 | 0.35612 | 0.35612 | 0.34796 | 0.3398 | 0.32041 | 0.30918 | 0.29388 | 0.21939 | 0.14286 | 0.088776 | 0.29082 | 0.28878 | 0.29082 | 0.28367 | 0.28061 | 0.27143 | 0.26531 | 0.2449 | 0.23265 | 0.21327 | 0.12653 | 0.046939 | 0.034694
| GRUDIE BRIDGE | BIDEN CLAN RAONAILD | MINIMUM HEADROOM | NH 06927 58342 | YES | NO | 0 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033
|  | BIDEN CLAN RAONAILD | EE |  |  |  |  | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033
|  | BIDEN CLAN RAONAILD | HT |  |  |  |  | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033
|  | BIDEN CLAN RAONAILD | HE |  |  |  |  | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033
|  | BIDEN CLAN RAONAILD | FB |  |  |  |  | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.1078 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033 | 0.1033
| ELGIN | BILBOHALL | MINIMUM HEADROOM | NJ 20782 61556 | YES | YES | 5.055 | 7.2226 | 16.3395 | 16.3212 | 16.2875 | 16.2609 | 16.1375 | 15.9936 | 15.7926 | 15.5681 | 15.464 | 14.8844 | 14.366 | 14.013 | 7.0691 | 16.0426 | 16.0018 | 15.9426 | 15.8763 | 15.7905 | 15.7069 | 15.5885 | 15.4977 | 15.414 | 15.2865 | 15.2803 | 15.266 | 7.3581 | 16.4079 | 16.3854 | 16.3375 | 16.2946 | 16.2099 | 16.1099 | 15.9538 | 15.7773 | 15.6814 | 15.2518 | 14.9181 | 14.6875
|  | BILBOHALL | EE |  |  |  |  | 7.2226 | 16.3405 | 16.3212 | 16.2977 | 16.2609 | 16.1416 | 16.0222 | 15.8497 | 15.6895 | 15.5834 | 14.8844 | 14.366 | 14.0375 | 7.0691 | 16.0426 | 16.0018 | 15.9426 | 15.8763 | 15.7916 | 15.714 | 15.5997 | 15.5181 | 15.4344 | 15.3344 | 15.3099 | 15.3446 | 7.3581 | 16.4089 | 16.3854 | 16.3375 | 16.2967 | 16.213 | 16.1283 | 15.9895 | 15.8558 | 15.7579 | 15.2518 | 14.9181 | 14.6875
|  | BILBOHALL | HT |  |  |  |  | 7.2246 | 16.3416 | 16.3273 | 16.2875 | 16.2722 | 16.1558 | 15.9936 | 15.7926 | 15.5681 | 15.464 | 14.9752 | 14.4579 | 14.013 | 7.0691 | 16.0426 | 16.0028 | 15.9436 | 15.8773 | 15.7916 | 15.7069 | 15.5885 | 15.4977 | 15.414 | 15.2865 | 15.2803 | 15.3099 | 7.3591 | 16.4089 | 16.3905 | 16.3477 | 16.3028 | 16.2232 | 16.1099 | 15.9538 | 15.7773 | 15.6814 | 15.3028 | 14.9783 | 14.7069
|  | BILBOHALL | HE |  |  |  |  | 7.2246 | 16.3395 | 16.3252 | 16.2967 | 16.2609 | 16.1375 | 16.0191 | 15.8416 | 15.6722 | 15.564 | 14.9885 | 14.4824 | 14.1967 | 7.0691 | 16.0426 | 16.0028 | 15.9436 | 15.8773 | 15.7905 | 15.714 | 15.5987 | 15.5181 | 15.4344 | 15.3303 | 15.3058 | 15.2997 | 7.3591 | 16.4079 | 16.3895 | 16.3385 | 16.2946 | 16.2099 | 16.1252 | 15.9844 | 15.8426 | 15.7456 | 15.3181 | 14.9926 | 14.7987
|  | BILBOHALL | FB |  |  |  |  | 7.2552 | 16.3875 | 16.3956 | 16.3824 | 16.3732 | 16.3385 | 16.3385 | 16.3007 | 16.2467 | 16.2171 | 15.7956 | 15.4171 | 15.266 | 7.0895 | 16.0793 | 16.064 | 16.0303 | 15.9936 | 15.9426 | 15.914 | 15.8538 | 15.7865 | 15.7426 | 15.466 | 15.3456 | 15.266 | 7.3816 | 16.4487 | 16.4507 | 16.4334 | 16.415 | 16.3814 | 16.3609 | 16.3252 | 16.2926 | 16.2865 | 15.9477 | 15.6058 | 15.5528
| RANNOCH | BLACKMOUNT | MINIMUM HEADROOM | NN 30077 41404 | YES | YES | 0 | 0.036551 | 0.037571 | 0.037571 | 0.027367 | 0.027367 | 0.027367 | 0.027367 | 0.021245 | 0.020224 | 0.017163 | 0.013082 | 0.011041 | 0.0079796 | 0.040214 | 0.040214 | 0.041235 | 0.031031 | 0.03001 | 0.02899 | 0.02899 | 0.025929 | 0.024908 | 0.022867 | 0.019806 | 0.021847 | 0.020827 | 0.038383 | 0.038383 | 0.038383 | 0.029199 | 0.028179 | 0.028179 | 0.028179 | 0.021036 | 0.018995 | 0.015934 | 0.011852 | 0.013893 | 0.010832
|  | BLACKMOUNT | EE |  |  |  |  | 0.036551 | 0.037571 | 0.037571 | 0.027367 | 0.028388 | 0.028388 | 0.027367 | 0.021245 | 0.020224 | 0.017163 | 0.014102 | 0.011041 | 0.009 | 0.040214 | 0.040214 | 0.041235 | 0.031031 | 0.03001 | 0.031031 | 0.031031 | 0.025929 | 0.024908 | 0.022867 | 0.020827 | 0.021847 | 0.021847 | 0.038383 | 0.038383 | 0.038383 | 0.029199 | 0.029199 | 0.028179 | 0.028179 | 0.021036 | 0.020015 | 0.016954 | 0.013893 | 0.013893 | 0.012872
|  | BLACKMOUNT | HT |  |  |  |  | 0.036551 | 0.037571 | 0.037571 | 0.028388 | 0.028388 | 0.028388 | 0.028388 | 0.022265 | 0.021245 | 0.018184 | 0.013082 | 0.012061 | 0.0079796 | 0.040214 | 0.040214 | 0.041235 | 0.031031 | 0.03001 | 0.031031 | 0.031031 | 0.025929 | 0.025929 | 0.022867 | 0.019806 | 0.021847 | 0.020827 | 0.038383 | 0.038383 | 0.038383 | 0.029199 | 0.029199 | 0.028179 | 0.028179 | 0.021036 | 0.020015 | 0.016954 | 0.011852 | 0.014913 | 0.010832
|  | BLACKMOUNT | HE |  |  |  |  | 0.036551 | 0.037571 | 0.037571 | 0.027367 | 0.027367 | 0.028388 | 0.027367 | 0.021245 | 0.020224 | 0.017163 | 0.015122 | 0.012061 | 0.011041 | 0.040214 | 0.040214 | 0.041235 | 0.031031 | 0.03001 | 0.031031 | 0.031031 | 0.025929 | 0.024908 | 0.022867 | 0.021847 | 0.021847 | 0.022867 | 0.038383 | 0.038383 | 0.038383 | 0.029199 | 0.028179 | 0.028179 | 0.028179 | 0.021036 | 0.018995 | 0.015934 | 0.014913 | 0.014913 | 0.013893
|  | BLACKMOUNT | FB |  |  |  |  | 0.036551 | 0.037571 | 0.037571 | 0.038592 | 0.038592 | 0.027367 | 0.028388 | 0.030429 | 0.028388 | 0.028388 | 0.026347 | 0.020224 | 0.018184 | 0.040214 | 0.040214 | 0.041235 | 0.041235 | 0.041235 | 0.02899 | 0.02899 | 0.033071 | 0.02899 | 0.02899 | 0.027969 | 0.024908 | 0.021847 | 0.038383 | 0.038383 | 0.038383 | 0.038383 | 0.038383 | 0.028179 | 0.028179 | 0.03226 | 0.029199 | 0.029199 | 0.026138 | 0.020015 | 0.015934
| BEAULY | BLACKSTAND | MINIMUM HEADROOM | NH 71036 59151 | YES | NO | 0.15 | 4.1851 | 4.1749 | 4.1586 | 4.1076 | 4.0392 | 3.878 | 3.7392 | 3.5586 | 3.4259 | 3.4035 | 2.9892 | 2.5443 | 2.1504 | 4.8655 | 4.8512 | 4.8308 | 4.788 | 4.7655 | 4.7053 | 4.6206 | 4.5176 | 4.4573 | 4.4757 | 4.2512 | 4.2165 | 4.0135 | 4.6345 | 4.6049 | 4.5763 | 4.4988 | 4.462 | 4.3416 | 4.2253 | 4.0733 | 3.9671 | 3.9671 | 3.6324 | 3.3641 | 3.162
|  | BLACKSTAND | EE |  |  |  |  | 4.1851 | 4.1749 | 4.1586 | 4.1147 | 4.0545 | 3.878 | 3.7647 | 3.5882 | 3.4586 | 3.4463 | 2.9892 | 2.5443 | 2.2096 | 4.8655 | 4.8512 | 4.8308 | 4.791 | 4.7686 | 4.7053 | 4.6247 | 4.5186 | 4.4624 | 4.4849 | 4.2798 | 4.2553 | 4.2124 | 4.6355 | 4.6049 | 4.5763 | 4.5039 | 4.4712 | 4.3416 | 4.2416 | 4.0937 | 3.9886 | 3.9957 | 3.6324 | 3.3743 | 3.208
|  | BLACKSTAND | HT |  |  |  |  | 4.1861 | 4.1759 | 4.1606 | 4.1188 | 4.0535 | 3.9239 | 3.7729 | 3.5953 | 3.4637 | 3.4535 | 3.1004 | 2.6147 | 2.1504 | 4.8655 | 4.8512 | 4.8308 | 4.79 | 4.7676 | 4.7104 | 4.6247 | 4.5176 | 4.4635 | 4.4818 | 4.2512 | 4.238 | 4.241 | 4.6345 | 4.6069 | 4.5784 | 4.5059 | 4.4702 | 4.3692 | 4.2457 | 4.0967 | 3.9916 | 3.9988 | 3.6855 | 3.4039 | 3.162
|  | BLACKSTAND | HE |  |  |  |  | 4.1861 | 4.1759 | 4.1606 | 4.1076 | 4.0392 | 3.882 | 3.7392 | 3.5586 | 3.4259 | 3.4035 | 3.0871 | 2.5851 | 2.2984 | 4.8655 | 4.8512 | 4.8308 | 4.788 | 4.7655 | 4.7063 | 4.6206 | 4.5196 | 4.4573 | 4.4757 | 4.2839 | 4.239 | 4.1645 | 4.6345 | 4.6069 | 4.5773 | 4.4988 | 4.462 | 4.3437 | 4.2253 | 4.0733 | 3.9671 | 3.9671 | 3.6886 | 3.3641 | 3.1804
|  | BLACKSTAND | FB |  |  |  |  | 4.2371 | 4.2555 | 4.281 | 4.2678 | 4.2535 | 4.232 | 4.2076 | 4.1555 | 4.1188 | 4.0565 | 3.8831 | 3.5606 | 3.4514 | 4.8961 | 4.9022 | 4.9104 | 4.8931 | 4.8849 | 4.8441 | 4.8155 | 4.7655 | 4.7257 | 4.6676 | 4.5359 | 4.2165 | 4.0135 | 4.6845 | 4.6804 | 4.6927 | 4.6661 | 4.6447 | 4.5978 | 4.5702 | 4.5171 | 4.4773 | 4.4386 | 4.2916 | 3.9651 | 3.9151
| COUPAR ANGUS | BLAIRGOWRIE | MINIMUM HEADROOM | NO 18741 44551 | NO | NO | 2.031 | 13.4936 | 13.3528 | 13.1528 | 12.7405 | 12.5497 | 11.6926 | 10.7701 | 9.8181 | 8.7752 | 8.2987 | 5.1885 | 2.4711 | 1.0222 | 15.113 | 15.0211 | 14.8895 | 14.5905 | 14.3956 | 13.8875 | 13.3477 | 12.7599 | 12.0997 | 11.8405 | 9.9813 | 9.1089 | 8.5568 | 14.4655 | 14.3349 | 14.1155 | 13.7074 | 13.4614 | 12.6798 | 11.8727 | 11.0237 | 10.0747 | 9.7176 | 7.0145 | 5.0421 | 4.0033
|  | BLAIRGOWRIE | EE |  |  |  |  | 13.4936 | 13.3528 | 13.1528 | 12.7824 | 12.5946 | 11.7252 | 10.8691 | 9.9681 | 8.9752 | 8.4344 | 5.1885 | 2.4711 | 1.0222 | 15.114 | 15.0222 | 14.8895 | 14.6089 | 14.415 | 13.912 | 13.3854 | 12.8303 | 12.1783 | 11.8548 | 10.0273 | 9.1089 | 8.5568 | 14.4655 | 14.3349 | 14.1155 | 13.737 | 13.491 | 12.7155 | 11.9492 | 11.1421 | 10.2257 | 9.7676 | 7.0145 | 5.0421 | 4.0033
|  | BLAIRGOWRIE | HT |  |  |  |  | 13.4946 | 13.3558 | 13.1701 | 12.7405 | 12.5579 | 11.7048 | 10.8293 | 9.8905 | 8.8426 | 8.3426 | 5.2007 | 2.6824 | 1.3099 | 15.113 | 15.0211 | 14.8905 | 14.5905 | 14.3956 | 13.8926 | 13.3834 | 12.8099 | 12.1181 | 11.8405 | 9.9813 | 9.2089 | 9.0456 | 14.4665 | 14.337 | 14.1237 | 13.7074 | 13.4625 | 12.6961 | 11.9318 | 11.1043 | 10.1329 | 9.7216 | 7.039 | 5.2288 | 4.3339
|  | BLAIRGOWRIE | HE |  |  |  |  | 13.4936 | 13.3528 | 13.1609 | 12.7538 | 12.5497 | 11.6926 | 10.7701 | 9.8181 | 8.7752 | 8.2987 | 5.7191 | 3.2181 | 2.2242 | 15.113 | 15.0222 | 14.8905 | 14.6017 | 14.4048 | 13.8875 | 13.3477 | 12.7599 | 12.0997 | 11.8854 | 10.4568 | 9.4773 | 9.0783 | 14.4665 | 14.3359 | 14.1186 | 13.7176 | 13.4614 | 12.6798 | 11.8727 | 11.0237 | 10.0747 | 9.7176 | 7.54 | 5.6543 | 4.9563
|  | BLAIRGOWRIE | FB |  |  |  |  | 13.6834 | 13.5609 | 13.5497 | 13.4364 | 13.4068 | 13.1109 | 12.9303 | 12.5813 | 12.1558 | 11.9262 | 10.4864 | 8.1885 | 6.6568 | 15.2803 | 15.1477 | 15.1375 | 15.0742 | 15.0283 | 14.762 | 14.6395 | 14.3415 | 14.0007 | 13.7099 | 12.3354 | 10.516 | 8.7609 | 14.6023 | 14.5421 | 14.4921 | 14.3655 | 14.3125 | 14.0084 | 13.8431 | 13.491 | 13.0778 | 12.79 | 11.2676 | 8.8523 | 7.6931
| STRATHLEVEN | BLAIRLINNANS | MINIMUM HEADROOM | NS 40709 85121 | YES | YES | 0.069 | 0.44694 | 0.44184 | 0.43878 | 0.43878 | 0.42857 | 0.41633 | 0.4051 | 0.39592 | 0.38163 | 0.37551 | 0.34184 | 0.31327 | 0.29898 | 0.57857 | 0.57551 | 0.57143 | 0.57041 | 0.56429 | 0.55918 | 0.54898 | 0.54796 | 0.53571 | 0.53163 | 0.49898 | 0.50204 | 0.50204 | 0.53878 | 0.53265 | 0.52857 | 0.52857 | 0.52041 | 0.51224 | 0.50204 | 0.4949 | 0.48265 | 0.47755 | 0.44796 | 0.43061 | 0.42143
|  | BLAIRLINNANS | EE |  |  |  |  | 0.45 | 0.44184 | 0.44184 | 0.43878 | 0.42959 | 0.41735 | 0.4051 | 0.39694 | 0.38163 | 0.37653 | 0.34184 | 0.31327 | 0.31837 | 0.58163 | 0.57551 | 0.57449 | 0.57143 | 0.56531 | 0.55918 | 0.54898 | 0.54796 | 0.53571 | 0.53367 | 0.5051 | 0.50714 | 0.51327 | 0.54082 | 0.53265 | 0.53163 | 0.52959 | 0.52143 | 0.51531 | 0.50204 | 0.4949 | 0.48265 | 0.48061 | 0.44796 | 0.43061 | 0.42551
|  | BLAIRLINNANS | HT |  |  |  |  | 0.45 | 0.44286 | 0.44184 | 0.44082 | 0.42959 | 0.42041 | 0.40816 | 0.4 | 0.38571 | 0.37857 | 0.34898 | 0.32041 | 0.31633 | 0.58163 | 0.57653 | 0.57143 | 0.57143 | 0.56429 | 0.55918 | 0.54898 | 0.54796 | 0.53571 | 0.53265 | 0.49898 | 0.50204 | 0.51122 | 0.54082 | 0.53265 | 0.52959 | 0.53061 | 0.52143 | 0.51327 | 0.50408 | 0.49694 | 0.48571 | 0.47959 | 0.45102 | 0.43469 | 0.42551
|  | BLAIRLINNANS | HE |  |  |  |  | 0.44694 | 0.44286 | 0.43878 | 0.43878 | 0.42857 | 0.41633 | 0.4051 | 0.39592 | 0.38163 | 0.37551 | 0.34694 | 0.31837 | 0.29898 | 0.57857 | 0.57551 | 0.57143 | 0.57041 | 0.56429 | 0.55918 | 0.54898 | 0.54796 | 0.53571 | 0.53163 | 0.5051 | 0.5051 | 0.5051 | 0.53878 | 0.53265 | 0.52857 | 0.52857 | 0.52041 | 0.51224 | 0.50204 | 0.4949 | 0.48265 | 0.47755 | 0.45102 | 0.43265 | 0.42143
|  | BLAIRLINNANS | FB |  |  |  |  | 0.45612 | 0.45306 | 0.45714 | 0.45204 | 0.44898 | 0.44592 | 0.4398 | 0.4398 | 0.43367 | 0.42959 | 0.40918 | 0.38367 | 0.37551 | 0.58776 | 0.58469 | 0.58367 | 0.57857 | 0.57959 | 0.57755 | 0.57041 | 0.56735 | 0.56327 | 0.55714 | 0.54082 | 0.51531 | 0.50204 | 0.54694 | 0.54286 | 0.54388 | 0.53878 | 0.53776 | 0.53469 | 0.52959 | 0.52959 | 0.52551 | 0.52245 | 0.50306 | 0.47245 | 0.47143
| BOAT OF GARTEN | BOAT OF GARTEN | MINIMUM HEADROOM | NH 95609 19427 | NO | YES | 0.436 | 7.4143 | 7.3867 | 7.3765 | 7.3367 | 7.2969 | 7.1949 | 7.0755 | 6.9622 | 6.8541 | 6.7622 | 6.6224 | 6.3582 | 6.1224 | 8.8694 | 8.8551 | 8.8367 | 8.801 | 8.7827 | 8.7337 | 8.6469 | 8.5714 | 8.499 | 8.4367 | 8.3582 | 8.3643 | 8.2367 | 8.2561 | 8.2276 | 8.2112 | 8.1592 | 8.1265 | 8.0653 | 7.9561 | 7.8561 | 7.7612 | 7.6806 | 7.5622 | 7.4316 | 7.3276
|  | BOAT OF GARTEN | EE |  |  |  |  | 7.4143 | 7.3867 | 7.3765 | 7.3449 | 7.3102 | 7.201 | 7.0929 | 6.9878 | 6.8867 | 6.7888 | 6.6224 | 6.3582 | 6.1602 | 8.8704 | 8.8551 | 8.8367 | 8.8031 | 8.7857 | 8.7337 | 8.649 | 8.5724 | 8.5031 | 8.4418 | 8.3888 | 8.3735 | 8.3908 | 8.2571 | 8.2276 | 8.2112 | 8.1673 | 8.1347 | 8.0704 | 7.9673 | 7.8724 | 7.7837 | 7.7071 | 7.5622 | 7.4316 | 7.3541
|  | BOAT OF GARTEN | HT |  |  |  |  | 7.4163 | 7.3878 | 7.3786 | 7.3439 | 7.3092 | 7.2255 | 7.1122 | 7.0031 | 6.9061 | 6.8071 | 6.6745 | 6.4061 | 6.1224 | 8.8694 | 8.8551 | 8.8367 | 8.8031 | 8.7827 | 8.7357 | 8.6469 | 8.5745 | 8.5031 | 8.4418 | 8.3582 | 8.3714 | 8.4296 | 8.2561 | 8.2286 | 8.2133 | 8.1673 | 8.1327 | 8.0867 | 7.9806 | 7.8837 | 7.7959 | 7.7194 | 7.5908 | 7.452 | 7.3276
|  | BOAT OF GARTEN | HE |  |  |  |  | 7.4163 | 7.3878 | 7.3796 | 7.3367 | 7.2969 | 7.1949 | 7.0755 | 6.9622 | 6.8541 | 6.7622 | 6.6704 | 6.3939 | 6.1929 | 8.8714 | 8.8551 | 8.8378 | 8.801 | 8.7827 | 8.7337 | 8.649 | 8.5714 | 8.499 | 8.4367 | 8.3918 | 8.3643 | 8.3327 | 8.2582 | 8.2286 | 8.2143 | 8.1592 | 8.1265 | 8.0653 | 7.9561 | 7.8561 | 7.7612 | 7.6806 | 7.5959 | 7.4347 | 7.3286
|  | BOAT OF GARTEN | FB |  |  |  |  | 7.4806 | 7.4765 | 7.4867 | 7.4949 | 7.4939 | 7.4622 | 7.448 | 7.4224 | 7.3847 | 7.3582 | 7.1571 | 7.0398 | 6.9724 | 8.9276 | 8.9153 | 8.9153 | 8.9133 | 8.9112 | 8.8724 | 8.852 | 8.8082 | 8.7612 | 8.7306 | 8.5347 | 8.3929 | 8.2367 | 8.3153 | 8.3051 | 8.3092 | 8.3092 | 8.3061 | 8.2806 | 8.2684 | 8.2245 | 8.1837 | 8.1551 | 7.9806 | 7.849 | 7.8194
| PETERHEAD SHELL | BODDAM | MINIMUM HEADROOM | NK 12219 42512 | YES | NO | 1.41 | -1.2472 | -1.3043 | -1.3615 | -1.4411 | -2.2584 | -3.0043 | -3.8064 | -3.9186 | -4.0247 | -4.0962 | -5.8227 | -6.14 | -6.3502 | 0.26302 | 0.21506 | 0.16506 | 0.10689 | -0.70739 | -1.4513 | -2.2258 | -2.2819 | -2.3431 | -2.3768 | -3.9349 | -4.0196 | -4.0421 | -0.12678 | -0.17882 | -0.23086 | -0.30025 | -1.0778 | -1.7972 | -2.5492 | -2.6196 | -2.7074 | -2.7625 | -4.3574 | -4.6094 | -4.7533
|  | BODDAM | EE |  |  |  |  | -1.24 | -1.3043 | -1.3615 | -1.4411 | -2.2574 | -3.0002 | -3.8064 | -3.9186 | -4.0247 | -4.0962 | -5.8227 | -6.1298 | -6.3115 | 0.27322 | 0.21506 | 0.16506 | 0.10893 | -0.70637 | -1.4421 | -2.2176 | -2.2819 | -2.338 | -2.3727 | -3.9278 | -4.0094 | -4.0421 | -0.11964 | -0.17882 | -0.23086 | -0.30025 | -1.0768 | -1.7921 | -2.5278 | -2.6196 | -2.7074 | -2.7625 | -4.3574 | -4.587 | -4.7196
|  | BODDAM | HT |  |  |  |  | -1.2441 | -1.3002 | -1.3564 | -1.436 | -2.2533 | -2.3574 | -2.489 | -2.5758 | -3.0717 | -3.8962 | -5.8043 | -6.14 | -6.3502 | 0.26812 | 0.21608 | 0.16608 | 0.10996 | -0.70535 | -0.78086 | -0.86556 | -0.90739 | -1.3717 | -2.1809 | -3.9349 | -4.0196 | -4.038 | -0.12372 | -0.17372 | -0.22678 | -0.29719 | -1.0747 | -1.1829 | -1.2962 | -1.3431 | -1.8043 | -2.5768 | -4.3533 | -4.6094 | -4.7533
|  | BODDAM | HE |  |  |  |  | -1.2472 | -1.3013 | -1.3543 | -1.438 | -2.2584 | -3.0043 | -3.8023 | -3.8931 | -4.0074 | -4.0707 | -5.6696 | -5.8727 | -5.9921 | 0.26302 | 0.21506 | 0.16506 | 0.10689 | -0.70739 | -1.4513 | -2.2258 | -2.2727 | -2.3431 | -2.3768 | -3.8849 | -3.8839 | -3.8809 | -0.12678 | -0.17474 | -0.22474 | -0.29617 | -1.0778 | -1.7972 | -2.5492 | -2.5972 | -2.6941 | -2.7462 | -4.236 | -4.3656 | -4.44
|  | BODDAM | FB |  |  |  |  | -1.1931 | -1.2268 | -1.2696 | -1.3135 | -1.6645 | -2.2054 | -2.8931 | -3.6962 | -3.7135 | -3.8462 | -4.437 | -5.2278 | -5.3829 | 0.31404 | 0.27934 | 0.23649 | 0.19873 | -0.15229 | -0.70433 | -1.4043 | -2.2288 | -2.238 | -2.3615 | -2.9329 | -3.7023 | -3.8309 | -0.075759 | -0.10637 | -0.14821 | -0.188 | -0.51964 | -1.0329 | -1.686 | -2.4533 | -2.4686 | -2.5982 | -3.1707 | -3.9319 | -4.039
| TUMMEL BRIDGE | BONSKEID | MINIMUM HEADROOM | NN 90919 60658 | YES | YES | 0.304 | 0.63469 | 0.62245 | 0.59592 | 0.53776 | 0.29082 | 0.14286 | -0.046939 | -0.24286 | -0.44592 | -0.58265 | -1.0969 | -1.5224 | -1.6204 | -1.6235 | -1.6286 | -1.6418 | -1.6633 | -1.7602 | -1.8398 | -1.9776 | -2.1398 | -2.2867 | -2.349 | -2.6918 | -2.8714 | -2.8449 | -2.3582 | -2.3612 | -2.3714 | -2.399 | -2.4133 | -2.5245 | -2.599 | -2.6684 | -2.7449 | -2.8041 | -3.2551 | -3.598 | -3.6296
|  | BONSKEID | EE |  |  |  |  | 0.64694 | 0.62653 | 0.6051 | 0.55102 | 0.48878 | 0.1602 | -0.023469 | -0.18061 | -0.3949 | -0.4949 | -1.0969 | -1.5224 | -1.6194 | -1.6173 | -1.6255 | -1.6316 | -1.6469 | -1.6622 | -1.8235 | -1.951 | -2.0582 | -2.2173 | -2.2796 | -2.6786 | -2.8714 | -2.8449 | -2.349 | -2.3592 | -2.3602 | -2.3796 | -2.398 | -2.5071 | -2.5571 | -2.6378 | -2.7184 | -2.7653 | -3.2551 | -3.598 | -3.6286
|  | BONSKEID | HT |  |  |  |  | 0.63469 | 0.62245 | 0.59592 | 0.53776 | 0.48163 | 0.16429 | -0.029592 | -0.24286 | -0.44592 | -0.47755 | -1.051 | -1.4408 | -1.6204 | -1.6235 | -1.6286 | -1.6418 | -1.6633 | -1.6786 | -1.8367 | -1.9776 | -2.1398 | -2.2867 | -2.2929 | -2.6918 | -2.8388 | -2.7949 | -2.3582 | -2.3612 | -2.3714 | -2.399 | -2.4133 | -2.5245 | -2.599 | -2.6673 | -2.7449 | -2.7745 | -3.2296 | -3.5347 | -3.6296
|  | BONSKEID | HE |  |  |  |  | 0.63776 | 0.62755 | 0.60204 | 0.54184 | 0.47755 | 0.14286 | -0.046939 | -0.22041 | -0.41939 | -0.58265 | -0.87653 | -1.1592 | -1.2459 | -1.6224 | -1.6265 | -1.6357 | -1.6531 | -1.6694 | -1.8398 | -1.9755 | -2.0959 | -2.2378 | -2.349 | -2.5245 | -2.599 | -2.5827 | -2.3551 | -2.3592 | -2.3643 | -2.3908 | -2.4112 | -2.5245 | -2.5806 | -2.6684 | -2.7449 | -2.8041 | -3.0531 | -3.25 | -3.2806
|  | BONSKEID | FB |  |  |  |  | 0.68061 | 0.67041 | 0.66939 | 0.62551 | 0.29082 | 0.26735 | 0.22959 | 0.20204 | 0.15102 | 0.11429 | -0.056122 | -0.25918 | -0.53367 | -1.598 | -1.5959 | -1.5939 | -1.6071 | -1.7602 | -1.7776 | -1.8071 | -1.8245 | -1.8673 | -1.902 | -2.0469 | -2.2459 | -2.5531 | -2.3224 | -2.3214 | -2.3153 | -2.3255 | -2.3929 | -2.402 | -2.4153 | -2.4306 | -2.4592 | -2.4765 | -2.5908 | -2.7418 | -2.8245
| PORT ANN | BOWMORE | MINIMUM HEADROOM | NR 32021 60211 | NO | YES | 0.841 | 4.7139 | 4.568 | 4.4731 | 4.3384 | 4.1271 | 3.7741 | 3.2333 | 2.7353 | 1.4588 | 1.1476 | -0.97796 | -3.0524 | -4.8933 | 5.0159 | 4.8802 | 4.8516 | 4.7741 | 4.6006 | 4.3537 | 3.822 | 3.2945 | 1.7935 | 1.4271 | -0.90755 | -3.2596 | -5.4678 | 4.7812 | 4.5894 | 4.5027 | 4.4047 | 4.1986 | 3.8792 | 3.2935 | 2.7445 | 1.2251 | 0.87102 | -1.5514 | -4.0249 | -6.2851
|  | BOWMORE | EE |  |  |  |  | 4.7159 | 4.5751 | 4.4731 | 4.3384 | 4.1271 | 3.7761 | 3.3118 | 2.9016 | 2.1547 | 1.9547 | 0.31694 | -1.929 | -2.9167 | 5.0169 | 4.8812 | 4.8516 | 4.7751 | 4.6006 | 4.368 | 3.97 | 3.5384 | 2.6924 | 2.47 | 0.81898 | -1.6994 | -2.7708 | 4.7833 | 4.5945 | 4.5027 | 4.4047 | 4.1986 | 3.8884 | 3.419 | 2.9649 | 2.1129 | 1.9067 | 0.14245 | -2.4841 | -3.6004
|  | BOWMORE | HT |  |  |  |  | 4.7149 | 4.5751 | 4.4843 | 4.3598 | 4.1465 | 3.7741 | 3.2333 | 2.7353 | 1.8067 | 1.4006 | -0.013673 | -2.5106 | -4.5086 | 5.0169 | 4.8812 | 4.8527 | 4.7741 | 4.6037 | 4.3537 | 3.822 | 3.2945 | 2.2537 | 1.8445 | 0.31694 | -2.4963 | -4.7586 | 4.7833 | 4.5955 | 4.5108 | 4.418 | 4.2108 | 3.8792 | 3.2935 | 2.7445 | 1.6741 | 1.2476 | -0.31673 | -3.2463 | -5.6096
|  | BOWMORE | HE |  |  |  |  | 4.7139 | 4.568 | 4.4771 | 4.3547 | 4.1455 | 3.7792 | 3.3639 | 2.7496 | 1.4588 | 1.1476 | -0.97796 | -3.0524 | -4.8933 | 5.0159 | 4.8802 | 4.8516 | 4.7741 | 4.6027 | 4.3649 | 3.9853 | 3.3159 | 1.7935 | 1.4271 | -0.90755 | -3.2596 | -5.4678 | 4.7812 | 4.5894 | 4.5057 | 4.4149 | 4.2098 | 3.8884 | 3.4537 | 2.7588 | 1.2251 | 0.87102 | -1.5514 | -4.0249 | -6.2851
|  | BOWMORE | FB |  |  |  |  | 4.7476 | 4.7802 | 4.7537 | 4.7812 | 4.472 | 4.4139 | 4.2271 | 3.969 | 3.5455 | 3.2598 | 2.4241 | 1.3741 | 0.59041 | 5.0424 | 5.0496 | 5.0404 | 5.0527 | 4.7782 | 4.7322 | 4.5241 | 4.2282 | 3.7016 | 3.4047 | 2.5353 | 1.3843 | 0.47 | 4.8312 | 4.8292 | 4.7873 | 4.8016 | 4.4639 | 4.4088 | 4.1904 | 3.9078 | 3.3894 | 3.0741 | 2.1833 | 0.87408 | 0.21286
| SHETLAND | BRAE | MINIMUM HEADROOM | HU3604068816 | YES | YES | 0.995 | -1.436 | -1.4054 | -1.3952 | -1.7268 | -2.1085 | -2.5034 | -2.9024 | -3.0105 | -3.1136 | -3.1758 | -3.6238 | -3.7748 | -3.9034 | -0.58603 | -0.57991 | -0.58603 | -0.90644 | -1.282 | -1.6534 | -2.0432 | -2.1013 | -2.1156 | -2.1564 | -2.5585 | -2.5534 | -2.5728 | -1.0901 | -1.084 | -1.0952 | -1.4503 | -1.8003 | -2.1544 | -2.5279 | -2.6085 | -2.686 | -2.7442 | -3.1595 | -3.2513 | -3.3217
|  | BRAE | EE |  |  |  |  | -1.435 | -1.4054 | -1.3952 | -1.7248 | -2.1044 | -2.5034 | -2.9024 | -3.0105 | -3.1136 | -3.1758 | -3.6238 | -3.7748 | -3.8758 | -0.58195 | -0.57991 | -0.58603 | -0.90644 | -1.282 | -1.6534 | -2.0432 | -2.0809 | -2.1156 | -2.1564 | -2.5401 | -2.533 | -2.5197 | -1.085 | -1.084 | -1.0952 | -1.4493 | -1.7871 | -2.1544 | -2.5279 | -2.6085 | -2.686 | -2.7442 | -3.1595 | -3.2483 | -3.2983
|  | BRAE | HT |  |  |  |  | -1.435 | -1.4003 | -1.3891 | -1.7105 | -2.0871 | -2.1697 | -2.2534 | -2.3534 | -2.5799 | -2.9136 | -3.5789 | -3.7585 | -3.9034 | -0.58603 | -0.57991 | -0.58399 | -0.9044 | -1.2809 | -1.3013 | -1.335 | -1.3707 | -1.5544 | -1.9075 | -2.5585 | -2.5534 | -2.5238 | -1.0901 | -1.0809 | -1.0911 | -1.4391 | -1.8003 | -1.8381 | -1.8962 | -1.9728 | -2.1758 | -2.5044 | -3.1432 | -3.2452 | -3.3217
|  | BRAE | HE |  |  |  |  | -1.436 | -1.4044 | -1.3932 | -1.7268 | -2.1085 | -2.4962 | -2.886 | -2.9911 | -3.0891 | -3.1564 | -3.5687 | -3.7677 | -3.8758 | -0.58501 | -0.57889 | -0.58501 | -0.90542 | -1.282 | -1.6534 | -2.0432 | -2.0799 | -2.1115 | -2.1513 | -2.535 | -2.5401 | -2.5462 | -1.0891 | -1.084 | -1.0942 | -1.4503 | -1.7881 | -2.1534 | -2.5166 | -2.5952 | -2.6697 | -2.7309 | -3.1238 | -3.2513 | -3.3126
|  | BRAE | FB |  |  |  |  | -1.4003 | -1.3493 | -1.3105 | -1.3881 | -1.6207 | -1.9146 | -2.2697 | -2.6677 | -2.6768 | -2.6738 | -2.8513 | -3.0962 | -3.1513 | -0.53705 | -0.52685 | -0.52583 | -0.62175 | -0.89726 | -1.236 | -1.6462 | -2.1013 | -2.1105 | -2.1228 | -2.2993 | -2.5105 | -2.5728 | -1.0462 | -1.0268 | -1.0156 | -1.1207 | -1.3605 | -1.6544 | -2.0105 | -2.4146 | -2.4238 | -2.4279 | -2.6105 | -2.8656 | -2.8636
| BRIDGE OF DUN | BRECHIN | MINIMUM HEADROOM | NO 60998 59682 | NO | NO | 2.524 | 4.1951 | 4.0931 | 4.0165 | 3.8543 | 3.3798 | 3.0645 | 2.1451 | 0.92673 | -1.3222 | -2.061 | -6.4824 | -11.1253 | -14.7365 | 6.1089 | 6.013 | 5.9711 | 5.8864 | 5.4548 | 5.2915 | 4.4926 | 3.4446 | 1.0262 | 0.33745 | -4.0074 | -8.5462 | -12.4503 | 4.8051 | 4.6693 | 4.6326 | 4.5244 | 4.0836 | 3.852 | 2.9785 | 1.8622 | -0.68985 | -1.4511 | -6.0878 | -11.1552 | -15.3041
|  | BRECHIN | EE |  |  |  |  | 4.1961 | 4.0951 | 4.0645 | 3.9492 | 3.4737 | 3.1522 | 2.4135 | 1.3696 | 0.037959 | -0.51714 | -4.659 | -9.4131 | -11.6345 | 6.1099 | 6.015 | 5.9977 | 5.9395 | 5.5109 | 5.3477 | 4.7997 | 3.8701 | 2.5681 | 2.1334 | -1.3564 | -5.833 | -7.7391 | 4.8071 | 4.6693 | 4.6632 | 4.5857 | 4.1459 | 3.903 | 3.2591 | 2.3326 | 0.90607 | 0.39077 | -3.6154 | -8.7205 | -10.997
|  | BRECHIN | HT |  |  |  |  | 4.1951 | 4.0931 | 4.0165 | 3.8543 | 3.3798 | 3.0645 | 2.1451 | 1.0502 | -0.54776 | -1.3233 | -5.208 | -10.1263 | -13.9784 | 6.1089 | 6.013 | 5.9711 | 5.8864 | 5.4548 | 5.2915 | 4.4926 | 3.4752 | 1.8374 | 1.1721 | -2.2677 | -6.9064 | -10.6248 | 4.8051 | 4.6693 | 4.6326 | 4.5244 | 4.0836 | 3.852 | 2.9785 | 1.9551 | 0.20607 | -0.53168 | -4.3643 | -9.6878 | -13.9307
|  | BRECHIN | HE |  |  |  |  | 4.1951 | 4.0971 | 4.0461 | 3.9002 | 3.4145 | 3.0778 | 2.2553 | 0.92673 | -1.3222 | -2.061 | -6.4824 | -11.1253 | -14.7365 | 6.1099 | 6.016 | 5.9895 | 5.9191 | 5.4854 | 5.317 | 4.7119 | 3.4446 | 1.0262 | 0.33745 | -4.0074 | -8.5462 | -12.4503 | 4.8071 | 4.6714 | 4.652 | 4.553 | 4.1071 | 3.8561 | 3.151 | 1.8622 | -0.68985 | -1.4511 | -6.0878 | -11.1552 | -15.3041
|  | BRECHIN | FB |  |  |  |  | 4.3033 | 4.238 | 4.2604 | 4.2186 | 4.0961 | 3.9839 | 3.6308 | 3.2951 | 2.5849 | 2.341 | 0.57571 | -2.4008 | -3.7447 | 6.1701 | 6.1252 | 6.1211 | 6.0599 | 5.9191 | 5.8007 | 5.3691 | 4.9538 | 4.1089 | 3.7885 | 2.167 | -0.82071 | -2.4595 | 4.9112 | 4.8091 | 4.8295 | 4.802 | 4.6836 | 4.5846 | 4.1908 | 3.7999 | 2.9704 | 2.6918 | 1.1163 | -2.3378 | -3.3521
| PERSLEY | BRIDGE OF DON | MINIMUM HEADROOM | NJ 94130 10184 | NO | NO | 6.325 | -3.9391 | -4.6595 | -5.1616 | -5.5881 | -5.8585 | -6.4014 | -8.5616 | -10.7493 | -12.9932 | -14.084 | -21.5544 | -32.8085 | -43.5238 | -0.70136 | -1.3861 | -1.8065 | -2.1299 | -2.335 | -2.6585 | -4.9667 | -7.4952 | -10.2524 | -11.3116 | -19.581 | -30.9503 | -43.434 | -1.8957 | -2.5896 | -3.0468 | -3.4427 | -3.7039 | -4.1774 | -6.6978 | -9.2478 | -12.1284 | -13.2641 | -21.9345 | -34.5253 | -47.4804
|  | BRIDGE OF DON | EE |  |  |  |  | -3.7758 | -4.6544 | -5.1228 | -5.5258 | -5.8003 | -6.3595 | -7.7738 | -9.6769 | -12.9932 | -14.084 | -20.3167 | -32.7952 | -37.7136 | -0.51871 | -1.383 | -1.7728 | -2.085 | -2.285 | -2.6187 | -4.0575 | -6.2289 | -10.2524 | -11.3116 | -16.8718 | -30.8156 | -36.034 | -1.7366 | -2.5896 | -3.0264 | -3.3978 | -3.657 | -4.1427 | -5.7784 | -7.9917 | -12.1284 | -13.2641 | -19.7376 | -34.4131 | -40.107
|  | BRIDGE OF DON | HT |  |  |  |  | -3.8738 | -4.6595 | -5.1616 | -5.5881 | -5.8585 | -6.4014 | -8.5616 | -10.7493 | -11.4912 | -12.685 | -19.1156 | -32.8085 | -43.5238 | -0.62993 | -1.3769 | -1.8065 | -2.1299 | -2.335 | -2.6585 | -4.9667 | -7.4942 | -8.2095 | -9.3514 | -15.4565 | -30.9503 | -43.434 | -1.8304 | -2.5825 | -3.0468 | -3.4427 | -3.7039 | -4.1774 | -6.6978 | -9.2478 | -10.1355 | -11.3621 | -18.257 | -34.5253 | -47.4804
|  | BRIDGE OF DON | HE |  |  |  |  | -3.9391 | -4.6473 | -5.0993 | -5.4932 | -5.7677 | -6.2442 | -7.7881 | -10.5779 | -11.1422 | -12.8687 | -21.5544 | -30.2003 | -31.5983 | -0.70136 | -1.3861 | -1.7718 | -2.081 | -2.285 | -2.5891 | -4.1861 | -7.4952 | -8.1371 | -10.1258 | -19.581 | -28.9524 | -29.783 | -1.8957 | -2.5784 | -3.0019 | -3.3733 | -3.6345 | -4.059 | -5.8396 | -9.1876 | -9.8937 | -11.9345 | -21.9345 | -31.9539 | -33.16
|  | BRIDGE OF DON | FB |  |  |  |  | -3.3554 | -3.9136 | -4.383 | -4.6687 | -4.9095 | -5.1207 | -6.0779 | -7.235 | -9.6054 | -10.3707 | -12.1993 | -15.9238 | -19.5503 | -0.11054 | -0.68197 | -1.1493 | -1.3952 | -1.6258 | -1.8085 | -2.9085 | -4.2401 | -7.0861 | -7.9544 | -10.5687 | -14.635 | -18.5881 | -1.3386 | -1.8764 | -2.3355 | -2.609 | -2.8508 | -3.057 | -4.1876 | -5.5519 | -8.4386 | -9.3345 | -11.6743 | -16.8549 | -19.8621
| BRIDGE OF DUN | BRIDGE OF DUN | MINIMUM HEADROOM | NO 66018 58883 | YES | NO | 0.051 | -0.0010204 | -0.005102 | -0.010204 | -0.032653 | -0.055102 | -0.2449 | -0.40408 | -0.45306 | -0.52551 | -0.68776 | -0.97347 | -1.0612 | -1.1235 | 0.13776 | 0.13367 | 0.12857 | 0.11837 | 0.11429 | -0.1051 | -0.23265 | -0.27245 | -0.33571 | -0.47653 | -0.7051 | -0.68367 | -0.65918 | 0.10102 | 0.094898 | 0.090816 | 0.073469 | 0.060204 | -0.16122 | -0.30714 | -0.36633 | -0.43367 | -0.58878 | -0.83061 | -0.8898 | -0.92755
|  | BRIDGE OF DUN | EE |  |  |  |  | -0.0010204 | -0.005102 | -0.010204 | -0.026531 | -0.047959 | -0.20408 | -0.26633 | -0.45306 | -0.52143 | -0.59796 | -0.93469 | -1.0153 | -1.0684 | 0.13776 | 0.13367 | 0.12959 | 0.11837 | 0.11531 | -0.046939 | -0.084694 | -0.27245 | -0.32041 | -0.37653 | -0.63469 | -0.62551 | -0.62449 | 0.10102 | 0.094898 | 0.090816 | 0.076531 | 0.065306 | -0.1102 | -0.16531 | -0.36633 | -0.42755 | -0.50204 | -0.78469 | -0.8398 | -0.87449
|  | BRIDGE OF DUN | HT |  |  |  |  | 0 | -0.005102 | -0.0091837 | -0.02551 | -0.044898 | -0.2449 | -0.40408 | -0.4449 | -0.52551 | -0.68776 | -0.97347 | -1.0612 | -1.1235 | 0.13878 | 0.13367 | 0.13061 | 0.11939 | 0.11633 | -0.1051 | -0.23265 | -0.27143 | -0.33571 | -0.47653 | -0.7051 | -0.68367 | -0.65918 | 0.10204 | 0.095918 | 0.091837 | 0.076531 | 0.067347 | -0.16122 | -0.30714 | -0.35816 | -0.43367 | -0.58878 | -0.83061 | -0.8898 | -0.92755
|  | BRIDGE OF DUN | HE |  |  |  |  | 0.0030612 | -0.005102 | -0.010204 | -0.032653 | -0.055102 | -0.10204 | -0.14286 | -0.3051 | -0.36327 | -0.40816 | -0.50204 | -0.62653 | -0.75306 | 0.1449 | 0.13367 | 0.12857 | 0.11837 | 0.11429 | 0.093878 | 0.060204 | -0.11429 | -0.15 | -0.17857 | -0.22551 | -0.24388 | -0.33061 | 0.10612 | 0.095918 | 0.091837 | 0.073469 | 0.060204 | 0.02449 | -0.02551 | -0.21837 | -0.27143 | -0.28571 | -0.36122 | -0.44388 | -0.55204
|  | BRIDGE OF DUN | FB |  |  |  |  | 0.022449 | 0.017347 | 0.019388 | 0.018367 | 0.0071429 | -0.0020408 | -0.016327 | -0.031633 | -0.043878 | -0.063265 | -0.15 | -0.20612 | -0.52551 | 0.15918 | 0.15612 | 0.1551 | 0.15612 | 0.14694 | 0.13469 | 0.12959 | 0.11429 | 0.1 | 0.083673 | 0.013265 | -0.061224 | -0.42857 | 0.12755 | 0.12143 | 0.12347 | 0.12347 | 0.11429 | 0.10408 | 0.096939 | 0.081633 | 0.071429 | 0.053061 | -0.030612 | -0.12245 | -0.44286
| ABERNETHY | BRIDGE OF EARN | MINIMUM HEADROOM | NO 13343 17764 | NO | YES | 0.747 | 11.0235 | 10.8633 | 10.6286 | 10.4194 | 10.3184 | 9.7571 | 9.2724 | 9.002 | 8.549 | 8.1959 | 6.9786 | 6.3653 | 6.0286 | 12.4102 | 12.3163 | 12.2296 | 12.1541 | 12.0888 | 11.6684 | 11.401 | 11.3398 | 11.0908 | 10.8602 | 10.2194 | 10.1663 | 10.1765 | 12.5056 | 12.3842 | 12.2066 | 12.0526 | 11.9587 | 11.4046 | 11.0066 | 10.825 | 10.4536 | 10.1505 | 9.1668 | 8.7668 | 8.5719
|  | BRIDGE OF EARN | EE |  |  |  |  | 11.0265 | 10.8633 | 10.6286 | 10.4194 | 10.3184 | 9.7571 | 9.2724 | 9.002 | 8.549 | 8.1959 | 6.9786 | 6.3653 | 6.0337 | 12.4122 | 12.3163 | 12.2306 | 12.1561 | 12.0898 | 11.6684 | 11.401 | 11.3469 | 11.0908 | 10.8602 | 10.249 | 10.1806 | 10.1765 | 12.5066 | 12.3842 | 12.2066 | 12.0526 | 11.9587 | 11.4046 | 11.0066 | 10.825 | 10.4536 | 10.1505 | 9.1668 | 8.7668 | 8.5719
|  | BRIDGE OF EARN | HT |  |  |  |  | 11.0265 | 10.8694 | 10.6551 | 10.4663 | 10.35 | 9.8806 | 9.4306 | 9.1337 | 8.6776 | 8.3214 | 7.0867 | 6.4245 | 6.0286 | 12.4112 | 12.3173 | 12.2316 | 12.1561 | 12.0888 | 11.7071 | 11.4643 | 11.3704 | 11.1082 | 10.8929 | 10.2194 | 10.1663 | 10.2071 | 12.5077 | 12.3893 | 12.224 | 12.0811 | 11.977 | 11.4923 | 11.125 | 10.9107 | 10.5352 | 10.2403 | 9.227 | 8.8087 | 8.577
|  | BRIDGE OF EARN | HE |  |  |  |  | 11.0235 | 10.8643 | 10.6357 | 10.452 | 10.3582 | 9.8959 | 9.349 | 9.0602 | 8.6653 | 8.2929 | 7.3 | 6.6439 | 6.3469 | 12.4102 | 12.3163 | 12.2296 | 12.1541 | 12.0929 | 11.7633 | 11.4082 | 11.3398 | 11.1571 | 10.9194 | 10.4663 | 10.3776 | 10.3378 | 12.5056 | 12.3842 | 12.2128 | 12.0719 | 11.9821 | 11.5291 | 11.0536 | 10.8546 | 10.5505 | 10.2342 | 9.4526 | 9.0138 | 8.8209
|  | BRIDGE OF EARN | FB |  |  |  |  | 11.1 | 11.0245 | 10.8663 | 10.7429 | 10.6867 | 10.5143 | 10.3173 | 10.1265 | 9.9327 | 9.8173 | 9.2153 | 8.6531 | 8.1347 | 12.4673 | 12.4061 | 12.3388 | 12.2878 | 12.2265 | 12.1459 | 12.0378 | 11.9388 | 11.8398 | 11.7541 | 11.4776 | 11.051 | 10.4082 | 12.5913 | 12.5077 | 12.4015 | 12.3087 | 12.2464 | 12.1128 | 11.9485 | 11.7934 | 11.6342 | 11.525 | 11.0474 | 10.4954 | 10.0066
| RANNOCH | BRIDGE OF GAUR | MINIMUM HEADROOM | NN 50676 57767 | YES | YES | 0.069 | 0.79592 | 0.79082 | 0.78776 | 0.78163 | 0.77755 | 0.76531 | 0.75204 | 0.74184 | 0.72857 | 0.72143 | 0.68571 | 0.65918 | 0.51327 | 0.85816 | 0.8551 | 0.85102 | 0.84898 | 0.84694 | 0.84082 | 0.82959 | 0.82551 | 0.81531 | 0.80918 | 0.77347 | 0.77143 | 0.62449 | 0.83163 | 0.82653 | 0.82245 | 0.81939 | 0.81429 | 0.8051 | 0.79286 | 0.78571 | 0.77347 | 0.76633 | 0.73265 | 0.71327 | 0.55408
|  | BRIDGE OF GAUR | EE |  |  |  |  | 0.79592 | 0.79082 | 0.78776 | 0.78265 | 0.77959 | 0.76837 | 0.75612 | 0.74694 | 0.73163 | 0.72551 | 0.68571 | 0.65918 | 0.51327 | 0.85816 | 0.8551 | 0.85204 | 0.85 | 0.84796 | 0.84082 | 0.83061 | 0.82653 | 0.81531 | 0.8102 | 0.77449 | 0.77245 | 0.62449 | 0.83163 | 0.82653 | 0.82245 | 0.82143 | 0.81633 | 0.80714 | 0.7949 | 0.78878 | 0.77449 | 0.76837 | 0.73265 | 0.71327 | 0.55408
|  | BRIDGE OF GAUR | HT |  |  |  |  | 0.79592 | 0.7949 | 0.78878 | 0.78367 | 0.77959 | 0.77041 | 0.75714 | 0.74796 | 0.73571 | 0.72653 | 0.70102 | 0.67347 | 0.66429 | 0.85816 | 0.85816 | 0.85204 | 0.85 | 0.84796 | 0.84082 | 0.83061 | 0.82653 | 0.81735 | 0.8102 | 0.78367 | 0.78367 | 0.7898 | 0.83163 | 0.83163 | 0.82347 | 0.82143 | 0.81531 | 0.80714 | 0.79694 | 0.7898 | 0.77857 | 0.77041 | 0.74694 | 0.72755 | 0.71429
|  | BRIDGE OF GAUR | HE |  |  |  |  | 0.79592 | 0.79082 | 0.78776 | 0.78163 | 0.77755 | 0.76531 | 0.75204 | 0.74184 | 0.72857 | 0.72143 | 0.69184 | 0.66327 | 0.66939 | 0.85816 | 0.8551 | 0.85102 | 0.84898 | 0.84694 | 0.84082 | 0.82959 | 0.82551 | 0.81633 | 0.80918 | 0.77347 | 0.77143 | 0.78469 | 0.83163 | 0.82755 | 0.82347 | 0.81939 | 0.81429 | 0.8051 | 0.79286 | 0.78571 | 0.77347 | 0.76633 | 0.73571 | 0.71429 | 0.71429
|  | BRIDGE OF GAUR | FB |  |  |  |  | 0.8 | 0.80102 | 0.80306 | 0.79796 | 0.7949 | 0.78469 | 0.77959 | 0.77551 | 0.77449 | 0.76939 | 0.74898 | 0.71939 | 0.7102 | 0.86327 | 0.8602 | 0.8602 | 0.85816 | 0.85612 | 0.84286 | 0.83878 | 0.83571 | 0.83367 | 0.82245 | 0.81122 | 0.77755 | 0.76327 | 0.83571 | 0.83571 | 0.83776 | 0.83265 | 0.82959 | 0.81837 | 0.81429 | 0.8102 | 0.80816 | 0.8 | 0.78367 | 0.75204 | 0.7449
| BROADFORD | BROADFORD | MINIMUM HEADROOM | NG 62656 24360 | YES | YES | 2.036 | 3.0603 | 3.0124 | 2.9583 | 2.9267 | 2.8981 | 1.9185 | 0.75013 | -0.54477 | -1.5346 | -1.8233 | -2.005 | -2.1621 | -2.3111 | 2.7675 | 2.7471 | 2.7277 | 2.7205 | 2.7124 | 1.9134 | 0.77768 | -0.5611 | -1.5989 | -1.8866 | -1.9478 | -1.9295 | -1.9672 | 2.8874 | 2.8506 | 2.7955 | 2.77 | 2.7741 | 1.8302 | 0.75064 | -0.4963 | -1.4677 | -1.7524 | -1.8749 | -1.9514 | -2.029
|  | BROADFORD | EE |  |  |  |  | 3.0624 | 3.0165 | 2.9614 | 2.9277 | 2.8981 | 2.7991 | 2.6399 | 1.7267 | 0.61441 | -0.65191 | -2.005 | -2.1621 | -2.2693 | 2.7685 | 2.7491 | 2.7277 | 2.7205 | 2.7124 | 2.6685 | 2.6175 | 1.893 | 0.75523 | -0.58049 | -1.9346 | -1.9172 | -1.8989 | 2.8884 | 2.8527 | 2.7976 | 2.77 | 2.7741 | 2.6976 | 2.5853 | 1.7017 | 0.66594 | -0.56365 | -1.8749 | -1.9514 | -1.9943
|  | BROADFORD | HT |  |  |  |  | 3.0614 | 3.0124 | 2.9593 | 2.9267 | 2.8991 | 1.9185 | 0.75013 | -0.54477 | -1.5346 | -1.8233 | -1.9611 | -2.1427 | -2.3111 | 2.7675 | 2.7471 | 2.7297 | 2.7216 | 2.7124 | 1.9134 | 0.77768 | -0.5611 | -1.5989 | -1.8866 | -1.9478 | -1.9295 | -1.8958 | 2.8874 | 2.8506 | 2.7966 | 2.77 | 2.7741 | 1.8302 | 0.75064 | -0.4963 | -1.4677 | -1.7524 | -1.8575 | -1.9494 | -2.029
|  | BROADFORD | HE |  |  |  |  | 3.0603 | 3.0124 | 2.9583 | 2.9338 | 2.9083 | 2.796 | 2.6562 | 1.6399 | 0.40421 | -1.0366 | -1.954 | -2.1346 | -2.2427 | 2.7675 | 2.7471 | 2.7297 | 2.7226 | 2.7144 | 2.6654 | 2.6205 | 1.7848 | 0.51543 | -1.0152 | -1.9325 | -1.9213 | -1.9213 | 2.8874 | 2.8506 | 2.7955 | 2.7761 | 2.7802 | 2.6955 | 2.5966 | 1.6149 | 0.45778 | -0.95242 | -1.8473 | -1.9371 | -1.9871
|  | BROADFORD | FB |  |  |  |  | 3.0991 | 3.0909 | 3.0603 | 3.0695 | 3.0787 | 3.0695 | 3.0409 | 3.0083 | 2.3358 | 1.5001 | -1.3611 | -1.4886 | -1.5223 | 2.796 | 2.7889 | 2.7848 | 2.7828 | 2.7869 | 2.7746 | 2.7389 | 2.7165 | 2.1491 | 1.2644 | -1.8121 | -1.9111 | -1.9672 | 2.9221 | 2.917 | 2.8966 | 2.9017 | 2.9068 | 2.8976 | 2.8557 | 2.8292 | 2.1578 | 1.3608 | -1.4616 | -1.5779 | -1.5851
| CARRADALE 1 | BRODICK | MINIMUM HEADROOM | NS 01976 35459 | NO | YES | 0.333 | 2.9712 | 2.9773 | 2.861 | 2.7457 | 2.6661 | 2.4804 | 2.2784 | 2.0876 | 1.958 | 1.8671 | 1.5702 | 1.2355 | 0.95082 | 4.1886 | 4.1927 | 4.1835 | 4.1886 | 4.1661 | 4.1304 | 4.0661 | 3.9927 | 4.0376 | 3.9896 | 3.8304 | 3.7631 | 3.5355 | 3.5835 | 3.5722 | 3.5304 | 3.4947 | 3.4488 | 3.3386 | 3.2059 | 3.0722 | 3.0161 | 2.9386 | 2.7141 | 2.5427 | 2.3957
|  | BRODICK | EE |  |  |  |  | 2.9712 | 2.9773 | 2.861 | 2.7539 | 2.6794 | 2.4896 | 2.2784 | 2.0876 | 1.958 | 1.8671 | 1.5702 | 1.2376 | 0.96612 | 4.1886 | 4.1927 | 4.1845 | 4.1906 | 4.1692 | 4.1314 | 4.0702 | 3.9927 | 4.0376 | 3.9896 | 3.8641 | 3.8896 | 3.9284 | 3.5835 | 3.5722 | 3.5304 | 3.4978 | 3.4529 | 3.3427 | 3.2059 | 3.0722 | 3.0161 | 2.9386 | 2.7141 | 2.5508 | 2.4294
|  | BRODICK | HT |  |  |  |  | 2.9712 | 2.9784 | 2.8886 | 2.7978 | 2.6896 | 2.5529 | 2.3743 | 2.1916 | 2.0508 | 1.9641 | 1.7141 | 1.3212 | 0.95082 | 4.1886 | 4.1937 | 4.1835 | 4.1937 | 4.1661 | 4.1355 | 4.0712 | 3.9967 | 4.0447 | 3.9957 | 3.8304 | 3.8661 | 3.9141 | 3.5835 | 3.5743 | 3.5447 | 3.5233 | 3.4712 | 3.3763 | 3.2549 | 3.1243 | 3.0671 | 2.9916 | 2.7702 | 2.5692 | 2.3957
|  | BRODICK | HE |  |  |  |  | 2.9824 | 3.0029 | 2.8753 | 2.7457 | 2.6661 | 2.4804 | 2.2967 | 2.1141 | 1.9855 | 1.8855 | 1.6753 | 1.2355 | 0.96 | 4.1947 | 4.2049 | 4.1855 | 4.1886 | 4.1733 | 4.1304 | 4.0661 | 3.9937 | 4.0416 | 3.9916 | 3.8733 | 3.8865 | 3.8641 | 3.5937 | 3.5978 | 3.5416 | 3.4947 | 3.4488 | 3.3386 | 3.2141 | 3.0835 | 3.0314 | 2.9498 | 2.7702 | 2.5427 | 2.411
|  | BRODICK | FB |  |  |  |  | 3.0365 | 3.1039 | 3.1049 | 3.1151 | 3.1233 | 3.1355 | 3.1263 | 3.1457 | 3.1294 | 3.1222 | 2.9916 | 2.7386 | 2.6692 | 4.2335 | 4.2763 | 4.2814 | 4.2947 | 4.3018 | 4.2957 | 4.2631 | 4.2467 | 4.2039 | 4.1763 | 4.0865 | 3.7631 | 3.5355 | 3.6467 | 3.6967 | 3.6835 | 3.6967 | 3.7018 | 3.7345 | 3.7243 | 3.7314 | 3.7161 | 3.709 | 3.6396 | 3.3478 | 3.3304
| BRORA | BRORA | MINIMUM HEADROOM | NC 90482 04236 | NO | NO | 0.872 | 4.0333 | 4.0302 | 4.02 | 3.9659 | 3.919 | 3.4261 | 2.9649 | 2.6129 | 2.4608 | 2.3731 | 2.0404 | 1.7476 | 1.5078 | 4.6843 | 4.6843 | 4.6863 | 4.6761 | 4.669 | 4.1873 | 3.7669 | 3.4547 | 3.3465 | 3.3057 | 3.2006 | 3.1914 | 3.1924 | 4.3904 | 4.3873 | 4.3669 | 4.3139 | 4.2527 | 3.8353 | 3.4037 | 3.0812 | 2.9506 | 2.8822 | 2.6516 | 2.4894 | 2.3496
|  | BRORA | EE |  |  |  |  | 4.0333 | 4.0312 | 4.02 | 3.969 | 3.9241 | 3.8343 | 3.7669 | 3.2731 | 2.8261 | 2.4833 | 2.0404 | 1.7476 | 1.5271 | 4.6873 | 4.6843 | 4.6863 | 4.6761 | 4.67 | 4.6241 | 4.6016 | 4.1394 | 3.7302 | 3.4159 | 3.2098 | 3.2016 | 3.2282 | 4.3914 | 4.3873 | 4.368 | 4.3149 | 4.2567 | 4.1924 | 4.1322 | 3.7292 | 3.3118 | 2.9904 | 2.6516 | 2.4894 | 2.3731
|  | BRORA | HT |  |  |  |  | 4.0343 | 4.0302 | 4.021 | 3.969 | 3.921 | 3.4261 | 2.9649 | 2.6129 | 2.4608 | 2.3731 | 2.1261 | 1.8027 | 1.5078 | 4.6873 | 4.6843 | 4.6863 | 4.6761 | 4.67 | 4.1873 | 3.7669 | 3.4547 | 3.3465 | 3.3057 | 3.2006 | 3.1914 | 3.2149 | 4.3914 | 4.3884 | 4.368 | 4.3149 | 4.2547 | 3.8353 | 3.4037 | 3.0812 | 2.9506 | 2.8822 | 2.6935 | 2.5098 | 2.3496
|  | BRORA | HE |  |  |  |  | 4.0333 | 4.0302 | 4.021 | 3.9659 | 3.919 | 3.8312 | 3.7629 | 3.2139 | 2.7261 | 2.3731 | 2.1108 | 1.7914 | 1.572 | 4.6843 | 4.6843 | 4.6863 | 4.6761 | 4.669 | 4.6292 | 4.6016 | 4.0873 | 3.6363 | 3.3251 | 3.218 | 3.2037 | 3.221 | 4.3904 | 4.3873 | 4.3669 | 4.3139 | 4.2527 | 4.1894 | 4.1302 | 3.6771 | 3.219 | 2.8945 | 2.6935 | 2.5139 | 2.3965
|  | BRORA | FB |  |  |  |  | 4.0567 | 4.07 | 4.0782 | 4.0639 | 4.0486 | 4.0271 | 4.0129 | 3.9955 | 3.6843 | 3.3608 | 2.6527 | 2.4741 | 2.4037 | 4.7118 | 4.7241 | 4.7343 | 4.7312 | 4.7353 | 4.722 | 4.7108 | 4.6833 | 4.3424 | 4.0118 | 3.3935 | 3.2802 | 3.1924 | 4.4067 | 4.4149 | 4.419 | 4.4006 | 4.3833 | 4.3608 | 4.3414 | 4.3057 | 4.0251 | 3.7108 | 3.0659 | 2.9078 | 2.8822
| MILTON OF CRAIGIE | BROUGHTY FERRY | MINIMUM HEADROOM | NO 46658 30758 | NO | NO | 1.811 | 5.882 | 5.9156 | 5.9105 | 5.8656 | 5.7167 | 5.5565 | 5.2983 | 5.0891 | 4.8197 | 4.5922 | 3.4095 | 2.5259 | 2.0065 | 7.7983 | 7.7769 | 7.5789 | 7.5759 | 7.431 | 7.2361 | 6.9708 | 6.733 | 6.4708 | 6.2422 | 5.2554 | 4.6116 | 3.0697 | 6.7922 | 6.8116 | 6.8381 | 6.7769 | 6.6167 | 6.4503 | 6.1493 | 5.9044 | 5.5973 | 5.3371 | 4.0656 | 3.2299 | 2.7534
|  | BROUGHTY FERRY | EE |  |  |  |  | 5.882 | 5.9167 | 5.9595 | 5.8759 | 5.7371 | 5.584 | 5.2983 | 5.0891 | 4.8197 | 4.5922 | 3.4095 | 2.5259 | 2.0065 | 7.7993 | 7.781 | 7.7769 | 7.6401 | 7.4361 | 7.2687 | 6.9708 | 6.7595 | 6.4708 | 6.2432 | 5.2554 | 4.6116 | 4.0136 | 6.7922 | 6.8126 | 6.8381 | 6.785 | 6.6269 | 6.484 | 6.1493 | 5.9156 | 5.5973 | 5.3371 | 4.0656 | 3.2299 | 2.7534
|  | BROUGHTY FERRY | HT |  |  |  |  | 5.882 | 5.9156 | 5.9595 | 5.8728 | 5.7167 | 5.5565 | 5.3463 | 5.0993 | 4.8616 | 4.6085 | 3.4514 | 2.6483 | 2.3197 | 7.7993 | 7.7769 | 7.7748 | 7.635 | 7.431 | 7.2361 | 7.0177 | 6.7585 | 6.5024 | 6.2422 | 5.3044 | 5.0565 | 4.9156 | 6.7932 | 6.8116 | 6.8412 | 6.784 | 6.6197 | 6.4503 | 6.2065 | 5.9208 | 5.6401 | 5.3463 | 4.1003 | 3.3667 | 3.0891
|  | BROUGHTY FERRY | HE |  |  |  |  | 5.882 | 5.9187 | 5.9616 | 5.8656 | 5.7248 | 5.5748 | 5.3514 | 5.0932 | 4.8738 | 4.6789 | 3.7228 | 3.1759 | 2.8412 | 7.7983 | 7.7779 | 7.7738 | 7.635 | 7.434 | 7.2585 | 7.0126 | 6.733 | 6.4881 | 6.2738 | 5.3738 | 4.9177 | 4.4105 | 6.7932 | 6.8146 | 6.8442 | 6.7769 | 6.6167 | 6.4748 | 6.2105 | 5.9044 | 5.6401 | 5.4126 | 4.3554 | 3.8881 | 3.6136
|  | BROUGHTY FERRY | FB |  |  |  |  | 5.9769 | 6.0534 | 5.9105 | 5.9718 | 5.9963 | 5.9759 | 5.882 | 5.8483 | 5.8912 | 5.8361 | 5.3616 | 4.4095 | 3.7259 | 7.8493 | 7.8442 | 7.5789 | 7.5759 | 7.5177 | 7.4279 | 7.2371 | 7.132 | 7.1024 | 6.9738 | 6.131 | 4.6422 | 3.0697 | 6.8738 | 6.9299 | 6.8442 | 6.882 | 6.8881 | 6.8554 | 6.7432 | 6.6942 | 6.735 | 6.6708 | 6.0708 | 4.8993 | 4.3238
| DUNOON | BRUCHAG | MINIMUM HEADROOM | NS 11372 57191 | NO | YES | 0.501 | 12.0459 | 12.0898 | 12.1235 | 12.1531 | 12.1765 | 12.1816 | 12.198 | 12.1959 | 12.1367 | 12.0847 | 11.8755 | 11.9612 | 11.9398 | 12.4398 | 12.449 | 12.452 | 12.45 | 12.4459 | 12.4184 | 12.401 | 12.3449 | 12.2571 | 12.1857 | 11.9184 | 12.0061 | 11.901 | 11.675 | 11.7077 | 11.7342 | 11.7566 | 11.776 | 11.773 | 11.7832 | 11.777 | 11.7556 | 11.7434 | 11.5485 | 11.6413 | 11.6015
|  | BRUCHAG | EE |  |  |  |  | 12.0469 | 12.0898 | 12.1235 | 12.1612 | 12.1969 | 12.1949 | 12.198 | 12.1959 | 12.1429 | 12.0878 | 11.8755 | 11.9806 | 11.9694 | 12.4398 | 12.449 | 12.452 | 12.4541 | 12.4551 | 12.4245 | 12.4041 | 12.3449 | 12.2571 | 12.1857 | 11.9184 | 12.0347 | 12.0214 | 11.676 | 11.7077 | 11.7342 | 11.7648 | 11.7934 | 11.7811 | 11.7832 | 11.777 | 11.7556 | 11.7434 | 11.5485 | 11.6536 | 11.6434
|  | BRUCHAG | HT |  |  |  |  | 12.0459 | 12.0898 | 12.1255 | 12.1551 | 12.1796 | 12.1847 | 12.199 | 12.2041 | 12.1367 | 12.0939 | 12.0184 | 11.9612 | 11.9531 | 12.4398 | 12.449 | 12.4541 | 12.45 | 12.4469 | 12.4184 | 12.401 | 12.3459 | 12.2571 | 12.1878 | 12.0602 | 12.0061 | 12.0092 | 11.675 | 11.7077 | 11.7362 | 11.7577 | 11.7781 | 11.773 | 11.7832 | 11.7842 | 11.7668 | 11.7607 | 11.677 | 11.6413 | 11.6332
|  | BRUCHAG | HE |  |  |  |  | 12.0459 | 12.0898 | 12.1245 | 12.1531 | 12.1765 | 12.1816 | 12.198 | 12.2 | 12.1388 | 12.0847 | 11.8857 | 11.9704 | 11.9398 | 12.4398 | 12.45 | 12.4531 | 12.45 | 12.4459 | 12.4194 | 12.4041 | 12.3449 | 12.2571 | 12.1878 | 11.9214 | 12.0194 | 11.9816 | 11.676 | 11.7077 | 11.7342 | 11.7566 | 11.776 | 11.774 | 11.7842 | 11.7852 | 11.7719 | 11.7536 | 11.5597 | 11.6495 | 11.623
|  | BRUCHAG | FB |  |  |  |  | 12.0745 | 12.1316 | 12.1724 | 12.2265 | 12.2643 | 12.302 | 12.3173 | 12.3265 | 12.3551 | 12.3571 | 12.1908 | 12.0694 | 11.9735 | 12.4582 | 12.4827 | 12.4918 | 12.5071 | 12.5112 | 12.5133 | 12.4939 | 12.4714 | 12.4653 | 12.4306 | 12.201 | 12.0388 | 11.901 | 11.7036 | 11.7505 | 11.7821 | 11.826 | 11.8587 | 11.8852 | 11.8954 | 11.8974 | 11.9189 | 11.9179 | 11.8138 | 11.6638 | 11.6015
| KEITH 1 | BUCKIE | MINIMUM HEADROOM | NJ 43291 64802 | NO | YES | 3.567 | 11.7897 | 11.6182 | 11.4335 | 11.0621 | 10.9172 | 10.0764 | 8.7509 | 7.2019 | 4.7366 | 3.9458 | -0.78178 | -5.8379 | -9.5532 | 13.6329 | 13.5248 | 13.5003 | 13.338 | 13.2829 | 12.8023 | 11.7237 | 10.5584 | 8.1503 | 7.5288 | 3.7768 | -0.58647 | -4.3783 | 12.7482 | 12.5635 | 12.4737 | 12.1656 | 12.0431 | 11.3278 | 10.036 | 8.5054 | 5.7778 | 4.9799 | 0.38292 | -4.8477 | -8.9599
|  | BUCKIE | EE |  |  |  |  | 11.7897 | 11.6213 | 11.4356 | 11.0856 | 10.9488 | 10.1356 | 9.005 | 7.6743 | 6.1601 | 5.5784 | 1.2937 | -4.0144 | -6.4073 | 13.6329 | 13.5258 | 13.5054 | 13.3554 | 13.3043 | 12.8166 | 12.0594 | 10.9962 | 9.7217 | 9.2962 | 6.486 | 2.1615 | 0.35741 | 12.7482 | 12.5656 | 12.4758 | 12.1829 | 12.0686 | 11.3625 | 10.3503 | 9.0105 | 7.4452 | 6.8666 | 3.0564 | -2.2395 | -4.5048
|  | BUCKIE | HT |  |  |  |  | 11.7897 | 11.6182 | 11.4346 | 11.0621 | 10.9172 | 10.0764 | 8.7509 | 7.3366 | 5.5631 | 4.705 | 0.75598 | -4.6359 | -8.8859 | 13.6329 | 13.5248 | 13.5003 | 13.338 | 13.2829 | 12.8023 | 11.7237 | 10.6023 | 8.9819 | 8.3299 | 5.5952 | 1.0554 | -2.5538 | 12.7492 | 12.5635 | 12.4737 | 12.1656 | 12.0431 | 11.3278 | 10.036 | 8.6186 | 6.738 | 5.9248 | 2.3084 | -3.213 | -7.6436
|  | BUCKIE | HE |  |  |  |  | 11.7897 | 11.6182 | 11.4335 | 11.0692 | 10.9192 | 10.0907 | 8.8499 | 7.2019 | 4.7366 | 3.9458 | -0.78178 | -5.8379 | -9.5532 | 13.6329 | 13.5248 | 13.5023 | 13.3472 | 13.2931 | 12.8084 | 11.9482 | 10.5584 | 8.1503 | 7.5288 | 3.7768 | -0.58647 | -4.3783 | 12.7503 | 12.5646 | 12.4748 | 12.1727 | 12.0462 | 11.3329 | 10.2043 | 8.5054 | 5.7778 | 4.9799 | 0.38292 | -4.8477 | -8.9599
|  | BUCKIE | FB |  |  |  |  | 11.8672 | 11.7682 | 11.656 | 11.4733 | 11.4019 | 11.1264 | 10.5692 | 10.0192 | 9.1192 | 8.8254 | 7.0254 | 4.157 | 2.8335 | 13.6982 | 13.6023 | 13.6003 | 13.5248 | 13.488 | 13.338 | 12.8819 | 12.3972 | 11.488 | 11.1339 | 9.5033 | 6.8727 | 5.0003 | 12.8584 | 12.6952 | 12.6788 | 12.5543 | 12.5329 | 12.335 | 11.7799 | 11.2146 | 10.2156 | 9.8901 | 8.1084 | 4.9278 | 3.9003
| FORT AUGUSTUS | BUNOICH | MINIMUM HEADROOM | NH 37662 09672 | YES | YES | 0 | 2.1549 | 2.1508 | 2.1498 | 2.1406 | 2.1233 | 2.0927 | 2.0702 | 2.0386 | 2.0427 | 2.0222 | 1.9722 | 1.9202 | 1.8814 | 2.0055 | 2.0014 | 2.0004 | 1.9994 | 1.9912 | 1.9831 | 1.9698 | 1.9535 | 1.9484 | 1.932 | 1.8963 | 1.8494 | 1.779 | 2.0873 | 2.0822 | 2.0812 | 2.0731 | 2.0618 | 2.0404 | 2.02 | 1.9945 | 1.9833 | 1.9639 | 1.921 | 1.9118 | 1.8924
|  | BUNOICH | EE |  |  |  |  | 2.1549 | 2.1508 | 2.1498 | 2.1416 | 2.1263 | 2.0927 | 2.0743 | 2.0427 | 2.0478 | 2.0284 | 1.9722 | 1.9202 | 1.8865 | 2.0055 | 2.0014 | 2.0004 | 1.9994 | 1.9912 | 1.9831 | 1.9708 | 1.9545 | 1.9484 | 1.9341 | 1.9035 | 1.8922 | 1.8759 | 2.0873 | 2.0822 | 2.0812 | 2.0741 | 2.0639 | 2.0414 | 2.0231 | 1.9986 | 1.9873 | 1.969 | 1.921 | 1.9118 | 1.8986
|  | BUNOICH | HT |  |  |  |  | 2.1549 | 2.1518 | 2.1498 | 2.1427 | 2.1263 | 2.1029 | 2.0784 | 2.0498 | 2.0508 | 2.0324 | 1.9876 | 1.9314 | 1.8814 | 2.0055 | 2.0014 | 2.0004 | 1.9994 | 1.9912 | 1.9841 | 1.9708 | 1.9535 | 1.9484 | 1.9351 | 1.8963 | 1.8933 | 1.8994 | 2.0873 | 2.0822 | 2.0812 | 2.0741 | 2.0639 | 2.0465 | 2.0251 | 1.9996 | 1.9884 | 1.9731 | 1.9302 | 1.9169 | 1.8965
|  | BUNOICH | HE |  |  |  |  | 2.1549 | 2.1518 | 2.1498 | 2.1406 | 2.1233 | 2.0927 | 2.0702 | 2.0386 | 2.0427 | 2.0222 | 1.9865 | 1.9284 | 1.8927 | 2.0055 | 2.0014 | 2.0004 | 1.9994 | 1.9912 | 1.9831 | 1.9698 | 1.9535 | 1.9484 | 1.932 | 1.9035 | 1.8912 | 1.8627 | 2.0873 | 2.0822 | 2.0812 | 2.0731 | 2.0618 | 2.0404 | 2.02 | 1.9945 | 1.9833 | 1.9639 | 1.9312 | 1.9139 | 1.8924
|  | BUNOICH | FB |  |  |  |  | 2.1702 | 2.1682 | 2.1712 | 2.1712 | 2.1733 | 2.1692 | 2.162 | 2.16 | 2.1518 | 2.1488 | 2.112 | 2.0712 | 2.0529 | 2.0157 | 2.0137 | 2.0096 | 2.0116 | 2.0106 | 2.0045 | 1.9933 | 1.9902 | 1.978 | 1.9718 | 1.9229 | 1.8494 | 1.779 | 2.1047 | 2.1027 | 2.1037 | 2.1037 | 2.1057 | 2.1006 | 2.0924 | 2.0924 | 2.0812 | 2.0782 | 2.0414 | 1.9914 | 1.9833
| THURSO | BURGARHILL | MINIMUM HEADROOM | HY 34441 26078 | YES | NO | 0 | -0.78673 | -0.78061 | -0.78673 | -0.83061 | -0.85204 | -1.1786 | -1.402 | -1.5714 | -1.7163 | -1.8571 | -2.2 | -2.3184 | -2.4459 | -0.16735 | -0.15918 | -0.15816 | -0.17245 | -0.18673 | -0.49184 | -0.65102 | -0.75306 | -0.86224 | -0.98367 | -1.3337 | -1.3286 | -1.3173 | -0.92449 | -0.91122 | -0.90714 | -0.92857 | -0.94694 | -1.052 | -1.1796 | -1.3041 | -1.4041 | -1.5367 | -1.8612 | -1.8959 | -1.951
|  | BURGARHILL | EE |  |  |  |  | -0.78673 | -0.78061 | -0.78673 | -0.82449 | -0.84388 | -1.1153 | -1.402 | -1.5459 | -1.6612 | -1.8439 | -2.2 | -2.3184 | -2.4459 | -0.16735 | -0.15918 | -0.15816 | -0.17245 | -0.18469 | -0.43061 | -0.65102 | -0.73571 | -0.80306 | -0.97959 | -1.3184 | -1.3153 | -1.3173 | -0.92449 | -0.91122 | -0.90612 | -0.92551 | -0.94388 | -1.0378 | -1.1796 | -1.2837 | -1.3602 | -1.5337 | -1.8612 | -1.8959 | -1.951
|  | BURGARHILL | HT |  |  |  |  | -0.78673 | -0.77959 | -0.78571 | -0.82347 | -0.84184 | -1.1786 | -1.3612 | -1.4857 | -1.6724 | -1.7765 | -2.1265 | -2.2827 | -2.4082 | -0.16735 | -0.15918 | -0.15816 | -0.17245 | -0.18673 | -0.49184 | -0.63061 | -0.71122 | -0.86224 | -0.96531 | -1.3337 | -1.3286 | -1.2949 | -0.92449 | -0.91122 | -0.90612 | -0.92449 | -0.94082 | -1.052 | -1.15 | -1.2449 | -1.4041 | -1.4969 | -1.8418 | -1.8908 | -1.9184
|  | BURGARHILL | HE |  |  |  |  | -0.78673 | -0.77959 | -0.78571 | -0.83061 | -0.85204 | -1.1255 | -1.3082 | -1.5714 | -1.7163 | -1.8571 | -1.9286 | -2.0806 | -2.1796 | -0.16735 | -0.15918 | -0.15816 | -0.17245 | -0.18673 | -0.43367 | -0.54796 | -0.75306 | -0.8449 | -0.98367 | -1.1163 | -1.1 | -1.0929 | -0.92449 | -0.91122 | -0.90714 | -0.92857 | -0.94694 | -1.0204 | -1.0888 | -1.3041 | -1.4041 | -1.5367 | -1.6173 | -1.6551 | -1.6867
|  | BURGARHILL | FB |  |  |  |  | -0.74082 | -0.72449 | -0.70306 | -0.70408 | -0.71122 | -1.05 | -1.0633 | -1.0918 | -1.1214 | -1.1316 | -1.2765 | -1.4704 | -1.6265 | -0.13265 | -0.12551 | -0.11122 | -0.11735 | -0.12857 | -0.47653 | -0.48878 | -0.5102 | -0.53776 | -0.54592 | -0.7051 | -0.90204 | -1.048 | -0.9 | -0.87857 | -0.85714 | -0.85306 | -0.84898 | -0.9398 | -0.95306 | -0.98163 | -1.0133 | -1.0224 | -1.1561 | -1.3071 | -1.4459
| ELGIN | BURGHEAD | MINIMUM HEADROOM | NJ 12666 68781 | NO | YES | 2.258 | 5.4193 | 5.4071 | 5.3713 | 4.9397 | 4.7897 | 4.3458 | 3.954 | 3.654 | 3.2652 | 2.9183 | 1.5785 | 0.6989 | 0.2938 | 6.9285 | 6.9111 | 6.8795 | 6.5918 | 6.4632 | 6.0836 | 5.8122 | 5.6183 | 5.2958 | 5.0581 | 3.9489 | 3.5958 | 3.5213 | 5.7708 | 5.7514 | 5.7086 | 5.4678 | 5.3586 | 4.9637 | 4.628 | 4.3821 | 4.0443 | 3.7331 | 2.5514 | 1.878 | 1.6157
|  | BURGHEAD | EE |  |  |  |  | 5.4193 | 5.4071 | 5.3754 | 4.955 | 4.806 | 4.3734 | 4.0213 | 3.7346 | 3.3295 | 3.0785 | 1.5785 | 0.6989 | 0.2938 | 6.9295 | 6.9132 | 6.8846 | 6.5999 | 6.4724 | 6.0958 | 5.8428 | 5.655 | 5.3295 | 5.1326 | 4.0142 | 3.605 | 3.5213 | 5.7708 | 5.7525 | 5.7117 | 5.477 | 5.3698 | 4.9841 | 4.681 | 4.4423 | 4.081 | 3.8525 | 2.5514 | 1.878 | 1.6157
|  | BURGHEAD | HT |  |  |  |  | 5.4224 | 5.4081 | 5.3713 | 4.9397 | 4.7918 | 4.356 | 4.002 | 3.7162 | 3.3193 | 3.0652 | 1.7091 | 0.83359 | 0.39686 | 6.9295 | 6.9111 | 6.8795 | 6.5918 | 6.4632 | 6.0836 | 5.8122 | 5.6183 | 5.2958 | 5.0948 | 3.9489 | 3.5958 | 3.6703 | 5.7729 | 5.7514 | 5.7086 | 5.4678 | 5.3586 | 4.9688 | 4.6576 | 4.4188 | 4.0637 | 3.8321 | 2.6106 | 1.9555 | 1.7035
|  | BURGHEAD | HE |  |  |  |  | 5.4224 | 5.4091 | 5.3764 | 4.9428 | 4.7897 | 4.3458 | 3.954 | 3.654 | 3.2652 | 2.9183 | 2.0979 | 1.154 | 0.88971 | 6.9285 | 6.9122 | 6.8816 | 6.5948 | 6.4673 | 6.0918 | 5.8142 | 5.6305 | 5.3479 | 5.0581 | 4.4734 | 4.0407 | 4.0775 | 5.7719 | 5.7525 | 5.7127 | 5.4708 | 5.3586 | 4.9637 | 4.628 | 4.3821 | 4.0443 | 3.7331 | 3.0055 | 2.2861 | 2.13
|  | BURGHEAD | FB |  |  |  |  | 5.4754 | 5.5081 | 5.5244 | 5.205 | 5.1244 | 5.0418 | 4.8173 | 4.6673 | 4.5183 | 4.4142 | 3.5591 | 2.5642 | 1.8785 | 6.9642 | 6.9713 | 6.9744 | 6.7234 | 6.6601 | 6.5928 | 6.3642 | 6.2213 | 6.0734 | 5.952 | 5.2642 | 4.3907 | 3.6132 | 5.8249 | 5.8474 | 5.8545 | 5.6463 | 5.5984 | 5.5525 | 5.3555 | 5.2127 | 5.0688 | 4.9627 | 4.2025 | 3.1433 | 2.6821
| BURGHMUIR | BURGHMUIR | MINIMUM HEADROOM | NO 08256 23702 | NO | YES | 13.56 | -6.876 | -6.9545 | -7.0433 | -7.4249 | -7.6249 | -8.4209 | -9.429 | -10.1137 | -10.7903 | -11.6423 | -15.6903 | -18.2005 | -19.2505 | -4.7418 | -4.8326 | -4.8591 | -5.0785 | -5.1928 | -5.7377 | -6.3683 | -6.7867 | -7.1336 | -7.4602 | -9.5704 | -10.304 | -10.8244 | -5.3864 | -5.4813 | -5.5252 | -5.864 | -6.063 | -6.7915 | -7.6558 | -8.264 | -8.8252 | -9.5221 | -13.0619 | -14.9711 | -15.8109
|  | BURGHMUIR | EE |  |  |  |  | -6.8749 | -6.9545 | -6.9627 | -7.2566 | -7.4515 | -8.3739 | -9.3545 | -10.0739 | -10.7903 | -11.3586 | -14.9647 | -18.2005 | -19.2505 | -4.7367 | -4.8285 | -4.8265 | -5.0183 | -5.1408 | -5.7112 | -6.3122 | -6.704 | -7.0785 | -7.4459 | -9.2734 | -10.304 | -10.7122 | -5.3854 | -5.4813 | -5.5007 | -5.7548 | -5.9466 | -6.7568 | -7.6007 | -8.2191 | -8.8252 | -9.3568 | -12.5252 | -14.9711 | -15.8109
|  | BURGHMUIR | HT |  |  |  |  | -6.8719 | -6.9535 | -7.0433 | -7.4249 | -7.6249 | -8.276 | -9.0209 | -9.7903 | -10.7729 | -11.6423 | -15.6903 | -17.9739 | -18.8025 | -4.7408 | -4.8326 | -4.8591 | -5.0785 | -5.1928 | -5.4979 | -5.8489 | -6.2326 | -6.7765 | -7.4061 | -9.5704 | -10.1673 | -10.2469 | -5.3834 | -5.4783 | -5.5252 | -5.864 | -6.063 | -6.613 | -7.2313 | -7.865 | -8.6874 | -9.5221 | -13.0619 | -14.8293 | -15.4303
|  | BURGHMUIR | HE |  |  |  |  | -6.876 | -6.9505 | -6.9974 | -7.3535 | -7.5729 | -8.4209 | -9.429 | -10.1137 | -10.777 | -11.2474 | -14.677 | -17.1617 | -18.0341 | -4.7418 | -4.8306 | -4.8408 | -5.0469 | -5.1632 | -5.7377 | -6.3683 | -6.7867 | -7.1336 | -7.4602 | -9.0775 | -9.9387 | -10.3846 | -5.3864 | -5.4783 | -5.4966 | -5.816 | -6.0283 | -6.7915 | -7.6558 | -8.264 | -8.815 | -9.264 | -12.0772 | -13.9793 | -14.7058
|  | BURGHMUIR | FB |  |  |  |  | -6.7086 | -6.6382 | -6.577 | -6.7464 | -6.8066 | -7.0903 | -7.4413 | -7.8331 | -8.028 | -8.176 | -9.7719 | -13.479 | -14.5545 | -4.6244 | -4.604 | -4.5795 | -4.7581 | -4.8122 | -5.0867 | -5.4153 | -5.7724 | -5.9183 | -6.0857 | -7.2857 | -9.5663 | -10.8244 | -5.2405 | -5.1946 | -5.1456 | -5.3221 | -5.366 | -5.6405 | -5.9711 | -6.3528 | -6.5323 | -6.7068 | -8.1487 | -11.5038 | -12.4691
| CLACHAN | BUTTERBRIDGE | MINIMUM HEADROOM | NN 19306 09936 | YES | YES | 0 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.098612 | 0.098612 | 0.098612 | 0.099633 | 0.099633 | 0.084327 | 0.084327 | 0.086367 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.091653 | 0.091653 | 0.091653 | 0.091653 | 0.091653 | 0.077367 | 0.077367 | 0.078388 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.095133 | 0.095133 | 0.095133 | 0.095133 | 0.095133 | 0.080847 | 0.081867 | 0.081867
|  | BUTTERBRIDGE | EE |  |  |  |  | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.10473 | 0.1129 | 0.086367 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.096755 | 0.10594 | 0.078388 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10126 | 0.10942 | 0.081867
|  | BUTTERBRIDGE | HT |  |  |  |  | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.10473 | 0.10473 | 0.10473 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.096755 | 0.096755 | 0.096755 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10126 | 0.10126 | 0.10126
|  | BUTTERBRIDGE | HE |  |  |  |  | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.10473 | 0.1129 | 0.1129 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.096755 | 0.10594 | 0.10594 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10126 | 0.10942 | 0.10942
|  | BUTTERBRIDGE | FB |  |  |  |  | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.098612 | 0.098612 | 0.098612 | 0.099633 | 0.099633 | 0.084327 | 0.084327 | 0.086367 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.091653 | 0.091653 | 0.091653 | 0.091653 | 0.091653 | 0.077367 | 0.077367 | 0.078388 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.095133 | 0.095133 | 0.095133 | 0.095133 | 0.095133 | 0.080847 | 0.081867 | 0.081867
| BRACO | CALLANDER | MINIMUM HEADROOM | NN 62995 07081 | NO | YES | 0.581 | 2.511 | 2.4988 | 2.3855 | 2.3192 | 1.9641 | 1.558 | 1.1457 | 0.95286 | 0.63755 | 0.34878 | -0.87367 | -1.9992 | -2.8094 | 3.6386 | 3.6457 | 3.5467 | 3.5212 | 3.4376 | 3.2835 | 3.1304 | 3.0427 | 2.8182 | 2.6355 | 1.8916 | 1.509 | 1.2518 | 3.0355 | 3.0304 | 2.9192 | 2.8641 | 2.7569 | 2.4457 | 2.0896 | 1.9763 | 1.7171 | 1.4753 | 0.5498 | -0.076735 | -0.65633
|  | CALLANDER | EE |  |  |  |  | 2.5131 | 2.5029 | 2.3896 | 2.3243 | 1.9702 | 1.6151 | 1.1661 | 0.95286 | 0.65694 | 0.37633 | -0.87367 | -1.9716 | -2.7094 | 3.6396 | 3.6498 | 3.5529 | 3.5304 | 3.4498 | 3.3171 | 3.1406 | 3.0427 | 2.8692 | 2.6876 | 1.9661 | 1.5427 | 1.2518 | 3.0365 | 3.0345 | 2.9263 | 2.8743 | 2.7886 | 2.4937 | 2.1039 | 1.9763 | 1.7355 | 1.4998 | 0.60082 | -0.052245 | -0.60224
|  | CALLANDER | HT |  |  |  |  | 2.511 | 2.4988 | 2.3855 | 2.3192 | 1.9651 | 1.558 | 1.2365 | 1.0161 | 0.64265 | 0.35184 | -0.86551 | -1.9992 | -2.8094 | 3.6386 | 3.6457 | 3.5467 | 3.5212 | 3.4376 | 3.2835 | 3.1508 | 3.0498 | 2.8182 | 2.6355 | 1.8916 | 1.509 | 1.3018 | 3.0355 | 3.0304 | 2.9192 | 2.8641 | 2.7569 | 2.4457 | 2.1763 | 2.0406 | 1.7294 | 1.4896 | 0.5498 | -0.076735 | -0.65633
|  | CALLANDER | HE |  |  |  |  | 2.512 | 2.5039 | 2.3927 | 2.3222 | 1.9641 | 1.5957 | 1.1457 | 0.99571 | 0.63755 | 0.34878 | -0.51959 | -1.339 | -1.8737 | 3.6396 | 3.6498 | 3.5518 | 3.5294 | 3.4488 | 3.312 | 3.1304 | 3.0671 | 2.8569 | 2.6733 | 2.1855 | 2.0192 | 1.8253 | 3.0376 | 3.0355 | 2.9273 | 2.8702 | 2.7824 | 2.4773 | 2.0896 | 2.0192 | 1.7171 | 1.4753 | 0.82837 | 0.52122 | 0.13449
|  | CALLANDER | FB |  |  |  |  | 2.5651 | 2.5784 | 2.5253 | 2.4947 | 2.4376 | 2.0682 | 2.0171 | 1.9396 | 1.8773 | 1.6784 | 1.2294 | 0.42633 | -0.19816 | 3.6763 | 3.6947 | 3.6549 | 3.6416 | 3.6131 | 3.5212 | 3.5049 | 3.4631 | 3.4202 | 3.3284 | 2.9671 | 2.2518 | 1.6018 | 3.0824 | 3.0967 | 3.0529 | 3.0284 | 2.9937 | 2.8978 | 2.861 | 2.7967 | 2.7212 | 2.5273 | 2.0916 | 1.3284 | 0.99673
| STORNOWAY | CALLANISH | MINIMUM HEADROOM | NB 22040 33554 | YES | YES | 0.295 | -0.30306 | -0.38673 | -0.40204 | -0.43673 | -0.48673 | -0.60612 | -0.72041 | -0.85408 | -0.98367 | -1.0551 | -1.3235 | -1.6 | -1.801 | 0.21735 | 0.15714 | 0.15816 | 0.14694 | 0.14184 | 0.095918 | 0.060204 | -0.016327 | -0.083673 | -0.12449 | -0.31429 | -0.33061 | -0.31531 | 0.19694 | 0.12245 | 0.11122 | 0.055102 | -0.0061224 | -0.083673 | -0.15408 | -0.2551 | -0.35102 | -0.4051 | -0.62551 | -0.75612 | -0.88673
|  | CALLANISH | EE |  |  |  |  | -0.30204 | -0.30918 | -0.40204 | -0.43367 | -0.48163 | -0.60306 | -0.71122 | -0.84694 | -0.97347 | -1.0398 | -1.3235 | -1.6 | -1.7939 | 0.21735 | 0.22551 | 0.15918 | 0.14796 | 0.14286 | 0.097959 | 0.061224 | -0.016327 | -0.083673 | -0.12449 | -0.28469 | -0.30612 | -0.28265 | 0.2 | 0.19388 | 0.11122 | 0.055102 | -0.0030612 | -0.082653 | -0.15102 | -0.25408 | -0.35 | -0.4051 | -0.62551 | -0.75306 | -0.88061
|  | CALLANISH | HT |  |  |  |  | -0.30306 | -0.38673 | -0.39796 | -0.43061 | -0.47653 | -0.58673 | -0.6949 | -0.82653 | -0.94898 | -1.0122 | -1.2194 | -1.5224 | -1.801 | 0.21735 | 0.15714 | 0.15816 | 0.14796 | 0.14286 | 0.095918 | 0.060204 | -0.013265 | -0.081633 | -0.12143 | -0.31429 | -0.33061 | -0.30816 | 0.19694 | 0.12245 | 0.11122 | 0.056122 | -0.0010204 | -0.076531 | -0.14694 | -0.24592 | -0.34286 | -0.39286 | -0.61224 | -0.73163 | -0.88673
|  | CALLANISH | HE |  |  |  |  | -0.30204 | -0.30816 | -0.4 | -0.43673 | -0.48673 | -0.60612 | -0.72041 | -0.85408 | -0.98367 | -1.0551 | -1.2388 | -1.5929 | -1.7878 | 0.21837 | 0.22449 | 0.1602 | 0.14694 | 0.14184 | 0.097959 | 0.060204 | -0.015306 | -0.081633 | -0.12041 | -0.28265 | -0.31224 | -0.30918 | 0.2 | 0.1949 | 0.11224 | 0.055102 | -0.0061224 | -0.083673 | -0.15408 | -0.2551 | -0.35102 | -0.40408 | -0.59286 | -0.75612 | -0.88265
|  | CALLANISH | FB |  |  |  |  | -0.27245 | -0.25918 | -0.24796 | -0.33571 | -0.34184 | -0.35102 | -0.36531 | -0.37857 | -0.37959 | -0.39592 | -0.53776 | -0.73776 | -0.80612 | 0.25306 | 0.26531 | 0.27143 | 0.2051 | 0.21122 | 0.19898 | 0.17551 | 0.16633 | 0.13673 | 0.097959 | -0.036735 | -0.22653 | -0.31531 | 0.23776 | 0.24694 | 0.2398 | 0.15714 | 0.13776 | 0.11531 | 0.076531 | 0.057143 | 0.015306 | -0.030612 | -0.17041 | -0.40306 | -0.4398
| TUMMEL BRIDGE | CALVINE | MINIMUM HEADROOM | NN 80186 65270 | YES | YES | 0.587 | -0.74898 | -0.75408 | -0.75816 | -0.77857 | -0.79082 | -0.85816 | -0.88776 | -0.93265 | -0.95204 | -1.0102 | -1.0908 | -1.1602 | -1.2224 | -0.2102 | -0.21429 | -0.21837 | -0.22653 | -0.23265 | -0.28878 | -0.30612 | -0.33673 | -0.3449 | -0.38776 | -0.47857 | -0.47857 | -0.46633 | -0.3949 | -0.40102 | -0.4051 | -0.41429 | -0.42245 | -0.46633 | -0.48469 | -0.52857 | -0.54388 | -0.59592 | -0.69184 | -0.71531 | -0.75102
|  | CALVINE | EE |  |  |  |  | -0.74898 | -0.75408 | -0.75816 | -0.77653 | -0.78776 | -0.80918 | -0.8398 | -0.86327 | -0.88265 | -0.96429 | -1.0765 | -1.1357 | -1.1806 | -0.2102 | -0.21429 | -0.21837 | -0.22653 | -0.23163 | -0.2398 | -0.25816 | -0.26633 | -0.27449 | -0.33878 | -0.42551 | -0.42245 | -0.42041 | -0.3949 | -0.40102 | -0.4051 | -0.41327 | -0.41837 | -0.43469 | -0.4551 | -0.46837 | -0.48163 | -0.54286 | -0.66837 | -0.68163 | -0.7102
|  | CALVINE | HT |  |  |  |  | -0.74898 | -0.75408 | -0.75612 | -0.77449 | -0.78571 | -0.85816 | -0.88776 | -0.93265 | -0.95204 | -1.0102 | -1.0908 | -1.1602 | -1.2224 | -0.2102 | -0.21327 | -0.21837 | -0.22653 | -0.23265 | -0.28878 | -0.30612 | -0.33673 | -0.3449 | -0.38776 | -0.47857 | -0.47857 | -0.46633 | -0.3949 | -0.40102 | -0.40408 | -0.41224 | -0.41939 | -0.46633 | -0.48469 | -0.52857 | -0.54388 | -0.59592 | -0.69184 | -0.71531 | -0.75102
|  | CALVINE | HE |  |  |  |  | -0.74898 | -0.75408 | -0.75714 | -0.77857 | -0.79082 | -0.81429 | -0.8449 | -0.86633 | -0.89082 | -0.89694 | -0.94388 | -1.0143 | -1.0663 | -0.2102 | -0.21429 | -0.21837 | -0.22653 | -0.23265 | -0.24082 | -0.2602 | -0.26633 | -0.27551 | -0.28878 | -0.31735 | -0.32347 | -0.32245 | -0.3949 | -0.40102 | -0.40408 | -0.41429 | -0.42245 | -0.43571 | -0.45714 | -0.47143 | -0.48469 | -0.50102 | -0.53469 | -0.55612 | -0.58878
|  | CALVINE | FB |  |  |  |  | -0.73878 | -0.74286 | -0.74286 | -0.74082 | -0.74694 | -0.7551 | -0.75918 | -0.76429 | -0.77449 | -0.78673 | -0.83163 | -0.87653 | -0.89694 | -0.20102 | -0.20612 | -0.20408 | -0.20612 | -0.20816 | -0.21327 | -0.21531 | -0.22041 | -0.23061 | -0.23673 | -0.26429 | -0.29184 | -0.30306 | -0.38469 | -0.3898 | -0.3898 | -0.3898 | -0.39286 | -0.39898 | -0.40408 | -0.4051 | -0.41531 | -0.42551 | -0.45612 | -0.4949 | -0.50306
| CARRADALE 1 | CAMPBELTOWN | MINIMUM HEADROOM | NR 71509 20746 | NO | YES | 0.486 | 8.3612 | 8.2867 | 7.9735 | 7.551 | 6.9255 | 6.0735 | 3.8357 | 0.90816 | -1.3888 | -2.1673 | -9.6765 | -20.5214 | -25.9122 | 8.948 | 8.8327 | 8.4776 | 8.1 | 7.499 | 6.851 | 4.3286 | 1.148 | -1.3337 | -2.0857 | -10.7439 | -22.1837 | -28.0694 | 8.8566 | 8.8342 | 8.5097 | 8.127 | 7.5117 | 6.7444 | 4.1607 | 0.87704 | -1.7464 | -2.5434 | -11.3556 | -23.6403 | -29.873
|  | CAMPBELTOWN | EE |  |  |  |  | 8.3612 | 8.2888 | 7.9735 | 7.551 | 6.9255 | 6.0735 | 4.4408 | 1.95 | -1.3888 | -2.1673 | -7.749 | -20.5214 | -25.9122 | 8.948 | 8.8337 | 8.4786 | 8.101 | 7.501 | 6.851 | 5.1847 | 2.5255 | -1.3337 | -2.0857 | -7.7082 | -22.1837 | -28.0694 | 8.8577 | 8.8362 | 8.5097 | 8.127 | 7.5128 | 6.7444 | 4.973 | 2.2087 | -1.7464 | -2.5434 | -8.6077 | -23.6403 | -29.873
|  | CAMPBELTOWN | HT |  |  |  |  | 8.3633 | 8.2878 | 7.9755 | 7.5714 | 6.952 | 6.1796 | 3.8357 | 1.1082 | 0.4898 | -0.37449 | -6.3041 | -13.9061 | -25.0204 | 8.948 | 8.8327 | 8.4776 | 8.1 | 7.499 | 6.9041 | 4.3286 | 1.3745 | 0.92755 | 0.072449 | -6.2418 | -14.302 | -27.299 | 8.8577 | 8.8342 | 8.5128 | 8.1372 | 7.524 | 6.826 | 4.1607 | 1.1046 | 0.55969 | -0.33929 | -6.9219 | -15.4821 | -28.8658
|  | CAMPBELTOWN | HE |  |  |  |  | 8.3612 | 8.2867 | 7.9776 | 7.5561 | 6.9276 | 6.1204 | 4.3449 | 0.90816 | 0.32857 | -1.4235 | -9.6765 | -17.9939 | -19.0847 | 8.948 | 8.8337 | 8.4796 | 8.102 | 7.5 | 6.8735 | 5.001 | 1.148 | 0.72245 | -1.2286 | -10.7439 | -20.0245 | -20.7306 | 8.8566 | 8.8342 | 8.5128 | 8.1301 | 7.5117 | 6.7781 | 4.8219 | 0.87704 | 0.36071 | -1.6291 | -11.3556 | -21.1495 | -22.1199
|  | CAMPBELTOWN | FB |  |  |  |  | 8.5071 | 8.4745 | 8.4418 | 8.4071 | 8.3663 | 8.0255 | 7.0204 | 5.7908 | 3.2173 | 2.2388 | -0.30306 | -3.9143 | -7.4786 | 9.0673 | 8.9704 | 8.8786 | 8.8041 | 8.7051 | 8.3418 | 7.1306 | 5.6582 | 2.5276 | 1.3735 | -1.3704 | -5.1082 | -9.0347 | 8.9638 | 8.9801 | 8.9719 | 8.923 | 8.8413 | 8.4954 | 7.2862 | 5.8158 | 2.6934 | 1.5944 | -1.1872 | -6.0699 | -9.0832
| COUPAR ANGUS | CAPUTH | MINIMUM HEADROOM | NO 09277 40265 | NO | NO | 0.868 | 5.351 | 5.3684 | 5.2061 | 4.9663 | 4.651 | 4.1061 | 3.6143 | 3.0531 | 2.552 | 1.9408 | 0.38571 | -0.72857 | -1.5082 | 7.802 | 7.7969 | 7.7449 | 7.5378 | 7.2633 | 6.8602 | 6.4908 | 6.0827 | 5.7102 | 5.1898 | 4.0571 | 3.5796 | 3.2214 | 6.7031 | 6.7041 | 6.5306 | 6.302 | 6.002 | 5.5163 | 5.0704 | 4.5694 | 4.1184 | 3.5367 | 2.1531 | 1.2786 | 0.68878
|  | CAPUTH | EE |  |  |  |  | 5.351 | 5.3684 | 5.2061 | 4.9765 | 4.6714 | 4.149 | 3.6143 | 3.0857 | 2.5816 | 1.9408 | 0.38571 | -0.72857 | -1.5082 | 7.802 | 7.7969 | 7.7449 | 7.5398 | 7.2653 | 6.8847 | 6.4908 | 6.0888 | 5.7102 | 5.1898 | 4.1 | 3.5796 | 3.2214 | 6.7031 | 6.7041 | 6.5306 | 6.3133 | 6.0143 | 5.552 | 5.0704 | 4.5929 | 4.1378 | 3.5367 | 2.1531 | 1.2786 | 0.68878
|  | CAPUTH | HT |  |  |  |  | 5.3541 | 5.3735 | 5.2184 | 4.9949 | 4.6918 | 4.1888 | 3.7133 | 3.1908 | 2.6582 | 2.0276 | 0.57653 | -0.57245 | -1.35 | 7.8031 | 7.798 | 7.7459 | 7.5408 | 7.2643 | 6.8816 | 6.5316 | 6.1265 | 5.7163 | 5.2041 | 4.0571 | 3.601 | 3.4765 | 6.7041 | 6.7071 | 6.5388 | 6.302 | 6.0276 | 5.5745 | 5.1449 | 4.6704 | 4.1827 | 3.5939 | 2.2571 | 1.3776 | 0.8551
|  | CAPUTH | HE |  |  |  |  | 5.3531 | 5.3724 | 5.2122 | 4.9663 | 4.651 | 4.1061 | 3.6143 | 3.0531 | 2.552 | 1.9816 | 0.99388 | -0.14184 | -0.82041 | 7.802 | 7.801 | 7.7449 | 7.5378 | 7.2633 | 6.8602 | 6.5071 | 6.0827 | 5.7102 | 5.2714 | 4.5561 | 4.0582 | 3.7459 | 6.7041 | 6.7071 | 6.5347 | 6.3071 | 6.002 | 5.5163 | 5.0796 | 4.5694 | 4.1184 | 3.5939 | 2.7041 | 1.8245 | 1.3122
|  | CAPUTH | FB |  |  |  |  | 5.602 | 5.4265 | 5.4398 | 5.448 | 5.3531 | 5.1551 | 4.9429 | 4.7612 | 4.5582 | 4.3898 | 3.4214 | 2.2071 | 1.2694 | 7.9 | 7.85 | 7.8531 | 7.8469 | 7.7857 | 7.6102 | 7.4102 | 7.248 | 7.0592 | 6.8929 | 6.0408 | 4.8745 | 3.8429 | 6.9551 | 6.75 | 6.748 | 6.7449 | 6.6255 | 6.4316 | 6.2469 | 6.0755 | 5.8776 | 5.7122 | 4.799 | 3.4347 | 2.7357
| ARBROATH | CARNOUSTIE | MINIMUM HEADROOM | NO 55631 35403 | NO | YES | 1.399 | 6.1857 | 5.6898 | 5.4163 | 5.0265 | 4.8796 | 4.2898 | 3.6337 | 2.949 | 2.2765 | 1.6837 | -0.48878 | -2.6918 | -3.6867 | 7.3939 | 6.8459 | 6.6122 | 6.3214 | 6.1684 | 5.8398 | 5.5041 | 5.1214 | 4.7418 | 4.3704 | 3.1898 | 2.3704 | 2.2429 | 6.8311 | 6.3321 | 6.0791 | 5.7321 | 5.5801 | 5.0526 | 4.5015 | 3.9158 | 3.3362 | 2.8199 | 1.024 | -0.62398 | -1.2474
|  | CARNOUSTIE | EE |  |  |  |  | 6.2449 | 5.6898 | 5.4276 | 5.0653 | 4.9408 | 4.3786 | 3.7724 | 3.0837 | 2.4735 | 1.8367 | -0.48878 | -2.6918 | -3.6867 | 7.4418 | 6.8469 | 6.6214 | 6.3449 | 6.1898 | 5.8561 | 5.5633 | 5.1418 | 4.801 | 4.3786 | 3.2194 | 2.3704 | 2.2429 | 6.8842 | 6.3332 | 6.0862 | 5.7617 | 5.6199 | 5.1209 | 4.6087 | 4.0015 | 3.4811 | 2.9128 | 1.024 | -0.62398 | -1.2474
|  | CARNOUSTIE | HT |  |  |  |  | 6.2102 | 5.7031 | 5.4163 | 5.0337 | 4.9051 | 4.402 | 3.8286 | 3.2102 | 2.648 | 2.051 | -0.3102 | -2.3429 | -3.6439 | 7.4133 | 6.8531 | 6.6122 | 6.3214 | 6.1684 | 5.8765 | 5.5378 | 5.1449 | 4.8112 | 4.4224 | 3.1898 | 2.7041 | 2.5694 | 6.8546 | 6.3423 | 6.0791 | 5.7332 | 5.5934 | 5.1505 | 4.6362 | 4.0862 | 3.5944 | 3.0617 | 1.1291 | -0.32398 | -1.176
|  | CARNOUSTIE | HE |  |  |  |  | 6.1857 | 5.6908 | 5.4245 | 5.0265 | 4.8796 | 4.2898 | 3.6337 | 2.949 | 2.2765 | 1.6837 | -0.13673 | -1.8582 | -2.6755 | 7.3939 | 6.8459 | 6.6184 | 6.3327 | 6.1755 | 5.8398 | 5.5041 | 5.1214 | 4.7418 | 4.3704 | 3.3439 | 2.8847 | 2.6082 | 6.8311 | 6.3321 | 6.0852 | 5.7321 | 5.5801 | 5.0526 | 4.5015 | 3.9158 | 3.3362 | 2.8199 | 1.2954 | 0.078061 | -0.4801
|  | CARNOUSTIE | FB |  |  |  |  | 6.4969 | 6.2878 | 5.9316 | 5.7827 | 5.598 | 5.4561 | 5.4224 | 5.3 | 5.1235 | 4.9622 | 4.1061 | 2.6031 | 1.8408 | 7.6531 | 7.4561 | 6.9837 | 6.8286 | 6.6071 | 6.4571 | 6.4255 | 6.2949 | 6.0745 | 5.8459 | 4.9541 | 3.4061 | 2.3439 | 7.1372 | 6.9342 | 6.5281 | 6.3985 | 6.2087 | 6.0689 | 6.0413 | 5.9209 | 5.7342 | 5.5311 | 4.6495 | 3.0515 | 2.5107
| KILLIN | CASHLIE | MINIMUM HEADROOM | NN 50711 42144 | YES | YES | 0.02 | 0.86735 | 0.86327 | 0.8551 | 0.85102 | 0.8449 | 0.83469 | 0.82347 | 0.81429 | 0.80102 | 0.79286 | 0.77041 | 0.75 | 0.73469 | 0.9102 | 0.90714 | 0.90306 | 0.89796 | 0.88571 | 0.87857 | 0.87143 | 0.86429 | 0.85408 | 0.8449 | 0.82653 | 0.82857 | 0.83265 | 0.89388 | 0.88878 | 0.88265 | 0.87959 | 0.87347 | 0.86633 | 0.85918 | 0.85 | 0.8398 | 0.83367 | 0.81531 | 0.8051 | 0.7949
|  | CASHLIE | EE |  |  |  |  | 0.86735 | 0.86327 | 0.85612 | 0.85306 | 0.84592 | 0.83673 | 0.82653 | 0.81735 | 0.80408 | 0.79388 | 0.77041 | 0.75 | 0.73673 | 0.91224 | 0.90714 | 0.90306 | 0.89796 | 0.88571 | 0.87857 | 0.87143 | 0.86429 | 0.85408 | 0.8449 | 0.82857 | 0.83367 | 0.84082 | 0.89388 | 0.88878 | 0.88367 | 0.88061 | 0.87347 | 0.86837 | 0.86122 | 0.85204 | 0.84082 | 0.83469 | 0.81531 | 0.8051 | 0.8
|  | CASHLIE | HT |  |  |  |  | 0.86735 | 0.86327 | 0.85918 | 0.85408 | 0.84694 | 0.83776 | 0.82959 | 0.82041 | 0.80714 | 0.79898 | 0.77857 | 0.7551 | 0.73469 | 0.91224 | 0.90714 | 0.90306 | 0.89796 | 0.88571 | 0.87857 | 0.87143 | 0.86531 | 0.85408 | 0.8449 | 0.82653 | 0.82857 | 0.83367 | 0.89388 | 0.88878 | 0.88673 | 0.88163 | 0.87449 | 0.86837 | 0.86224 | 0.85408 | 0.84286 | 0.83776 | 0.82041 | 0.80714 | 0.7949
|  | CASHLIE | HE |  |  |  |  | 0.86735 | 0.86327 | 0.8551 | 0.85102 | 0.8449 | 0.83469 | 0.82347 | 0.81429 | 0.80102 | 0.79286 | 0.77653 | 0.75204 | 0.73571 | 0.91224 | 0.90714 | 0.90306 | 0.89796 | 0.88571 | 0.87857 | 0.87143 | 0.86531 | 0.85408 | 0.8449 | 0.82959 | 0.83163 | 0.83265 | 0.89388 | 0.88878 | 0.88265 | 0.87959 | 0.87347 | 0.86633 | 0.85918 | 0.85 | 0.8398 | 0.83367 | 0.81837 | 0.80612 | 0.79592
|  | CASHLIE | FB |  |  |  |  | 0.86939 | 0.86633 | 0.86837 | 0.86735 | 0.86122 | 0.85816 | 0.85714 | 0.85204 | 0.84796 | 0.84388 | 0.82551 | 0.8102 | 0.80306 | 0.9102 | 0.90714 | 0.90918 | 0.90612 | 0.89898 | 0.89694 | 0.89184 | 0.88673 | 0.88163 | 0.87551 | 0.85918 | 0.84796 | 0.84388 | 0.89592 | 0.89388 | 0.8949 | 0.89286 | 0.88776 | 0.88367 | 0.88367 | 0.87959 | 0.87551 | 0.87245 | 0.85714 | 0.8449 | 0.83878
| KILLIN | CHAORACH | MINIMUM HEADROOM | NN 45400 27553 | YES | YES | 0.023 | 0.27857 | 0.28163 | 0.27755 | 0.27347 | 0.26633 | 0.26531 | 0.25714 | 0.25408 | 0.25 | 0.24694 | 0.23265 | 0.22347 | 0.21633 | -0.086735 | -0.083673 | -0.086735 | -0.086735 | -0.091837 | -0.093878 | -0.094898 | -0.1 | -0.1 | -0.10408 | -0.11429 | -0.11531 | -0.11735 | -0.23571 | -0.23367 | -0.24082 | -0.24286 | -0.24898 | -0.25102 | -0.25714 | -0.26224 | -0.26327 | -0.26633 | -0.27755 | -0.28776 | -0.3
|  | CHAORACH | EE |  |  |  |  | 0.27857 | 0.28163 | 0.28163 | 0.27857 | 0.27143 | 0.27143 | 0.26327 | 0.26224 | 0.25816 | 0.25408 | 0.24082 | 0.23265 | 0.22347 | -0.086735 | -0.082653 | -0.081633 | -0.081633 | -0.089796 | -0.090816 | -0.092857 | -0.094898 | -0.095918 | -0.1 | -0.10714 | -0.11122 | -0.11531 | -0.23571 | -0.23265 | -0.23265 | -0.23265 | -0.24286 | -0.24592 | -0.24796 | -0.25102 | -0.25408 | -0.25714 | -0.26837 | -0.28163 | -0.29286
|  | CHAORACH | HT |  |  |  |  | 0.27857 | 0.28163 | 0.27755 | 0.27347 | 0.26633 | 0.26531 | 0.25714 | 0.25408 | 0.25 | 0.24694 | 0.23265 | 0.22347 | 0.21633 | -0.086735 | -0.083673 | -0.086735 | -0.086735 | -0.091837 | -0.093878 | -0.094898 | -0.1 | -0.1 | -0.10408 | -0.11429 | -0.11531 | -0.11735 | -0.23571 | -0.23367 | -0.24082 | -0.24286 | -0.24898 | -0.25102 | -0.25714 | -0.26224 | -0.26327 | -0.26633 | -0.27755 | -0.28776 | -0.3
|  | CHAORACH | HE |  |  |  |  | 0.27857 | 0.28163 | 0.28265 | 0.27857 | 0.27143 | 0.27041 | 0.26327 | 0.26224 | 0.25816 | 0.25408 | 0.24082 | 0.23265 | 0.22347 | -0.086735 | -0.083673 | -0.081633 | -0.081633 | -0.089796 | -0.091837 | -0.092857 | -0.095918 | -0.095918 | -0.1 | -0.10714 | -0.11224 | -0.11735 | -0.23571 | -0.23367 | -0.23265 | -0.23265 | -0.24388 | -0.24694 | -0.24796 | -0.25204 | -0.2551 | -0.25816 | -0.26939 | -0.28061 | -0.29388
|  | CHAORACH | FB |  |  |  |  | 0.28163 | 0.28163 | 0.28265 | 0.27959 | 0.27755 | 0.28061 | 0.27755 | 0.27449 | 0.27143 | 0.27449 | 0.26531 | 0.25816 | 0.2551 | -0.084694 | -0.082653 | -0.082653 | -0.083673 | -0.083673 | -0.082653 | -0.082653 | -0.085714 | -0.085714 | -0.085714 | -0.097959 | -0.10204 | -0.1051 | -0.23469 | -0.23163 | -0.23163 | -0.23367 | -0.23469 | -0.23367 | -0.23469 | -0.23469 | -0.23367 | -0.23265 | -0.2449 | -0.25 | -0.25
| ARBROATH | CHARLES AVENUE | MINIMUM HEADROOM | NO 62954 41097 | NO | YES | 1.139 | 4.5392 | 4.7953 | 4.8249 | 4.8902 | 4.8912 | 4.477 | 3.9821 | 3.6341 | 3.1137 | 2.7208 | 0.35961 | -1.5435 | -2.7669 | 6.7943 | 6.9759 | 6.9453 | 7.0096 | 7.0219 | 6.6504 | 6.2402 | 5.9627 | 5.579 | 5.3157 | 3.7076 | 2.778 | 2.13 | 5.6259 | 5.8219 | 5.7504 | 5.7912 | 5.7647 | 5.3341 | 4.8698 | 4.4963 | 3.9953 | 3.6341 | 1.4423 | -0.14856 | -1.1435
|  | CHARLES AVENUE | EE |  |  |  |  | 4.5392 | 4.7963 | 4.8341 | 4.8923 | 4.9025 | 4.477 | 3.9882 | 3.6341 | 3.1137 | 2.7208 | 0.35961 | -1.5435 | -2.7669 | 6.7943 | 6.978 | 6.9453 | 7.0127 | 7.0239 | 6.6504 | 6.2647 | 5.9627 | 5.579 | 5.3168 | 3.7076 | 2.778 | 2.13 | 5.6259 | 5.8239 | 5.7504 | 5.7933 | 5.7719 | 5.3341 | 4.8841 | 4.4963 | 3.9953 | 3.6341 | 1.4423 | -0.14856 | -1.1435
|  | CHARLES AVENUE | HT |  |  |  |  | 4.5525 | 4.7963 | 4.8249 | 4.9106 | 4.9198 | 4.7147 | 4.4096 | 4.0759 | 3.4596 | 2.8106 | 0.57083 | -1.2465 | -2.3608 | 6.8076 | 6.9759 | 6.9463 | 7.0096 | 7.0249 | 6.8545 | 6.5851 | 6.3259 | 5.8392 | 5.3157 | 3.8035 | 3.1423 | 2.8902 | 5.6412 | 5.8229 | 5.7565 | 5.8065 | 5.7821 | 5.6065 | 5.2923 | 4.9259 | 4.3249 | 3.7014 | 1.6453 | 0.17798 | -0.64447
|  | CHARLES AVENUE | HE |  |  |  |  | 4.5514 | 4.7953 | 4.8382 | 4.8902 | 4.8912 | 4.4872 | 3.9821 | 3.6423 | 3.1239 | 2.7933 | 1.1739 | -0.34958 | -1.0067 | 6.8065 | 6.977 | 6.9453 | 7.0106 | 7.0219 | 6.679 | 6.2402 | 5.978 | 5.6086 | 5.3974 | 4.2933 | 3.5892 | 3.2494 | 5.6412 | 5.8219 | 5.7525 | 5.7912 | 5.7647 | 5.3525 | 4.8698 | 4.5106 | 4.0219 | 3.728 | 2.2504 | 1.0086 | 0.52083
|  | CHARLES AVENUE | FB |  |  |  |  | 4.6351 | 4.9229 | 5.0412 | 5.2576 | 5.3933 | 5.3443 | 5.2341 | 5.1576 | 5.2106 | 5.2219 | 4.7402 | 3.0239 | 2.2045 | 6.8565 | 7.0494 | 7.0841 | 7.2198 | 7.2872 | 7.1606 | 6.9831 | 6.8494 | 6.827 | 6.7249 | 5.8484 | 3.9708 | 2.6749 | 5.7249 | 5.9576 | 5.9861 | 6.1433 | 6.2331 | 6.1433 | 6.0004 | 5.8821 | 5.9106 | 5.8882 | 5.1698 | 3.0851 | 2.5178
| CHARLESTON | CHARLESTON | MINIMUM HEADROOM | NO 35734 31818 | NO | YES | 1.962 | 7.6918 | 7.6908 | 7.6878 | 7.5112 | 7.4031 | 7.2816 | 7.0969 | 6.9531 | 6.8051 | 6.6929 | 5.5327 | 4.7531 | 4.4582 | 3.5337 | 3.5429 | 3.5459 | 3.4684 | 3.4214 | 3.3643 | 3.2102 | 3.05 | 2.7827 | 2.6429 | 1.6337 | 1.1143 | 0.88163 | 4.2495 | 4.2577 | 4.2556 | 4.1699 | 3.9791 | 3.7658 | 3.4434 | 3.1862 | 2.9056 | 2.7546 | 1.5577 | 0.84949 | 0.58929
|  | CHARLESTON | EE |  |  |  |  | 7.6929 | 7.6908 | 7.6888 | 7.5459 | 7.4459 | 7.3194 | 7.1867 | 7.0224 | 6.8582 | 6.7724 | 5.5327 | 4.7531 | 4.4582 | 3.5388 | 3.5459 | 3.5602 | 3.4939 | 3.448 | 3.3857 | 3.2898 | 3.1112 | 2.8357 | 2.7153 | 1.6337 | 1.1143 | 0.88163 | 4.2546 | 4.2607 | 4.273 | 4.1985 | 4.024 | 3.775 | 3.5628 | 3.2791 | 2.975 | 2.8423 | 1.5577 | 0.84949 | 0.58929
|  | CHARLESTON | HT |  |  |  |  | 7.6918 | 7.6969 | 7.6878 | 7.5112 | 7.4031 | 7.2816 | 7.0969 | 6.9531 | 6.8051 | 6.6929 | 5.5694 | 4.9122 | 4.7847 | 3.5337 | 3.5429 | 3.5459 | 3.4684 | 3.4214 | 3.3643 | 3.2102 | 3.05 | 2.7827 | 2.6429 | 1.6878 | 1.3051 | 1.2929 | 4.2495 | 4.2577 | 4.2556 | 4.1699 | 3.9791 | 3.7658 | 3.4434 | 3.1862 | 2.9056 | 2.7546 | 1.6107 | 1.0199 | 0.92602
|  | CHARLESTON | HE |  |  |  |  | 7.6918 | 7.6959 | 7.6888 | 7.5418 | 7.4439 | 7.3449 | 7.1694 | 7.0173 | 6.8735 | 6.8143 | 6.1704 | 5.5898 | 5.4694 | 3.5357 | 3.5459 | 3.5551 | 3.4847 | 3.4388 | 3.3888 | 3.252 | 3.0816 | 2.8398 | 2.7653 | 2.148 | 1.7092 | 1.6245 | 4.2505 | 4.2597 | 4.2679 | 4.1903 | 4.0117 | 3.8209 | 3.5117 | 3.2474 | 2.9821 | 2.9046 | 2.1832 | 1.6607 | 1.5811
|  | CHARLESTON | FB |  |  |  |  | 7.7276 | 7.7459 | 7.7612 | 7.652 | 7.6347 | 7.6276 | 7.5949 | 7.5112 | 7.4327 | 7.3796 | 7.0235 | 6.4704 | 5.8133 | 3.5551 | 3.5684 | 3.5806 | 3.5306 | 3.5235 | 3.5214 | 3.4949 | 3.4439 | 3.398 | 3.3286 | 2.8561 | 1.9867 | 1.1735 | 4.2811 | 4.3026 | 4.3179 | 4.273 | 4.273 | 4.275 | 4.2536 | 4.0872 | 3.9617 | 3.8526 | 3.2189 | 2.3383 | 1.7668
| ARDMORE | CLACHAN | MINIMUM HEADROOM | NF 81863 64360 | NO | YES | 0.996 | -0.074735 | -0.23188 | -0.24616 | -0.27576 | -0.36045 | -0.48902 | -0.588 | -1.0074 | -1.1747 | -1.2502 | -1.6502 | -1.8564 | -2.0104 | 0.72527 | 0.56302 | 0.55588 | 0.51098 | 0.41812 | 0.34159 | 0.29363 | -0.10535 | -0.23392 | -0.30535 | -0.67576 | -0.688 | -0.59412 | 0.58751 | 0.39363 | 0.38241 | 0.34261 | 0.262 | 0.18751 | 0.11404 | -0.28494 | -0.42882 | -0.49514 | -0.8329 | -0.98086 | -1.039
|  | CLACHAN | EE |  |  |  |  | -0.074735 | -0.073714 | -0.24616 | -0.27167 | -0.31351 | -0.48698 | -0.5829 | -0.87678 | -1.1247 | -1.2186 | -1.6502 | -1.8553 | -2.0013 | 0.72527 | 0.70996 | 0.55588 | 0.512 | 0.45996 | 0.3518 | 0.30282 | 0.047714 | -0.16045 | -0.24208 | -0.60535 | -0.60024 | -0.56555 | 0.58751 | 0.58751 | 0.38241 | 0.34567 | 0.31608 | 0.18955 | 0.11812 | -0.14922 | -0.37065 | -0.45127 | -0.82984 | -0.95229 | -1.0247
|  | CLACHAN | HT |  |  |  |  | -0.074735 | -0.23188 | -0.2431 | -0.26861 | -0.36045 | -0.4829 | -0.57882 | -1.0074 | -1.1747 | -1.2502 | -1.6115 | -1.8564 | -2.0104 | 0.72527 | 0.56302 | 0.5569 | 0.51302 | 0.41812 | 0.34159 | 0.29363 | -0.10535 | -0.23392 | -0.30535 | -0.67576 | -0.688 | -0.59412 | 0.58751 | 0.39363 | 0.38445 | 0.34873 | 0.262 | 0.18751 | 0.11506 | -0.28494 | -0.42882 | -0.49514 | -0.8329 | -0.98086 | -1.039
|  | CLACHAN | HE |  |  |  |  | -0.074735 | -0.073714 | -0.24616 | -0.27576 | -0.32065 | -0.48902 | -0.588 | -0.71555 | -0.81045 | -0.89514 | -1.0707 | -1.3462 | -1.5104 | 0.72527 | 0.70996 | 0.55588 | 0.51098 | 0.45996 | 0.35078 | 0.30282 | 0.22016 | 0.17424 | 0.10282 | -0.073714 | -0.08698 | -0.085959 | 0.58751 | 0.58853 | 0.38241 | 0.34261 | 0.31098 | 0.18853 | 0.11404 | 0.01302 | -0.055347 | -0.1278 | -0.27882 | -0.45433 | -0.55535
|  | CLACHAN | FB |  |  |  |  | -0.020653 | -0.0022857 | 0.01302 | -0.14514 | -0.13902 | -0.15331 | -0.21249 | -0.238 | -0.26555 | -0.27576 | -0.41249 | -0.61555 | -0.66555 | 0.75792 | 0.74976 | 0.73955 | 0.58751 | 0.56608 | 0.54159 | 0.47731 | 0.43751 | 0.39363 | 0.37322 | 0.19669 | -0.0073878 | -0.058408 | 0.63853 | 0.65282 | 0.66404 | 0.4671 | 0.47424 | 0.46098 | 0.39261 | 0.3671 | 0.33853 | 0.33241 | 0.18139 | 0.0079184 | -0.016571
| CARRADALE 1 | CLAONAIG | MINIMUM HEADROOM | NR 86915 56467 | YES | YES | 0 | 0.27068 | 0.26762 | 0.2615 | 0.25537 | 0.25027 | 0.24007 | 0.22578 | 0.21864 | 0.20843 | 0.19925 | 0.17782 | 0.1666 | 0.15843 | 0.27498 | 0.27192 | 0.26682 | 0.26376 | 0.25968 | 0.25457 | 0.24233 | 0.23825 | 0.226 | 0.21478 | 0.19743 | 0.19131 | 0.19437 | 0.27793 | 0.27589 | 0.26875 | 0.26569 | 0.25957 | 0.25344 | 0.2412 | 0.23508 | 0.22589 | 0.21569 | 0.1963 | 0.18814 | 0.18712
|  | CLAONAIG | EE |  |  |  |  | 0.27476 | 0.26864 | 0.2615 | 0.25843 | 0.25129 | 0.24007 | 0.23088 | 0.21966 | 0.20843 | 0.19925 | 0.17782 | 0.1666 | 0.1615 | 0.27804 | 0.27396 | 0.26886 | 0.2658 | 0.25968 | 0.25457 | 0.24641 | 0.23825 | 0.226 | 0.21478 | 0.19743 | 0.19845 | 0.20151 | 0.28099 | 0.27793 | 0.27181 | 0.26773 | 0.25957 | 0.25344 | 0.24426 | 0.23508 | 0.22589 | 0.21569 | 0.1963 | 0.19324 | 0.18916
|  | CLAONAIG | HT |  |  |  |  | 0.27476 | 0.26864 | 0.2615 | 0.25946 | 0.25231 | 0.24109 | 0.23292 | 0.2217 | 0.2115 | 0.20129 | 0.18803 | 0.16762 | 0.15843 | 0.27804 | 0.27396 | 0.26784 | 0.26682 | 0.25968 | 0.25457 | 0.24641 | 0.23825 | 0.226 | 0.21478 | 0.20049 | 0.19131 | 0.19743 | 0.28099 | 0.27793 | 0.27079 | 0.26875 | 0.26059 | 0.25344 | 0.2463 | 0.2361 | 0.22793 | 0.21569 | 0.2014 | 0.18814 | 0.18712
|  | CLAONAIG | HE |  |  |  |  | 0.27068 | 0.26762 | 0.2615 | 0.25537 | 0.25027 | 0.24109 | 0.22578 | 0.21864 | 0.21048 | 0.20027 | 0.18394 | 0.1666 | 0.15843 | 0.27498 | 0.27192 | 0.26682 | 0.26376 | 0.2607 | 0.25662 | 0.24233 | 0.23927 | 0.22804 | 0.2158 | 0.19845 | 0.19539 | 0.19437 | 0.27793 | 0.27589 | 0.26875 | 0.26569 | 0.26059 | 0.25446 | 0.2412 | 0.23712 | 0.22589 | 0.21671 | 0.19936 | 0.1912 | 0.18712
|  | CLAONAIG | FB |  |  |  |  | 0.28803 | 0.2768 | 0.27476 | 0.27272 | 0.2717 | 0.26762 | 0.26456 | 0.25946 | 0.25639 | 0.25435 | 0.23088 | 0.21354 | 0.20537 | 0.29233 | 0.28008 | 0.27804 | 0.27498 | 0.27498 | 0.26988 | 0.26784 | 0.26274 | 0.25662 | 0.25559 | 0.22804 | 0.20764 | 0.19947 | 0.2963 | 0.28508 | 0.28304 | 0.27997 | 0.27895 | 0.27589 | 0.27385 | 0.26773 | 0.26467 | 0.26263 | 0.24018 | 0.21569 | 0.21059
| CLAYHILLS | CLAYHILLS | MINIMUM HEADROOM | NJ 94047 05518 | NO | NO | 8.274 | 2.218 | 2.2006 | 2.1792 | 2.0945 | 2.0016 | 1.672 | 1.2618 | 0.82918 | 0.3649 | -0.17388 | -2.9739 | -5.4576 | -6.9076 | 6.4159 | 6.3435 | 6.3108 | 6.2476 | 6.2118 | 5.7894 | 5.3761 | 4.9863 | 4.5445 | 4.0047 | 2.1302 | 0.43939 | -2.7841 | 4.1312 | 4.0976 | 4.0649 | 3.9833 | 3.8996 | 3.7067 | 3.4343 | 2.9761 | 2.4802 | 1.8965 | -0.80449 | -3.0943 | -4.3922
|  | CLAYHILLS | EE |  |  |  |  | 2.2241 | 2.2129 | 2.1792 | 2.1078 | 2.0292 | 1.672 | 1.2618 | 0.82918 | 0.3649 | -0.17388 | -2.9739 | -5.4576 | -6.9076 | 6.419 | 6.3557 | 6.318 | 6.2588 | 6.2251 | 5.7894 | 5.3945 | 4.9863 | 4.5445 | 4.0047 | 2.1302 | 0.56082 | -0.66571 | 4.1333 | 4.0986 | 4.0659 | 3.9863 | 3.9261 | 3.7139 | 3.4343 | 2.9761 | 2.4802 | 1.8965 | -0.80449 | -3.0943 | -4.3922
|  | CLAYHILLS | HT |  |  |  |  | 2.2322 | 2.2312 | 2.2169 | 2.1435 | 2.0761 | 1.7343 | 1.3057 | 0.88224 | 0.42612 | -0.12388 | -2.7096 | -4.7637 | -5.5953 | 6.4159 | 6.3527 | 6.3108 | 6.2476 | 6.2118 | 5.8027 | 5.3873 | 4.9924 | 4.5639 | 4.0169 | 2.4894 | 1.5792 | 1.1924 | 4.1404 | 4.119 | 4.0976 | 4.0149 | 3.9557 | 3.7353 | 3.4669 | 3.02 | 2.5363 | 1.9404 | -0.52898 | -2.3239 | -2.9882
|  | CLAYHILLS | HE |  |  |  |  | 2.218 | 2.2006 | 2.1833 | 2.0945 | 2.0016 | 1.7649 | 1.3241 | 1.0067 | 0.51796 | 0.07 | -1.8086 | -3.6055 | -4.7984 | 6.419 | 6.3598 | 6.322 | 6.2618 | 6.2241 | 5.8363 | 5.3761 | 5.068 | 4.5476 | 4.0669 | 2.6608 | 1.2139 | 0.057755 | 4.1312 | 4.0976 | 4.0649 | 3.9833 | 3.8996 | 3.7067 | 3.4527 | 3.1251 | 2.5802 | 2.0751 | 0.28633 | -1.4178 | -2.4616
|  | CLAYHILLS | FB |  |  |  |  | 2.3057 | 2.3445 | 2.4139 | 2.4118 | 2.3996 | 2.3384 | 2.2924 | 2.1894 | 2.0629 | 1.9159 | 0.77 | -1.6351 | -3.7239 | 6.418 | 6.3435 | 6.3404 | 6.3047 | 6.2618 | 6.1312 | 6.0149 | 5.8271 | 5.518 | 5.1537 | 3.4955 | 0.43939 | -2.7841 | 4.2088 | 4.221 | 4.269 | 4.2598 | 4.2496 | 4.2037 | 4.1649 | 4.0659 | 3.9424 | 3.7986 | 2.7537 | -0.017755 | -1.9198
| DOUNREAY | COLDBACKIE | MINIMUM HEADROOM | NC 62182 59590 | YES | NO | 0.606 | -0.16313 | -0.16721 | -0.17945 | -0.19884 | -0.22333 | -0.27231 | -0.31313 | -0.35802 | -0.40394 | -0.44374 | -0.56517 | -0.69986 | -0.80496 | 0.031771 | 0.02871 | 0.019527 | 0.014424 | 0.0032 | -0.025371 | -0.065167 | -0.093739 | -0.11925 | -0.12639 | -0.18966 | -0.1866 | -0.19782 | -0.04578 | -0.048841 | -0.058024 | -0.07231 | -0.089657 | -0.13149 | -0.18456 | -0.22435 | -0.26517 | -0.28047 | -0.35802 | -0.42639 | -0.48762
|  | COLDBACKIE | EE |  |  |  |  | -0.16313 | -0.16721 | -0.17945 | -0.19578 | -0.21823 | -0.24986 | -0.27945 | -0.33558 | -0.39272 | -0.42843 | -0.56517 | -0.69986 | -0.80394 | 0.031771 | 0.02871 | 0.019527 | 0.015445 | 0.0052408 | -0.0049633 | -0.031494 | -0.070269 | -0.10598 | -0.12231 | -0.17945 | -0.17843 | -0.17027 | -0.04578 | -0.048841 | -0.058024 | -0.069249 | -0.084555 | -0.11211 | -0.15292 | -0.20598 | -0.25496 | -0.28047 | -0.35802 | -0.42639 | -0.48149
|  | COLDBACKIE | HT |  |  |  |  | -0.16313 | -0.16619 | -0.17945 | -0.19782 | -0.21925 | -0.27231 | -0.31313 | -0.35802 | -0.40394 | -0.42741 | -0.51517 | -0.66211 | -0.80496 | 0.031771 | 0.029731 | 0.019527 | 0.014424 | 0.0032 | -0.025371 | -0.065167 | -0.093739 | -0.11925 | -0.12435 | -0.18966 | -0.1866 | -0.17435 | -0.04578 | -0.04782 | -0.058024 | -0.070269 | -0.085576 | -0.13149 | -0.18456 | -0.22435 | -0.26517 | -0.28047 | -0.33864 | -0.407 | -0.48762
|  | COLDBACKIE | HE |  |  |  |  | -0.16313 | -0.16721 | -0.17945 | -0.19884 | -0.22333 | -0.257 | -0.28558 | -0.34578 | -0.4019 | -0.44374 | -0.52537 | -0.68149 | -0.78966 | 0.031771 | 0.02871 | 0.019527 | 0.015445 | 0.0032 | -0.0070041 | -0.032514 | -0.075371 | -0.11007 | -0.12639 | -0.18047 | -0.18353 | -0.19374 | -0.04578 | -0.048841 | -0.058024 | -0.07231 | -0.089657 | -0.11619 | -0.15496 | -0.21109 | -0.26415 | -0.26619 | -0.33864 | -0.41721 | -0.47741
|  | COLDBACKIE | FB |  |  |  |  | -0.14374 | -0.14374 | -0.14374 | -0.14374 | -0.16007 | -0.16721 | -0.17639 | -0.19476 | -0.21415 | -0.24272 | -0.3417 | -0.38762 | -0.41211 | 0.048098 | 0.047078 | 0.042996 | 0.046057 | 0.037894 | 0.034833 | 0.023608 | 0.010343 | -0.011086 | -0.035576 | -0.11007 | -0.16415 | -0.19782 | -0.027412 | -0.025371 | -0.025371 | -0.02231 | -0.032514 | -0.034555 | -0.043739 | -0.057004 | -0.079453 | -0.10394 | -0.1917 | -0.26007 | -0.26721
| DUNOON | COLINTRAIVE | MINIMUM HEADROOM | NS 03209 74814 | YES | YES | 0 | 0.44204 | 0.44306 | 0.43796 | 0.43388 | 0.42776 | 0.41755 | 0.40939 | 0.39204 | 0.38694 | 0.37265 | 0.34816 | 0.32878 | 0.31653 | 0.46541 | 0.46541 | 0.46337 | 0.46031 | 0.45622 | 0.45214 | 0.445 | 0.43071 | 0.43071 | 0.41541 | 0.38582 | 0.3899 | 0.39398 | 0.45321 | 0.45321 | 0.44913 | 0.44505 | 0.43791 | 0.43077 | 0.42158 | 0.4073 | 0.40321 | 0.39097 | 0.3675 | 0.35423 | 0.34607
|  | COLINTRAIVE | EE |  |  |  |  | 0.44204 | 0.44306 | 0.43796 | 0.4349 | 0.42878 | 0.41857 | 0.41041 | 0.39306 | 0.38694 | 0.37673 | 0.34816 | 0.32878 | 0.32061 | 0.46541 | 0.46541 | 0.46337 | 0.46133 | 0.45622 | 0.45316 | 0.445 | 0.43071 | 0.43071 | 0.41541 | 0.39194 | 0.39602 | 0.40418 | 0.45321 | 0.45321 | 0.44913 | 0.44607 | 0.43893 | 0.43179 | 0.4226 | 0.40832 | 0.40321 | 0.39301 | 0.3675 | 0.35423 | 0.35423
|  | COLINTRAIVE | HT |  |  |  |  | 0.44204 | 0.44306 | 0.44 | 0.43388 | 0.4298 | 0.41959 | 0.41041 | 0.39612 | 0.39102 | 0.38082 | 0.35429 | 0.33388 | 0.31755 | 0.46541 | 0.46541 | 0.46439 | 0.46031 | 0.45622 | 0.45214 | 0.445 | 0.43071 | 0.43071 | 0.41541 | 0.38582 | 0.3899 | 0.40112 | 0.45321 | 0.45321 | 0.45015 | 0.44505 | 0.43995 | 0.43281 | 0.42362 | 0.40934 | 0.40628 | 0.39607 | 0.37158 | 0.35832 | 0.35321
|  | COLINTRAIVE | HE |  |  |  |  | 0.44204 | 0.4451 | 0.43898 | 0.43388 | 0.42776 | 0.41755 | 0.40939 | 0.39204 | 0.38694 | 0.37265 | 0.35224 | 0.33082 | 0.31653 | 0.46541 | 0.46847 | 0.46439 | 0.46031 | 0.45622 | 0.45214 | 0.445 | 0.43071 | 0.43071 | 0.41541 | 0.39194 | 0.39296 | 0.395 | 0.45321 | 0.45628 | 0.44913 | 0.44505 | 0.43791 | 0.43077 | 0.42158 | 0.4073 | 0.40423 | 0.39097 | 0.36954 | 0.35526 | 0.34607
|  | COLINTRAIVE | FB |  |  |  |  | 0.45429 | 0.45224 | 0.45122 | 0.4502 | 0.44714 | 0.44408 | 0.44102 | 0.43694 | 0.43388 | 0.42878 | 0.40224 | 0.38082 | 0.37367 | 0.47765 | 0.47561 | 0.47357 | 0.47357 | 0.47153 | 0.46745 | 0.46439 | 0.46235 | 0.45827 | 0.44908 | 0.42561 | 0.40112 | 0.39398 | 0.4675 | 0.46342 | 0.46138 | 0.45934 | 0.4573 | 0.45321 | 0.45117 | 0.44709 | 0.44301 | 0.43587 | 0.41342 | 0.38587 | 0.38485
| STORNOWAY | COLL | MINIMUM HEADROOM | NB 47510 40182 | YES | YES | 0.108 | 0.6 | 5.839 | 5.8176 | 5.7798 | 5.7196 | 5.5471 | 5.3839 | 5.2124 | 5.0349 | 4.9227 | 4.6982 | 4.3441 | 4.0635 | 1.2434 | 6.7155 | 6.7073 | 6.6931 | 6.6839 | 6.6206 | 6.5624 | 6.4992 | 6.4216 | 6.3614 | 6.3114 | 6.2961 | 6.1267 | 1.1589 | 6.5084 | 6.488 | 6.442 | 6.4288 | 6.2992 | 6.1808 | 6.0492 | 5.9155 | 5.8237 | 5.6359 | 5.3614 | 5.1533
|  | COLL | EE |  |  |  |  | 0.60306 | 5.839 | 5.8176 | 5.7839 | 5.7278 | 5.5492 | 5.3971 | 5.2267 | 5.0512 | 4.9482 | 4.6982 | 4.3441 | 4.0635 | 1.2434 | 6.7155 | 6.7073 | 6.6971 | 6.6849 | 6.6247 | 6.5655 | 6.5033 | 6.4288 | 6.3706 | 6.3492 | 6.3308 | 6.3073 | 1.161 | 6.5084 | 6.488 | 6.4431 | 6.4329 | 6.3022 | 6.19 | 6.0614 | 5.9288 | 5.8441 | 5.6359 | 5.3614 | 5.1655
|  | COLL | HT |  |  |  |  | 0.60102 | 5.8471 | 5.8227 | 5.7859 | 5.7318 | 5.5696 | 5.4145 | 5.2482 | 5.0767 | 4.9778 | 4.8359 | 4.442 | 4.0665 | 1.2434 | 6.7257 | 6.7073 | 6.6931 | 6.6859 | 6.6247 | 6.5665 | 6.5033 | 6.4267 | 6.3696 | 6.3114 | 6.3165 | 6.3339 | 1.1589 | 6.5186 | 6.491 | 6.4471 | 6.4359 | 6.3155 | 6.2002 | 6.0747 | 5.9431 | 5.8614 | 5.7247 | 5.4308 | 5.1533
|  | COLL | HE |  |  |  |  | 0.6 | 5.8471 | 5.8216 | 5.7798 | 5.7196 | 5.5471 | 5.3839 | 5.2124 | 5.0349 | 4.9227 | 4.8053 | 4.3441 | 4.0992 | 1.2434 | 6.7237 | 6.7073 | 6.6951 | 6.6839 | 6.6206 | 6.5624 | 6.4992 | 6.4216 | 6.3614 | 6.3349 | 6.3073 | 6.2533 | 1.1589 | 6.5155 | 6.49 | 6.442 | 6.4288 | 6.2992 | 6.1808 | 6.0492 | 5.9155 | 5.8237 | 5.7155 | 5.3727 | 5.1931
|  | COLL | FB |  |  |  |  | 0.64184 | 5.9227 | 5.9543 | 5.9604 | 5.9573 | 5.9522 | 5.9512 | 5.941 | 5.9063 | 5.892 | 5.6696 | 5.5063 | 5.4247 | 1.2781 | 6.7716 | 6.788 | 6.789 | 6.7788 | 6.7665 | 6.7298 | 6.7145 | 6.6727 | 6.6543 | 6.4665 | 6.2961 | 6.1267 | 1.2028 | 6.5849 | 6.6022 | 6.6084 | 6.591 | 6.5788 | 6.5471 | 6.5349 | 6.4992 | 6.4798 | 6.3084 | 6.1624 | 6.1329
| CLAYHILLS | COMMERCE STREET | MINIMUM HEADROOM | NJ 94816 06282 | NO | NO | 4.474 | 7.6398 | 7.6715 | 7.6225 | 7.5745 | 7.5102 | 7.4102 | 7.2602 | 7.1766 | 7.0694 | 6.9317 | 5.8592 | 4.5888 | 4.6276 | 8.9704 | 8.9715 | 8.9072 | 8.8429 | 8.7694 | 8.6694 | 8.5368 | 8.4664 | 8.3745 | 8.2511 | 7.149 | 5.7592 | 5.1102 | 8.2608 | 8.2648 | 8.1863 | 8.1138 | 8.0281 | 7.923 | 7.7791 | 7.6995 | 7.5975 | 7.4648 | 6.6138 | 5.3108 | 5.4026
|  | COMMERCE STREET | EE |  |  |  |  | 7.6439 | 7.6786 | 7.6307 | 7.5898 | 7.5307 | 7.447 | 7.3215 | 7.2409 | 7.1409 | 6.9358 | 5.8592 | 4.5888 | 4.6276 | 8.9756 | 8.9888 | 8.9204 | 8.8623 | 8.7929 | 8.7041 | 8.5847 | 8.5184 | 8.4286 | 8.2868 | 7.149 | 5.7592 | 5.6715 | 8.2689 | 8.2791 | 8.2077 | 8.1414 | 8.0628 | 7.9679 | 7.8383 | 7.7608 | 7.6638 | 7.5138 | 6.6138 | 5.3108 | 5.4026
|  | COMMERCE STREET | HT |  |  |  |  | 7.6449 | 7.6807 | 7.6327 | 7.5919 | 7.5337 | 7.4572 | 7.3256 | 7.2449 | 7.1429 | 6.9786 | 5.949 | 4.7531 | 4.6633 | 8.9756 | 8.9878 | 8.9204 | 8.8602 | 8.7939 | 8.7113 | 8.5909 | 8.5296 | 8.447 | 8.3051 | 7.2858 | 6.0674 | 5.948 | 8.271 | 8.2842 | 8.2148 | 8.1485 | 8.0699 | 7.973 | 7.8434 | 7.7669 | 7.671 | 7.5148 | 6.7189 | 5.4985 | 5.4403
|  | COMMERCE STREET | HE |  |  |  |  | 7.6398 | 7.6715 | 7.6225 | 7.5745 | 7.5102 | 7.4102 | 7.2602 | 7.1766 | 7.0694 | 6.9317 | 6.1307 | 5.5164 | 5.3898 | 8.9704 | 8.9786 | 8.9072 | 8.8429 | 8.7694 | 8.6694 | 8.5368 | 8.4664 | 8.3745 | 8.2511 | 7.3531 | 6.6062 | 6.3102 | 8.2608 | 8.2648 | 8.1863 | 8.1138 | 8.0281 | 7.923 | 7.7791 | 7.6995 | 7.5975 | 7.4648 | 6.8669 | 6.2465 | 6.1424
|  | COMMERCE STREET | FB |  |  |  |  | 7.6633 | 7.6898 | 7.7174 | 7.7113 | 7.7164 | 7.7062 | 7.6653 | 7.5929 | 7.5337 | 7.4429 | 7.1521 | 6.3623 | 5.0674 | 8.9796 | 8.9715 | 8.9694 | 8.9368 | 8.9153 | 8.8796 | 8.8194 | 8.7429 | 8.6796 | 8.5837 | 8.2398 | 6.9511 | 5.1102 | 8.2883 | 8.2903 | 8.2985 | 8.2659 | 8.2454 | 8.2189 | 8.1628 | 8.0965 | 8.0414 | 7.9485 | 7.6587 | 6.7087 | 5.6689
| ST FILLANS | COMRIE | MINIMUM HEADROOM | NN 76887 22417 | YES | YES | 0 | 0.045735 | 0.046755 | 0.035531 | 0.035531 | 0.03349 | 0.026347 | 0.021245 | 0.021245 | 0.018184 | 0.014102 | 0.011041 | 0.0059388 | 0.0028776 | 0.045316 | 0.045316 | 0.033071 | 0.034092 | 0.032051 | 0.027969 | 0.023888 | 0.023888 | 0.022867 | 0.019806 | 0.015724 | 0.014704 | 0.016745 | 0.046546 | 0.046546 | 0.035321 | 0.035321 | 0.034301 | 0.026138 | 0.022056 | 0.020015 | 0.018995 | 0.015934 | 0.012872 | 0.0098112 | 0.00675
|  | COMRIE | EE |  |  |  |  | 0.045735 | 0.046755 | 0.035531 | 0.035531 | 0.03349 | 0.026347 | 0.022265 | 0.023286 | 0.018184 | 0.017163 | 0.011041 | 0.0069592 | 0.0049184 | 0.045316 | 0.045316 | 0.033071 | 0.034092 | 0.032051 | 0.027969 | 0.024908 | 0.025929 | 0.022867 | 0.021847 | 0.017765 | 0.016745 | 0.019806 | 0.046546 | 0.046546 | 0.035321 | 0.035321 | 0.034301 | 0.026138 | 0.022056 | 0.023077 | 0.018995 | 0.017974 | 0.012872 | 0.0098112 | 0.0098112
|  | COMRIE | HT |  |  |  |  | 0.045735 | 0.046755 | 0.035531 | 0.035531 | 0.03349 | 0.027367 | 0.022265 | 0.021245 | 0.018184 | 0.015122 | 0.012061 | 0.0059388 | 0.0028776 | 0.045316 | 0.045316 | 0.033071 | 0.034092 | 0.032051 | 0.02899 | 0.024908 | 0.023888 | 0.022867 | 0.019806 | 0.015724 | 0.014704 | 0.016745 | 0.046546 | 0.046546 | 0.035321 | 0.035321 | 0.034301 | 0.027158 | 0.022056 | 0.020015 | 0.018995 | 0.015934 | 0.012872 | 0.0098112 | 0.00675
|  | COMRIE | HE |  |  |  |  | 0.045735 | 0.046755 | 0.035531 | 0.035531 | 0.03349 | 0.026347 | 0.021245 | 0.022265 | 0.018184 | 0.014102 | 0.012061 | 0.0069592 | 0.0059388 | 0.045316 | 0.045316 | 0.033071 | 0.034092 | 0.032051 | 0.027969 | 0.023888 | 0.025929 | 0.022867 | 0.019806 | 0.017765 | 0.017765 | 0.017765 | 0.046546 | 0.046546 | 0.035321 | 0.035321 | 0.034301 | 0.026138 | 0.022056 | 0.023077 | 0.018995 | 0.015934 | 0.013893 | 0.010832 | 0.0087908
|  | COMRIE | FB |  |  |  |  | 0.045735 | 0.046755 | 0.046755 | 0.039612 | 0.039612 | 0.038592 | 0.038592 | 0.03451 | 0.032469 | 0.032469 | 0.024306 | 0.016143 | 0.017163 | 0.045316 | 0.045316 | 0.045316 | 0.037153 | 0.037153 | 0.037153 | 0.037153 | 0.033071 | 0.031031 | 0.031031 | 0.024908 | 0.016745 | 0.016745 | 0.046546 | 0.046546 | 0.046546 | 0.039403 | 0.039403 | 0.039403 | 0.039403 | 0.035321 | 0.033281 | 0.03124 | 0.024097 | 0.017974 | 0.016954
| TAYNUILT | CONNEL | MINIMUM HEADROOM | NM 91213 33970 | YES | YES | 0.891 | -0.93412 | -1.027 | -1.0443 | -1.0872 | -1.0984 | -1.4076 | -1.578 | -1.729 | -1.8831 | -1.9964 | -2.5351 | -2.8096 | -2.9147 | -0.30861 | -0.45963 | -0.46473 | -0.47392 | -0.48106 | -0.74127 | -0.89841 | -1.0147 | -1.1423 | -1.2658 | -1.7117 | -1.8515 | -1.879 | -0.5331 | -0.70045 | -0.71678 | -0.75555 | -0.78208 | -1.079 | -1.2117 | -1.3504 | -1.4933 | -1.6117 | -2.1086 | -2.33 | -2.3943
|  | CONNEL | EE |  |  |  |  | -0.93412 | -0.94433 | -1.0443 | -1.0862 | -1.0933 | -1.3974 | -1.577 | -1.7188 | -1.8821 | -1.9872 | -2.5351 | -2.8096 | -2.9147 | -0.30861 | -0.3178 | -0.46473 | -0.47392 | -0.48106 | -0.73718 | -0.89127 | -0.99127 | -1.1341 | -1.2219 | -1.6953 | -1.8515 | -1.879 | -0.53208 | -0.54739 | -0.71678 | -0.75555 | -0.778 | -1.0698 | -1.2076 | -1.3362 | -1.4882 | -1.5882 | -2.1086 | -2.33 | -2.3943
|  | CONNEL | HT |  |  |  |  | -0.9331 | -1.027 | -1.0351 | -1.0729 | -1.08 | -1.3647 | -1.5351 | -1.6556 | -1.8413 | -1.9964 | -2.4627 | -2.6311 | -2.7545 | -0.30759 | -0.45963 | -0.46269 | -0.4729 | -0.48004 | -0.72188 | -0.87698 | -0.96678 | -1.127 | -1.2658 | -1.7117 | -1.7219 | -1.6902 | -0.53208 | -0.70045 | -0.71065 | -0.74637 | -0.76984 | -1.0423 | -1.178 | -1.2882 | -1.4637 | -1.6117 | -2.0698 | -2.176 | -2.2392
|  | CONNEL | HE |  |  |  |  | -0.93412 | -0.94433 | -1.0433 | -1.0872 | -1.0984 | -1.4076 | -1.578 | -1.729 | -1.8831 | -1.9698 | -2.376 | -2.5382 | -2.6117 | -0.30861 | -0.31984 | -0.46473 | -0.47392 | -0.48106 | -0.74127 | -0.89841 | -1.0147 | -1.1423 | -1.2107 | -1.5872 | -1.5811 | -1.577 | -0.5331 | -0.54841 | -0.71678 | -0.75555 | -0.78208 | -1.079 | -1.2117 | -1.3504 | -1.4933 | -1.5739 | -1.9709 | -2.0698 | -2.1045
|  | CONNEL | FB |  |  |  |  | -0.90249 | -0.8831 | -0.87188 | -0.95045 | -0.96167 | -1.2433 | -1.2535 | -1.277 | -1.3025 | -1.3096 | -1.4953 | -1.73 | -1.9841 | -0.28412 | -0.27596 | -0.27494 | -0.42596 | -0.43208 | -0.71678 | -0.73208 | -0.75963 | -0.79433 | -0.80453 | -0.99127 | -1.2474 | -1.578 | -0.50249 | -0.49127 | -0.4882 | -0.64127 | -0.65453 | -0.93922 | -0.95249 | -0.97902 | -1.0076 | -1.0127 | -1.2066 | -1.4443 | -1.6719
| BEAULY | CONON BRIDGE | MINIMUM HEADROOM | NH 54996 55499 | NO | NO | 1.356 | 1.3562 | 9.6661 | 9.4641 | 9.1978 | 9.0743 | 8.4325 | 7.6386 | 7.1529 | 6.7621 | 6.4865 | 5.4631 | 4.5314 | 3.859 | 2.8161 | 10.7794 | 10.7182 | 10.6406 | 10.5988 | 10.3427 | 9.9682 | 9.7029 | 9.5202 | 9.3855 | 8.9447 | 8.8978 | 8.6488 | 2.3377 | 10.4636 | 10.3115 | 10.1136 | 10.0075 | 9.535 | 8.9218 | 8.5177 | 8.1973 | 7.9626 | 7.1534 | 6.5564 | 6.135
|  | CONON BRIDGE | EE |  |  |  |  | 1.3603 | 9.6661 | 9.4702 | 9.2008 | 9.0794 | 8.6916 | 8.0182 | 7.457 | 6.9365 | 6.5345 | 5.4631 | 4.5314 | 3.908 | 2.8172 | 10.7794 | 10.7212 | 10.6437 | 10.5998 | 10.5825 | 10.3376 | 9.9906 | 9.6825 | 9.4325 | 9.0121 | 8.9335 | 8.8447 | 2.3397 | 10.4636 | 10.3156 | 10.1146 | 10.0105 | 9.7575 | 9.2564 | 8.7891 | 8.3524 | 8.0054 | 7.1534 | 6.5564 | 6.1871
|  | CONON BRIDGE | HT |  |  |  |  | 1.3562 | 9.6896 | 9.4641 | 9.1978 | 9.0743 | 8.4325 | 7.6386 | 7.1529 | 6.7621 | 6.4916 | 5.5447 | 4.5886 | 3.859 | 2.8172 | 10.8029 | 10.7182 | 10.6406 | 10.5988 | 10.3427 | 9.9682 | 9.7029 | 9.5202 | 9.3855 | 8.9447 | 8.8978 | 8.9243 | 2.3387 | 10.4881 | 10.3115 | 10.1136 | 10.0075 | 9.535 | 8.9218 | 8.5177 | 8.1973 | 7.9636 | 7.1758 | 6.5697 | 6.135
|  | CONON BRIDGE | HE |  |  |  |  | 1.3562 | 9.6886 | 9.4641 | 9.2008 | 9.0774 | 8.6733 | 8.0284 | 7.4447 | 6.9039 | 6.4865 | 5.6468 | 4.6314 | 4.0825 | 2.8161 | 10.8029 | 10.7182 | 10.6416 | 10.5998 | 10.5661 | 10.3406 | 9.9712 | 9.6427 | 9.3916 | 9.0202 | 8.91 | 8.7692 | 2.3377 | 10.4881 | 10.3115 | 10.1156 | 10.0085 | 9.7411 | 9.2636 | 8.7728 | 8.3207 | 7.9626 | 7.2646 | 6.6064 | 6.2534
|  | CONON BRIDGE | FB |  |  |  |  | 1.4807 | 9.8814 | 9.7804 | 9.659 | 9.6457 | 9.5712 | 9.3223 | 9.0988 | 8.9355 | 8.709 | 7.9498 | 7.3468 | 7.1304 | 2.8906 | 10.8978 | 10.8539 | 10.8202 | 10.8151 | 10.7508 | 10.6345 | 10.5263 | 10.3661 | 10.1519 | 9.5468 | 9.0172 | 8.6488 | 2.4499 | 10.6462 | 10.5738 | 10.486 | 10.4697 | 10.3932 | 10.2013 | 10.0279 | 9.8881 | 9.6697 | 8.985 | 8.3615 | 8.2615
| BEAULY | CONON FALLS | MINIMUM HEADROOM | NH 38745 57593 | YES | NO | 0.264 | 0.1867 | 0.17956 | 0.1765 | 0.16731 | 0.16119 | 0.14384 | 0.12752 | 0.11731 | 0.10099 | 0.092824 | 0.050988 | 0.027518 | 0.029559 | 0.10191 | 0.096804 | 0.090682 | 0.081498 | 0.070273 | 0.063131 | 0.047824 | 0.039661 | 0.023335 | 0.018233 | -0.022584 | -0.021563 | -0.0134 | 0.12645 | 0.1193 | 0.11318 | 0.099916 | 0.087671 | 0.076447 | 0.05808 | 0.048896 | 0.03359 | 0.024406 | -0.018451 | -0.027635 | -0.032737
|  | CONON FALLS | EE |  |  |  |  | 0.1867 | 0.17956 | 0.1765 | 0.16936 | 0.16323 | 0.14487 | 0.12956 | 0.1214 | 0.10507 | 0.096906 | 0.050988 | 0.027518 | 0.035682 | 0.10191 | 0.096804 | 0.090682 | 0.081498 | 0.070273 | 0.063131 | 0.047824 | 0.040682 | 0.024355 | 0.018233 | -0.016461 | -0.01442 | -0.0052367 | 0.12645 | 0.1193 | 0.11318 | 0.10094 | 0.088692 | 0.076447 | 0.0591 | 0.050937 | 0.03461 | 0.025427 | -0.017431 | -0.024573 | -0.023553
|  | CONON FALLS | HT |  |  |  |  | 0.1867 | 0.17956 | 0.1765 | 0.16936 | 0.16323 | 0.14895 | 0.13058 | 0.1214 | 0.10609 | 0.097927 | 0.058131 | 0.03058 | 0.03058 | 0.10191 | 0.096804 | 0.090682 | 0.081498 | 0.070273 | 0.063131 | 0.047824 | 0.039661 | 0.023335 | 0.018233 | -0.022584 | -0.021563 | -0.0134 | 0.12645 | 0.1193 | 0.11318 | 0.10094 | 0.088692 | 0.078488 | 0.0591 | 0.050937 | 0.035631 | 0.025427 | -0.018451 | -0.027635 | -0.032737
|  | CONON FALLS | HE |  |  |  |  | 0.1867 | 0.18058 | 0.1765 | 0.16731 | 0.16119 | 0.14384 | 0.12752 | 0.11731 | 0.10099 | 0.092824 | 0.058131 | 0.028539 | 0.029559 | 0.10191 | 0.096804 | 0.090682 | 0.081498 | 0.070273 | 0.063131 | 0.047824 | 0.039661 | 0.023335 | 0.018233 | -0.017482 | -0.016461 | -0.01238 | 0.12645 | 0.1193 | 0.11318 | 0.099916 | 0.087671 | 0.076447 | 0.05808 | 0.048896 | 0.03359 | 0.024406 | -0.013349 | -0.022533 | -0.029676
|  | CONON FALLS | FB |  |  |  |  | 0.19487 | 0.19282 | 0.19384 | 0.18568 | 0.18568 | 0.1765 | 0.17038 | 0.16936 | 0.16425 | 0.15711 | 0.12854 | 0.10405 | 0.093845 | 0.10497 | 0.10191 | 0.10089 | 0.092722 | 0.091702 | 0.080478 | 0.075376 | 0.070273 | 0.065171 | 0.057008 | 0.029457 | 0.0019061 | -0.0062571 | 0.13053 | 0.12849 | 0.12543 | 0.11522 | 0.1142 | 0.10298 | 0.096855 | 0.090733 | 0.086651 | 0.076447 | 0.046855 | 0.015222 | 0.011141
| DUDHOPE | CONSTABLE STREET | MINIMUM HEADROOM | NO 40903 30821 | NO | NO | 4.362 | 13.2819 | 13.3604 | 13.3513 | 13.3319 | 13.2482 | 13.0482 | 12.8686 | 12.6268 | 12.1992 | 11.6064 | 9.0625 | 6.8502 | 5.7176 | 15.4441 | 15.4972 | 15.3941 | 15.2727 | 15.037 | 14.6053 | 14.2758 | 13.9798 | 13.6441 | 13.1421 | 11.4441 | 9.8982 | 7.7339 | 14.4584 | 14.5084 | 14.4758 | 14.4492 | 14.1798 | 13.6625 | 13.2207 | 12.8574 | 12.4411 | 11.8451 | 9.4207 | 7.3931 | 6.3819
|  | CONSTABLE STREET | EE |  |  |  |  | 13.2849 | 13.3604 | 13.3553 | 13.3329 | 13.2482 | 13.0666 | 12.9156 | 12.6329 | 12.1992 | 11.6064 | 9.0625 | 6.8502 | 5.7176 | 15.4451 | 15.4972 | 15.3941 | 15.2798 | 15.0441 | 14.6758 | 14.2758 | 13.9798 | 13.6441 | 13.1421 | 11.4441 | 9.8982 | 8.8104 | 14.4584 | 14.5084 | 14.4758 | 14.4492 | 14.1798 | 13.7309 | 13.2207 | 12.8574 | 12.4411 | 11.8451 | 9.4207 | 7.3931 | 6.3819
|  | CONSTABLE STREET | HT |  |  |  |  | 13.2931 | 13.3829 | 13.3829 | 13.3707 | 13.288 | 13.0482 | 12.8686 | 12.6268 | 12.2513 | 11.6564 | 9.2553 | 7.3768 | 6.936 | 15.4441 | 15.4972 | 15.3941 | 15.2727 | 15.037 | 14.6053 | 14.3043 | 14.0145 | 13.6819 | 13.1819 | 11.7329 | 10.7758 | 10.5298 | 14.4676 | 14.5227 | 14.5023 | 14.4737 | 14.1921 | 13.6625 | 13.2717 | 12.9094 | 12.5094 | 11.9166 | 9.6615 | 7.9717 | 7.6023
|  | CONSTABLE STREET | HE |  |  |  |  | 13.2819 | 13.3615 | 13.3513 | 13.3319 | 13.2482 | 13.0747 | 12.9329 | 12.737 | 12.3411 | 11.9023 | 10.3125 | 9.0615 | 8.3625 | 15.4441 | 15.4982 | 15.4135 | 15.3023 | 15.0717 | 14.7135 | 14.3094 | 14.0319 | 13.6594 | 13.2645 | 12.1349 | 11.1145 | 10.2788 | 14.4625 | 14.5135 | 14.4849 | 14.4574 | 14.2217 | 13.8013 | 13.3094 | 12.988 | 12.5462 | 12.0992 | 10.6115 | 9.4809 | 8.8809
|  | CONSTABLE STREET | FB |  |  |  |  | 13.3421 | 13.4707 | 13.5472 | 13.5849 | 13.6125 | 13.588 | 13.5523 | 13.4819 | 13.3951 | 13.3533 | 12.7615 | 10.4635 | 8.8472 | 15.4686 | 15.5431 | 15.5778 | 15.5747 | 15.5013 | 15.3156 | 15.1819 | 14.8921 | 14.5798 | 14.4064 | 12.9615 | 10.2615 | 7.7339 | 14.5115 | 14.6094 | 14.6533 | 14.689 | 14.7125 | 14.6839 | 14.6513 | 14.5431 | 14.2574 | 14.1462 | 12.8656 | 10.5421 | 9.0574
| ALNESS | CONTULLICH | MINIMUM HEADROOM | NN 59226 32752 | YES | NO | 0 | 0.080245 | 0.080245 | 0.079224 | 0.076163 | 0.073102 | 0.06698 | 0.063918 | 0.060857 | 0.055755 | 0.051673 | 0.044531 | 0.039429 | 0.035347 | 0.080429 | 0.081449 | 0.080429 | 0.078388 | 0.076347 | 0.072265 | 0.070224 | 0.067163 | 0.063082 | 0.059 | 0.052878 | 0.051857 | 0.052878 | 0.079827 | 0.079827 | 0.078806 | 0.076765 | 0.072684 | 0.066561 | 0.0635 | 0.061459 | 0.057378 | 0.053296 | 0.046153 | 0.042071 | 0.042071
|  | CONTULLICH | EE |  |  |  |  | 0.080245 | 0.080245 | 0.079224 | 0.076163 | 0.077184 | 0.068 | 0.063918 | 0.060857 | 0.055755 | 0.051673 | 0.044531 | 0.039429 | 0.037388 | 0.080429 | 0.081449 | 0.080429 | 0.078388 | 0.078388 | 0.072265 | 0.070224 | 0.067163 | 0.063082 | 0.059 | 0.053898 | 0.052878 | 0.055939 | 0.079827 | 0.079827 | 0.078806 | 0.076765 | 0.075745 | 0.066561 | 0.0635 | 0.061459 | 0.057378 | 0.053296 | 0.046153 | 0.042071 | 0.044112
|  | CONTULLICH | HT |  |  |  |  | 0.080245 | 0.080245 | 0.079224 | 0.076163 | 0.077184 | 0.068 | 0.063918 | 0.061878 | 0.055755 | 0.052694 | 0.044531 | 0.039429 | 0.035347 | 0.080429 | 0.081449 | 0.080429 | 0.078388 | 0.078388 | 0.072265 | 0.070224 | 0.067163 | 0.063082 | 0.059 | 0.052878 | 0.051857 | 0.053898 | 0.079827 | 0.079827 | 0.078806 | 0.076765 | 0.075745 | 0.067582 | 0.0635 | 0.061459 | 0.057378 | 0.054316 | 0.046153 | 0.042071 | 0.042071
|  | CONTULLICH | HE |  |  |  |  | 0.080245 | 0.080245 | 0.079224 | 0.076163 | 0.073102 | 0.06698 | 0.064939 | 0.060857 | 0.056776 | 0.051673 | 0.045551 | 0.039429 | 0.036367 | 0.080429 | 0.081449 | 0.080429 | 0.078388 | 0.076347 | 0.072265 | 0.070224 | 0.067163 | 0.063082 | 0.059 | 0.053898 | 0.051857 | 0.052878 | 0.079827 | 0.079827 | 0.078806 | 0.076765 | 0.072684 | 0.066561 | 0.065541 | 0.061459 | 0.058398 | 0.053296 | 0.046153 | 0.042071 | 0.042071
|  | CONTULLICH | FB |  |  |  |  | 0.091469 | 0.083306 | 0.084327 | 0.083306 | 0.081265 | 0.078204 | 0.080245 | 0.073102 | 0.071061 | 0.06902 | 0.058816 | 0.054735 | 0.050653 | 0.092673 | 0.08451 | 0.08451 | 0.08451 | 0.081449 | 0.078388 | 0.080429 | 0.073286 | 0.072265 | 0.070224 | 0.063082 | 0.06002 | 0.055939 | 0.092071 | 0.082888 | 0.082888 | 0.083908 | 0.078806 | 0.076765 | 0.078806 | 0.072684 | 0.071663 | 0.069622 | 0.057378 | 0.054316 | 0.051255
| FORT WILLIAM | CORRAN | MINIMUM HEADROOM | NN 02545 63126 | YES | NO | 0.746 | -0.69053 | -0.69461 | -0.70584 | -0.73237 | -0.77931 | -0.84257 | -0.89869 | -0.9742 | -1.0364 | -1.0722 | -1.2232 | -1.3681 | -1.4773 | -0.51808 | -0.51808 | -0.52522 | -0.53543 | -0.55278 | -0.57727 | -0.60176 | -0.63237 | -0.6589 | -0.6691 | -0.7589 | -0.76604 | -0.80482 | -0.64869 | -0.65686 | -0.67318 | -0.69257 | -0.72727 | -0.7742 | -0.80584 | -0.84869 | -0.89971 | -0.9191 | -1.0558 | -1.1201 | -1.1691
|  | CORRAN | EE |  |  |  |  | -0.69053 | -0.69257 | -0.70584 | -0.72829 | -0.77522 | -0.84257 | -0.89155 | -0.96604 | -1.0262 | -1.0589 | -1.2232 | -1.3681 | -1.4681 | -0.51706 | -0.51808 | -0.52522 | -0.53441 | -0.55278 | -0.57727 | -0.59461 | -0.62931 | -0.6538 | -0.66604 | -0.75278 | -0.76094 | -0.75992 | -0.64869 | -0.65584 | -0.67216 | -0.69053 | -0.72727 | -0.7742 | -0.79563 | -0.84563 | -0.89359 | -0.91196 | -1.0518 | -1.1201 | -1.1548
|  | CORRAN | HT |  |  |  |  | -0.68951 | -0.69461 | -0.70584 | -0.72727 | -0.76808 | -0.81808 | -0.88033 | -0.9538 | -1.016 | -1.0426 | -1.162 | -1.3069 | -1.4773 | -0.51706 | -0.51808 | -0.52522 | -0.53441 | -0.54665 | -0.57727 | -0.60176 | -0.63237 | -0.6589 | -0.66604 | -0.7589 | -0.76604 | -0.75073 | -0.64869 | -0.65584 | -0.67318 | -0.69053 | -0.72012 | -0.76808 | -0.80584 | -0.84359 | -0.89053 | -0.90584 | -1.0558 | -1.1007 | -1.165
|  | CORRAN | HE |  |  |  |  | -0.68951 | -0.69461 | -0.70584 | -0.73237 | -0.77931 | -0.84053 | -0.89869 | -0.9742 | -1.0364 | -1.0722 | -1.1793 | -1.3426 | -1.4375 | -0.51808 | -0.51808 | -0.52522 | -0.53543 | -0.54767 | -0.57624 | -0.59563 | -0.63135 | -0.65584 | -0.6691 | -0.74971 | -0.75992 | -0.78135 | -0.64869 | -0.65686 | -0.67318 | -0.69257 | -0.72216 | -0.77216 | -0.79665 | -0.84869 | -0.89971 | -0.9191 | -1.0375 | -1.115 | -1.1691
|  | CORRAN | FB |  |  |  |  | -0.66196 | -0.65584 | -0.65278 | -0.65482 | -0.66502 | -0.68033 | -0.69053 | -0.70073 | -0.72318 | -0.73849 | -0.83441 | -0.9191 | -0.95176 | -0.50584 | -0.50176 | -0.50176 | -0.50584 | -0.5089 | -0.5191 | -0.5242 | -0.53237 | -0.54767 | -0.5589 | -0.65278 | -0.74359 | -0.80482 | -0.63441 | -0.63237 | -0.63951 | -0.64461 | -0.65584 | -0.6742 | -0.68441 | -0.69461 | -0.72114 | -0.73135 | -0.83339 | -0.92522 | -0.93951
| KILLIN | COSHIEVILLE | MINIMUM HEADROOM | NN 77193 48683 | YES | YES | 1.425 | -0.09449 | -0.086327 | -0.088367 | -0.12 | -0.15061 | -0.45061 | -0.64959 | -0.77612 | -0.96694 | -1.0271 | -1.4578 | -1.7588 | -1.8873 | 0.51776 | 0.50959 | 0.4902 | 0.45347 | 0.39633 | 0.11265 | -0.059796 | -0.15163 | -0.30061 | -0.3649 | -0.72408 | -0.83531 | -0.83837 | 0.2249 | 0.23306 | 0.23204 | 0.21163 | 0.18816 | -0.075102 | -0.25265 | -0.33531 | -0.50265 | -0.55571 | -0.9302 | -1.1618 | -1.2424
|  | COSHIEVILLE | EE |  |  |  |  | -0.093469 | -0.086327 | -0.086327 | -0.1098 | -0.14245 | -0.4302 | -0.61694 | -0.72408 | -0.92714 | -1.0067 | -1.4578 | -1.7588 | -1.8873 | 0.51776 | 0.50959 | 0.49224 | 0.45551 | 0.39837 | 0.11878 | -0.051633 | -0.12918 | -0.29653 | -0.3649 | -0.70265 | -0.83531 | -0.83837 | 0.22592 | 0.23306 | 0.23408 | 0.21878 | 0.19429 | -0.059796 | -0.2251 | -0.29449 | -0.47408 | -0.54347 | -0.9302 | -1.1618 | -1.2424
|  | COSHIEVILLE | HT |  |  |  |  | -0.09449 | -0.086327 | -0.088367 | -0.12 | -0.15061 | -0.4251 | -0.62918 | -0.71898 | -0.9149 | -0.99653 | -1.4118 | -1.5853 | -1.7129 | 0.51776 | 0.50959 | 0.4902 | 0.45347 | 0.39633 | 0.13306 | -0.047551 | -0.11082 | -0.27408 | -0.34857 | -0.72408 | -0.73224 | -0.69449 | 0.2249 | 0.23408 | 0.23204 | 0.21163 | 0.18816 | -0.052653 | -0.23429 | -0.28837 | -0.46286 | -0.53633 | -0.90571 | -1.0169 | -1.0812
|  | COSHIEVILLE | HE |  |  |  |  | -0.09449 | -0.086327 | -0.087347 | -0.11592 | -0.15061 | -0.45061 | -0.64959 | -0.77612 | -0.96694 | -1.0271 | -1.322 | -1.4843 | -1.5629 | 0.51776 | 0.50959 | 0.49122 | 0.45449 | 0.39735 | 0.11265 | -0.059796 | -0.15163 | -0.30061 | -0.35061 | -0.60367 | -0.59041 | -0.55367 | 0.22592 | 0.23408 | 0.23204 | 0.21571 | 0.18918 | -0.075102 | -0.25265 | -0.33531 | -0.50265 | -0.55571 | -0.81286 | -0.91184 | -0.95163
|  | COSHIEVILLE | FB |  |  |  |  | -0.080204 | -0.066939 | -0.053673 | -0.057755 | -0.07 | -0.36388 | -0.38224 | -0.39857 | -0.43939 | -0.44653 | -0.59347 | -0.75673 | -1.021 | 0.53918 | 0.53306 | 0.52694 | 0.50959 | 0.48 | 0.15653 | 0.1249 | 0.11163 | 0.074898 | 0.040204 | -0.078163 | -0.20265 | -0.43531 | 0.25755 | 0.27082 | 0.28612 | 0.2902 | 0.28612 | 0.012653 | -0.0067347 | -0.01898 | -0.054694 | -0.080204 | -0.21286 | -0.33735 | -0.57102
| COUPAR ANGUS | COUPAR ANGUS | MINIMUM HEADROOM | NO 21784 39212 | NO | NO | 7.396 | 2.8429 | 2.7816 | 2.7582 | 2.3337 | 1.8796 | 1.5592 | 1.2184 | 1.0286 | 0.70816 | 0.4898 | -0.75918 | -1.1571 | -1.4041 | 3.0592 | 2.9816 | 2.9378 | 2.5194 | 2.0724 | 1.7622 | 1.4337 | 1.2633 | 0.96633 | 0.74898 | -0.36327 | -0.68469 | -0.91224 | 2.3259 | 2.2524 | 2.2157 | 1.7739 | 1.3024 | 0.9749 | 0.63 | 0.4402 | 0.1198 | -0.10265 | -1.3567 | -1.7384 | -1.971
|  | COUPAR ANGUS | EE |  |  |  |  | 2.8429 | 2.7939 | 2.7582 | 2.3408 | 1.8867 | 1.5765 | 1.2184 | 1.0561 | 0.74286 | 0.53265 | -0.75918 | -1.1571 | -1.4041 | 3.0592 | 2.9939 | 2.9378 | 2.5235 | 2.0755 | 1.7776 | 1.4337 | 1.2816 | 0.98776 | 0.77959 | -0.35612 | -0.68469 | -0.91224 | 2.3259 | 2.2657 | 2.2157 | 1.781 | 1.3096 | 0.99327 | 0.63 | 0.46469 | 0.15143 | -0.063878 | -1.3567 | -1.7384 | -1.971
|  | COUPAR ANGUS | HT |  |  |  |  | 2.8449 | 2.7949 | 2.7582 | 2.3337 | 1.8796 | 1.5745 | 1.2551 | 1.0857 | 0.75 | 0.4898 | -0.71224 | -1.0765 | -1.2184 | 3.0602 | 2.9939 | 2.9378 | 2.5194 | 2.0724 | 1.7786 | 1.4765 | 1.3204 | 1.0071 | 0.74898 | -0.36327 | -0.66837 | -0.7449 | 2.328 | 2.2667 | 2.2157 | 1.7739 | 1.3024 | 0.99327 | 0.6698 | 0.50143 | 0.16469 | -0.10265 | -1.32 | -1.6771 | -1.8037
|  | COUPAR ANGUS | HE |  |  |  |  | 2.8449 | 2.7949 | 2.7582 | 2.3378 | 1.8827 | 1.5592 | 1.2408 | 1.0286 | 0.70816 | 0.54796 | -0.42551 | -0.71735 | -0.8898 | 3.0602 | 2.9939 | 2.9388 | 2.5235 | 2.0755 | 1.7622 | 1.4592 | 1.2633 | 0.96633 | 0.79898 | -0.073469 | -0.29286 | -0.47449 | 2.328 | 2.2657 | 2.2157 | 1.778 | 1.3055 | 0.9749 | 0.65449 | 0.4402 | 0.1198 | -0.046531 | -1.0282 | -1.3016 | -1.4669
|  | COUPAR ANGUS | FB |  |  |  |  | 3.0592 | 2.7816 | 2.7908 | 2.7 | 2.3357 | 2.1857 | 2.0816 | 1.8735 | 1.7122 | 1.6541 | 1.0765 | 0.081633 | -0.57551 | 3.1949 | 2.9816 | 2.9704 | 2.8592 | 2.4929 | 2.3184 | 2.1959 | 1.9806 | 1.8153 | 1.7367 | 1.1306 | 0.11837 | -0.65102 | 2.5708 | 2.2524 | 2.2504 | 2.1453 | 1.7627 | 1.6014 | 1.4882 | 1.2729 | 1.1127 | 1.0463 | 0.45857 | -0.69653 | -1.1884
| CRAIGIEBUCKLER | CRAIGIEBUCKLER | MINIMUM HEADROOM | NJ 90775 04519 | NO | NO | 4.166 | 14.1199 | 14.0832 | 14.0363 | 13.923 | 13.874 | 13.5546 | 13.1771 | 12.772 | 12.3914 | 12.0352 | 10.6873 | 9.9424 | 9.5301 | 14.6101 | 14.5795 | 14.5326 | 14.4724 | 14.4948 | 14.3346 | 14.1254 | 13.8969 | 13.7081 | 13.4979 | 12.8693 | 12.8642 | 12.7785 | 14.6305 | 14.5856 | 14.5265 | 14.4377 | 14.4061 | 14.1387 | 13.8173 | 13.4714 | 13.1459 | 12.8387 | 11.6989 | 11.1459 | 10.8489
|  | CRAIGIEBUCKLER | EE |  |  |  |  | 14.1199 | 14.0832 | 14.0363 | 13.923 | 13.874 | 13.5546 | 13.1771 | 12.772 | 12.3914 | 12.0352 | 10.6873 | 9.9424 | 9.5301 | 14.6112 | 14.5795 | 14.5326 | 14.4724 | 14.4948 | 14.3346 | 14.1254 | 13.8969 | 13.7091 | 13.504 | 12.9193 | 12.8642 | 12.8061 | 14.6305 | 14.5856 | 14.5265 | 14.4377 | 14.4061 | 14.1387 | 13.8173 | 13.4714 | 13.1459 | 12.8387 | 11.6989 | 11.1459 | 10.8489
|  | CRAIGIEBUCKLER | HT |  |  |  |  | 14.121 | 14.0934 | 14.0536 | 13.9352 | 13.8944 | 13.5699 | 13.2005 | 12.8046 | 12.4312 | 12.0638 | 10.722 | 10.0454 | 9.7699 | 14.6101 | 14.5795 | 14.5336 | 14.4734 | 14.4959 | 14.3367 | 14.1254 | 13.901 | 13.7081 | 13.4979 | 12.8693 | 12.9499 | 13.0642 | 14.6316 | 14.5959 | 14.5408 | 14.4459 | 14.4173 | 14.1469 | 13.8305 | 13.4897 | 13.1714 | 12.8571 | 11.7152 | 11.2152 | 11.0469
|  | CRAIGIEBUCKLER | HE |  |  |  |  | 14.124 | 14.0903 | 14.0454 | 13.9301 | 13.8863 | 13.5975 | 13.2516 | 12.8822 | 12.5322 | 12.224 | 11.0546 | 10.471 | 10.074 | 14.6112 | 14.5805 | 14.5336 | 14.4744 | 14.4969 | 14.3408 | 14.1316 | 13.9101 | 13.7183 | 13.5112 | 12.9387 | 12.8969 | 12.7785 | 14.6326 | 14.5969 | 14.5346 | 14.4448 | 14.4152 | 14.1663 | 13.8652 | 13.5428 | 13.2397 | 12.9622 | 11.9673 | 11.555 | 11.2632
|  | CRAIGIEBUCKLER | FB |  |  |  |  | 14.2781 | 14.2965 | 14.3159 | 14.3067 | 14.2893 | 14.1934 | 14.2036 | 14.0954 | 13.9832 | 13.8597 | 13.3056 | 12.5495 | 12.1322 | 14.7305 | 14.7203 | 14.7173 | 14.7152 | 14.6948 | 14.6081 | 14.6091 | 14.5152 | 14.4081 | 14.2959 | 13.8295 | 13.2448 | 12.8693 | 14.7785 | 14.7826 | 14.7897 | 14.7816 | 14.7367 | 14.6356 | 14.6612 | 14.552 | 14.4367 | 14.3112 | 13.7663 | 12.9571 | 12.6908
| REDMOSS | CRAIGINCHES | MINIMUM HEADROOM | NJ 94694 04089 | NO | NO | 1.904 | 9.1891 | 9.1279 | 9.0677 | 9.0044 | 8.9096 | 8.78 | 8.631 | 8.4636 | 8.2555 | 8.03 | 6.8096 | 5.8585 | 5.4463 | 11.6891 | 11.6044 | 11.5381 | 11.4861 | 11.3973 | 11.2626 | 11.1391 | 11.0065 | 10.8606 | 10.7024 | 10.3044 | 9.7228 | 9.0177 | 9.5667 | 9.5147 | 9.4636 | 9.4116 | 9.333 | 9.2228 | 9.1065 | 8.9708 | 8.8279 | 8.6963 | 7.8779 | 7.1371 | 6.783
|  | CRAIGINCHES | EE |  |  |  |  | 9.1891 | 9.1279 | 9.0677 | 9.0085 | 8.9096 | 8.781 | 8.6361 | 8.4738 | 8.2718 | 8.0493 | 7.0198 | 6.0718 | 5.5055 | 11.6891 | 11.6044 | 11.5391 | 11.4871 | 11.3973 | 11.2891 | 11.1524 | 11.0147 | 10.8749 | 10.7075 | 10.3065 | 9.7228 | 9.03 | 9.5667 | 9.5167 | 9.4636 | 9.4116 | 9.333 | 9.233 | 9.1116 | 8.981 | 8.8463 | 8.7147 | 8.0626 | 7.2871 | 6.783
|  | CRAIGINCHES | HT |  |  |  |  | 9.1983 | 9.1473 | 9.0912 | 9.03 | 8.9422 | 8.7861 | 8.631 | 8.4636 | 8.2555 | 8.03 | 6.8096 | 5.8585 | 5.4463 | 11.6902 | 11.6085 | 11.5412 | 11.4922 | 11.4044 | 11.2657 | 11.1391 | 11.0065 | 10.8606 | 10.7024 | 10.3044 | 10.0891 | 9.8218 | 9.5749 | 9.5279 | 9.484 | 9.4351 | 9.3555 | 9.2351 | 9.1065 | 8.9708 | 8.8279 | 8.6963 | 7.8779 | 7.1371 | 6.8269
|  | CRAIGINCHES | HE |  |  |  |  | 9.1912 | 9.13 | 9.0687 | 9.0044 | 8.9177 | 8.78 | 8.6555 | 8.5126 | 8.3391 | 8.184 | 7.3371 | 6.7412 | 6.2942 | 11.6891 | 11.6075 | 11.5381 | 11.4861 | 11.4004 | 11.2626 | 11.1534 | 11.0238 | 10.8851 | 10.7708 | 10.4463 | 10.284 | 9.9228 | 9.5687 | 9.5147 | 9.4636 | 9.4147 | 9.334 | 9.2228 | 9.1198 | 9.0004 | 8.8738 | 8.783 | 8.3157 | 7.8677 | 7.53
|  | CRAIGINCHES | FB |  |  |  |  | 9.2228 | 9.2524 | 9.1963 | 9.1708 | 9.1493 | 9.0881 | 9.0422 | 8.9708 | 8.9096 | 8.834 | 8.4514 | 7.7881 | 7.1514 | 11.7096 | 11.7351 | 11.6412 | 11.6187 | 11.6106 | 11.5361 | 11.5004 | 11.4249 | 11.3789 | 11.3044 | 10.9861 | 10.5402 | 9.0177 | 9.5973 | 9.6279 | 9.5759 | 9.5585 | 9.5442 | 9.4871 | 9.4473 | 9.3973 | 9.3453 | 9.282 | 8.9932 | 8.4942 | 8.1075
| CRAIGIEBUCKLER | CRAIGTON | MINIMUM HEADROOM | NJ 89195 03438 | NO | NO | 1.177 | 3.5242 | 2.2486 | 0.92008 | 0.25069 | -2.9279 | -3.7085 | -4.2667 | -4.6871 | -5.0952 | -5.3616 | -6.6585 | -7.586 | -8.1228 | 5.4548 | 4.3272 | 3.3058 | 2.9935 | 2.0129 | 1.7078 | 1.3731 | 1.1772 | 0.99661 | 0.79967 | -0.016657 | 0.019057 | 0.05069 | 5.0211 | 3.8578 | 2.715 | 2.2435 | 0.13232 | -0.48196 | -0.9636 | -1.3167 | -1.6534 | -1.8973 | -3.0738 | -3.7258 | -4.0483
|  | CRAIGTON | EE |  |  |  |  | 4.0058 | 2.2486 | 0.92926 | 0.29967 | -2.6952 | -3.536 | -4.082 | -4.5034 | -4.9156 | -5.2769 | -6.6585 | -7.485 | -8.0554 | 5.9007 | 4.3272 | 3.3058 | 2.9935 | 2.1344 | 1.716 | 1.3874 | 1.1925 | 1.016 | 0.81089 | 0.080282 | 0.090486 | 0.1313 | 5.4476 | 3.8578 | 2.716 | 2.2619 | 0.30069 | -0.36564 | -0.83911 | -1.1901 | -1.536 | -1.8371 | -3.0524 | -3.6085 | -3.9718
|  | CRAIGTON | HT |  |  |  |  | 3.7313 | 2.3446 | 1.0282 | 0.39049 | -2.9279 | -3.2595 | -3.6411 | -4.0432 | -4.5248 | -5.1034 | -6.6126 | -7.586 | -8.1228 | 5.6435 | 4.3813 | 3.3078 | 2.9997 | 2.0129 | 1.8742 | 1.6966 | 1.5007 | 1.2282 | 0.84151 | -0.016657 | 0.019057 | 0.11089 | 5.2027 | 3.9242 | 2.7578 | 2.3017 | 0.13232 | -0.13809 | -0.46053 | -0.79931 | -1.2146 | -1.7156 | -3.0738 | -3.7258 | -4.0483
|  | CRAIGTON | HE |  |  |  |  | 3.5242 | 2.2599 | 0.92008 | 0.25069 | -2.7758 | -3.7085 | -4.2667 | -4.6871 | -5.0952 | -5.3616 | -6.5524 | -7.2105 | -7.5962 | 5.4548 | 4.3303 | 3.3058 | 2.9935 | 2.1323 | 1.7078 | 1.3731 | 1.1772 | 0.99661 | 0.79967 | 0.070078 | 0.060894 | 0.05069 | 5.0211 | 3.865 | 2.715 | 2.2435 | 0.24559 | -0.48196 | -0.9636 | -1.3167 | -1.6534 | -1.8973 | -2.9626 | -3.4105 | -3.6656
|  | CRAIGTON | FB |  |  |  |  | 4.9884 | 3.6813 | 2.266 | 1.5548 | -0.7289 | -1.8789 | -2.1789 | -2.5136 | -2.632 | -2.8003 | -3.432 | -4.1911 | -4.4636 | 6.7823 | 5.5895 | 4.3874 | 3.8986 | 2.9384 | 2.3507 | 2.0599 | 1.7435 | 1.6548 | 1.5333 | 1.0691 | 0.5364 | 0.4313 | 6.3099 | 5.117 | 3.867 | 3.2864 | 1.667 | 0.7864 | 0.5211 | 0.20783 | 0.11498 | -0.035024 | -0.53707 | -1.3626 | -1.5207
| BRACO | CRIEFF | MINIMUM HEADROOM | NN 85626 22119 | NO | YES | 2.375 | 5.779 | 14.3325 | 14.2141 | 13.8223 | 13.5896 | 12.7988 | 12.0141 | 11.3274 | 10.5284 | 9.8019 | 7.357 | 5.4009 | 4.2039 | 8.4892 | 16.6488 | 16.5886 | 16.2988 | 16.1662 | 15.655 | 15.157 | 14.7162 | 14.1917 | 13.5896 | 12.1213 | 11.3998 | 10.905 | 7.4163 | 15.7213 | 15.6396 | 15.2805 | 15.0733 | 14.3958 | 13.7152 | 13.1182 | 12.4376 | 11.7672 | 9.6784 | 8.1856 | 7.307
|  | CRIEFF | EE |  |  |  |  | 5.779 | 14.3325 | 14.2141 | 13.8243 | 13.606 | 12.8192 | 12.0233 | 11.3274 | 10.5927 | 9.8019 | 7.357 | 5.4009 | 4.2039 | 8.4913 | 16.6488 | 16.5886 | 16.2988 | 16.1662 | 15.655 | 15.157 | 14.7162 | 14.2213 | 13.5958 | 12.1519 | 11.3998 | 10.905 | 7.4173 | 15.7213 | 15.6396 | 15.2805 | 15.0856 | 14.4019 | 13.7152 | 13.1182 | 12.4825 | 11.7672 | 9.6784 | 8.1856 | 7.307
|  | CRIEFF | HT |  |  |  |  | 5.7811 | 14.3366 | 14.2345 | 13.8611 | 13.6396 | 12.9182 | 12.1631 | 11.455 | 10.7407 | 9.9356 | 7.5703 | 5.6366 | 4.4386 | 8.4892 | 16.6509 | 16.5907 | 16.3029 | 16.1672 | 15.6998 | 15.207 | 14.7294 | 14.2386 | 13.5896 | 12.1213 | 11.5294 | 11.3662 | 7.4173 | 15.7264 | 15.6539 | 15.3039 | 15.105 | 14.4774 | 13.8192 | 13.205 | 12.5845 | 11.8509 | 9.8223 | 8.3856 | 7.5662
|  | CRIEFF | HE |  |  |  |  | 5.779 | 14.3345 | 14.2203 | 13.8223 | 13.5896 | 12.7988 | 12.0141 | 11.3509 | 10.5284 | 9.8019 | 8.0284 | 6.1427 | 5.2529 | 8.4913 | 16.6498 | 16.5886 | 16.2988 | 16.1662 | 15.6703 | 15.1784 | 14.7845 | 14.1917 | 13.6539 | 12.6539 | 11.8876 | 11.4815 | 7.4163 | 15.7243 | 15.6437 | 15.2805 | 15.0733 | 14.3958 | 13.7172 | 13.159 | 12.4376 | 11.7896 | 10.2825 | 8.8305 | 8.1754
|  | CRIEFF | FB |  |  |  |  | 6.0239 | 14.5641 | 14.4417 | 14.3937 | 14.3437 | 14.058 | 13.8784 | 13.7427 | 13.4356 | 13.1417 | 11.7539 | 9.9835 | 8.7896 | 8.6566 | 16.7886 | 16.6866 | 16.6519 | 16.6029 | 16.3417 | 16.1937 | 16.0866 | 15.809 | 15.5376 | 14.3264 | 12.5774 | 11.0958 | 7.6928 | 15.9376 | 15.806 | 15.7794 | 15.7254 | 15.4488 | 15.2856 | 15.1621 | 14.8682 | 14.5856 | 13.2733 | 11.2805 | 10.4539
| PORT ANN | CRINAN | MINIMUM HEADROOM | NR 79620 92347 | YES | YES | 0.079 | 0.096939 | -0.10102 | -0.10204 | -0.13265 | -0.16224 | -0.27449 | -0.44082 | -0.50816 | -0.67551 | -0.83673 | -1.0663 | -1.0929 | -1.1061 | 0.40408 | 0.23571 | 0.23776 | 0.22653 | 0.22143 | 0.13367 | -0.017347 | -0.071429 | -0.22347 | -0.38061 | -0.59286 | -0.56735 | -0.54388 | 0.22041 | 0.019388 | 0.017347 | -0.005102 | -0.026531 | -0.13265 | -0.30204 | -0.36531 | -0.52449 | -0.68265 | -0.89694 | -0.90204 | -0.91122
|  | CRINAN | EE |  |  |  |  | 0.1 | -0.10102 | -0.10204 | -0.13265 | -0.16224 | -0.21837 | -0.26633 | -0.38163 | -0.58571 | -0.81735 | -1.0408 | -1.052 | -1.102 | 0.40612 | 0.23571 | 0.23776 | 0.22653 | 0.22143 | 0.1898 | 0.15408 | 0.061224 | -0.12041 | -0.34898 | -0.54796 | -0.51735 | -0.54388 | 0.22245 | 0.019388 | 0.017347 | -0.005102 | -0.026531 | -0.071429 | -0.12857 | -0.2398 | -0.43776 | -0.64694 | -0.86224 | -0.86327 | -0.91122
|  | CRINAN | HT |  |  |  |  | 0.10102 | -0.1 | -0.10102 | -0.12959 | -0.1602 | -0.27449 | -0.44082 | -0.50816 | -0.67551 | -0.83673 | -1.0663 | -1.0929 | -1.1061 | 0.40612 | 0.23571 | 0.23776 | 0.22653 | 0.22143 | 0.13367 | -0.017347 | -0.071429 | -0.22347 | -0.38061 | -0.59286 | -0.56735 | -0.53776 | 0.22245 | 0.020408 | 0.018367 | -0.0030612 | -0.02551 | -0.13265 | -0.30204 | -0.36531 | -0.52449 | -0.68265 | -0.89694 | -0.90204 | -0.90204
|  | CRINAN | HE |  |  |  |  | 0.096939 | -0.1 | -0.10204 | -0.13061 | -0.16224 | -0.21939 | -0.27041 | -0.31224 | -0.45 | -0.61633 | -0.72959 | -0.77245 | -0.79388 | 0.40408 | 0.23673 | 0.23776 | 0.22653 | 0.22245 | 0.18878 | 0.15 | 0.12653 | 0.016327 | -0.13265 | -0.22449 | -0.20816 | -0.2102 | 0.22041 | 0.021429 | 0.018367 | -0.0030612 | -0.02551 | -0.072449 | -0.13265 | -0.17245 | -0.3051 | -0.4551 | -0.56939 | -0.58367 | -0.58776
|  | CRINAN | FB |  |  |  |  | 0.12041 | 0.11735 | 0.1051 | 0.096939 | 0.081633 | 0.060204 | -0.26633 | -0.28878 | -0.30306 | -0.33061 | -0.43776 | -0.53265 | -0.65918 | 0.43061 | 0.42653 | 0.41122 | 0.41122 | 0.4102 | 0.39082 | 0.096939 | 0.080612 | 0.071429 | 0.05 | -0.036735 | -0.13163 | -0.27755 | 0.24184 | 0.23571 | 0.22041 | 0.21429 | 0.20408 | 0.18673 | -0.1551 | -0.17347 | -0.18265 | -0.2051 | -0.30408 | -0.41429 | -0.53469
| PORT ANN | CROMALT | MINIMUM HEADROOM | NN 08395 07755 | YES | YES | 0 | 2.1327 | 2.1296 | 2.1245 | 2.1459 | 2.1388 | 2.1255 | 2.0918 | 2.0429 | 1.9959 | 1.9643 | 1.748 | 1.7245 | 1.7122 | 2.1913 | 2.1893 | 2.1862 | 2.449 | 2.448 | 2.4347 | 2.4194 | 2.3908 | 2.3673 | 2.3357 | 2.1173 | 2.1173 | 2.1204 | 2.1824 | 2.1783 | 2.1722 | 2.3102 | 2.3071 | 2.2827 | 2.2571 | 2.2265 | 2.1908 | 2.1571 | 1.9255 | 1.9102 | 1.9041
|  | CROMALT | EE |  |  |  |  | 2.1347 | 2.1327 | 2.1276 | 2.1643 | 2.1582 | 2.1398 | 2.1296 | 2.0888 | 2.0459 | 2.0276 | 1.748 | 1.7245 | 1.7122 | 2.1923 | 2.1913 | 2.1872 | 2.4571 | 2.4561 | 2.4449 | 2.4357 | 2.4092 | 2.3929 | 2.3755 | 2.1173 | 2.1173 | 2.1204 | 2.1855 | 2.1824 | 2.1753 | 2.3245 | 2.3204 | 2.301 | 2.2857 | 2.2469 | 2.2265 | 2.2092 | 1.9255 | 1.9102 | 1.9041
|  | CROMALT | HT |  |  |  |  | 2.1327 | 2.1296 | 2.1245 | 2.1459 | 2.1388 | 2.1255 | 2.0918 | 2.0429 | 1.9959 | 1.9643 | 1.8949 | 1.8704 | 1.8408 | 2.1913 | 2.1893 | 2.1862 | 2.449 | 2.448 | 2.4347 | 2.4194 | 2.3908 | 2.3673 | 2.3357 | 2.2704 | 2.2684 | 2.2714 | 2.1824 | 2.1783 | 2.1722 | 2.3102 | 2.3071 | 2.2827 | 2.2571 | 2.2265 | 2.1908 | 2.1571 | 2.0867 | 2.0673 | 2.0592
|  | CROMALT | HE |  |  |  |  | 2.1327 | 2.1306 | 2.1276 | 2.1592 | 2.152 | 2.1337 | 2.1092 | 2.0673 | 2.0204 | 2.0031 | 1.901 | 1.8694 | 1.849 | 2.1913 | 2.1903 | 2.1872 | 2.4531 | 2.452 | 2.4418 | 2.4265 | 2.401 | 2.3806 | 2.3633 | 2.2776 | 2.2714 | 2.2571 | 2.1824 | 2.1793 | 2.1742 | 2.3194 | 2.3163 | 2.2969 | 2.2694 | 2.2306 | 2.2092 | 2.1898 | 2.0939 | 2.0704 | 2.0571
|  | CROMALT | FB |  |  |  |  | 2.1571 | 2.1582 | 2.1653 | 2.2143 | 2.2184 | 2.2153 | 2.2143 | 2.2092 | 2.1806 | 2.1714 | 2.0837 | 1.9959 | 1.9745 | 2.2128 | 2.2107 | 2.2117 | 2.4827 | 2.4867 | 2.4755 | 2.4745 | 2.4643 | 2.4449 | 2.4316 | 2.3612 | 2.2592 | 2.2082 | 2.2069 | 2.2038 | 2.2069 | 2.3673 | 2.3724 | 2.3602 | 2.3592 | 2.35 | 2.3235 | 2.3163 | 2.2337 | 2.1276 | 2.1163
| ALNESS | CROSSHILLS | MINIMUM HEADROOM | NH 65470 70156 | NO | NO | 4.128 | 4.3344 | 4.3487 | 4.3212 | 4.1436 | 4.0467 | 2.263 | 0.6028 | -1.1707 | -2.4972 | -3.0258 | -4.3278 | -5.5717 | -6.4462 | 6.1293 | 6.1406 | 6.1365 | 6.0967 | 6.0589 | 4.664 | 3.2589 | 1.6079 | 0.43342 | 0.11505 | -0.31046 | -0.39822 | -0.50128 | 5.5094 | 5.5074 | 5.4941 | 5.3482 | 5.2635 | 3.7033 | 2.2452 | 0.6625 | -0.49975 | -0.93138 | -1.9344 | -2.7497 | -3.2773
|  | CROSSHILLS | EE |  |  |  |  | 4.3355 | 4.3497 | 4.3222 | 4.1436 | 4.0467 | 3.4824 | 2.8599 | 1.4304 | -0.15944 | -1.8941 | -4.3278 | -5.5717 | -6.3666 | 6.1293 | 6.1416 | 6.1365 | 6.0967 | 6.0599 | 5.8895 | 5.6467 | 4.4365 | 3.0283 | 1.3895 | -0.27169 | -0.39822 | -0.47271 | 5.5105 | 5.5094 | 5.4952 | 5.3492 | 5.2635 | 4.7921 | 4.3135 | 3.0992 | 1.6594 | 0.095151 | -1.9344 | -2.7497 | -3.2436
|  | CROSSHILLS | HT |  |  |  |  | 4.3344 | 4.3487 | 4.3212 | 4.1436 | 4.0467 | 2.263 | 0.6028 | -1.1707 | -2.4972 | -3.0258 | -4.2717 | -5.4686 | -6.4462 | 6.1293 | 6.1406 | 6.1365 | 6.0967 | 6.0589 | 4.664 | 3.2589 | 1.6079 | 0.43342 | 0.11505 | -0.31046 | -0.37067 | -0.38189 | 5.5094 | 5.5074 | 5.4941 | 5.3482 | 5.2635 | 3.7033 | 2.2452 | 0.6625 | -0.49975 | -0.93138 | -1.9048 | -2.6732 | -3.2773
|  | CROSSHILLS | HE |  |  |  |  | 4.3344 | 4.3487 | 4.3222 | 4.1487 | 4.0579 | 3.4691 | 2.9089 | 1.3977 | -0.32475 | -2.2288 | -3.9023 | -5.1176 | -5.7656 | 6.1293 | 6.1416 | 6.1365 | 6.0967 | 6.062 | 5.8548 | 5.6457 | 4.313 | 2.7579 | 0.9028 | -0.20944 | -0.31658 | -0.39311 | 5.5094 | 5.5094 | 5.4962 | 5.3523 | 5.2707 | 4.7492 | 4.336 | 3.0339 | 1.4727 | -0.23342 | -1.6375 | -2.4334 | -2.8375
|  | CROSSHILLS | FB |  |  |  |  | 4.4181 | 4.4569 | 4.4804 | 4.4038 | 4.3355 | 4.315 | 4.1324 | 3.9467 | 3.061 | 2.0344 | -1.5033 | -2.0952 | -2.3707 | 6.1844 | 6.2089 | 6.2181 | 6.1946 | 6.1161 | 6.1038 | 6.015 | 5.9242 | 5.014 | 3.912 | 0.27219 | -0.18291 | -0.50128 | 5.5931 | 5.6156 | 5.6135 | 5.5574 | 5.4441 | 5.4084 | 5.2207 | 5.0452 | 4.3074 | 3.3033 | -0.08138 | -0.52832 | -0.73954
| KEITH 1 | CULLEN | MINIMUM HEADROOM | NJ 51590 65032 | YES | YES | 0.277 | 6.3255 | 6.3367 | 6.3214 | 6.2888 | 6.0796 | 5.9194 | 5.7969 | 5.6112 | 5.5255 | 5.3673 | 5.048 | 4.8643 | 4.7786 | 6.3362 | 6.3393 | 6.3189 | 6.2893 | 6.1219 | 5.9944 | 5.8872 | 5.7107 | 5.626 | 5.4352 | 5.1128 | 4.9852 | 4.8934 | 6.3401 | 6.3492 | 6.3298 | 6.2941 | 6.0227 | 5.8594 | 5.739 | 5.5564 | 5.4686 | 5.2901 | 4.9676 | 4.8237 | 4.7543
|  | CULLEN | EE |  |  |  |  | 6.3286 | 6.3398 | 6.3429 | 6.3133 | 6.1163 | 6.0194 | 5.8408 | 5.6653 | 5.5541 | 5.3969 | 5.048 | 4.8643 | 4.7786 | 6.3393 | 6.3393 | 6.3352 | 6.3107 | 6.1434 | 6.074 | 5.9117 | 5.7495 | 5.626 | 5.4556 | 5.1372 | 4.9852 | 4.8934 | 6.3441 | 6.3503 | 6.3462 | 6.3156 | 6.0513 | 5.9543 | 5.7737 | 5.6023 | 5.4747 | 5.3135 | 4.9676 | 4.8237 | 4.7543
|  | CULLEN | HT |  |  |  |  | 6.3255 | 6.3367 | 6.3214 | 6.2888 | 6.0796 | 5.9194 | 5.799 | 5.6337 | 5.5255 | 5.3673 | 5.0551 | 4.8796 | 4.8418 | 6.3362 | 6.3393 | 6.3189 | 6.2893 | 6.1219 | 5.9944 | 5.8893 | 5.7281 | 5.626 | 5.4352 | 5.1128 | 4.9934 | 5.0179 | 6.3401 | 6.3492 | 6.3298 | 6.2941 | 6.0227 | 5.8594 | 5.7431 | 5.5747 | 5.4686 | 5.2901 | 4.9686 | 4.8319 | 4.8156
|  | CULLEN | HE |  |  |  |  | 6.3276 | 6.3398 | 6.3347 | 6.301 | 6.0959 | 5.998 | 5.7969 | 5.6112 | 5.5388 | 5.3888 | 5.1551 | 5.0827 | 5.001 | 6.3372 | 6.3423 | 6.3281 | 6.3015 | 6.1332 | 6.0628 | 5.8872 | 5.7107 | 5.6372 | 5.473 | 5.2577 | 5.2454 | 5.1597 | 6.3421 | 6.3513 | 6.339 | 6.3054 | 6.036 | 5.936 | 5.739 | 5.5564 | 5.4696 | 5.3135 | 5.0758 | 5.0431 | 4.9758
|  | CULLEN | FB |  |  |  |  | 6.3806 | 6.3929 | 6.4122 | 6.4061 | 6.4061 | 6.3878 | 6.3816 | 6.3622 | 6.3286 | 6.3041 | 6.1459 | 5.901 | 5.3653 | 6.3893 | 6.3842 | 6.3964 | 6.3832 | 6.3781 | 6.3403 | 6.3179 | 6.2699 | 6.2219 | 6.1842 | 6.0077 | 5.6189 | 5.0015 | 6.3911 | 6.3962 | 6.4105 | 6.4003 | 6.3941 | 6.3758 | 6.3656 | 6.3452 | 6.3003 | 6.2666 | 6.1135 | 5.7798 | 5.2574
| INVERNESS | CULLODEN | MINIMUM HEADROOM | NH 71240 45502 | NO | NO | 3.889 | 7.9257 | 17.4114 | 17.0359 | 16.7523 | 16.5216 | 15.2288 | 14.191 | 13.0257 | 11.9216 | 11.0808 | 8.2094 | 6.2686 | 4.7553 | 11.2196 | 19.2747 | 19.1553 | 19.1165 | 18.9859 | 18.6339 | 18.3033 | 17.8788 | 17.4808 | 17.0992 | 15.8869 | 15.6951 | 15.0869 | 10.0206 | 18.789 | 18.5063 | 18.3278 | 18.1359 | 17.2104 | 16.4349 | 15.5645 | 14.7512 | 14.0972 | 11.8839 | 10.638 | 9.8665
|  | CULLODEN | EE |  |  |  |  | 7.9267 | 17.4114 | 17.0359 | 16.7533 | 16.5329 | 15.7063 | 14.3533 | 13.0941 | 11.9818 | 11.3206 | 8.2114 | 6.2992 | 4.9206 | 11.2196 | 19.2747 | 19.1553 | 19.1165 | 18.989 | 18.7686 | 18.3492 | 17.9104 | 17.4951 | 17.1727 | 16.0165 | 15.6951 | 15.4849 | 10.0216 | 18.789 | 18.5063 | 18.3288 | 18.1451 | 17.541 | 16.5502 | 15.6125 | 14.7839 | 14.2574 | 11.9165 | 10.6431 | 9.9257
|  | CULLODEN | HT |  |  |  |  | 7.9257 | 17.4125 | 17.039 | 16.7563 | 16.5216 | 15.2288 | 14.191 | 13.0257 | 11.9737 | 11.0808 | 8.2094 | 6.2686 | 4.7553 | 11.2206 | 19.2747 | 19.1563 | 19.1165 | 18.9859 | 18.6339 | 18.3033 | 17.8788 | 17.4808 | 17.0992 | 15.8869 | 15.7369 | 15.7614 | 10.0206 | 18.79 | 18.5084 | 18.3288 | 18.1359 | 17.2104 | 16.4349 | 15.5645 | 14.7808 | 14.0972 | 11.8839 | 10.638 | 9.8665
|  | CULLODEN | HE |  |  |  |  | 7.9257 | 17.4125 | 17.038 | 16.7523 | 16.5257 | 15.4594 | 14.2584 | 13.0278 | 11.9216 | 11.2645 | 8.5278 | 6.6931 | 5.74 | 11.2206 | 19.2747 | 19.1563 | 19.1165 | 18.988 | 18.7043 | 18.3298 | 17.8992 | 17.49 | 17.1706 | 16.0584 | 15.7318 | 15.4125 | 10.0206 | 18.789 | 18.5074 | 18.3278 | 18.139 | 17.3716 | 16.4849 | 15.5716 | 14.7512 | 14.2267 | 12.1308 | 10.9114 | 10.3074
|  | CULLODEN | FB |  |  |  |  | 8.1818 | 17.7829 | 17.5645 | 17.39 | 17.3686 | 17.3706 | 16.6849 | 15.9655 | 15.4829 | 15.3227 | 13.4757 | 12.1686 | 11.6359 | 11.3727 | 19.4757 | 19.4104 | 19.3594 | 19.3369 | 19.3308 | 19.0594 | 18.7492 | 18.5023 | 18.3543 | 17.2992 | 16.0288 | 15.0869 | 10.2543 | 19.0941 | 18.9614 | 18.838 | 18.8125 | 18.8196 | 18.3206 | 17.79 | 17.4176 | 17.2614 | 15.7604 | 14.3869 | 14.1145
| CRAIGIEBUCKLER | CULTER | MINIMUM HEADROOM | NJ 84009 00884 | NO | NO | 1.088 | 4.5959 | 4.499 | 4.3316 | 4.1367 | 3.9908 | 3.5551 | 3.0898 | 2.6571 | 2.2265 | 1.898 | 0.31939 | -0.86939 | -1.6694 | 6.8296 | 6.7857 | 6.7357 | 6.6378 | 6.5592 | 6.3959 | 6.2153 | 6.0133 | 5.8184 | 5.5949 | 4.6184 | 4.3653 | 4.1418 | 6.051 | 5.9806 | 5.8653 | 5.7204 | 5.6347 | 5.3041 | 4.9388 | 4.5786 | 4.2214 | 3.9327 | 2.5041 | 1.7265 | 1.2051
|  | CULTER | EE |  |  |  |  | 4.5959 | 4.499 | 4.3378 | 4.1551 | 4.0194 | 3.6143 | 3.1786 | 2.7653 | 2.3643 | 2.0153 | 0.31939 | -0.86939 | -1.6694 | 6.8296 | 6.7867 | 6.7388 | 6.6408 | 6.5622 | 6.402 | 6.2255 | 6.0255 | 5.8367 | 5.6184 | 4.6184 | 4.3653 | 4.1418 | 6.051 | 5.9918 | 5.8694 | 5.7327 | 5.6551 | 5.3439 | 4.9969 | 4.6469 | 4.3092 | 4.0031 | 2.5041 | 1.7265 | 1.2051
|  | CULTER | HT |  |  |  |  | 4.5969 | 4.5173 | 4.3704 | 4.1929 | 4.0582 | 3.6408 | 3.2031 | 2.7878 | 2.3776 | 2.0061 | 0.57041 | -0.57857 | -1.3306 | 6.8296 | 6.7888 | 6.7388 | 6.6429 | 6.5602 | 6.398 | 6.2163 | 6.0133 | 5.8184 | 5.5949 | 4.852 | 4.7418 | 4.7133 | 6.052 | 5.9806 | 5.8898 | 5.7551 | 5.6776 | 5.3592 | 5.0122 | 4.6612 | 4.3143 | 3.999 | 2.7939 | 2.0571 | 1.6
|  | CULTER | HE |  |  |  |  | 4.5969 | 4.501 | 4.3316 | 4.1367 | 3.9908 | 3.5551 | 3.0898 | 2.6571 | 2.2265 | 1.898 | 0.6449 | -0.41633 | -1.0276 | 6.8296 | 6.7857 | 6.7357 | 6.6378 | 6.5592 | 6.3959 | 6.2153 | 6.0133 | 5.8194 | 5.6041 | 4.9051 | 4.6449 | 4.399 | 6.051 | 5.9918 | 5.8653 | 5.7204 | 5.6347 | 5.3041 | 4.9388 | 4.5786 | 4.2214 | 3.9327 | 2.8847 | 2.1541 | 1.7245
|  | CULTER | FB |  |  |  |  | 4.7255 | 4.7204 | 4.652 | 4.5653 | 4.4949 | 4.3327 | 4.2918 | 4.202 | 4.0939 | 3.9857 | 3.3531 | 2.4469 | 2.0704 | 6.9143 | 6.9 | 6.8765 | 6.8551 | 6.8102 | 6.7286 | 6.6949 | 6.6204 | 6.5316 | 6.4184 | 5.8235 | 4.9776 | 4.4122 | 6.1867 | 6.1704 | 6.1429 | 6.0806 | 6.0316 | 5.9041 | 5.8888 | 5.8031 | 5.702 | 5.5939 | 4.9929 | 4.0459 | 3.8469
| ELGIN | CUMMING STREET | MINIMUM HEADROOM | NJ 21542 63007 | NO | YES | 4.356 | 8.012 | 7.912 | 7.8182 | 7.3427 | 7.2661 | 6.7069 | 6.4478 | 6.2447 | 5.958 | 5.7376 | 4.2835 | 2.7549 | 1.8069 | 7.9916 | 7.8876 | 7.8141 | 7.3927 | 7.3182 | 6.8325 | 6.5845 | 6.5386 | 6.2825 | 6.0763 | 5.3488 | 4.7569 | 3.9376 | 8.4095 | 8.3268 | 8.2462 | 7.783 | 7.7115 | 7.1779 | 6.9391 | 6.7768 | 6.2462 | 5.8391 | 4.236 | 2.9258 | 2.1473
|  | CUMMING STREET | EE |  |  |  |  | 8.012 | 7.9192 | 7.8467 | 7.3947 | 7.3141 | 6.7457 | 6.4743 | 6.2702 | 5.9886 | 5.7988 | 4.2835 | 2.7549 | 1.8069 | 7.9916 | 7.8927 | 7.8335 | 7.4284 | 7.3549 | 6.8478 | 6.6457 | 6.5447 | 6.3039 | 6.1835 | 5.3488 | 4.7569 | 4.3182 | 8.4095 | 8.3309 | 8.2697 | 7.8207 | 7.7432 | 7.2013 | 6.9687 | 6.7952 | 6.2973 | 6.0666 | 4.236 | 2.9258 | 2.1473
|  | CUMMING STREET | HT |  |  |  |  | 8.012 | 7.912 | 7.8182 | 7.3427 | 7.2661 | 6.7069 | 6.4478 | 6.3039 | 6.0478 | 5.8018 | 4.5018 | 3.0855 | 2.1437 | 7.9916 | 7.8876 | 7.8141 | 7.3927 | 7.3182 | 6.8325 | 6.5845 | 6.561 | 6.3192 | 6.0763 | 5.4223 | 4.9886 | 4.7733 | 8.4095 | 8.3268 | 8.2462 | 7.783 | 7.7115 | 7.1779 | 6.9391 | 6.8207 | 6.3748 | 5.8391 | 4.4136 | 3.2483 | 2.5595
|  | CUMMING STREET | HE |  |  |  |  | 8.012 | 7.9151 | 7.8365 | 7.3672 | 7.2845 | 6.7161 | 6.4559 | 6.2447 | 5.958 | 5.7376 | 4.8284 | 3.3988 | 2.7784 | 7.9916 | 7.8896 | 7.8294 | 7.412 | 7.3365 | 6.8365 | 6.6518 | 6.5386 | 6.2825 | 6.0967 | 5.6253 | 5.0518 | 4.7345 | 8.4095 | 8.3289 | 8.2636 | 7.8003 | 7.7248 | 7.1819 | 6.9585 | 6.7768 | 6.2462 | 5.8391 | 4.8299 | 3.5126 | 3.035
|  | CUMMING STREET | FB |  |  |  |  | 8.0937 | 7.9967 | 7.9692 | 7.6039 | 7.6039 | 7.2182 | 7.16 | 7.0712 | 6.96 | 6.9018 | 6.459 | 5.6325 | 4.4743 | 8.1314 | 7.9641 | 7.9427 | 7.608 | 7.6049 | 7.2253 | 7.1263 | 6.9998 | 6.8518 | 6.758 | 6.1161 | 5.0804 | 3.9376 | 8.5034 | 8.3993 | 8.383 | 8.0126 | 8.0075 | 7.6166 | 7.5626 | 7.4717 | 7.3656 | 7.3034 | 6.6054 | 4.9248 | 3.7707
| ST FILLANS | DALCHONZIE | MINIMUM HEADROOM | NN 74079 21921 | YES | YES | 0.652 | 4.568 | 4.3843 | 4.3292 | 4.1108 | 3.8343 | 3.5404 | 3.218 | 2.8578 | 2.5373 | 2.3292 | 1.2057 | 0.47102 | -0.0065306 | 5.1739 | 5.0147 | 4.9902 | 4.8137 | 4.5443 | 4.3178 | 4.0708 | 3.7698 | 3.5137 | 3.3555 | 2.5147 | 2.1422 | 1.8943 | 5.2031 | 5.0194 | 4.9714 | 4.749 | 4.4684 | 4.2255 | 3.9357 | 3.6 | 3.3082 | 3.1173 | 2.1071 | 1.5143 | 1.1367
|  | DALCHONZIE | EE |  |  |  |  | 4.569 | 4.3873 | 4.3547 | 4.1578 | 3.8782 | 3.6057 | 3.2435 | 2.8976 | 2.5537 | 2.3435 | 1.2057 | 0.47102 | -0.0065306 | 5.1739 | 5.0157 | 4.9994 | 4.832 | 4.5586 | 4.3545 | 4.0708 | 3.8035 | 3.5392 | 3.3871 | 2.5147 | 2.1422 | 1.8943 | 5.2051 | 5.0214 | 4.9918 | 4.7837 | 4.5031 | 4.2786 | 3.95 | 3.6367 | 3.3265 | 3.1398 | 2.1071 | 1.5143 | 1.1367
|  | DALCHONZIE | HT |  |  |  |  | 4.568 | 4.3843 | 4.3292 | 4.1108 | 3.8343 | 3.5516 | 3.218 | 2.8578 | 2.5394 | 2.3292 | 1.2659 | 0.49959 | 0.23122 | 5.1739 | 5.0147 | 4.9902 | 4.8137 | 4.5443 | 4.3351 | 4.0729 | 3.7698 | 3.5137 | 3.3555 | 2.5188 | 2.1453 | 2.1729 | 5.2031 | 5.0194 | 4.9714 | 4.749 | 4.4684 | 4.2388 | 3.9357 | 3.6 | 3.3082 | 3.1173 | 2.149 | 1.5327 | 1.3765
|  | DALCHONZIE | HE |  |  |  |  | 4.57 | 4.3863 | 4.3455 | 4.1312 | 3.8486 | 3.5404 | 3.2282 | 2.8853 | 2.5373 | 2.3669 | 1.6894 | 0.9598 | 0.84347 | 5.1739 | 5.0167 | 4.9973 | 4.8229 | 4.5535 | 4.3178 | 4.0922 | 3.828 | 3.5586 | 3.4494 | 2.9718 | 2.5831 | 2.6412 | 5.2051 | 5.0214 | 4.9847 | 4.7643 | 4.4796 | 4.2255 | 3.948 | 3.6388 | 3.3255 | 3.1776 | 2.5765 | 1.9796 | 1.9347
|  | DALCHONZIE | FB |  |  |  |  | 4.6312 | 4.6271 | 4.6078 | 4.2924 | 4.1955 | 4.1792 | 4.1435 | 3.92 | 3.7945 | 3.6731 | 3.0741 | 2.3476 | 1.9271 | 5.2137 | 5.2014 | 5.1892 | 4.9055 | 4.8106 | 4.7922 | 4.7382 | 4.5198 | 4.4076 | 4.2851 | 3.7341 | 3.0453 | 2.6014 | 5.2582 | 5.248 | 5.2306 | 4.9092 | 4.8082 | 4.7908 | 4.7367 | 4.5153 | 4.3949 | 4.2704 | 3.7214 | 2.9755 | 2.6265
| NAIRN | DALCROSS | MINIMUM HEADROOM | NH 76333 51847 | NO | YES | 3.269 | 9.0818 | 8.9267 | 8.691 | 8.4165 | 8.3982 | 7.241 | 6.0951 | 5.0441 | 4.3624 | 3.8737 | 2.7084 | 2.5247 | 2.4573 | 9.5604 | 9.5094 | 9.4624 | 9.3971 | 9.3808 | 8.6308 | 7.642 | 6.7522 | 6.3349 | 6.2104 | 5.9145 | 5.9002 | 5.9155 | 9.1681 | 9.0568 | 8.9313 | 8.7619 | 8.7344 | 7.8313 | 6.767 | 5.814 | 5.2834 | 4.9977 | 4.3048 | 4.1772 | 4.1477
|  | DALCROSS | EE |  |  |  |  | 9.0818 | 8.9298 | 8.691 | 8.4165 | 8.3992 | 8.0706 | 7.4716 | 6.5635 | 5.3727 | 4.4716 | 2.7084 | 2.5247 | 2.4573 | 9.5624 | 9.5094 | 9.4624 | 9.3982 | 9.3818 | 9.2522 | 8.9512 | 8.3961 | 7.4859 | 6.59 | 5.9267 | 5.9002 | 5.9155 | 9.1691 | 9.0579 | 8.9313 | 8.7619 | 8.7344 | 8.5538 | 8.0793 | 7.3721 | 6.3691 | 5.4905 | 4.3048 | 4.1772 | 4.1477
|  | DALCROSS | HT |  |  |  |  | 9.0818 | 8.9278 | 8.692 | 8.4165 | 8.3982 | 7.241 | 6.0951 | 5.0441 | 4.3624 | 3.8737 | 2.7624 | 2.6482 | 2.538 | 9.5604 | 9.5094 | 9.4624 | 9.3971 | 9.3808 | 8.6308 | 7.642 | 6.7522 | 6.3349 | 6.2104 | 5.9145 | 5.9247 | 5.9502 | 9.1681 | 9.0568 | 8.9323 | 8.7619 | 8.7344 | 7.8313 | 6.767 | 5.814 | 5.2834 | 4.9977 | 4.3405 | 4.2538 | 4.1752
|  | DALCROSS | HE |  |  |  |  | 9.0818 | 8.9267 | 8.691 | 8.4227 | 8.4063 | 7.8788 | 7.3573 | 6.4278 | 5.1492 | 4.2053 | 2.8257 | 2.7135 | 2.6298 | 9.5604 | 9.5094 | 9.4624 | 9.3982 | 9.3818 | 9.189 | 8.9278 | 8.3461 | 7.2931 | 6.3278 | 5.9676 | 5.9747 | 5.9737 | 9.1681 | 9.0568 | 8.9323 | 8.764 | 8.7385 | 8.4293 | 8.0048 | 7.2834 | 6.1619 | 5.214 | 4.3732 | 4.2936 | 4.2374
|  | DALCROSS | FB |  |  |  |  | 9.1573 | 9.0604 | 8.8869 | 8.6951 | 8.6869 | 8.6645 | 8.2563 | 7.8951 | 7.2135 | 6.6461 | 4.1461 | 3.9931 | 3.6451 | 9.5869 | 9.5553 | 9.5084 | 9.4624 | 9.4533 | 9.438 | 9.342 | 9.2461 | 8.7033 | 8.0104 | 6.2573 | 6.1522 | 6.0145 | 9.215 | 9.1538 | 9.0538 | 8.9364 | 8.9232 | 8.9048 | 8.663 | 8.4507 | 7.8436 | 7.1997 | 5.1058 | 4.9772 | 4.8436
| TAYNUILT | DALMALLY | MINIMUM HEADROOM | NN 15538 26930 | YES | YES | 0.011 | 0.8949 | 0.88469 | 0.88265 | 0.87449 | 0.86327 | 0.84796 | 0.83367 | 0.81224 | 0.80306 | 0.79184 | 0.7602 | 0.73673 | 0.7398 | 0.93673 | 0.92653 | 0.92755 | 0.92347 | 0.91837 | 0.91224 | 0.90204 | 0.88571 | 0.88469 | 0.87143 | 0.84286 | 0.84388 | 0.85306 | 0.91837 | 0.90714 | 0.90612 | 0.89796 | 0.89082 | 0.87857 | 0.86633 | 0.85 | 0.84286 | 0.83163 | 0.80408 | 0.78878 | 0.77959
|  | DALMALLY | EE |  |  |  |  | 0.8949 | 0.88469 | 0.88367 | 0.87551 | 0.86531 | 0.85102 | 0.83367 | 0.81224 | 0.80306 | 0.79184 | 0.7602 | 0.7551 | 0.74388 | 0.93673 | 0.92653 | 0.92755 | 0.92347 | 0.92041 | 0.91224 | 0.90204 | 0.88571 | 0.88469 | 0.87143 | 0.84796 | 0.85204 | 0.86224 | 0.91939 | 0.90714 | 0.90714 | 0.89898 | 0.89388 | 0.88163 | 0.86633 | 0.85 | 0.84286 | 0.83163 | 0.80408 | 0.78878 | 0.78469
|  | DALMALLY | HT |  |  |  |  | 0.8949 | 0.88469 | 0.88469 | 0.87755 | 0.86837 | 0.8551 | 0.8398 | 0.81939 | 0.81122 | 0.79898 | 0.76837 | 0.7398 | 0.74184 | 0.93673 | 0.92653 | 0.92755 | 0.92347 | 0.91837 | 0.91224 | 0.90306 | 0.88571 | 0.88469 | 0.87143 | 0.84286 | 0.84388 | 0.85612 | 0.91939 | 0.90816 | 0.90714 | 0.90102 | 0.89286 | 0.88265 | 0.87143 | 0.8551 | 0.84796 | 0.83673 | 0.81122 | 0.79388 | 0.77959
|  | DALMALLY | HE |  |  |  |  | 0.8949 | 0.88469 | 0.88265 | 0.87449 | 0.86327 | 0.84796 | 0.83469 | 0.81327 | 0.80612 | 0.79388 | 0.76939 | 0.73673 | 0.7398 | 0.93673 | 0.92653 | 0.92755 | 0.92347 | 0.91837 | 0.91224 | 0.90204 | 0.88571 | 0.88469 | 0.87143 | 0.84796 | 0.84796 | 0.85306 | 0.91837 | 0.90816 | 0.90612 | 0.89796 | 0.89082 | 0.87857 | 0.86735 | 0.85102 | 0.8449 | 0.83367 | 0.81122 | 0.79082 | 0.77959
|  | DALMALLY | FB |  |  |  |  | 0.90612 | 0.90408 | 0.9 | 0.89286 | 0.8949 | 0.89082 | 0.88776 | 0.88061 | 0.87653 | 0.87449 | 0.85306 | 0.82653 | 0.82143 | 0.94592 | 0.94184 | 0.93878 | 0.93469 | 0.93776 | 0.93061 | 0.92959 | 0.92041 | 0.91735 | 0.91224 | 0.8898 | 0.86633 | 0.85408 | 0.92857 | 0.92551 | 0.92245 | 0.91429 | 0.91735 | 0.91327 | 0.91122 | 0.90408 | 0.90102 | 0.89592 | 0.87755 | 0.85306 | 0.85102
| TAYNUILT | DALMALLY SCHOOL | MINIMUM HEADROOM | NN 17249 27128 | YES | YES | 0 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137
|  | DALMALLY SCHOOL | EE |  |  |  |  | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137
|  | DALMALLY SCHOOL | HT |  |  |  |  | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137
|  | DALMALLY SCHOOL | HE |  |  |  |  | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137
|  | DALMALLY SCHOOL | FB |  |  |  |  | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.065578 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.14393 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137 | 0.12137
| INVERNESS | DALNEIGH | MINIMUM HEADROOM | NH 65564 44955 | YES | NO | 2.494 | 4.3932 | 4.3993 | 4.3218 | 4.1799 | 4.132 | 2.7585 | 1.5085 | 0.41461 | -0.39661 | -0.94253 | -3.5691 | -5.8384 | -7.1925 | 5.9356 | 5.954 | 5.9305 | 5.8754 | 5.9275 | 4.9132 | 4.0285 | 3.2632 | 2.7816 | 2.5224 | 1.4724 | 0.804 | -0.19702 | 5.242 | 5.2379 | 5.1593 | 5.0277 | 4.9522 | 3.6787 | 2.5062 | 1.5032 | 0.85624 | 0.45114 | -1.705 | -3.4152 | -4.3887
|  | DALNEIGH | EE |  |  |  |  | 4.3932 | 4.3993 | 4.3218 | 4.1799 | 4.135 | 3.4942 | 2.8809 | 1.5952 | 0.2942 | -0.73641 | -3.5691 | -5.8384 | -7.1925 | 5.9356 | 5.956 | 5.9305 | 5.8764 | 5.9295 | 5.5918 | 5.2775 | 4.3418 | 3.4295 | 2.7224 | 1.4928 | 0.804 | 0.2142 | 5.242 | 5.2379 | 5.1593 | 5.0277 | 4.9522 | 4.342 | 3.8175 | 2.6726 | 1.5287 | 0.64094 | -1.705 | -3.4152 | -4.3887
|  | DALNEIGH | HT |  |  |  |  | 4.3962 | 4.4044 | 4.333 | 4.186 | 4.132 | 2.7585 | 1.5085 | 0.41461 | -0.39661 | -0.94253 | -3.4721 | -5.4966 | -6.6925 | 5.9356 | 5.954 | 5.9305 | 5.8754 | 5.9275 | 4.9132 | 4.0285 | 3.2632 | 2.7816 | 2.5224 | 1.4724 | 1.1295 | 1.056 | 5.2481 | 5.2471 | 5.1746 | 5.0369 | 4.9644 | 3.6787 | 2.5062 | 1.5032 | 0.85624 | 0.45114 | -1.658 | -3.1233 | -3.9356
|  | DALNEIGH | HE |  |  |  |  | 4.3993 | 4.4095 | 4.3411 | 4.2003 | 4.1575 | 3.6013 | 2.9922 | 1.6503 | 0.30747 | -0.64457 | -2.7007 | -4.4772 | -5.5201 | 5.9367 | 5.9591 | 5.9377 | 5.8836 | 5.9387 | 5.603 | 5.2969 | 4.2805 | 3.304 | 2.6469 | 1.7428 | 1.2673 | 0.704 | 5.246 | 5.246 | 5.1736 | 5.0409 | 4.9542 | 4.393 | 3.8807 | 2.6858 | 1.5001 | 0.64502 | -1.0295 | -2.2958 | -3.056
|  | DALNEIGH | FB |  |  |  |  | 4.5218 | 4.5871 | 4.5707 | 4.586 | 4.6003 | 4.5564 | 4.5126 | 4.4044 | 3.6524 | 3.0085 | 1.1779 | -0.2558 | -1.3487 | 6.0438 | 6.0826 | 6.0805 | 6.0877 | 6.0836 | 6.0101 | 5.9785 | 5.855 | 5.1785 | 4.5601 | 2.856 | 1.3907 | -0.19702 | 5.3828 | 5.4226 | 5.4103 | 5.4011 | 5.3756 | 5.3195 | 5.2471 | 5.1358 | 4.3379 | 3.6471 | 1.8369 | 0.77767 | -0.14478
| COUPAR ANGUS | DALRULZION | MINIMUM HEADROOM | NO 13498 58153 | NO | NO | 0.069 | 0.87551 | 0.87653 | 0.88163 | 0.86224 | 0.82347 | 0.54388 | 0.4051 | 0.31633 | 0.24592 | 0.068367 | -0.26327 | -0.2398 | -0.19184 | 1.3673 | 1.351 | 1.3439 | 1.3204 | 1.2684 | 0.97041 | 0.82857 | 0.72755 | 0.65612 | 0.48163 | 0.14184 | 0.17347 | 0.23776 | 1.0633 | 1.049 | 1.0378 | 1.0173 | 0.98776 | 0.69082 | 0.54898 | 0.44694 | 0.37653 | 0.20102 | -0.13061 | -0.11122 | -0.041837
|  | DALRULZION | EE |  |  |  |  | 0.87551 | 0.87653 | 0.88163 | 0.86531 | 0.82347 | 0.60102 | 0.56122 | 0.31633 | 0.25612 | 0.15612 | -0.17143 | -0.15204 | -0.15918 | 1.3673 | 1.351 | 1.3439 | 1.3204 | 1.2684 | 1.0316 | 0.98367 | 0.72755 | 0.66939 | 0.57347 | 0.23265 | 0.26633 | 0.26837 | 1.0633 | 1.049 | 1.0388 | 1.0184 | 0.98776 | 0.74898 | 0.70306 | 0.44694 | 0.38673 | 0.2898 | -0.044898 | -0.019388 | -0.022449
|  | DALRULZION | HT |  |  |  |  | 0.87653 | 0.87755 | 0.88265 | 0.86429 | 0.82551 | 0.54388 | 0.4051 | 0.31939 | 0.24592 | 0.068367 | -0.26327 | -0.2398 | -0.19184 | 1.3684 | 1.351 | 1.3449 | 1.3204 | 1.2694 | 0.97041 | 0.82857 | 0.72959 | 0.65612 | 0.48163 | 0.14184 | 0.17347 | 0.23776 | 1.0633 | 1.05 | 1.0388 | 1.0184 | 0.98878 | 0.69082 | 0.54898 | 0.45 | 0.37653 | 0.20102 | -0.13061 | -0.11122 | -0.041837
|  | DALRULZION | HE |  |  |  |  | 0.87653 | 0.87653 | 0.88163 | 0.86224 | 0.82347 | 0.76735 | 0.72857 | 0.48163 | 0.43469 | 0.36735 | 0.23367 | 0.23673 | 0.17857 | 1.3684 | 1.351 | 1.3439 | 1.3204 | 1.2694 | 1.2041 | 1.1571 | 0.89592 | 0.85 | 0.78469 | 0.64388 | 0.65102 | 0.60102 | 1.0633 | 1.05 | 1.0378 | 1.0173 | 0.98776 | 0.92143 | 0.87551 | 0.61429 | 0.56735 | 0.50102 | 0.36837 | 0.36633 | 0.31224
|  | DALRULZION | FB |  |  |  |  | 0.90204 | 0.92653 | 0.93469 | 0.9398 | 0.91429 | 0.88776 | 0.87551 | 0.84694 | 0.81429 | 0.80612 | 0.69184 | 0.5449 | 0.11122 | 1.3929 | 1.401 | 1.3959 | 1.398 | 1.3663 | 1.3296 | 1.3112 | 1.2684 | 1.2235 | 1.2092 | 1.0582 | 0.9102 | 0.46633 | 1.0867 | 1.0908 | 1.0878 | 1.0878 | 1.0724 | 1.0469 | 1.0347 | 1.0061 | 0.96633 | 0.9551 | 0.81327 | 0.64592 | 0.23469
| BOAT OF GARTEN | DALWHINNIE | MINIMUM HEADROOM | NN 63711 84671 | YES | YES | 0.061 | 0.27857 | 0.27551 | 0.27245 | 0.25306 | 0.23776 | 0.2102 | 0.18061 | 0.15918 | 0.12755 | 0.12245 | 0.071429 | 0.0061224 | -0.05102 | 0.43163 | 0.42857 | 0.42449 | 0.41327 | 0.4102 | 0.39796 | 0.37551 | 0.36837 | 0.34694 | 0.33878 | 0.3051 | 0.30306 | 0.2898 | 0.29694 | 0.29694 | 0.29184 | 0.28061 | 0.27143 | 0.25102 | 0.22041 | 0.20612 | 0.17653 | 0.16327 | 0.11735 | 0.10306 | 0.072449
|  | DALWHINNIE | EE |  |  |  |  | 0.27959 | 0.27653 | 0.27245 | 0.25612 | 0.2449 | 0.21429 | 0.18878 | 0.16735 | 0.14592 | 0.12245 | 0.071429 | 0.0061224 | -0.05102 | 0.43265 | 0.42959 | 0.42449 | 0.41327 | 0.4102 | 0.39796 | 0.37551 | 0.36837 | 0.35714 | 0.34184 | 0.30918 | 0.30714 | 0.29694 | 0.3 | 0.29796 | 0.2949 | 0.28061 | 0.27551 | 0.25102 | 0.22245 | 0.20918 | 0.19286 | 0.17245 | 0.11735 | 0.10408 | 0.072449
|  | DALWHINNIE | HT |  |  |  |  | 0.27959 | 0.27653 | 0.27245 | 0.25612 | 0.2449 | 0.22245 | 0.19388 | 0.17347 | 0.15408 | 0.13061 | 0.096939 | 0.022449 | -0.044898 | 0.43265 | 0.42959 | 0.42449 | 0.41327 | 0.4102 | 0.39898 | 0.37551 | 0.36837 | 0.35816 | 0.34184 | 0.3051 | 0.30714 | 0.31531 | 0.3 | 0.29796 | 0.2949 | 0.28061 | 0.27551 | 0.25612 | 0.22755 | 0.21327 | 0.19796 | 0.17449 | 0.12857 | 0.11122 | 0.083673
|  | DALWHINNIE | HE |  |  |  |  | 0.27857 | 0.27551 | 0.27245 | 0.25306 | 0.23776 | 0.2102 | 0.18061 | 0.15918 | 0.12755 | 0.13265 | 0.087755 | 0.016327 | -0.031633 | 0.43163 | 0.42857 | 0.42449 | 0.41531 | 0.41122 | 0.4 | 0.37653 | 0.36939 | 0.34694 | 0.33878 | 0.31224 | 0.30306 | 0.29388 | 0.29694 | 0.29694 | 0.29184 | 0.28061 | 0.27143 | 0.25102 | 0.22041 | 0.20612 | 0.17653 | 0.16327 | 0.12347 | 0.10306 | 0.077551
|  | DALWHINNIE | FB |  |  |  |  | 0.29694 | 0.29286 | 0.29184 | 0.2898 | 0.28469 | 0.28163 | 0.26939 | 0.26327 | 0.25918 | 0.25102 | 0.20612 | 0.15204 | 0.13776 | 0.45204 | 0.44286 | 0.44184 | 0.43776 | 0.43673 | 0.43061 | 0.42041 | 0.41633 | 0.40918 | 0.39694 | 0.36735 | 0.31429 | 0.2898 | 0.32143 | 0.31429 | 0.31429 | 0.31327 | 0.31122 | 0.30612 | 0.29592 | 0.29082 | 0.28469 | 0.27449 | 0.23878 | 0.17857 | 0.17245
| WILLOWDALE | DENBURN | MINIMUM HEADROOM | NJ 93484 06342 | NO | NO | 0.775 | 8.0647 | 8.0728 | 8.0432 | 7.9738 | 7.8891 | 7.7718 | 7.6289 | 7.4912 | 7.4024 | 7.2575 | 5.6391 | 4.2269 | 3.5218 | 10.5473 | 10.5514 | 10.5167 | 10.4657 | 10.3942 | 10.2381 | 10.0626 | 9.7391 | 9.5942 | 9.3524 | 7.6993 | 5.9636 | 3.2096 | 9.3427 | 9.3468 | 9.305 | 9.2427 | 9.0315 | 8.6692 | 8.3948 | 7.9131 | 7.6968 | 7.4029 | 5.7529 | 4.9009 | 4.7162
|  | DENBURN | EE |  |  |  |  | 8.0687 | 8.081 | 8.0544 | 7.9871 | 7.8973 | 7.7891 | 7.6565 | 7.5218 | 7.4524 | 7.28 | 5.6391 | 4.2269 | 3.5218 | 10.5483 | 10.5534 | 10.5208 | 10.4708 | 10.3942 | 10.2963 | 10.0728 | 9.7596 | 9.7034 | 9.3575 | 7.6993 | 6.5034 | 5.5728 | 9.3458 | 9.3529 | 9.3141 | 9.2539 | 9.0478 | 8.7672 | 8.4284 | 7.9754 | 7.8988 | 7.4519 | 5.9121 | 5.1019 | 4.7774
|  | DENBURN | HT |  |  |  |  | 8.0749 | 8.0953 | 8.0749 | 8.0157 | 7.931 | 7.7871 | 7.6606 | 7.532 | 7.4024 | 7.2575 | 5.8014 | 4.5993 | 4.3177 | 10.5483 | 10.5534 | 10.5208 | 10.4718 | 10.3942 | 10.2381 | 10.0626 | 9.8187 | 9.5942 | 9.4238 | 8.0677 | 7.4014 | 7.2351 | 9.3509 | 9.3652 | 9.3335 | 9.2764 | 9.0682 | 8.6692 | 8.4009 | 8.0233 | 7.6968 | 7.4754 | 5.7529 | 4.9009 | 4.7162
|  | DENBURN | HE |  |  |  |  | 8.0647 | 8.0728 | 8.0432 | 7.9738 | 7.8891 | 7.7718 | 7.6289 | 7.4912 | 7.4198 | 7.2596 | 6.2871 | 5.2983 | 4.8208 | 10.5473 | 10.5514 | 10.5167 | 10.4657 | 10.3953 | 10.2953 | 10.0677 | 9.7391 | 9.6759 | 9.3524 | 8.0463 | 7.0014 | 6.2402 | 9.3427 | 9.3468 | 9.305 | 9.2427 | 9.0315 | 8.7519 | 8.3948 | 7.9131 | 7.8254 | 7.4029 | 6.0927 | 5.406 | 5.1958
|  | DENBURN | FB |  |  |  |  | 8.1238 | 8.1616 | 8.2055 | 8.1902 | 8.1708 | 8.1422 | 8.0912 | 8.0157 | 7.9391 | 7.8575 | 7.5473 | 6.4606 | 5.1493 | 10.5687 | 10.5728 | 10.5851 | 10.5606 | 10.5187 | 10.4106 | 10.2442 | 10.0014 | 9.7891 | 9.5708 | 8.4861 | 5.9636 | 3.2096 | 9.3999 | 9.4264 | 9.4641 | 9.4478 | 9.4213 | 9.4019 | 9.358 | 9.1458 | 8.9448 | 8.7601 | 7.908 | 6.2213 | 5.5988
| TAYNUILT | DERVAIG | MINIMUM HEADROOM | NM 42441 51227 | YES | YES | 0.547 | 1.42 | 1.4016 | 1.3955 | 1.3557 | 1.1118 | 0.85776 | 0.63122 | 0.35673 | 0.16184 | 0.081224 | -0.69224 | -1.1218 | -1.2973 | 1.8906 | 1.8641 | 1.8671 | 1.8467 | 1.609 | 1.4447 | 1.2814 | 1.0957 | 0.94061 | 0.87122 | 0.19163 | 0.0028571 | 0.030408 | 1.442 | 1.4339 | 1.4237 | 1.3676 | 1.2186 | 1.0186 | 0.79816 | 0.5349 | 0.32776 | 0.26449 | -0.48857 | -0.82633 | -0.9202
|  | DERVAIG | EE |  |  |  |  | 1.42 | 1.4343 | 1.3955 | 1.3557 | 1.1169 | 0.87102 | 0.63122 | 0.35673 | 0.16184 | 0.081224 | -0.69224 | -1.1218 | -1.2973 | 1.8906 | 1.8978 | 1.8671 | 1.8508 | 1.609 | 1.4518 | 1.2896 | 1.0998 | 0.97122 | 0.91918 | 0.25388 | 0.030408 | 0.030408 | 1.442 | 1.4553 | 1.4237 | 1.3676 | 1.2227 | 1.0267 | 0.80122 | 0.5349 | 0.3298 | 0.27571 | -0.48347 | -0.82327 | -0.9202
|  | DERVAIG | HT |  |  |  |  | 1.421 | 1.4016 | 1.4067 | 1.3731 | 1.1353 | 0.9251 | 0.6802 | 0.42306 | 0.20367 | 0.10265 | -0.61265 | -1.0606 | -1.2586 | 1.8916 | 1.8641 | 1.8692 | 1.8498 | 1.612 | 1.4743 | 1.2865 | 1.0957 | 0.94061 | 0.87122 | 0.19163 | 0.0028571 | 0.074286 | 1.442 | 1.4339 | 1.4349 | 1.3829 | 1.2369 | 1.0635 | 0.81857 | 0.55735 | 0.33082 | 0.26449 | -0.48857 | -0.82633 | -0.90898
|  | DERVAIG | HE |  |  |  |  | 1.422 | 1.4373 | 1.3996 | 1.3567 | 1.1118 | 0.85776 | 0.63633 | 0.39653 | 0.17306 | 0.13429 | -0.4351 | -0.67184 | -0.80755 | 1.8927 | 1.8978 | 1.8682 | 1.8467 | 1.609 | 1.4447 | 1.2814 | 1.1202 | 0.95592 | 0.95286 | 0.44265 | 0.48857 | 0.49878 | 1.442 | 1.4563 | 1.4278 | 1.3686 | 1.2186 | 1.0186 | 0.79816 | 0.56551 | 0.32776 | 0.32163 | -0.27939 | -0.38755 | -0.44265
|  | DERVAIG | FB |  |  |  |  | 1.4516 | 1.4955 | 1.5333 | 1.5118 | 1.5261 | 1.3833 | 1.3843 | 1.3802 | 1.2731 | 1.2322 | 0.91388 | 0.27408 | -0.1198 | 1.9345 | 1.959 | 1.9794 | 1.9549 | 1.9682 | 1.7294 | 1.7243 | 1.6937 | 1.5794 | 1.5243 | 1.2131 | 0.59163 | 0.15592 | 1.4686 | 1.5104 | 1.542 | 1.5318 | 1.54 | 1.4094 | 1.4114 | 1.3849 | 1.24 | 1.1686 | 0.82878 | 0.17878 | -0.18755
| BEAULY | DINGWALL | MINIMUM HEADROOM | NH 53956 59680 | NO | NO | 2.115 | 3.9986 | 3.9812 | 3.8465 | 3.6047 | 3.4312 | 2.472 | 1.6139 | 0.79652 | 0.15979 | -0.16776 | -1.68 | -3.0678 | -4.0872 | 7.2139 | 7.1924 | 7.0506 | 7.0271 | 6.7873 | 6.2822 | 5.6649 | 5.1139 | 4.6812 | 4.4384 | 3.5975 | 3.2659 | 2.7628 | 5.0378 | 5.0215 | 4.9491 | 4.7889 | 4.6287 | 3.743 | 2.9583 | 2.2093 | 1.6378 | 1.3491 | 0.14601 | -0.84787 | -1.4826
|  | DINGWALL | EE |  |  |  |  | 4.0006 | 3.9833 | 3.8506 | 3.6077 | 3.4322 | 3.0373 | 2.4271 | 1.6006 | 0.75877 | 0.027135 | -1.68 | -3.0678 | -4.0137 | 7.2139 | 7.1924 | 7.1414 | 7.0608 | 6.7873 | 6.6475 | 6.3608 | 5.7914 | 5.1741 | 4.6037 | 3.621 | 3.2659 | 2.9659 | 5.0399 | 5.0225 | 4.9542 | 4.7909 | 4.6287 | 4.2378 | 3.7644 | 3.0195 | 2.2532 | 1.5623 | 0.14601 | -0.84787 | -1.4826
|  | DINGWALL | HT |  |  |  |  | 3.9986 | 3.9822 | 3.8465 | 3.6047 | 3.4312 | 2.472 | 1.6139 | 0.79652 | 0.15979 | -0.16776 | -1.5137 | -2.9453 | -4.0872 | 7.2139 | 7.1924 | 7.1404 | 7.0598 | 6.7873 | 6.2822 | 5.6649 | 5.1139 | 4.6812 | 4.4384 | 3.5975 | 3.2884 | 3.1363 | 5.0378 | 5.0215 | 4.9491 | 4.7889 | 4.6287 | 3.743 | 2.9583 | 2.2093 | 1.6378 | 1.3491 | 0.23887 | -0.72848 | -1.4489
|  | DINGWALL | HE |  |  |  |  | 4.0006 | 3.9812 | 3.8475 | 3.6077 | 3.4353 | 2.968 | 2.4618 | 1.5986 | 0.74856 | -0.014702 | -1.2086 | -2.4739 | -3.2147 | 7.2139 | 7.1924 | 7.1404 | 7.0598 | 6.7873 | 6.6118 | 6.371 | 5.7404 | 5.1088 | 4.5343 | 3.8567 | 3.6404 | 3.3588 | 5.0389 | 5.0215 | 4.9501 | 4.7909 | 4.6317 | 4.1909 | 3.7899 | 2.997 | 2.2093 | 1.4848 | 0.53785 | -0.2846 | -0.78256
|  | DINGWALL | FB |  |  |  |  | 4.0822 | 4.1149 | 3.9884 | 3.8955 | 3.9016 | 3.8618 | 3.6669 | 3.5292 | 3.1516 | 2.7394 | 1.4465 | 0.4455 | -0.1096 | 7.2955 | 7.319 | 7.0506 | 7.0271 | 7.0282 | 6.9731 | 6.8241 | 6.7833 | 6.4516 | 6.0251 | 4.7159 | 3.6373 | 2.7628 | 5.1236 | 5.1674 | 5.044 | 5.0011 | 5.0205 | 4.997 | 4.8552 | 4.7358 | 4.3491 | 3.9123 | 2.5552 | 1.5889 | 1.2093
| CARRADALE 1 | DIPPEN | MINIMUM HEADROOM | NR 80026 37592 | YES | YES | 0.023 | 0.55408 | 0.55408 | 0.54388 | 0.52041 | 0.5051 | 0.45714 | 0.44184 | 0.39796 | 0.35612 | 0.32959 | 0.24184 | 0.17143 | 0.11939 | 0.64286 | 0.64286 | 0.64082 | 0.63367 | 0.63061 | 0.61633 | 0.60408 | 0.58163 | 0.56633 | 0.54796 | 0.50306 | 0.48571 | 0.43265 | 0.61633 | 0.61633 | 0.60918 | 0.58673 | 0.57347 | 0.53776 | 0.5051 | 0.47041 | 0.45204 | 0.45 | 0.38469 | 0.33673 | 0.30102
|  | DIPPEN | EE |  |  |  |  | 0.55408 | 0.55612 | 0.54592 | 0.52245 | 0.51224 | 0.47245 | 0.45816 | 0.41429 | 0.38061 | 0.3551 | 0.24184 | 0.17143 | 0.11939 | 0.64286 | 0.64286 | 0.64082 | 0.63367 | 0.63367 | 0.62041 | 0.6102 | 0.58571 | 0.57449 | 0.55408 | 0.51327 | 0.5102 | 0.50204 | 0.61735 | 0.61633 | 0.6102 | 0.59082 | 0.57959 | 0.54286 | 0.51633 | 0.48265 | 0.45204 | 0.46429 | 0.38469 | 0.33673 | 0.30408
|  | DIPPEN | HT |  |  |  |  | 0.55714 | 0.55408 | 0.54388 | 0.52041 | 0.5051 | 0.45714 | 0.44184 | 0.40102 | 0.35612 | 0.32959 | 0.27041 | 0.19286 | 0.11939 | 0.64388 | 0.64388 | 0.64082 | 0.63571 | 0.63061 | 0.61633 | 0.60408 | 0.58469 | 0.56633 | 0.54796 | 0.50306 | 0.50408 | 0.51327 | 0.61633 | 0.61633 | 0.60918 | 0.58673 | 0.57347 | 0.53776 | 0.50612 | 0.47347 | 0.46735 | 0.45 | 0.39694 | 0.35408 | 0.30714
|  | DIPPEN | HE |  |  |  |  | 0.55918 | 0.5551 | 0.54694 | 0.52551 | 0.50918 | 0.46633 | 0.44388 | 0.39796 | 0.36327 | 0.33571 | 0.26122 | 0.17857 | 0.12551 | 0.6449 | 0.64286 | 0.64082 | 0.63776 | 0.63265 | 0.61939 | 0.60612 | 0.58163 | 0.57041 | 0.55102 | 0.51327 | 0.50306 | 0.48367 | 0.61939 | 0.61633 | 0.61122 | 0.59082 | 0.57653 | 0.54184 | 0.5051 | 0.47041 | 0.47143 | 0.45102 | 0.39388 | 0.33776 | 0.30102
|  | DIPPEN | FB |  |  |  |  | 0.57551 | 0.57653 | 0.57755 | 0.57857 | 0.57755 | 0.57449 | 0.56531 | 0.55408 | 0.54184 | 0.5449 | 0.46224 | 0.41224 | 0.39184 | 0.65204 | 0.65204 | 0.65204 | 0.65204 | 0.65204 | 0.64796 | 0.64286 | 0.63571 | 0.62653 | 0.62449 | 0.56122 | 0.48571 | 0.43265 | 0.63265 | 0.63163 | 0.63367 | 0.63367 | 0.63061 | 0.62653 | 0.62143 | 0.61531 | 0.60714 | 0.6051 | 0.5398 | 0.47041 | 0.46122
| BRORA | DORNOCH | MINIMUM HEADROOM | NH 79721 89953 | YES | NO | 1.416 | -0.0069306 | -0.037543 | -0.083461 | -0.13856 | -0.1906 | -0.56305 | -0.99367 | -1.3998 | -1.6151 | -1.6508 | -2.0477 | -2.4957 | -2.8641 | 1.129 | 1.1249 | 1.1127 | 1.0953 | 1.08 | 0.75144 | 0.3596 | -0.0046857 | -0.16999 | -0.16387 | -0.29856 | -0.2853 | -0.27816 | 0.6294 | 0.58144 | 0.55184 | 0.50287 | 0.46919 | 0.14878 | -0.26244 | -0.65632 | -0.8655 | -0.90734 | -1.2247 | -1.4818 | -1.7084
|  | DORNOCH | EE |  |  |  |  | -0.0059102 | -0.034482 | -0.082441 | -0.13346 | -0.1855 | -0.28856 | -0.43346 | -0.7804 | -1.2008 | -1.5335 | -2.0477 | -2.4957 | -2.8335 | 1.129 | 1.1259 | 1.1147 | 1.0974 | 1.082 | 1.0586 | 1.0076 | 0.66266 | 0.27491 | -0.03938 | -0.26591 | -0.26489 | -0.23938 | 0.63042 | 0.5845 | 0.55389 | 0.50695 | 0.47123 | 0.37736 | 0.25389 | -0.067543 | -0.46448 | -0.80122 | -1.2247 | -1.4818 | -1.6716
|  | DORNOCH | HT |  |  |  |  | -0.0069306 | -0.037543 | -0.083461 | -0.13856 | -0.1906 | -0.56305 | -0.99367 | -1.3998 | -1.6151 | -1.6386 | -1.9018 | -2.3988 | -2.8641 | 1.131 | 1.1249 | 1.1127 | 1.0974 | 1.08 | 0.75144 | 0.3596 | -0.0046857 | -0.16999 | -0.16387 | -0.29856 | -0.2853 | -0.26183 | 0.6294 | 0.58246 | 0.55184 | 0.50287 | 0.46919 | 0.14878 | -0.26244 | -0.65632 | -0.8655 | -0.90632 | -1.1645 | -1.4451 | -1.7084
|  | DORNOCH | HE |  |  |  |  | -0.0069306 | -0.037543 | -0.083461 | -0.1304 | -0.17938 | -0.2804 | -0.43244 | -0.81509 | -1.2712 | -1.6508 | -1.9263 | -2.4498 | -2.7875 | 1.131 | 1.1249 | 1.1127 | 1.0953 | 1.081 | 1.0596 | 1.0086 | 0.62899 | 0.20246 | -0.14346 | -0.25571 | -0.25571 | -0.25162 | 0.6294 | 0.58144 | 0.55184 | 0.51001 | 0.47736 | 0.3845 | 0.25593 | -0.095094 | -0.52979 | -0.90734 | -1.1533 | -1.4543 | -1.6512
|  | DORNOCH | FB |  |  |  |  | 0.036947 | 0.041029 | 0.026743 | 0.031845 | 0.030824 | 0.012457 | 0.0032735 | -0.024278 | -0.25285 | -0.53244 | -1.2335 | -1.4131 | -1.4824 | 1.1667 | 1.1657 | 1.1657 | 1.1688 | 1.1718 | 1.1596 | 1.1535 | 1.128 | 0.88919 | 0.59429 | -0.073053 | -0.1955 | -0.27816 | 0.70389 | 0.6794 | 0.65389 | 0.65797 | 0.65797 | 0.6447 | 0.63348 | 0.59266 | 0.40593 | 0.12736 | -0.56856 | -0.80122 | -0.83489
| CLACHAN | DOUGLAS PIER | MINIMUM HEADROOM | NS 19396 99616 | YES | YES | 0.196 | -0.026988 | -0.028008 | -0.036171 | -0.047396 | -0.062702 | -0.094335 | -0.13107 | -0.16168 | -0.18719 | -0.20862 | -0.30658 | -0.38617 | -0.4525 | 0.32709 | 0.32403 | 0.31791 | 0.31281 | 0.30056 | 0.29138 | 0.27709 | 0.25567 | 0.23526 | 0.22607 | 0.17709 | 0.15669 | 0.10669 | 0.13322 | 0.13118 | 0.11995 | 0.11281 | 0.099543 | 0.077094 | 0.048522 | 0.0097469 | -0.024947 | -0.045355 | -0.11474 | -0.15046 | -0.18617
|  | DOUGLAS PIER | EE |  |  |  |  | -0.026988 | -0.025967 | -0.036171 | -0.046376 | -0.060661 | -0.094335 | -0.13005 | -0.1474 | -0.18719 | -0.20658 | -0.30658 | -0.38617 | -0.4525 | 0.32709 | 0.32505 | 0.31791 | 0.31281 | 0.3026 | 0.29138 | 0.27709 | 0.25567 | 0.23526 | 0.22709 | 0.18322 | 0.18424 | 0.17199 | 0.13322 | 0.13322 | 0.11995 | 0.11281 | 0.10056 | 0.077094 | 0.048522 | 0.0097469 | -0.024947 | -0.039233 | -0.1025 | -0.14229 | -0.18005
|  | DOUGLAS PIER | HT |  |  |  |  | -0.024947 | -0.023927 | -0.03209 | -0.046376 | -0.059641 | -0.089233 | -0.12087 | -0.16168 | -0.17699 | -0.1974 | -0.28209 | -0.36474 | -0.44536 | 0.32709 | 0.32505 | 0.31893 | 0.31281 | 0.30158 | 0.29138 | 0.27811 | 0.25567 | 0.23628 | 0.22607 | 0.17709 | 0.17811 | 0.18628 | 0.13424 | 0.13526 | 0.12403 | 0.11281 | 0.10158 | 0.079135 | 0.052604 | 0.015869 | -0.016784 | -0.034131 | -0.11474 | -0.13413 | -0.16576
|  | DOUGLAS PIER | HE |  |  |  |  | -0.023927 | -0.028008 | -0.034131 | -0.047396 | -0.062702 | -0.094335 | -0.13107 | -0.1474 | -0.18719 | -0.20862 | -0.28311 | -0.37597 | -0.43413 | 0.32913 | 0.32403 | 0.31995 | 0.31383 | 0.30056 | 0.29138 | 0.27709 | 0.25669 | 0.23526 | 0.22607 | 0.18628 | 0.17811 | 0.15975 | 0.13526 | 0.13118 | 0.12199 | 0.11281 | 0.099543 | 0.077094 | 0.048522 | 0.0097469 | -0.024947 | -0.045355 | -0.1127 | -0.15046 | -0.18617
|  | DOUGLAS PIER | FB |  |  |  |  | -0.0014776 | -0.0045388 | -0.00045714 | -0.0045388 | -0.0096408 | -0.026988 | -0.040253 | -0.042294 | -0.059641 | -0.068824 | -0.14127 | -0.21066 | -0.23719 | 0.34036 | 0.3373 | 0.33628 | 0.33322 | 0.3322 | 0.31995 | 0.31179 | 0.30669 | 0.29444 | 0.2873 | 0.23934 | 0.15669 | 0.10669 | 0.15873 | 0.1526 | 0.1526 | 0.14954 | 0.14954 | 0.12811 | 0.11485 | 0.11077 | 0.094441 | 0.085257 | 0.01791 | -0.075967 | -0.086171
| ARDMORE | DRIMORE | MINIMUM HEADROOM | NF 77377 40049 | YES | YES | 0.058 | 1.402 | 1.4031 | 1.3918 | 1.3735 | 1.352 | 1.3133 | 1.2837 | 1.2265 | 1.1867 | 1.149 | 1.0286 | 0.93163 | 0.83673 | 1.7041 | 1.7082 | 1.6908 | 1.6735 | 1.6459 | 1.6306 | 1.6061 | 1.5694 | 1.5531 | 1.5184 | 1.4265 | 1.4408 | 1.448 | 1.5082 | 1.5122 | 1.5071 | 1.4918 | 1.4755 | 1.4408 | 1.4061 | 1.3673 | 1.3755 | 1.3571 | 1.2908 | 1.2194 | 1.1582
|  | DRIMORE | EE |  |  |  |  | 1.4031 | 1.4061 | 1.3918 | 1.3796 | 1.3551 | 1.3316 | 1.2837 | 1.2265 | 1.1888 | 1.152 | 1.0286 | 0.93163 | 0.84082 | 1.7051 | 1.7102 | 1.6908 | 1.6796 | 1.6459 | 1.6306 | 1.6061 | 1.5694 | 1.5531 | 1.5184 | 1.4265 | 1.449 | 1.4622 | 1.5082 | 1.5133 | 1.5071 | 1.4949 | 1.4765 | 1.4408 | 1.4092 | 1.3704 | 1.3786 | 1.3612 | 1.2908 | 1.2194 | 1.1653
|  | DRIMORE | HT |  |  |  |  | 1.4031 | 1.4061 | 1.3929 | 1.3806 | 1.3582 | 1.3133 | 1.2908 | 1.2357 | 1.1959 | 1.1633 | 1.0929 | 0.96531 | 0.83673 | 1.7051 | 1.7102 | 1.6908 | 1.6796 | 1.6459 | 1.6306 | 1.6061 | 1.5694 | 1.5551 | 1.5204 | 1.4459 | 1.4408 | 1.449 | 1.5082 | 1.5133 | 1.5082 | 1.4959 | 1.4796 | 1.448 | 1.4153 | 1.3786 | 1.3857 | 1.3684 | 1.3367 | 1.248 | 1.1653
|  | DRIMORE | HE |  |  |  |  | 1.402 | 1.4031 | 1.3929 | 1.3735 | 1.352 | 1.3306 | 1.2837 | 1.2265 | 1.1867 | 1.149 | 1.0633 | 0.94898 | 0.86429 | 1.7041 | 1.7082 | 1.6918 | 1.6735 | 1.6469 | 1.6316 | 1.6071 | 1.5704 | 1.5551 | 1.5224 | 1.4296 | 1.4469 | 1.448 | 1.5082 | 1.5122 | 1.5082 | 1.4918 | 1.4755 | 1.4408 | 1.4061 | 1.3673 | 1.3755 | 1.3571 | 1.3173 | 1.2204 | 1.1582
|  | DRIMORE | FB |  |  |  |  | 1.4245 | 1.4327 | 1.4429 | 1.4449 | 1.4429 | 1.4408 | 1.4357 | 1.4224 | 1.4204 | 1.4122 | 1.3398 | 1.2571 | 1.251 | 1.7214 | 1.7255 | 1.7214 | 1.7133 | 1.6969 | 1.6898 | 1.6776 | 1.6571 | 1.6541 | 1.6408 | 1.5643 | 1.4541 | 1.4582 | 1.5194 | 1.5286 | 1.5378 | 1.5398 | 1.5388 | 1.5388 | 1.5357 | 1.5337 | 1.5347 | 1.5306 | 1.4929 | 1.4408 | 1.4327
| CEANNACROC | DRUMNADROCHIT | MINIMUM HEADROOM | NH 50306 29824 | YES | NO | 1.457 | 2.3258 | 2.2452 | 2.2166 | 2.1482 | 2.0748 | 1.6697 | 1.4023 | 1.1503 | 0.96762 | 0.85436 | 0.57579 | 0.26252 | -0.020131 | 3.4942 | 3.4768 | 3.4605 | 3.4493 | 3.4329 | 3.0972 | 2.8962 | 2.734 | 2.6411 | 2.5982 | 2.5421 | 2.5544 | 2.4962 | 3.0064 | 2.9431 | 2.9544 | 2.9227 | 2.8911 | 2.5472 | 2.3166 | 2.1227 | 1.9891 | 1.9135 | 1.7921 | 1.6023 | 1.3982
|  | DRUMNADROCHIT | EE |  |  |  |  | 2.3278 | 2.2503 | 2.2207 | 2.1513 | 2.0829 | 1.8584 | 1.7799 | 1.3819 | 1.0931 | 0.89416 | 0.57579 | 0.26252 | -0.020131 | 3.4942 | 3.4768 | 3.4605 | 3.4503 | 3.434 | 3.388 | 3.3574 | 3.0309 | 2.8033 | 2.6452 | 2.5635 | 2.5595 | 2.5442 | 3.0084 | 2.9482 | 2.9574 | 2.9248 | 2.8962 | 2.7503 | 2.6921 | 2.3574 | 2.1207 | 1.9595 | 1.7921 | 1.6023 | 1.3982
|  | DRUMNADROCHIT | HT |  |  |  |  | 2.3258 | 2.2452 | 2.2166 | 2.1482 | 2.0799 | 1.6697 | 1.4023 | 1.1503 | 0.96762 | 0.88803 | 0.68599 | 0.33293 | 0.0074204 | 3.4942 | 3.4768 | 3.4605 | 3.4493 | 3.434 | 3.0972 | 2.8962 | 2.734 | 2.6411 | 2.5982 | 2.5421 | 2.5544 | 2.586 | 3.0064 | 2.9431 | 2.9544 | 2.9227 | 2.8942 | 2.5472 | 2.3166 | 2.1227 | 1.9891 | 1.935 | 1.8503 | 1.6523 | 1.4411
|  | DRUMNADROCHIT | HE |  |  |  |  | 2.3258 | 2.2452 | 2.2166 | 2.1482 | 2.0748 | 1.887 | 1.7829 | 1.3554 | 1.0554 | 0.85436 | 0.68395 | 0.32783 | 0.10436 | 3.4942 | 3.4768 | 3.4605 | 3.4493 | 3.4329 | 3.3891 | 3.3564 | 2.9972 | 2.7625 | 2.6054 | 2.5656 | 2.5717 | 2.5595 | 3.0064 | 2.9442 | 2.9544 | 2.9227 | 2.8911 | 2.7686 | 2.6901 | 2.3258 | 2.0799 | 1.9135 | 1.8472 | 1.6288 | 1.4758
|  | DRUMNADROCHIT | FB |  |  |  |  | 2.388 | 2.3554 | 2.3595 | 2.3758 | 2.3686 | 2.337 | 2.3135 | 2.2982 | 2.0748 | 1.9176 | 1.5166 | 1.3401 | 1.2656 | 3.5197 | 3.5105 | 3.5115 | 3.5135 | 3.5105 | 3.4829 | 3.4625 | 3.4493 | 3.2013 | 3.036 | 2.6748 | 2.5717 | 2.4962 | 3.0666 | 3.0513 | 3.0625 | 3.0707 | 3.0758 | 3.0493 | 3.0278 | 3.036 | 2.8176 | 2.6768 | 2.3176 | 2.1829 | 2.1523
| GRUDIE BRIDGE | DRUMRUNIE | MINIMUM HEADROOM | NC 16664 05298 | YES | NO | 0 | 0.070694 | 0.063551 | 0.065592 | 0.058449 | 0.051306 | 0.036 | 0.024776 | 0.008449 | 0.0023265 | -0.010939 | -0.043592 | -0.072163 | -0.079306 | 0.10882 | 0.10269 | 0.10678 | 0.10371 | 0.098612 | 0.09249 | 0.086367 | 0.073102 | 0.073102 | 0.059837 | 0.031265 | 0.031265 | 0.041469 | 0.096388 | 0.088224 | 0.092306 | 0.086184 | 0.080061 | 0.068837 | 0.058633 | 0.044347 | 0.039245 | 0.027 | -0.0015714 | -0.017898 | -0.034224
|  | DRUMRUNIE | EE |  |  |  |  | 0.070694 | 0.064571 | 0.066612 | 0.059469 | 0.054367 | 0.036 | 0.025796 | 0.01151 | 0.0053878 | -0.0078776 | -0.043592 | -0.055837 | -0.078286 | 0.10984 | 0.10269 | 0.10678 | 0.10371 | 0.098612 | 0.09351 | 0.086367 | 0.073102 | 0.073102 | 0.059837 | 0.036367 | 0.039429 | 0.047592 | 0.096388 | 0.088224 | 0.092306 | 0.087204 | 0.081082 | 0.068837 | 0.058633 | 0.046388 | 0.041286 | 0.030061 | -0.0015714 | -0.017898 | -0.029122
|  | DRUMRUNIE | HT |  |  |  |  | 0.070694 | 0.063551 | 0.065592 | 0.059469 | 0.054367 | 0.041102 | 0.027837 | 0.012531 | 0.0064082 | -0.0058367 | -0.033388 | -0.072163 | -0.079306 | 0.10984 | 0.10269 | 0.10678 | 0.10371 | 0.098612 | 0.094531 | 0.086367 | 0.073102 | 0.073102 | 0.059837 | 0.031265 | 0.031265 | 0.041469 | 0.096388 | 0.088224 | 0.092306 | 0.087204 | 0.081082 | 0.071898 | 0.059653 | 0.047408 | 0.042306 | 0.031082 | 0.0035306 | -0.017898 | -0.034224
|  | DRUMRUNIE | HE |  |  |  |  | 0.070694 | 0.063551 | 0.065592 | 0.058449 | 0.051306 | 0.036 | 0.024776 | 0.008449 | 0.0023265 | -0.010939 | -0.035429 | -0.049714 | -0.072163 | 0.10882 | 0.10269 | 0.10678 | 0.10371 | 0.098612 | 0.09249 | 0.086367 | 0.073102 | 0.073102 | 0.059837 | 0.035347 | 0.036367 | 0.04249 | 0.096388 | 0.088224 | 0.092306 | 0.086184 | 0.080061 | 0.068837 | 0.058633 | 0.044347 | 0.039245 | 0.027 | 0.0035306 | -0.017898 | -0.032184
|  | DRUMRUNIE | FB |  |  |  |  | 0.078857 | 0.082939 | 0.078857 | 0.077837 | 0.077837 | 0.073755 | 0.071714 | 0.064571 | 0.06151 | 0.059469 | 0.03702 | 0.013551 | 0.0064082 | 0.118 | 0.12004 | 0.11494 | 0.11188 | 0.1129 | 0.10984 | 0.10678 | 0.10065 | 0.099633 | 0.096571 | 0.078204 | 0.052694 | 0.046571 | 0.10557 | 0.10761 | 0.10455 | 0.10251 | 0.10353 | 0.10047 | 0.097408 | 0.091286 | 0.089245 | 0.087204 | 0.064755 | 0.040265 | 0.038224
| STRATHLEVEN | DRYMEN | MINIMUM HEADROOM | NS 48494 88026 | YES | YES | 0.525 | -1.599 | -1.5949 | -1.6051 | -1.6316 | -1.6745 | -1.7469 | -1.8663 | -1.9776 | -2.0827 | -2.1898 | -2.4398 | -2.7571 | -2.9867 | -0.71224 | -0.71837 | -0.73673 | -0.75306 | -0.78776 | -0.83061 | -0.90816 | -0.96939 | -1.0296 | -1.1031 | -1.202 | -1.252 | -1.4184 | -0.96327 | -0.96429 | -0.97959 | -1.0041 | -1.0429 | -1.1153 | -1.1959 | -1.2888 | -1.3776 | -1.4765 | -1.6724 | -1.8816 | -2.0224
|  | DRYMEN | EE |  |  |  |  | -1.599 | -1.5929 | -1.601 | -1.6276 | -1.6684 | -1.7408 | -1.8602 | -1.9704 | -2.0735 | -2.1816 | -2.4214 | -2.7184 | -2.9214 | -0.71122 | -0.71735 | -0.73163 | -0.74898 | -0.78265 | -0.82347 | -0.89592 | -0.95612 | -1.0143 | -1.0898 | -1.1541 | -1.2184 | -1.2755 | -0.96224 | -0.96327 | -0.97653 | -1.001 | -1.0388 | -1.1122 | -1.1908 | -1.2806 | -1.3694 | -1.4663 | -1.6429 | -1.8459 | -1.9724
|  | DRYMEN | HT |  |  |  |  | -1.599 | -1.5949 | -1.6051 | -1.6316 | -1.6745 | -1.7469 | -1.8663 | -1.9776 | -2.0827 | -2.1898 | -2.4398 | -2.7571 | -2.9867 | -0.71224 | -0.71735 | -0.73673 | -0.75306 | -0.78776 | -0.83061 | -0.90816 | -0.96939 | -1.0296 | -1.1031 | -1.202 | -1.252 | -1.248 | -0.96327 | -0.96327 | -0.97959 | -1.0041 | -1.0429 | -1.1153 | -1.1959 | -1.2888 | -1.3776 | -1.4765 | -1.6724 | -1.8816 | -2.0224
|  | DRYMEN | HE |  |  |  |  | -1.599 | -1.5939 | -1.601 | -1.6276 | -1.6714 | -1.7418 | -1.8592 | -1.9673 | -2.0735 | -2.1837 | -2.3745 | -2.6969 | -2.8918 | -0.71122 | -0.71837 | -0.73163 | -0.74796 | -0.78265 | -0.82347 | -0.89796 | -0.95816 | -1.0184 | -1.0908 | -1.148 | -1.2357 | -1.3092 | -0.96224 | -0.96429 | -0.97755 | -1.001 | -1.0408 | -1.1143 | -1.1908 | -1.2786 | -1.3684 | -1.4694 | -1.6133 | -1.8347 | -1.9684
|  | DRYMEN | FB |  |  |  |  | -1.5684 | -1.5418 | -1.5286 | -1.5276 | -1.5357 | -1.552 | -1.5918 | -1.6163 | -1.6551 | -1.6806 | -1.8673 | -2.0408 | -2.1592 | -0.68776 | -0.68061 | -0.67959 | -0.68163 | -0.70204 | -0.72551 | -0.76735 | -0.79388 | -0.83878 | -0.86837 | -1.0765 | -1.2408 | -1.4184 | -0.93469 | -0.91633 | -0.91122 | -0.91224 | -0.92245 | -0.94184 | -0.97755 | -1.002 | -1.0418 | -1.0684 | -1.2796 | -1.4429 | -1.5082
| DUNVEGAN | DRYNOCH | MINIMUM HEADROOM | NG 41080 31292 | YES | NO | 1.745 | 0.56873 | 0.56057 | 0.5371 | 0.50037 | 0.43098 | 0.31976 | 0.18098 | 0.062612 | -0.071061 | -0.15065 | -0.42514 | -0.69351 | -0.92412 | 0.57537 | 0.57741 | 0.56924 | 0.55904 | 0.52435 | 0.47537 | 0.38455 | 0.31414 | 0.22945 | 0.17027 | -0.054224 | -0.037898 | 0.013122 | 0.60215 | 0.59399 | 0.57154 | 0.5297 | 0.4695 | 0.41542 | 0.30623 | 0.21542 | 0.11134 | 0.047051 | -0.16621 | -0.30703 | -0.41723
|  | DRYNOCH | EE |  |  |  |  | 0.56873 | 0.56159 | 0.5371 | 0.50445 | 0.43608 | 0.31976 | 0.18302 | 0.064653 | -0.06698 | -0.13841 | -0.42514 | -0.69351 | -0.91392 | 0.57537 | 0.57843 | 0.56924 | 0.55904 | 0.52435 | 0.47639 | 0.38455 | 0.31516 | 0.22945 | 0.17027 | -0.015449 | -0.0011633 | 0.053939 | 0.60215 | 0.59399 | 0.57256 | 0.5297 | 0.47358 | 0.41542 | 0.30726 | 0.21644 | 0.11338 | 0.054194 | -0.16621 | -0.30703 | -0.39274
|  | DRYNOCH | HT |  |  |  |  | 0.56873 | 0.56057 | 0.53812 | 0.50445 | 0.44016 | 0.33506 | 0.19833 | 0.085061 | -0.04249 | -0.11086 | -0.33739 | -0.62208 | -0.92412 | 0.57639 | 0.57741 | 0.56924 | 0.55904 | 0.52435 | 0.47537 | 0.38455 | 0.31414 | 0.23047 | 0.17027 | -0.054224 | -0.037898 | 0.013122 | 0.60215 | 0.59399 | 0.57256 | 0.53174 | 0.47562 | 0.4246 | 0.31644 | 0.2297 | 0.1297 | 0.071541 | -0.12438 | -0.27948 | -0.41315
|  | DRYNOCH | HE |  |  |  |  | 0.57078 | 0.56261 | 0.53812 | 0.50037 | 0.43098 | 0.3218 | 0.18098 | 0.062612 | -0.071061 | -0.15065 | -0.34555 | -0.64963 | -0.84963 | 0.57639 | 0.57945 | 0.57027 | 0.55904 | 0.52435 | 0.47741 | 0.38557 | 0.31618 | 0.23149 | 0.17129 | -0.011367 | -0.0072857 | 0.015163 | 0.60317 | 0.59603 | 0.57154 | 0.53072 | 0.4695 | 0.41542 | 0.30623 | 0.21542 | 0.11134 | 0.047051 | -0.1203 | -0.30499 | -0.41723
|  | DRYNOCH | FB |  |  |  |  | 0.6218 | 0.63608 | 0.63914 | 0.64016 | 0.632 | 0.60139 | 0.58404 | 0.54731 | 0.53302 | 0.51771 | 0.3371 | 0.14629 | 0.096286 | 0.61414 | 0.62027 | 0.62027 | 0.62639 | 0.62231 | 0.5968 | 0.58353 | 0.5468 | 0.52537 | 0.47537 | 0.28965 | 0.10496 | 0.074347 | 0.64297 | 0.65317 | 0.65419 | 0.65419 | 0.64399 | 0.62358 | 0.60726 | 0.57154 | 0.56236 | 0.5246 | 0.38889 | 0.21338 | 0.18583
| KEITH 2 | DUFFTOWN | MINIMUM HEADROOM | NJ 32060 39722 | NO | YES | 1.483 | 0.26082 | 0.24347 | 0.22306 | 8.1986 | 8.1578 | 7.9006 | 7.669 | 7.4578 | 7.2108 | 7.072 | 6.4873 | 5.8261 | 5.5139 | 1.7435 | 1.7312 | 1.719 | 8.9669 | 8.9598 | 8.8159 | 8.7516 | 8.6567 | 8.5261 | 8.3955 | 8.1424 | 7.9057 | 7.9006 | 0.64653 | 0.62816 | 0.60673 | 8.2439 | 8.202 | 8.0214 | 7.8908 | 7.7561 | 7.602 | 7.5031 | 7.098 | 6.6184 | 6.4143
|  | DUFFTOWN | EE |  |  |  |  | 0.26082 | 0.24551 | 0.22918 | 8.222 | 8.1761 | 7.9231 | 7.719 | 7.4578 | 7.222 | 7.0863 | 6.4873 | 5.8261 | 5.5139 | 1.7435 | 1.7333 | 1.7251 | 9.0108 | 8.9761 | 8.8292 | 8.77 | 8.6669 | 8.5261 | 8.4455 | 8.17 | 7.9231 | 7.9006 | 0.64653 | 0.6302 | 0.61898 | 8.2643 | 8.2163 | 8.0357 | 7.9163 | 7.7582 | 7.6143 | 7.5163 | 7.098 | 6.6184 | 6.4143
|  | DUFFTOWN | HT |  |  |  |  | 0.26184 | 0.24347 | 0.22306 | 8.2149 | 8.171 | 7.9271 | 7.7129 | 7.4761 | 7.3016 | 7.0843 | 6.5924 | 5.9394 | 5.6363 | 1.7435 | 1.7312 | 1.719 | 8.9955 | 8.9598 | 8.8159 | 8.7537 | 8.6567 | 8.5741 | 8.3955 | 8.1424 | 7.9057 | 7.9976 | 0.64653 | 0.62816 | 0.60673 | 8.2439 | 8.2031 | 8.0337 | 7.9235 | 7.7827 | 7.6653 | 7.5367 | 7.1643 | 6.6969 | 6.5347
|  | DUFFTOWN | HE |  |  |  |  | 0.26184 | 0.24551 | 0.22714 | 8.2078 | 8.1578 | 7.9006 | 7.669 | 7.4639 | 7.2108 | 7.072 | 6.6996 | 6.2751 | 6.0129 | 1.7435 | 1.7333 | 1.7241 | 9.0047 | 8.971 | 8.822 | 8.7516 | 8.671 | 8.5506 | 8.47 | 8.3088 | 8.3047 | 8.3027 | 0.64755 | 0.6302 | 0.61388 | 8.2541 | 8.202 | 8.0214 | 7.8908 | 7.7561 | 7.602 | 7.5031 | 7.2122 | 6.9071 | 6.7367
|  | DUFFTOWN | FB |  |  |  |  | 0.28327 | 0.29041 | 0.28837 | 8.1986 | 8.1771 | 8.1404 | 8.122 | 8.0894 | 8.0578 | 8.021 | 7.7424 | 7.4955 | 7.0904 | 1.7578 | 1.77 | 1.768 | 8.9669 | 8.9618 | 8.9414 | 8.922 | 8.8986 | 8.8812 | 8.8598 | 8.7078 | 8.522 | 8.1353 | 0.66694 | 0.67816 | 0.67408 | 8.252 | 8.2388 | 8.2082 | 8.1765 | 8.1418 | 8.1194 | 8.0857 | 7.9051 | 7.6459 | 7.4898
| BRACO | DUNBLANE | MINIMUM HEADROOM | NN 77907 01544 | NO | YES | 2.67 | 1.3742 | 1.4099 | 1.3446 | 1.3527 | 1.1242 | 0.80681 | 0.40069 | 0.0088531 | -0.34115 | -0.72278 | -2.0718 | -3.0054 | -3.4871 | 3.8492 | 3.842 | 3.7471 | 3.7614 | 3.4145 | 3.0685 | 2.6277 | 2.2451 | 1.8839 | 1.5165 | 0.27773 | -0.28758 | -0.43145 | 3.2147 | 3.2372 | 3.1668 | 3.1933 | 2.9239 | 2.6208 | 2.1678 | 1.7698 | 1.3923 | 1.0045 | -0.34038 | -1.1414 | -1.4853
|  | DUNBLANE | EE |  |  |  |  | 1.3823 | 1.4323 | 1.3803 | 1.4099 | 1.2109 | 0.88947 | 0.54457 | 0.19151 | -0.15951 | -0.50645 | -1.8095 | -2.683 | -3.1177 | 3.8553 | 3.8553 | 3.7685 | 3.7961 | 3.4634 | 3.1002 | 2.7267 | 2.3502 | 2.0022 | 1.6543 | 0.52773 | -0.079412 | -0.35288 | 3.2198 | 3.2545 | 3.1943 | 3.2351 | 2.9831 | 2.6719 | 2.2933 | 1.9025 | 1.5423 | 1.1851 | -0.088341 | -0.87303 | -1.1955
|  | DUNBLANE | HT |  |  |  |  | 1.3742 | 1.4099 | 1.3446 | 1.3527 | 1.1242 | 0.80681 | 0.40069 | 0.0088531 | -0.34115 | -0.72278 | -2.0718 | -3.0054 | -3.4871 | 3.8492 | 3.842 | 3.7471 | 3.7614 | 3.4145 | 3.0685 | 2.6277 | 2.2451 | 1.8839 | 1.5165 | 0.27773 | -0.28758 | -0.39064 | 3.2147 | 3.2372 | 3.1668 | 3.1933 | 2.9239 | 2.6208 | 2.1678 | 1.7698 | 1.3923 | 1.0045 | -0.34038 | -1.1414 | -1.4853
|  | DUNBLANE | HE |  |  |  |  | 1.3823 | 1.4313 | 1.3833 | 1.4078 | 1.2027 | 0.90069 | 0.53844 | 0.22314 | -0.15033 | -0.44931 | -1.5973 | -2.2411 | -2.7248 | 3.8543 | 3.8543 | 3.7685 | 3.7951 | 3.4594 | 3.1216 | 2.7206 | 2.3839 | 2.0094 | 1.7155 | 0.68385 | 0.32569 | -0.042678 | 3.2219 | 3.2504 | 3.1953 | 3.2331 | 2.977 | 2.6841 | 2.2872 | 1.9392 | 1.5515 | 1.2474 | 0.11574 | -0.41079 | -0.79854
|  | DUNBLANE | FB |  |  |  |  | 1.514 | 1.5813 | 1.6017 | 1.616 | 1.6058 | 1.5507 | 1.5344 | 1.4313 | 1.3211 | 1.0201 | 0.12926 | -1.086 | -1.882 | 3.9777 | 3.9798 | 3.9502 | 3.9288 | 3.8808 | 3.7767 | 3.7461 | 3.5981 | 3.44 | 2.9839 | 1.9257 | 0.61038 | -0.43145 | 3.3678 | 3.4188 | 3.4341 | 3.4453 | 3.4351 | 3.3729 | 3.3708 | 3.2617 | 3.1392 | 2.78 | 1.8004 | 0.39737 | -0.1465
| DUNOON | DUNOON | MINIMUM HEADROOM | NS 17135 77531 | NO | YES | 0.41 | 11.998 | 11.7633 | 11.5367 | 11.2653 | 10.9296 | 10.3296 | 9.6469 | 9.2531 | 8.7051 | 8.0878 | 5.2133 | 2.8633 | 1.6102 | 13.5337 | 13.298 | 13.0633 | 12.8082 | 12.5082 | 12.1071 | 11.598 | 11.3633 | 10.9776 | 10.3776 | 8.5102 | 7.2347 | 6.5173 | 12.898 | 12.6633 | 12.4367 | 12.1582 | 11.7735 | 11.1918 | 10.5051 | 10.1531 | 9.652 | 9.0347 | 6.4735 | 4.5153 | 3.5082
|  | DUNOON | EE |  |  |  |  | 12.0061 | 12.0173 | 11.6378 | 11.2867 | 10.9561 | 10.3714 | 9.6827 | 9.2602 | 8.7347 | 8.0878 | 5.2133 | 2.8633 | 1.6102 | 13.5429 | 13.5337 | 13.1449 | 12.8112 | 12.5082 | 12.1224 | 11.6143 | 11.3633 | 10.9837 | 10.4286 | 8.5102 | 7.2347 | 6.5173 | 12.9061 | 12.9031 | 12.5265 | 12.1714 | 11.7867 | 11.2276 | 10.5306 | 10.1531 | 9.6673 | 9.0347 | 6.4735 | 4.5153 | 3.5082
|  | DUNOON | HT |  |  |  |  | 11.999 | 11.7633 | 11.5367 | 11.3051 | 10.9857 | 10.499 | 9.8408 | 9.4724 | 8.9347 | 8.1918 | 5.6245 | 3.3898 | 2.2582 | 13.5357 | 13.298 | 13.0633 | 12.8143 | 12.5133 | 12.1888 | 11.6857 | 11.4663 | 11.0408 | 10.3776 | 8.6061 | 7.5112 | 7.2735 | 12.899 | 12.6633 | 12.4367 | 12.1837 | 11.802 | 11.3378 | 10.6602 | 10.3306 | 9.8163 | 9.0837 | 6.8031 | 4.9745 | 4.1612
|  | DUNOON | HE |  |  |  |  | 11.998 | 12.0173 | 11.6255 | 11.2653 | 10.9296 | 10.3296 | 9.6469 | 9.2531 | 8.7051 | 8.1112 | 6.0653 | 4.2173 | 3.4 | 13.5337 | 13.5337 | 13.1449 | 12.8082 | 12.5143 | 12.1071 | 11.598 | 11.3796 | 10.9776 | 10.4929 | 9.0653 | 8.1551 | 7.6786 | 12.898 | 12.902 | 12.5276 | 12.1582 | 11.7735 | 11.1918 | 10.5051 | 10.1592 | 9.652 | 9.0847 | 7.2449 | 5.7469 | 5.1143
|  | DUNOON | FB |  |  |  |  | 12.0704 | 12.1439 | 12.151 | 11.8684 | 11.7633 | 11.6367 | 11.4602 | 11.2163 | 10.8714 | 10.8143 | 9.5184 | 7.5469 | 5.9551 | 13.5806 | 13.6163 | 13.5888 | 13.302 | 13.1622 | 13.0071 | 12.8082 | 12.5612 | 12.199 | 12.1194 | 10.7184 | 8.7286 | 6.8061 | 12.9694 | 13.0255 | 13.0214 | 12.7398 | 12.6306 | 12.5235 | 12.3143 | 12.0429 | 11.6439 | 11.5592 | 10.148 | 7.8173 | 6.702
| DUNVEGAN | DUNVEGAN | MINIMUM HEADROOM | NG 27646 47150 | YES | NO | 0.83 | 1.0809 | 1.0778 | 1.0615 | 1.0237 | 0.90434 | 0.083935 | -0.69464 | -1.3906 | -1.7528 | -1.8385 | -2.1446 | -2.4518 | -2.6926 | 1.437 | 1.4329 | 1.4196 | 1.4043 | 1.3686 | 0.51047 | -0.23545 | -0.89464 | -1.1865 | -1.2293 | -1.2752 | -1.2691 | -1.262 | 1.2778 | 1.2707 | 1.2543 | 1.2115 | 1.1472 | 0.26455 | -0.44362 | -1.0773 | -1.3926 | -1.4599 | -1.661 | -1.8385 | -1.9732
|  | DUNVEGAN | EE |  |  |  |  | 1.0809 | 1.0778 | 1.0615 | 1.0268 | 0.91353 | 0.79618 | 0.67067 | -0.15484 | -0.96913 | -1.6355 | -2.1446 | -2.4518 | -2.6742 | 1.437 | 1.4329 | 1.4196 | 1.4043 | 1.3686 | 1.335 | 1.2819 | 0.47679 | -0.29056 | -0.96504 | -1.2599 | -1.2426 | -1.2222 | 1.2778 | 1.2707 | 1.2543 | 1.2156 | 1.1533 | 1.0921 | 1.0013 | 0.10842 | -0.63239 | -1.2518 | -1.661 | -1.8385 | -1.9528
|  | DUNVEGAN | HT |  |  |  |  | 1.0819 | 1.0788 | 1.0656 | 1.0288 | 0.91047 | 0.083935 | -0.69464 | -1.3906 | -1.7528 | -1.8385 | -2.0314 | -2.3773 | -2.6926 | 1.438 | 1.4339 | 1.4217 | 1.4054 | 1.3696 | 0.51047 | -0.23545 | -0.89464 | -1.1865 | -1.2293 | -1.2752 | -1.2691 | -1.2344 | 1.2788 | 1.2727 | 1.2574 | 1.2166 | 1.1523 | 0.26455 | -0.44362 | -1.0773 | -1.3926 | -1.4599 | -1.6038 | -1.8028 | -1.9732
|  | DUNVEGAN | HE |  |  |  |  | 1.0819 | 1.0778 | 1.0625 | 1.0237 | 0.90434 | 0.7972 | 0.66965 | -0.25586 | -1.1283 | -1.8283 | -2.0416 | -2.3936 | -2.6079 | 1.438 | 1.4329 | 1.4196 | 1.4043 | 1.3686 | 1.3339 | 1.2819 | 0.37067 | -0.46198 | -1.1701 | -1.2538 | -1.2518 | -1.2385 | 1.2788 | 1.2707 | 1.2543 | 1.2115 | 1.1472 | 1.0911 | 0.99924 | 0.013527 | -0.78443 | -1.4365 | -1.5987 | -1.8069 | -1.9252
|  | DUNVEGAN | FB |  |  |  |  | 1.1329 | 1.1605 | 1.1778 | 1.1615 | 1.1186 | 1.0911 | 1.0492 | 1.0278 | 0.5023 | -0.068106 | -1.2957 | -1.4508 | -1.5161 | 1.4799 | 1.4901 | 1.4921 | 1.4799 | 1.4676 | 1.4513 | 1.4186 | 1.4043 | 0.76557 | 0.15944 | -1.1171 | -1.2181 | -1.262 | 1.3278 | 1.3441 | 1.3554 | 1.3482 | 1.3309 | 1.3145 | 1.2829 | 1.2676 | 0.61047 | 0.073731 | -1.1181 | -1.2487 | -1.2661
| DYCE | DYCE NORTH | MINIMUM HEADROOM | NJ 89092 12705 | NO | YES | 0.728 | 4.2122 | 4.0776 | 4.0041 | 3.8582 | 3.7041 | 3.4316 | 2.0071 | 0.45306 | -2.3714 | -2.8327 | -6.4 | -15.8041 | -23.6776 | 6.8827 | 6.7898 | 6.7449 | 6.6765 | 6.5918 | 6.4541 | 4.8561 | 3.05 | -0.24592 | -0.6449 | -4.4857 | -15.0714 | -24.5347 | 5.9255 | 5.8337 | 5.7571 | 5.649 | 5.5184 | 5.2918 | 3.6235 | 1.7816 | -1.6102 | -2.0714 | -6.201 | -17.5398 | -27.1827
|  | DYCE NORTH | EE |  |  |  |  | 4.3133 | 4.0776 | 4.0041 | 3.8582 | 3.7041 | 3.4316 | 2.5153 | 1.1796 | -1.1276 | -1.5469 | -4.6061 | -12.8592 | -16.3714 | 6.9939 | 6.7929 | 6.751 | 6.6765 | 6.598 | 6.4663 | 5.5092 | 4.0347 | 1.3418 | 0.99082 | -1.9776 | -11.5347 | -15.4439 | 6.0306 | 5.8337 | 5.7571 | 5.649 | 5.5194 | 5.299 | 4.2673 | 2.7265 | -0.037755 | -0.44898 | -3.8949 | -13.9092 | -18.0867
|  | DYCE NORTH | HT |  |  |  |  | 4.248 | 4.0816 | 4.0112 | 3.8663 | 3.7071 | 3.4316 | 2.0071 | 0.4898 | -2.3714 | -2.8327 | -6.4 | -15.8041 | -23.6776 | 6.9224 | 6.7898 | 6.7449 | 6.6765 | 6.5918 | 6.4541 | 4.8561 | 3.152 | -0.24592 | -0.6449 | -4.1776 | -15.0714 | -24.4153 | 5.9633 | 5.8337 | 5.7643 | 5.6561 | 5.5184 | 5.2918 | 3.6235 | 1.8541 | -1.6102 | -2.0714 | -6.1031 | -17.5398 | -27.1827
|  | DYCE NORTH | HE |  |  |  |  | 4.2122 | 4.0888 | 4.0061 | 3.8786 | 3.7194 | 3.4429 | 2.4673 | 0.45306 | 0.21224 | -0.80204 | -6.3551 | -14.9255 | -23.1112 | 6.8827 | 6.7929 | 6.751 | 6.6827 | 6.6051 | 6.4582 | 5.4031 | 3.05 | 2.9092 | 1.7724 | -4.4857 | -14.6449 | -24.5347 | 5.9255 | 5.8378 | 5.7745 | 5.65 | 5.5337 | 5.3051 | 4.1878 | 1.7816 | 1.5867 | 0.40204 | -6.201 | -16.6827 | -26.7755
|  | DYCE NORTH | FB |  |  |  |  | 4.7204 | 4.5133 | 4.2847 | 4.201 | 4.1163 | 4.0184 | 3.3418 | 2.5602 | 0.83265 | 0.32245 | -0.85408 | -2.8 | -4.3469 | 7.399 | 7.1786 | 6.9673 | 6.9143 | 6.849 | 6.7827 | 6.0143 | 5.0908 | 2.9949 | 2.4173 | 1.199 | -0.85204 | -2.5255 | 6.4286 | 6.2214 | 6.0245 | 5.952 | 5.8612 | 5.7745 | 4.9888 | 4.0418 | 1.9184 | 1.3133 | 0.0030612 | -2.6663 | -4.0245
| THURSO | EDAY | MINIMUM HEADROOM | HY 56341 33422 | YES | NO | 0.556 | 0.67084 | 0.65961 | 0.65859 | 0.64635 | 0.63308 | 0.62186 | 0.60451 | 0.58308 | 0.56676 | 0.56267 | 0.529 | 0.51369 | 0.51982 | 0.51573 | 0.50961 | 0.50859 | 0.50553 | 0.50247 | 0.49737 | 0.49022 | 0.48002 | 0.47186 | 0.47186 | 0.45247 | 0.45145 | 0.44533 | 0.46573 | 0.45859 | 0.45859 | 0.45247 | 0.44533 | 0.43512 | 0.41982 | 0.40247 | 0.38818 | 0.38512 | 0.35859 | 0.34737 | 0.34124
|  | EDAY | EE |  |  |  |  | 0.67084 | 0.66063 | 0.65859 | 0.64839 | 0.63512 | 0.62288 | 0.60451 | 0.58308 | 0.56676 | 0.56267 | 0.529 | 0.51369 | 0.52492 | 0.51573 | 0.50961 | 0.50859 | 0.50655 | 0.50247 | 0.49839 | 0.49022 | 0.48002 | 0.47186 | 0.47186 | 0.45451 | 0.45349 | 0.45961 | 0.46573 | 0.45859 | 0.45859 | 0.45451 | 0.44533 | 0.43512 | 0.42084 | 0.40349 | 0.38818 | 0.38512 | 0.35859 | 0.34737 | 0.34839
|  | EDAY | HT |  |  |  |  | 0.67084 | 0.65961 | 0.65859 | 0.64839 | 0.63512 | 0.62288 | 0.60859 | 0.5892 | 0.5739 | 0.56982 | 0.53308 | 0.51676 | 0.51982 | 0.51573 | 0.50961 | 0.50859 | 0.50553 | 0.50247 | 0.49839 | 0.49124 | 0.48104 | 0.47288 | 0.47186 | 0.45247 | 0.45145 | 0.45451 | 0.46573 | 0.45859 | 0.45859 | 0.45451 | 0.44635 | 0.43614 | 0.4239 | 0.40757 | 0.39329 | 0.39022 | 0.36063 | 0.34737 | 0.34124
|  | EDAY | HE |  |  |  |  | 0.67084 | 0.65961 | 0.65859 | 0.64635 | 0.63308 | 0.62186 | 0.60451 | 0.58308 | 0.56676 | 0.56267 | 0.53512 | 0.5188 | 0.52084 | 0.51573 | 0.50961 | 0.50859 | 0.50553 | 0.50247 | 0.49737 | 0.49124 | 0.48002 | 0.47186 | 0.47186 | 0.45553 | 0.45349 | 0.45145 | 0.46573 | 0.45859 | 0.45859 | 0.45247 | 0.44533 | 0.43614 | 0.41982 | 0.40247 | 0.38818 | 0.38512 | 0.36165 | 0.34941 | 0.34124
|  | EDAY | FB |  |  |  |  | 0.67594 | 0.67696 | 0.67084 | 0.6688 | 0.66063 | 0.65655 | 0.65349 | 0.64431 | 0.64022 | 0.63614 | 0.60961 | 0.57696 | 0.56573 | 0.51676 | 0.52084 | 0.51778 | 0.51676 | 0.51267 | 0.51267 | 0.51063 | 0.50553 | 0.50145 | 0.49839 | 0.48206 | 0.45961 | 0.44533 | 0.46676 | 0.47186 | 0.4688 | 0.47084 | 0.46573 | 0.46165 | 0.46063 | 0.45451 | 0.45043 | 0.44635 | 0.42186 | 0.39022 | 0.38614
| THURSO | EDAY TIDAL | MINIMUM HEADROOM | HY 54226 31320 | YES | NO | 0 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816
|  | EDAY TIDAL | EE |  |  |  |  | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816
|  | EDAY TIDAL | HT |  |  |  |  | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816
|  | EDAY TIDAL | HE |  |  |  |  | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816
|  | EDAY TIDAL | FB |  |  |  |  | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.41224 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.80408 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816 | 0.60816
| FIDDES | EDZELL | MINIMUM HEADROOM | NO 63500 70513 | YES | NO | 1.648 | 1.3684 | 1.3163 | 1.2459 | 1.2102 | 1.0071 | 0.53877 | 0.028563 | -0.45409 | -1.0408 | -1.4194 | -2.0908 | -2.3255 | -2.5327 | 1.6175 | 1.5961 | 1.5716 | 1.5502 | 1.3257 | 0.98591 | 0.67877 | 0.36244 | 0.013461 | -0.11817 | -0.37225 | -0.37327 | -0.35797 | 1.3965 | 1.3598 | 1.3088 | 1.2537 | 1.019 | 0.70162 | 0.32509 | -0.082049 | -0.54838 | -0.76878 | -1.2218 | -1.38 | -1.5167
|  | EDZELL | EE |  |  |  |  | 1.3694 | 1.3398 | 1.2673 | 1.2102 | 1.0071 | 0.59387 | 0.33775 | -0.18572 | -0.57756 | -0.8847 | -2.0194 | -2.3163 | -2.4684 | 1.6175 | 1.6053 | 1.5798 | 1.5533 | 1.3267 | 1.0094 | 0.78285 | 0.43591 | 0.14407 | 0.03489 | -0.30491 | -0.33756 | -0.3294 | 1.3965 | 1.3751 | 1.322 | 1.2537 | 1.019 | 0.71387 | 0.46897 | 0.083257 | -0.27184 | -0.47082 | -1.1851 | -1.378 | -1.4739
|  | EDZELL | HT |  |  |  |  | 1.3694 | 1.3163 | 1.2459 | 1.2214 | 1.0184 | 0.53877 | 0.028563 | -0.45409 | -1.0408 | -1.4194 | -2.0908 | -2.3255 | -2.5327 | 1.6175 | 1.5961 | 1.5716 | 1.5502 | 1.3257 | 0.98591 | 0.67877 | 0.36244 | 0.013461 | -0.11817 | -0.37225 | -0.37327 | -0.35797 | 1.3975 | 1.3598 | 1.3088 | 1.2608 | 1.0251 | 0.70162 | 0.32509 | -0.082049 | -0.54838 | -0.76878 | -1.2218 | -1.38 | -1.5167
|  | EDZELL | HE |  |  |  |  | 1.3684 | 1.3408 | 1.2826 | 1.2316 | 1.0194 | 0.69081 | 0.40203 | -0.0296 | -0.42348 | -0.68776 | -1.2092 | -1.8357 | -2.148 | 1.6175 | 1.6033 | 1.5808 | 1.5553 | 1.3308 | 1.0675 | 0.83387 | 0.49611 | 0.2155 | 0.11754 | -0.052865 | -0.17021 | -0.24164 | 1.3975 | 1.3751 | 1.3322 | 1.2639 | 1.0292 | 0.75775 | 0.50162 | 0.12509 | -0.21674 | -0.40756 | -0.77797 | -1.1708 | -1.3637
|  | EDZELL | FB |  |  |  |  | 1.4194 | 1.4112 | 1.4143 | 1.3806 | 1.1786 | 0.95305 | 0.71224 | 0.49489 | 0.26224 | 0.085706 | -0.28572 | -0.88062 | -1.4786 | 1.64 | 1.638 | 1.64 | 1.6288 | 1.4145 | 1.1828 | 0.94918 | 0.73183 | 0.50326 | 0.44101 | 0.28081 | 0.030808 | -0.27736 | 1.4282 | 1.4241 | 1.419 | 1.3914 | 1.1833 | 0.94754 | 0.71795 | 0.50162 | 0.3006 | 0.17407 | -0.11776 | -0.62593 | -0.86776
| MILTON OF CRAIGIE | EDZELL STREET | MINIMUM HEADROOM | NO 47103 32070 | YES | NO | 0.009 | 9.15 | 9.1592 | 9.1551 | 9.1378 | 9.1082 | 9.0378 | 8.9633 | 8.8816 | 8.8306 | 8.7439 | 8.352 | 8.0653 | 7.8786 | 9.0531 | 9.0418 | 9.0286 | 9.0041 | 8.9418 | 8.8643 | 8.7571 | 8.6745 | 8.5612 | 8.4551 | 8.0276 | 6.9194 | 5.5663 | 9.2286 | 9.2255 | 9.2173 | 9.2122 | 9.1765 | 9.1061 | 9.0071 | 8.9163 | 8.9133 | 8.8347 | 8.4031 | 8.15 | 8.0143
|  | EDZELL STREET | EE |  |  |  |  | 9.15 | 9.1592 | 9.1551 | 9.1378 | 9.1102 | 9.0378 | 8.9633 | 8.8816 | 8.8306 | 8.7439 | 8.3939 | 8.0653 | 7.8786 | 9.0541 | 9.0439 | 9.0316 | 9.0224 | 8.9847 | 8.9224 | 8.8378 | 8.7592 | 8.7724 | 8.6878 | 8.3235 | 7.9286 | 7.4316 | 9.2286 | 9.2255 | 9.2173 | 9.2122 | 9.1796 | 9.1061 | 9.0071 | 8.9163 | 8.9133 | 8.8347 | 8.4031 | 8.15 | 8.0143
|  | EDZELL STREET | HT |  |  |  |  | 9.15 | 9.1602 | 9.1602 | 9.1398 | 9.1082 | 9.0398 | 8.9684 | 8.8918 | 8.8429 | 8.7561 | 8.352 | 8.1 | 7.998 | 9.0531 | 9.0418 | 9.0296 | 9.0194 | 8.9806 | 8.9214 | 8.8388 | 8.7633 | 8.7724 | 8.6929 | 8.4122 | 8.4163 | 8.3388 | 9.2296 | 9.2255 | 9.2204 | 9.2122 | 9.1776 | 9.1061 | 9.0143 | 8.9255 | 8.9255 | 8.848 | 8.4173 | 8.2071 | 8.15
|  | EDZELL STREET | HE |  |  |  |  | 9.151 | 9.1612 | 9.1622 | 9.1398 | 9.1092 | 9.0408 | 8.9673 | 8.8908 | 8.8398 | 8.7582 | 8.4776 | 8.2755 | 8.1235 | 9.0541 | 9.0429 | 9.0316 | 9.0204 | 8.9837 | 8.9214 | 8.8367 | 8.7612 | 8.7714 | 8.6918 | 8.3439 | 7.9469 | 7.4153 | 9.2306 | 9.2265 | 9.2224 | 9.2133 | 9.1765 | 9.1061 | 9.0112 | 8.9265 | 8.9235 | 8.851 | 8.4949 | 8.3143 | 8.201
|  | EDZELL STREET | FB |  |  |  |  | 9.1898 | 9.2163 | 9.2327 | 9.2398 | 9.2276 | 9.2122 | 9.1806 | 9.1745 | 9.1378 | 9.1051 | 8.9724 | 8.7235 | 8.4888 | 9.0592 | 9.049 | 9.0286 | 9.0041 | 8.9418 | 8.8643 | 8.7571 | 8.6745 | 8.5612 | 8.4551 | 8.0276 | 6.9194 | 5.5663 | 9.2837 | 9.3051 | 9.3184 | 9.3276 | 9.3214 | 9.3112 | 9.2745 | 9.2561 | 9.2061 | 9.1643 | 9.048 | 8.6071 | 8.4663
| ELGIN | ELGIN | MINIMUM HEADROOM | NJ 21256 64664 | NO | YES | 1.439 | 6.58 | 6.1882 | 6.0637 | 5.9127 | 5.7229 | 5.2453 | 4.4209 | 3.4484 | 2.2923 | 1.5535 | -3.874 | -6.6598 | -7.3822 | 8.1392 | 7.7974 | 7.7729 | 7.7362 | 7.6709 | 7.5178 | 7.3117 | 6.9678 | 6.5453 | 6.0984 | 3.3127 | 2.6056 | 2.2147 | 7.5545 | 7.18 | 7.13 | 7.0372 | 6.8953 | 6.526 | 5.9566 | 5.229 | 4.376 | 3.7535 | -0.50669 | -2.3781 | -2.8393
|  | ELGIN | EE |  |  |  |  | 6.6494 | 6.1882 | 6.0637 | 5.9127 | 5.7229 | 5.2719 | 4.7821 | 4.0392 | 3.2545 | 2.7913 | -2.371 | -6.6598 | -7.3822 | 8.2035 | 7.7974 | 7.7729 | 7.7362 | 7.676 | 7.53 | 7.4402 | 7.177 | 6.9107 | 6.728 | 3.8453 | 2.6056 | 2.4076 | 7.6219 | 7.18 | 7.13 | 7.0372 | 6.8964 | 6.5484 | 6.2127 | 5.6453 | 5.0556 | 4.6913 | 0.55351 | -2.3781 | -2.8393
|  | ELGIN | HT |  |  |  |  | 6.6096 | 6.2066 | 6.0821 | 5.9372 | 5.7229 | 5.2453 | 4.4209 | 3.4484 | 2.2923 | 1.5535 | -3.874 | -6.5291 | -7.3251 | 8.1658 | 7.8147 | 7.7749 | 7.7372 | 7.6709 | 7.5178 | 7.3117 | 6.9678 | 6.5453 | 6.0984 | 3.3127 | 2.7004 | 2.63 | 7.5831 | 7.1974 | 7.1392 | 7.0515 | 6.8953 | 6.526 | 5.9566 | 5.229 | 4.376 | 3.7535 | -0.50669 | -2.2873 | -2.8006
|  | ELGIN | HE |  |  |  |  | 6.58 | 6.1902 | 6.0678 | 5.9331 | 5.7515 | 5.2953 | 4.7994 | 4.0994 | 3.3596 | 2.8902 | -1.4526 | -4.6108 | -6.8057 | 8.1392 | 7.8015 | 7.7729 | 7.7372 | 7.679 | 7.5321 | 7.4382 | 7.1872 | 6.9331 | 6.7525 | 4.0953 | 3.2147 | 2.4851 | 7.5545 | 7.1821 | 7.1311 | 7.0474 | 6.9147 | 6.5607 | 6.2219 | 5.6851 | 5.1239 | 4.7576 | 1.1821 | -0.99649 | -2.4832
|  | ELGIN | FB |  |  |  |  | 6.8647 | 6.5831 | 6.3749 | 6.28 | 6.1443 | 5.9158 | 5.677 | 5.4147 | 5.1617 | 4.9178 | 2.9096 | -1.2547 | -3.6526 | 8.3953 | 8.1423 | 7.9851 | 7.929 | 7.8504 | 7.729 | 7.6107 | 7.4627 | 7.3933 | 7.2729 | 5.9086 | 3.3739 | 2.2147 | 7.8433 | 7.5749 | 7.4076 | 7.3362 | 7.2402 | 7.08 | 6.8882 | 6.6709 | 6.5045 | 6.3015 | 4.5882 | 0.79433 | -0.44241
| ARBROATH | ELLIOT DEPOT | MINIMUM HEADROOM | NO 62251 40381 | YES | YES | 2.98 | -7.2318 | -7.3033 | -7.391 | -7.4655 | -7.5543 | -10.9818 | -11.1533 | -11.2778 | -11.441 | -11.541 | -11.9747 | -12.3543 | -12.5492 | -6.5584 | -6.6022 | -6.639 | -6.6757 | -6.7737 | -10.9461 | -11.039 | -11.0716 | -11.1584 | -11.2084 | -11.4033 | -11.4135 | -11.4135 | -6.8482 | -6.9084 | -6.9818 | -7.0278 | -7.1206 | -11.3329 | -11.4931 | -11.589 | -11.7329 | -11.8206 | -12.1839 | -12.4655 | -12.5982
|  | ELLIOT DEPOT | EE |  |  |  |  | -7.1563 | -7.3033 | -7.391 | -7.4655 | -7.5543 | -7.7288 | -7.8849 | -8.0175 | -8.1655 | -8.289 | -8.8553 | -9.4573 | -9.692 | -6.4747 | -6.6022 | -6.639 | -6.6737 | -6.7737 | -6.8737 | -6.9553 | -7.0022 | -7.0788 | -7.1482 | -7.3716 | -7.7706 | -7.791 | -6.7665 | -6.9084 | -6.9706 | -7.0278 | -7.1206 | -7.2604 | -7.4043 | -7.5145 | -7.642 | -7.7563 | -8.2604 | -8.8502 | -8.9941
|  | ELLIOT DEPOT | HT |  |  |  |  | -7.1992 | -7.2982 | -7.3747 | -7.4482 | -7.54 | -7.7033 | -7.8614 | -7.988 | -8.1267 | -8.2543 | -8.7686 | -9.4175 | -9.6308 | -6.5237 | -6.6002 | -6.6349 | -6.6747 | -6.7716 | -6.8635 | -6.9604 | -7.0053 | -7.0808 | -7.1502 | -7.3624 | -7.7155 | -7.6584 | -6.8145 | -6.9043 | -6.9757 | -7.0155 | -7.1135 | -7.241 | -7.391 | -7.4941 | -7.6165 | -7.7329 | -8.2022 | -8.7982 | -8.9002
|  | ELLIOT DEPOT | HE |  |  |  |  | -7.2318 | -7.3033 | -7.3839 | -7.4543 | -7.5441 | -10.9818 | -11.1533 | -11.2778 | -11.441 | -11.541 | -11.9747 | -12.3543 | -12.5492 | -6.5584 | -6.6022 | -6.6369 | -6.6747 | -6.7726 | -10.9461 | -11.039 | -11.0716 | -11.1584 | -11.2084 | -11.4033 | -11.4135 | -11.4135 | -6.8482 | -6.9084 | -6.9818 | -7.0186 | -7.1155 | -11.3329 | -11.4931 | -11.589 | -11.7329 | -11.8206 | -12.1839 | -12.4655 | -12.5982
|  | ELLIOT DEPOT | FB |  |  |  |  | -6.9675 | -7.1186 | -7.2512 | -7.3818 | -7.4012 | -7.4349 | -7.4543 | -7.4839 | -7.4971 | -7.541 | -7.7706 | -8.1308 | -8.3359 | -6.2839 | -6.4278 | -6.5369 | -6.6757 | -6.7002 | -6.7267 | -6.7461 | -6.7747 | -6.7829 | -6.8135 | -6.9757 | -7.192 | -7.5829 | -6.5757 | -6.7288 | -6.8604 | -6.9829 | -7.0135 | -7.0267 | -7.0502 | -7.0808 | -7.0951 | -7.1369 | -7.3196 | -7.641 | -7.9359
| DYCE | ELLON | MINIMUM HEADROOM | NJ 95510 30054 | NO | YES | 2.433 | -1.1534 | 24.3216 | 24.1033 | 23.5165 | 22.1186 | 20.2778 | 17.8839 | 16.1788 | 13.7992 | 12.6124 | 5.088 | 0.80429 | -2.5253 | 1.7686 | 26.6002 | 26.5104 | 26.1482 | 24.8747 | 23.4176 | 21.5227 | 20.5053 | 18.6124 | 17.7053 | 12.2298 | 9.342 | 6.4329 | 0.42597 | 26.0227 | 25.8624 | 25.4094 | 24.0839 | 22.441 | 20.2788 | 18.7614 | 16.3982 | 15.3727 | 8.5482 | 4.4553 | 0.99918
|  | ELLON | EE |  |  |  |  | -1.1156 | 24.342 | 24.2186 | 23.7533 | 22.3298 | 20.5339 | 18.3135 | 16.888 | 15.0747 | 14.1431 | 6.8778 | 1.99 | -0.45184 | 1.8022 | 26.6145 | 26.5584 | 26.2308 | 24.9573 | 23.4512 | 21.6063 | 20.8359 | 19.5849 | 19.0135 | 14.4665 | 11.2073 | 9.9033 | 0.46066 | 26.0349 | 25.941 | 25.5706 | 24.2267 | 22.6063 | 20.5676 | 19.3512 | 17.7176 | 16.9737 | 10.7482 | 6.2237 | 4.1359
|  | ELLON | HT |  |  |  |  | -1.1432 | 24.3216 | 24.1033 | 23.5165 | 22.1186 | 21.1247 | 19.5849 | 18.1553 | 15.741 | 13.7257 | 6.2176 | 1.1655 | -2.4141 | 1.7788 | 26.6002 | 26.5104 | 26.1482 | 24.8747 | 24.3859 | 23.2992 | 22.3053 | 20.2594 | 18.6829 | 13.692 | 10.3614 | 7.9257 | 0.43719 | 26.0227 | 25.8624 | 25.4094 | 24.0839 | 23.3441 | 22.0257 | 20.7747 | 18.4624 | 16.5829 | 10.0063 | 5.2757 | 1.838
|  | ELLON | HE |  |  |  |  | -1.1534 | 24.34 | 24.1655 | 23.6206 | 22.1635 | 20.2778 | 17.8839 | 16.1788 | 13.7992 | 12.6124 | 5.088 | 0.80429 | -2.5253 | 1.7686 | 26.6114 | 26.5431 | 26.2012 | 24.9298 | 23.4176 | 21.5227 | 20.5053 | 18.6124 | 17.7053 | 12.2298 | 9.342 | 6.4329 | 0.42597 | 26.0329 | 25.9053 | 25.4818 | 24.1196 | 22.441 | 20.2788 | 18.7614 | 16.3982 | 15.3727 | 8.5482 | 4.4553 | 0.99918
|  | ELLON | FB |  |  |  |  | -0.785 | 24.8798 | 24.7624 | 24.6594 | 24.1686 | 23.2655 | 21.791 | 20.0624 | 19.2635 | 18.8951 | 15.2716 | 11.4216 | 10.089 | 2.0584 | 26.9788 | 26.8482 | 26.7492 | 26.2676 | 25.2053 | 23.6431 | 21.7808 | 21.0492 | 20.7186 | 18.5145 | 15.389 | 13.8451 | 0.78311 | 26.4941 | 26.3788 | 26.3135 | 25.8257 | 24.9237 | 23.5533 | 21.9676 | 21.0635 | 20.6237 | 17.4747 | 13.6247 | 12.742
| TAYNUILT | EREDINE | MINIMUM HEADROOM | NM 97142 09376 | YES | YES | 0 | 0.18294 | 0.1809 | 0.17069 | 0.16355 | 0.16355 | 0.15437 | 0.14824 | 0.14008 | 0.13294 | 0.12784 | 0.11355 | 0.10845 | 0.10539 | 0.18229 | 0.18024 | 0.1731 | 0.17004 | 0.17004 | 0.1629 | 0.1578 | 0.15167 | 0.14249 | 0.14147 | 0.12514 | 0.12616 | 0.12922 | 0.18516 | 0.18006 | 0.16986 | 0.16578 | 0.16476 | 0.15761 | 0.15353 | 0.14537 | 0.13822 | 0.13516 | 0.12088 | 0.11884 | 0.1168
|  | EREDINE | EE |  |  |  |  | 0.18294 | 0.1809 | 0.17069 | 0.16457 | 0.16355 | 0.15539 | 0.14927 | 0.1411 | 0.13294 | 0.1309 | 0.11355 | 0.10947 | 0.10743 | 0.18229 | 0.18024 | 0.1731 | 0.17004 | 0.17004 | 0.1629 | 0.1578 | 0.15167 | 0.14249 | 0.14147 | 0.1282 | 0.13024 | 0.13535 | 0.18516 | 0.18006 | 0.16986 | 0.1668 | 0.16578 | 0.15863 | 0.15353 | 0.14639 | 0.13822 | 0.1372 | 0.12292 | 0.11986 | 0.11884
|  | EREDINE | HT |  |  |  |  | 0.18294 | 0.1809 | 0.17171 | 0.16457 | 0.16457 | 0.15641 | 0.15233 | 0.14314 | 0.14008 | 0.13294 | 0.11763 | 0.10845 | 0.10641 | 0.18229 | 0.18024 | 0.1731 | 0.17004 | 0.17004 | 0.1629 | 0.1578 | 0.15167 | 0.14861 | 0.14147 | 0.12514 | 0.12616 | 0.13024 | 0.18516 | 0.18006 | 0.1719 | 0.1668 | 0.16578 | 0.15863 | 0.15455 | 0.14843 | 0.14639 | 0.13822 | 0.12088 | 0.11884 | 0.11782
|  | EREDINE | HE |  |  |  |  | 0.18294 | 0.1809 | 0.17171 | 0.16355 | 0.16355 | 0.15437 | 0.14824 | 0.14008 | 0.136 | 0.12784 | 0.11559 | 0.10947 | 0.10539 | 0.18229 | 0.18024 | 0.1731 | 0.17004 | 0.17004 | 0.1629 | 0.1578 | 0.15167 | 0.14861 | 0.14147 | 0.1282 | 0.12922 | 0.12922 | 0.18516 | 0.18006 | 0.17088 | 0.16578 | 0.16476 | 0.15761 | 0.15353 | 0.14537 | 0.14333 | 0.13516 | 0.12394 | 0.11884 | 0.1168
|  | EREDINE | FB |  |  |  |  | 0.19518 | 0.18702 | 0.18192 | 0.1809 | 0.17784 | 0.17273 | 0.17069 | 0.16865 | 0.16763 | 0.16457 | 0.15335 | 0.1411 | 0.136 | 0.19555 | 0.18637 | 0.18127 | 0.17922 | 0.17922 | 0.17412 | 0.16902 | 0.16698 | 0.16698 | 0.16392 | 0.15065 | 0.13739 | 0.13331 | 0.19741 | 0.1872 | 0.1821 | 0.18006 | 0.17802 | 0.17292 | 0.17088 | 0.16782 | 0.16884 | 0.16373 | 0.15353 | 0.13822 | 0.13618
| INVERNESS | ERROGIE | MINIMUM HEADROOM | NH 56674 22810 | YES | NO | 0.051 | 0.86531 | 0.85816 | 0.8551 | 0.85 | 0.8449 | 0.82857 | 0.82245 | 0.81224 | 0.79796 | 0.79592 | 0.76837 | 0.7449 | 0.73061 | 0.90714 | 0.9 | 0.89694 | 0.89388 | 0.89082 | 0.87959 | 0.87755 | 0.87143 | 0.85918 | 0.85918 | 0.83367 | 0.83061 | 0.83673 | 0.88878 | 0.88163 | 0.87857 | 0.87449 | 0.87041 | 0.85612 | 0.85102 | 0.84082 | 0.82959 | 0.82857 | 0.80306 | 0.7898 | 0.78061
|  | ERROGIE | EE |  |  |  |  | 0.86633 | 0.85816 | 0.85612 | 0.85 | 0.84796 | 0.83469 | 0.82347 | 0.81633 | 0.80204 | 0.8 | 0.76837 | 0.7449 | 0.73163 | 0.90714 | 0.9 | 0.89694 | 0.89388 | 0.89184 | 0.88571 | 0.87755 | 0.87245 | 0.86122 | 0.85918 | 0.83367 | 0.83673 | 0.84286 | 0.8898 | 0.88163 | 0.87857 | 0.87449 | 0.87245 | 0.86224 | 0.85204 | 0.84388 | 0.83163 | 0.83061 | 0.80306 | 0.7898 | 0.78469
|  | ERROGIE | HT |  |  |  |  | 0.86633 | 0.86224 | 0.8551 | 0.85 | 0.84694 | 0.83265 | 0.82551 | 0.81837 | 0.80408 | 0.80102 | 0.78265 | 0.75408 | 0.73061 | 0.90714 | 0.90306 | 0.89694 | 0.89388 | 0.89082 | 0.88061 | 0.87857 | 0.87245 | 0.85918 | 0.8602 | 0.83776 | 0.83061 | 0.83673 | 0.8898 | 0.88673 | 0.87857 | 0.87449 | 0.87143 | 0.8602 | 0.85306 | 0.8449 | 0.83367 | 0.83061 | 0.81327 | 0.79286 | 0.78061
|  | ERROGIE | HE |  |  |  |  | 0.86531 | 0.85918 | 0.8551 | 0.85 | 0.8449 | 0.82857 | 0.82245 | 0.81224 | 0.79796 | 0.79592 | 0.78061 | 0.75102 | 0.73878 | 0.90714 | 0.90102 | 0.89694 | 0.89388 | 0.89082 | 0.87959 | 0.87755 | 0.87143 | 0.85918 | 0.8602 | 0.84082 | 0.83469 | 0.84184 | 0.88878 | 0.88367 | 0.87857 | 0.87551 | 0.87041 | 0.85612 | 0.85102 | 0.84082 | 0.82959 | 0.82857 | 0.81224 | 0.79082 | 0.78571
|  | ERROGIE | FB |  |  |  |  | 0.87041 | 0.87041 | 0.86735 | 0.86224 | 0.86224 | 0.85918 | 0.85612 | 0.85612 | 0.85 | 0.84898 | 0.82755 | 0.81327 | 0.80816 | 0.9102 | 0.91224 | 0.90714 | 0.90408 | 0.90306 | 0.90102 | 0.9 | 0.8949 | 0.88878 | 0.88673 | 0.86939 | 0.85408 | 0.84286 | 0.89388 | 0.89286 | 0.8898 | 0.88571 | 0.88469 | 0.88265 | 0.88061 | 0.87959 | 0.87347 | 0.87347 | 0.85204 | 0.83571 | 0.83265
| ABERNETHY | ERROL | MINIMUM HEADROOM | NO 23206 23038 | NO | YES | 0.708 | 1.7602 | 1.5571 | 1.4878 | 1.2755 | 1.052 | 0.47959 | 0.0010204 | -0.75612 | -2.1878 | -2.699 | -4.8878 | -7.4347 | -9.7031 | 3.3173 | 3.2541 | 3.2276 | 3.1653 | 2.9745 | 2.6255 | 2.1949 | 1.5857 | 0.088776 | -0.33163 | -2.3378 | -4.6602 | -6.9969 | 2.7184 | 2.6184 | 2.5622 | 2.4245 | 2.2265 | 1.7714 | 1.2735 | 0.52551 | -1.0878 | -1.5898 | -3.8704 | -6.6133 | -9.1735
|  | ERROL | EE |  |  |  |  | 1.7612 | 1.5582 | 1.4878 | 1.2755 | 1.0571 | 0.53776 | 0.078571 | -0.56837 | -1.4653 | -1.8612 | -3.6469 | -6.448 | -7.7684 | 3.3173 | 3.2551 | 3.2276 | 3.1653 | 2.9755 | 2.6673 | 2.3439 | 1.8051 | 0.97245 | 0.70204 | -0.6051 | -3.1214 | -4.1245 | 2.7194 | 2.6194 | 2.5622 | 2.4245 | 2.2296 | 1.8163 | 1.3949 | 0.7551 | -0.18776 | -0.53776 | -2.202 | -5.1388 | -6.4276
|  | ERROL | HT |  |  |  |  | 1.7612 | 1.5592 | 1.5031 | 1.2929 | 1.0755 | 0.60306 | 0.0010204 | -0.67755 | -1.6949 | -2.1082 | -3.9276 | -6.998 | -9.3857 | 3.3173 | 3.2551 | 3.2296 | 3.1653 | 2.9765 | 2.7031 | 2.1949 | 1.6071 | 0.61531 | 0.32551 | -1.1306 | -3.9204 | -6.1184 | 2.7194 | 2.6204 | 2.5745 | 2.4347 | 2.2418 | 1.8663 | 1.2735 | 0.58673 | -0.51224 | -0.88061 | -2.6367 | -5.8857 | -8.4592
|  | ERROL | HE |  |  |  |  | 1.7602 | 1.5571 | 1.4959 | 1.2776 | 1.052 | 0.47959 | 0.038776 | -0.75612 | -2.1878 | -2.699 | -4.8878 | -7.4347 | -9.7031 | 3.3173 | 3.2541 | 3.2286 | 3.1653 | 2.9745 | 2.6255 | 2.3071 | 1.5857 | 0.088776 | -0.33163 | -2.3378 | -4.6602 | -6.9969 | 2.7184 | 2.6184 | 2.5673 | 2.4255 | 2.2265 | 1.7714 | 1.3551 | 0.52551 | -1.0878 | -1.5898 | -3.8704 | -6.6133 | -9.1735
|  | ERROL | FB |  |  |  |  | 1.8439 | 1.8449 | 1.8082 | 1.7633 | 1.4796 | 1.3939 | 1.1571 | 0.88673 | 0.32755 | 0.16122 | -0.79082 | -1.9082 | -2.7092 | 3.3622 | 3.3663 | 3.3571 | 3.3347 | 3.2367 | 3.1857 | 2.9551 | 2.6724 | 2.0561 | 1.8837 | 1.0959 | 0.079592 | -0.71837 | 2.7867 | 2.801 | 2.7857 | 2.7459 | 2.5643 | 2.5184 | 2.2653 | 1.9684 | 1.3449 | 1.1724 | 0.27041 | -0.97449 | -1.6245
| FASNAKYLE | FASNAKYLE | MINIMUM HEADROOM | NH 31948 29998 | YES | YES | 0.086 | 0.49388 | 0.49082 | 0.48367 | 0.45816 | 0.44388 | 0.3949 | 0.36633 | 0.35612 | 0.33163 | 0.30714 | 0.2449 | 0.17959 | 0.13061 | 0.62449 | 0.62143 | 0.61735 | 0.60306 | 0.60612 | 0.58571 | 0.57347 | 0.55 | 0.53776 | 0.51633 | 0.47653 | 0.47857 | 0.46735 | 0.48571 | 0.48469 | 0.48061 | 0.46122 | 0.4602 | 0.42245 | 0.40102 | 0.37143 | 0.35102 | 0.32551 | 0.27551 | 0.26939 | 0.24694
|  | FASNAKYLE | EE |  |  |  |  | 0.49796 | 0.49082 | 0.48367 | 0.46429 | 0.44898 | 0.3949 | 0.37143 | 0.3602 | 0.33673 | 0.31429 | 0.2449 | 0.17959 | 0.13367 | 0.62959 | 0.62143 | 0.61837 | 0.61122 | 0.60612 | 0.58571 | 0.57347 | 0.55102 | 0.53878 | 0.51837 | 0.48571 | 0.48367 | 0.49184 | 0.49286 | 0.48469 | 0.48163 | 0.47143 | 0.46122 | 0.42245 | 0.40408 | 0.37347 | 0.3551 | 0.33163 | 0.27551 | 0.27041 | 0.2602
|  | FASNAKYLE | HT |  |  |  |  | 0.49592 | 0.49184 | 0.48367 | 0.46531 | 0.44898 | 0.41122 | 0.38061 | 0.36837 | 0.34082 | 0.32041 | 0.27143 | 0.19694 | 0.13061 | 0.62755 | 0.62449 | 0.61735 | 0.61122 | 0.60612 | 0.58673 | 0.57449 | 0.55102 | 0.53878 | 0.51837 | 0.47653 | 0.47857 | 0.49082 | 0.49082 | 0.49082 | 0.48061 | 0.47143 | 0.46122 | 0.43163 | 0.40918 | 0.37857 | 0.35714 | 0.33469 | 0.28673 | 0.27449 | 0.25102
|  | FASNAKYLE | HE |  |  |  |  | 0.49388 | 0.49184 | 0.48469 | 0.45816 | 0.44388 | 0.3949 | 0.36633 | 0.35612 | 0.33163 | 0.30714 | 0.26531 | 0.18367 | 0.13571 | 0.62449 | 0.62143 | 0.61837 | 0.60306 | 0.60714 | 0.58571 | 0.57347 | 0.55 | 0.53776 | 0.51633 | 0.48571 | 0.48061 | 0.47551 | 0.48571 | 0.48571 | 0.48061 | 0.46122 | 0.4602 | 0.42347 | 0.40102 | 0.37143 | 0.35102 | 0.32551 | 0.28776 | 0.26939 | 0.24694
|  | FASNAKYLE | FB |  |  |  |  | 0.51327 | 0.50714 | 0.50918 | 0.5051 | 0.49796 | 0.49286 | 0.48367 | 0.47857 | 0.46633 | 0.46429 | 0.41633 | 0.37245 | 0.3602 | 0.64184 | 0.63776 | 0.63571 | 0.63367 | 0.63061 | 0.62551 | 0.61531 | 0.60714 | 0.59082 | 0.59082 | 0.5449 | 0.49694 | 0.46735 | 0.50918 | 0.50714 | 0.50714 | 0.50612 | 0.50306 | 0.5 | 0.4898 | 0.48265 | 0.47041 | 0.47041 | 0.42245 | 0.37347 | 0.37041
| TUMMEL BRIDGE | FINCASTLE | MINIMUM HEADROOM | NN 87976 61147 | YES | YES | 0 | 0.072082 | 0.073102 | 0.071061 | 0.06902 | 0.062898 | 0.054735 | 0.052694 | 0.045551 | 0.044531 | 0.040449 | 0.025143 | 0.021061 | 0.01902 | 0.075327 | 0.076347 | 0.073286 | 0.072265 | 0.066143 | 0.061041 | 0.06002 | 0.054918 | 0.054918 | 0.049816 | 0.036551 | 0.036551 | 0.039612 | 0.072684 | 0.073704 | 0.071663 | 0.068602 | 0.0635 | 0.055337 | 0.054316 | 0.047173 | 0.047173 | 0.043092 | 0.028806 | 0.025745 | 0.023704
|  | FINCASTLE | EE |  |  |  |  | 0.072082 | 0.073102 | 0.071061 | 0.06902 | 0.06698 | 0.055755 | 0.053714 | 0.045551 | 0.045551 | 0.041469 | 0.026163 | 0.023102 | 0.022082 | 0.075327 | 0.076347 | 0.073286 | 0.072265 | 0.069204 | 0.062061 | 0.06002 | 0.054918 | 0.054918 | 0.049816 | 0.039612 | 0.039612 | 0.044714 | 0.072684 | 0.073704 | 0.071663 | 0.068602 | 0.067582 | 0.055337 | 0.055337 | 0.047173 | 0.047173 | 0.044112 | 0.029827 | 0.027786 | 0.027786
|  | FINCASTLE | HT |  |  |  |  | 0.072082 | 0.073102 | 0.071061 | 0.06902 | 0.06698 | 0.055755 | 0.053714 | 0.046571 | 0.046571 | 0.041469 | 0.025143 | 0.021061 | 0.021061 | 0.075327 | 0.076347 | 0.073286 | 0.072265 | 0.069204 | 0.062061 | 0.06002 | 0.054918 | 0.054918 | 0.049816 | 0.036551 | 0.036551 | 0.041653 | 0.072684 | 0.073704 | 0.071663 | 0.068602 | 0.067582 | 0.056357 | 0.055337 | 0.048194 | 0.048194 | 0.044112 | 0.028806 | 0.025745 | 0.026765
|  | FINCASTLE | HE |  |  |  |  | 0.072082 | 0.073102 | 0.071061 | 0.06902 | 0.062898 | 0.054735 | 0.052694 | 0.046571 | 0.044531 | 0.040449 | 0.028204 | 0.023102 | 0.01902 | 0.075327 | 0.076347 | 0.073286 | 0.072265 | 0.066143 | 0.061041 | 0.06002 | 0.054918 | 0.054918 | 0.049816 | 0.039612 | 0.038592 | 0.039612 | 0.072684 | 0.073704 | 0.071663 | 0.068602 | 0.0635 | 0.055337 | 0.054316 | 0.048194 | 0.047173 | 0.043092 | 0.030847 | 0.026765 | 0.023704
|  | FINCASTLE | FB |  |  |  |  | 0.084327 | 0.085347 | 0.073102 | 0.073102 | 0.074122 | 0.071061 | 0.068 | 0.065959 | 0.064939 | 0.061878 | 0.049633 | 0.040449 | 0.036367 | 0.088592 | 0.088592 | 0.076347 | 0.074306 | 0.076347 | 0.073286 | 0.070224 | 0.070224 | 0.069204 | 0.063082 | 0.055939 | 0.047776 | 0.043694 | 0.085949 | 0.085949 | 0.073704 | 0.072684 | 0.073704 | 0.071663 | 0.068602 | 0.067582 | 0.066561 | 0.061459 | 0.051255 | 0.03901 | 0.036969
| SHETLAND | FIRTH | MINIMUM HEADROOM | HU4396874166 | YES | YES | 0.15 | -1.8827 | -2.7092 | -3.548 | -4.4306 | -5.3061 | -6.1704 | -7.0755 | -7.9786 | -8.0388 | -8.049 | -8.1316 | -8.1898 | -8.2367 | -1.6398 | -2.5531 | -3.4776 | -4.4153 | -5.3633 | -6.3194 | -7.2847 | -8.248 | -8.2663 | -8.2643 | -8.2939 | -8.2806 | -8.3 | -1.6847 | -2.5194 | -3.3643 | -4.2367 | -5.1061 | -5.9796 | -6.8643 | -7.7469 | -7.7857 | -7.7908 | -7.8367 | -7.8582 | -7.8735
|  | FIRTH | EE |  |  |  |  | -1.8806 | -2.7092 | -3.5469 | -4.4194 | -5.2959 | -6.1561 | -7.0541 | -7.951 | -8.0133 | -8.0276 | -8.1316 | -8.1898 | -8.2265 | -1.6388 | -2.552 | -3.4776 | -4.4133 | -5.3622 | -6.3153 | -7.2786 | -8.2388 | -8.2551 | -8.2551 | -8.2867 | -8.2755 | -8.2633 | -1.6847 | -2.5173 | -3.3633 | -4.2296 | -5.1 | -5.9714 | -6.8561 | -7.7276 | -7.7663 | -7.7745 | -7.8357 | -7.8582 | -7.8673
|  | FIRTH | HT |  |  |  |  | -1.8827 | -2.7082 | -3.548 | -4.4276 | -5.2878 | -6.1704 | -7.0755 | -7.9786 | -8.0388 | -8.049 | -8.1173 | -8.1816 | -8.2367 | -1.6398 | -2.552 | -3.4776 | -4.4153 | -5.3633 | -6.3194 | -7.2847 | -8.248 | -8.2663 | -8.2643 | -8.2939 | -8.2806 | -8.2582 | -1.6847 | -2.5173 | -3.3633 | -4.2367 | -5.1061 | -5.9796 | -6.8582 | -7.7469 | -7.7857 | -7.7908 | -7.8367 | -7.8582 | -7.8735
|  | FIRTH | HE |  |  |  |  | -1.8816 | -2.7092 | -3.548 | -4.4306 | -5.3061 | -6.1622 | -7.0643 | -7.9633 | -8.0276 | -8.0398 | -8.1122 | -8.1806 | -8.2265 | -1.6388 | -2.5531 | -3.4776 | -4.4153 | -5.3633 | -6.3143 | -7.2816 | -8.2439 | -8.2612 | -8.2592 | -8.2837 | -8.2765 | -8.2765 | -1.6847 | -2.5194 | -3.3643 | -4.2347 | -5.1041 | -5.9745 | -6.8643 | -7.7357 | -7.7765 | -7.7827 | -7.8286 | -7.8571 | -7.8714
|  | FIRTH | FB |  |  |  |  | -1.8602 | -2.6776 | -3.5 | -4.3306 | -5.1816 | -6.0337 | -6.8898 | -7.752 | -7.7663 | -7.7765 | -7.8378 | -7.9 | -7.9204 | -1.6245 | -2.5367 | -3.452 | -4.3806 | -5.3235 | -6.2724 | -7.2163 | -8.1724 | -8.1735 | -8.1806 | -8.2092 | -8.2724 | -8.3 | -1.6663 | -2.4949 | -3.3296 | -4.1704 | -5.0214 | -5.8704 | -6.7235 | -7.5837 | -7.5929 | -7.598 | -7.6449 | -7.7163 | -7.7214
| FORT WILLIAM | FISHNISH | MINIMUM HEADROOM | NM 66623 42191 | YES | NO | 0 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394
|  | FISHNISH | EE |  |  |  |  | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394
|  | FISHNISH | HT |  |  |  |  | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394
|  | FISHNISH | HE |  |  |  |  | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394
|  | FISHNISH | FB |  |  |  |  | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.23192 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.21494 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394 | 0.22394
| THURSO | FLOTTA | MINIMUM HEADROOM | NC 94318 95432 | YES | NO | 0 | -0.42449 | -0.42755 | -0.43571 | -0.44796 | -0.45408 | -0.46429 | -0.47449 | -0.48673 | -0.49694 | -0.50306 | -0.52245 | -0.53878 | -0.54898 | -0.35918 | -0.3602 | -0.36429 | -0.36633 | -0.36531 | -0.36837 | -0.37143 | -0.37653 | -0.37653 | -0.38163 | -0.39082 | -0.39184 | -0.3949 | -0.12653 | -0.13061 | -0.13878 | -0.15 | -0.15306 | -0.16429 | -0.17041 | -0.18265 | -0.18673 | -0.19694 | -0.21633 | -0.22551 | -0.22959
|  | FLOTTA | EE |  |  |  |  | -0.42347 | -0.42755 | -0.43469 | -0.44796 | -0.45306 | -0.46122 | -0.47245 | -0.48469 | -0.49184 | -0.50102 | -0.52245 | -0.53878 | -0.54796 | -0.35918 | -0.3602 | -0.36429 | -0.36633 | -0.36531 | -0.36735 | -0.37143 | -0.37653 | -0.37653 | -0.38163 | -0.39082 | -0.38878 | -0.38776 | -0.12653 | -0.13061 | -0.13878 | -0.15 | -0.15204 | -0.16224 | -0.17041 | -0.18163 | -0.18469 | -0.19592 | -0.21633 | -0.22449 | -0.22449
|  | FLOTTA | HT |  |  |  |  | -0.42449 | -0.42755 | -0.43571 | -0.44796 | -0.45306 | -0.46429 | -0.47041 | -0.48163 | -0.48673 | -0.4949 | -0.51837 | -0.53367 | -0.54898 | -0.35918 | -0.3602 | -0.36327 | -0.36633 | -0.36531 | -0.36735 | -0.37143 | -0.37653 | -0.37551 | -0.38061 | -0.39082 | -0.39082 | -0.38776 | -0.12653 | -0.13061 | -0.13878 | -0.15 | -0.15306 | -0.16429 | -0.16837 | -0.18061 | -0.18163 | -0.19388 | -0.21429 | -0.22551 | -0.22755
|  | FLOTTA | HE |  |  |  |  | -0.42449 | -0.42755 | -0.43571 | -0.44694 | -0.45408 | -0.46327 | -0.47449 | -0.48673 | -0.49694 | -0.50306 | -0.51837 | -0.53571 | -0.54694 | -0.35918 | -0.3602 | -0.36327 | -0.36633 | -0.36531 | -0.36837 | -0.37143 | -0.37653 | -0.37653 | -0.38163 | -0.38878 | -0.39184 | -0.39286 | -0.12653 | -0.13061 | -0.13878 | -0.15 | -0.15306 | -0.16327 | -0.17041 | -0.18265 | -0.18673 | -0.19694 | -0.21327 | -0.22449 | -0.22959
|  | FLOTTA | FB |  |  |  |  | -0.41735 | -0.42245 | -0.42449 | -0.42959 | -0.43367 | -0.4398 | -0.44388 | -0.44388 | -0.44796 | -0.44898 | -0.46939 | -0.4898 | -0.49898 | -0.35102 | -0.35714 | -0.3551 | -0.35816 | -0.35816 | -0.36327 | -0.36429 | -0.36429 | -0.36633 | -0.36735 | -0.37653 | -0.38776 | -0.3949 | -0.11735 | -0.12449 | -0.12653 | -0.13265 | -0.13776 | -0.1449 | -0.14694 | -0.14796 | -0.15204 | -0.15408 | -0.17755 | -0.20204 | -0.2051
| ELGIN | FOCHABERS | MINIMUM HEADROOM | NC 94318 95432 | NO | YES | 3.349 | 5.6276 | 5.6041 | 5.5755 | 5.4653 | 4.3837 | 3.1888 | 2.8245 | 2.4408 | 2.0337 | 1.4 | -2.4959 | -3.5469 | -4.1408 | 6.0184 | 5.999 | 5.9449 | 5.9214 | 4.8357 | 3.7592 | 3.6092 | 3.448 | 3.3092 | 3.0133 | -0.15714 | -0.28367 | -0.31633 | 5.7505 | 5.723 | 5.6781 | 5.6158 | 4.5842 | 3.5117 | 3.3148 | 3.075 | 2.7719 | 2.277 | -1.2158 | -2.0403 | -2.4699
|  | FOCHABERS | EE |  |  |  |  | 5.6296 | 5.6051 | 5.5918 | 5.5153 | 4.4316 | 3.2327 | 2.902 | 2.5031 | 2.049 | 1.7755 | -2.3888 | -3.5469 | -4.0959 | 6.0194 | 6 | 5.9776 | 5.9408 | 4.8531 | 3.7663 | 3.6327 | 3.4755 | 3.3112 | 3.1673 | 0.11224 | -0.28265 | -0.31531 | 5.7515 | 5.723 | 5.6913 | 5.6495 | 4.6168 | 3.5342 | 3.3597 | 3.1291 | 2.7862 | 2.5577 | -1.0964 | -2.0403 | -2.4699
|  | FOCHABERS | HT |  |  |  |  | 5.6286 | 5.6041 | 5.5755 | 5.4653 | 4.3837 | 4.0694 | 3.6429 | 3.1908 | 2.3704 | 1.4 | -2.4959 | -3.4133 | -4.1408 | 6.0184 | 5.999 | 5.9684 | 5.9214 | 4.8357 | 4.6857 | 4.5235 | 4.349 | 3.8704 | 3.0133 | -0.15714 | -0.28367 | -0.31633 | 5.7515 | 5.723 | 5.6781 | 5.6158 | 4.5842 | 4.4056 | 4.1638 | 3.8413 | 3.174 | 2.277 | -1.2158 | -1.9066 | -2.4444
|  | FOCHABERS | HE |  |  |  |  | 5.6276 | 5.6051 | 5.5878 | 5.4918 | 4.401 | 3.1888 | 2.8245 | 2.4408 | 2.0337 | 1.7714 | -1.7041 | -3.0449 | -3.6969 | 6.0184 | 6 | 5.9745 | 5.9337 | 4.8449 | 3.7592 | 3.6092 | 3.448 | 3.3092 | 3.1837 | 0.29388 | -0.080612 | -0.1602 | 5.7505 | 5.723 | 5.6872 | 5.6362 | 4.6005 | 3.5117 | 3.3148 | 3.075 | 2.7719 | 2.5536 | -0.62602 | -1.6638 | -2.1515
|  | FOCHABERS | FB |  |  |  |  | 5.6724 | 5.6796 | 5.6255 | 5.6051 | 5.1735 | 4.4082 | 3.9531 | 3.6663 | 3.5041 | 3.4092 | 1.8357 | -1.0582 | -1.7051 | 6.05 | 6.0541 | 5.9449 | 5.9316 | 5.4663 | 4.7051 | 4.2551 | 4.0061 | 3.9092 | 3.8327 | 2.6041 | 0.23571 | -0.057143 | 5.7913 | 5.7862 | 5.7342 | 5.7168 | 5.2638 | 4.5036 | 4.0811 | 3.824 | 3.7128 | 3.6546 | 2.3699 | -0.38316 | -0.72092
| NAIRN | FORRES | MINIMUM HEADROOM | NJ 03362 59425 | NO | YES | 2.073 | 3.2961 | 2.889 | 2.4502 | 2.0135 | 1.5267 | 24.1869 | 23.3512 | 22.7175 | 22.0022 | 21.0818 | 16.4022 | 14.8033 | 14.0431 | 6.4369 | 5.9237 | 5.4747 | 5.0767 | 4.5992 | 26.8114 | 26.0716 | 25.5237 | 24.8828 | 24.2186 | 20.2696 | 19.4226 | 18.9145 | 5.3293 | 4.8578 | 4.4119 | 3.9834 | 3.515 | 26.3145 | 25.5288 | 24.9431 | 24.2808 | 23.4696 | 19.1237 | 17.7604 | 17.0982
|  | FORRES | EE |  |  |  |  | 3.3675 | 2.89 | 2.4624 | 2.0624 | 1.5747 | 24.2002 | 23.3655 | 22.7175 | 22.0022 | 21.6145 | 16.7849 | 14.8033 | 14.0431 | 6.4941 | 5.9237 | 5.4808 | 5.1043 | 4.6277 | 26.8614 | 26.1104 | 25.5522 | 24.9155 | 24.592 | 20.6441 | 19.4226 | 18.9145 | 5.3915 | 4.8578 | 4.4201 | 4.0344 | 3.5527 | 26.3359 | 25.5461 | 24.9431 | 24.2808 | 23.9155 | 19.4655 | 17.7604 | 17.0982
|  | FORRES | HT |  |  |  |  | 3.3257 | 2.9022 | 2.4502 | 2.0135 | 1.5267 | 24.3788 | 23.7716 | 23.0563 | 22.0308 | 21.0818 | 16.4022 | 15.0155 | 14.2175 | 6.4594 | 5.9349 | 5.4747 | 5.0767 | 4.5992 | 26.9982 | 26.5206 | 25.9308 | 25.0471 | 24.2186 | 20.2696 | 19.592 | 19.4033 | 5.3558 | 4.8691 | 4.4119 | 3.9834 | 3.515 | 26.5073 | 25.9645 | 25.3165 | 24.3757 | 23.4696 | 19.1237 | 17.988 | 17.3686
|  | FORRES | HE |  |  |  |  | 3.2961 | 2.889 | 2.4553 | 2.0502 | 1.5665 | 24.1869 | 23.3512 | 22.7369 | 22.0328 | 21.7033 | 17.642 | 15.6828 | 14.9063 | 6.4369 | 5.9247 | 5.4788 | 5.0961 | 4.6186 | 26.8114 | 26.0716 | 25.5237 | 24.8828 | 24.6196 | 21.1941 | 19.9257 | 19.3992 | 5.3293 | 4.8578 | 4.416 | 4.0099 | 3.5456 | 26.3145 | 25.5288 | 24.9543 | 24.292 | 23.9859 | 20.1818 | 18.5339 | 17.8869
|  | FORRES | FB |  |  |  |  | 3.6512 | 3.2808 | 3.0573 | 2.8196 | 2.6053 | 25.6982 | 25.2604 | 24.7288 | 24.5145 | 24.2849 | 22.3757 | 18.5614 | 17.2624 | 6.7369 | 6.241 | 6.0033 | 5.7288 | 5.4747 | 28.0135 | 27.5777 | 27.0288 | 26.7726 | 26.4767 | 24.4869 | 20.8594 | 19.142 | 5.6681 | 5.2293 | 5.0007 | 4.7487 | 4.5119 | 27.6931 | 27.2808 | 26.7533 | 26.5369 | 26.2951 | 24.4277 | 20.5451 | 19.5931
| DOUNREAY | FORSS | MINIMUM HEADROOM | ND 02614 69148 | YES | NO | 0.795 | -1.4582 | -1.4633 | -1.4765 | -1.5092 | -1.5316 | -1.5837 | -1.6031 | -1.65 | -1.6878 | -1.7296 | -1.8429 | -1.9837 | -2.0969 | -1.2296 | -1.2327 | -1.2388 | -1.2459 | -1.2541 | -1.2745 | -1.2918 | -1.3163 | -1.3255 | -1.3449 | -1.3837 | -1.3857 | -1.3888 | -1.0418 | -1.052 | -1.0694 | -1.1031 | -1.1296 | -1.1796 | -1.2204 | -1.2755 | -1.3031 | -1.3449 | -1.4255 | -1.4643 | -1.498
|  | FORSS | EE |  |  |  |  | -1.4582 | -1.4633 | -1.4765 | -1.5041 | -1.5296 | -1.5796 | -1.599 | -1.6449 | -1.6806 | -1.7173 | -1.8429 | -1.9837 | -2.0969 | -1.2296 | -1.2306 | -1.2388 | -1.2459 | -1.2541 | -1.2735 | -1.2908 | -1.3143 | -1.3235 | -1.3439 | -1.3745 | -1.3755 | -1.3888 | -1.0418 | -1.051 | -1.0694 | -1.1 | -1.1296 | -1.1786 | -1.2184 | -1.2745 | -1.301 | -1.3316 | -1.4214 | -1.4561 | -1.498
|  | FORSS | HT |  |  |  |  | -1.4582 | -1.4633 | -1.4755 | -1.5041 | -1.5316 | -1.5786 | -1.598 | -1.6357 | -1.6806 | -1.7143 | -1.7969 | -1.9531 | -2.0918 | -1.2296 | -1.2316 | -1.2388 | -1.2459 | -1.2541 | -1.2745 | -1.2908 | -1.3041 | -1.3245 | -1.3439 | -1.3837 | -1.3857 | -1.3786 | -1.0408 | -1.051 | -1.0694 | -1.1 | -1.1296 | -1.1786 | -1.2173 | -1.2541 | -1.301 | -1.3449 | -1.4255 | -1.4643 | -1.4837
|  | FORSS | HE |  |  |  |  | -1.4582 | -1.4633 | -1.4755 | -1.5092 | -1.5316 | -1.5837 | -1.6031 | -1.65 | -1.6878 | -1.7296 | -1.8061 | -1.9724 | -2.0796 | -1.2296 | -1.2327 | -1.2388 | -1.2459 | -1.2541 | -1.2745 | -1.2918 | -1.3163 | -1.3255 | -1.3449 | -1.3745 | -1.3796 | -1.3837 | -1.0408 | -1.052 | -1.0694 | -1.1031 | -1.1296 | -1.1796 | -1.2204 | -1.2755 | -1.3031 | -1.3337 | -1.4102 | -1.45 | -1.4714
|  | FORSS | FB |  |  |  |  | -1.4429 | -1.4469 | -1.4469 | -1.4582 | -1.4694 | -1.4786 | -1.4898 | -1.499 | -1.5102 | -1.5235 | -1.6082 | -1.6663 | -1.6735 | -1.2184 | -1.2204 | -1.2214 | -1.2255 | -1.2286 | -1.2357 | -1.2469 | -1.2531 | -1.2592 | -1.2694 | -1.3173 | -1.3724 | -1.3878 | -1.0224 | -1.0306 | -1.0378 | -1.0561 | -1.0684 | -1.0847 | -1.1092 | -1.1173 | -1.1327 | -1.1592 | -1.2551 | -1.3449 | -1.3561
| BRACO | FORTEVIOT | MINIMUM HEADROOM | NO 04539 18092 | YES | YES | 0.231 | 5.4044 | 5.3962 | 5.3697 | 5.3156 | 5.1248 | 4.8605 | 4.5524 | 4.3911 | 4.1932 | 4.0595 | 3.3626 | 2.7942 | 2.636 | 5.4037 | 5.3925 | 5.369 | 5.3313 | 5.0497 | 4.818 | 4.5425 | 4.3997 | 4.2354 | 4.1558 | 3.6486 | 3.3456 | 3.3823 | 5.5474 | 5.5403 | 5.5117 | 5.4689 | 5.1821 | 4.9454 | 4.6403 | 4.477 | 4.2872 | 4.176 | 3.5474 | 3.075 | 2.9944
|  | FORTEVIOT | EE |  |  |  |  | 5.4105 | 5.4003 | 5.3748 | 5.3207 | 5.136 | 4.884 | 4.5799 | 4.3911 | 4.1932 | 4.0769 | 3.3626 | 2.7942 | 2.636 | 5.4058 | 5.3935 | 5.3711 | 5.3333 | 5.0548 | 4.8292 | 4.5558 | 4.3997 | 4.2354 | 4.1568 | 3.6486 | 3.3456 | 3.3823 | 5.5546 | 5.5434 | 5.5158 | 5.4699 | 5.1913 | 4.9658 | 4.6607 | 4.477 | 4.2872 | 4.1811 | 3.5474 | 3.075 | 2.9944
|  | FORTEVIOT | HT |  |  |  |  | 5.4044 | 5.3962 | 5.3697 | 5.3177 | 5.132 | 4.9218 | 4.6462 | 4.5207 | 4.3095 | 4.0993 | 3.5238 | 2.9381 | 2.6473 | 5.4037 | 5.3925 | 5.369 | 5.3313 | 5.0497 | 4.8588 | 4.5915 | 4.5129 | 4.3313 | 4.1558 | 3.7527 | 3.4415 | 3.415 | 5.5474 | 5.5403 | 5.5117 | 5.4689 | 5.1872 | 5.0015 | 4.7148 | 4.6015 | 4.3974 | 4.1985 | 3.6832 | 3.2005 | 3.0097
|  | FORTEVIOT | HE |  |  |  |  | 5.4085 | 5.4003 | 5.3738 | 5.3156 | 5.1248 | 4.8605 | 4.5524 | 4.4013 | 4.2258 | 4.0595 | 3.5503 | 3.286 | 3.2003 | 5.4048 | 5.3935 | 5.3711 | 5.3343 | 5.0507 | 4.818 | 4.5425 | 4.4333 | 4.3037 | 4.168 | 3.7997 | 3.7956 | 3.8578 | 5.5525 | 5.5413 | 5.5148 | 5.4689 | 5.1821 | 4.9454 | 4.6403 | 4.4974 | 4.3383 | 4.176 | 3.7178 | 3.5434 | 3.5199
|  | FORTEVIOT | FB |  |  |  |  | 5.4697 | 5.4758 | 5.4595 | 5.4473 | 5.4207 | 5.3656 | 5.2901 | 5.2126 | 5.1881 | 4.9697 | 4.585 | 4.1238 | 3.7728 | 5.4497 | 5.4435 | 5.4241 | 5.4109 | 5.3905 | 5.3364 | 5.2619 | 5.1721 | 5.1548 | 4.8129 | 4.4201 | 3.9833 | 3.6037 | 5.6138 | 5.6138 | 5.5944 | 5.5852 | 5.5648 | 5.5127 | 5.4372 | 5.3444 | 5.3229 | 4.9985 | 4.6076 | 4.0638 | 3.8454
| INVERNESS | FOYERS | MINIMUM HEADROOM | NH 49740 21044 | YES | NO | 0.237 | 0.50359 | 0.49645 | 0.49339 | 0.48727 | 0.4791 | 0.4638 | 0.44339 | 0.43216 | 0.42094 | 0.40257 | 0.37706 | 0.35461 | 0.33829 | 0.5842 | 0.57604 | 0.57298 | 0.5689 | 0.56686 | 0.55767 | 0.54441 | 0.53727 | 0.53012 | 0.51992 | 0.50257 | 0.49033 | 0.48727 | 0.53114 | 0.51992 | 0.5189 | 0.51176 | 0.50665 | 0.49135 | 0.474 | 0.4638 | 0.45665 | 0.43727 | 0.41482 | 0.38114 | 0.37094
|  | FOYERS | EE |  |  |  |  | 0.50359 | 0.49645 | 0.49339 | 0.48829 | 0.48114 | 0.46584 | 0.44849 | 0.43931 | 0.4291 | 0.41482 | 0.37706 | 0.35665 | 0.33829 | 0.5842 | 0.57604 | 0.57298 | 0.5689 | 0.56686 | 0.55767 | 0.54441 | 0.53829 | 0.53012 | 0.52196 | 0.50461 | 0.49135 | 0.49033 | 0.53114 | 0.51992 | 0.5189 | 0.51176 | 0.50665 | 0.49339 | 0.47706 | 0.46788 | 0.46073 | 0.44543 | 0.41482 | 0.38114 | 0.37094
|  | FOYERS | HT |  |  |  |  | 0.50563 | 0.49645 | 0.49441 | 0.48931 | 0.48216 | 0.46992 | 0.44951 | 0.44135 | 0.43012 | 0.41584 | 0.38522 | 0.37196 | 0.34543 | 0.5842 | 0.57604 | 0.574 | 0.5689 | 0.56686 | 0.55767 | 0.54441 | 0.53829 | 0.53012 | 0.52196 | 0.50257 | 0.50257 | 0.50461 | 0.53114 | 0.52094 | 0.5189 | 0.51278 | 0.50767 | 0.49543 | 0.47706 | 0.46992 | 0.46176 | 0.44543 | 0.41686 | 0.39747 | 0.38012
|  | FOYERS | HE |  |  |  |  | 0.50461 | 0.49645 | 0.49441 | 0.48727 | 0.4791 | 0.4638 | 0.44339 | 0.43216 | 0.42094 | 0.40257 | 0.38114 | 0.35461 | 0.34237 | 0.5842 | 0.57604 | 0.574 | 0.5689 | 0.56686 | 0.55767 | 0.54441 | 0.53727 | 0.53012 | 0.51992 | 0.50563 | 0.49033 | 0.49441 | 0.53114 | 0.52094 | 0.5189 | 0.51176 | 0.50665 | 0.49135 | 0.474 | 0.4638 | 0.45665 | 0.43727 | 0.41686 | 0.38114 | 0.37604
|  | FOYERS | FB |  |  |  |  | 0.50869 | 0.5138 | 0.50767 | 0.50665 | 0.50665 | 0.50359 | 0.49543 | 0.49339 | 0.48931 | 0.4842 | 0.46278 | 0.43114 | 0.41992 | 0.58931 | 0.59135 | 0.58318 | 0.5842 | 0.58522 | 0.58114 | 0.57196 | 0.5689 | 0.56584 | 0.55869 | 0.53931 | 0.50359 | 0.48727 | 0.53624 | 0.53931 | 0.53318 | 0.53012 | 0.53114 | 0.52604 | 0.51992 | 0.51584 | 0.51176 | 0.50563 | 0.4842 | 0.44747 | 0.44237
| FRASERBURGH | FRASERBURGH | MINIMUM HEADROOM | NH 51502 69028 | NO | YES | 4.602 | 16.2834 | 15.6293 | 14.9844 | 14.0232 | 12.7793 | 11.0181 | 9.111 | 7.9691 | 6.8059 | 5.6497 | 0.49567 | -2.8696 | -5.3482 | 20.0048 | 19.3202 | 18.7028 | 17.963 | 16.9212 | 15.7895 | 14.5742 | 14.1895 | 13.7844 | 13.263 | 9.8906 | 8.6263 | 7.8508 | 19.3406 | 18.7089 | 18.1212 | 17.2773 | 16.1518 | 14.6732 | 13.0681 | 12.1926 | 11.2957 | 10.3804 | 6.0865 | 3.4671 | 1.7375
|  | FRASERBURGH | EE |  |  |  |  | 16.4426 | 15.6293 | 14.9844 | 14.0457 | 12.8293 | 11.0855 | 9.2089 | 8.0732 | 6.9446 | 5.7702 | 0.49567 | -2.7492 | -5.1758 | 20.1865 | 19.3202 | 18.7048 | 17.9651 | 16.9283 | 15.7895 | 14.5844 | 14.1926 | 13.7987 | 13.263 | 9.9957 | 8.6263 | 7.8508 | 19.4936 | 18.7089 | 18.1212 | 17.2906 | 16.1844 | 14.713 | 13.1324 | 12.2548 | 11.3885 | 10.4477 | 6.0865 | 3.4671 | 1.7375
|  | FRASERBURGH | HT |  |  |  |  | 16.3467 | 15.6589 | 14.9967 | 14.0763 | 12.8712 | 11.9283 | 10.8406 | 9.7334 | 8.1661 | 6.0895 | 0.65995 | -2.8696 | -5.3482 | 20.0773 | 19.3508 | 18.7028 | 17.963 | 16.9212 | 16.6518 | 16.262 | 15.8385 | 14.912 | 13.3732 | 9.8906 | 8.7508 | 8.4191 | 19.4008 | 18.7385 | 18.1304 | 17.31 | 16.21 | 15.4946 | 14.6528 | 13.7885 | 12.4936 | 10.6957 | 6.1651 | 3.7334 | 1.9497
|  | FRASERBURGH | HE |  |  |  |  | 16.2834 | 15.6375 | 15.0038 | 14.0232 | 12.7793 | 11.0181 | 9.111 | 7.9691 | 6.8059 | 5.6497 | 1.214 | -1.7431 | -3.29 | 20.0048 | 19.3253 | 18.712 | 17.964 | 16.9273 | 15.7967 | 14.5742 | 14.1895 | 13.7844 | 13.2712 | 10.3375 | 9.3742 | 8.6518 | 19.3406 | 18.7161 | 18.1365 | 17.2773 | 16.1518 | 14.6732 | 13.0681 | 12.1926 | 11.2957 | 10.3804 | 6.6028 | 4.5528 | 3.4742
|  | FRASERBURGH | FB |  |  |  |  | 17.0651 | 16.4385 | 15.9028 | 15.4589 | 14.6946 | 13.7691 | 12.6824 | 11.511 | 11.2467 | 10.7895 | 8.8518 | 6.2273 | 5.5232 | 20.7702 | 20.1314 | 19.4957 | 19.06 | 18.2967 | 17.361 | 16.263 | 15.0651 | 14.9059 | 14.6048 | 13.1926 | 10.91 | 9.4089 | 20.0895 | 19.4834 | 18.9487 | 18.5559 | 17.8314 | 16.9753 | 15.9579 | 14.86 | 14.6304 | 14.2497 | 12.5283 | 9.8916 | 9.4824
| LUNANHEAD | FRIOCKHEIM | MINIMUM HEADROOM | NO 58834 49317 | YES | YES | 0.22 | 2.7541 | 2.748 | 2.7367 | 2.7082 | 2.6388 | 2.2449 | 1.9163 | 1.6704 | 1.3908 | 1.2653 | 0.51633 | -0.12653 | -0.58776 | 3.8755 | 3.8592 | 3.8398 | 3.8184 | 3.7653 | 3.4296 | 3.198 | 3.0102 | 2.8102 | 2.8184 | 2.3776 | 2.1949 | 2.0408 | 3.1898 | 3.1735 | 3.152 | 3.1092 | 3.0347 | 2.6929 | 2.4092 | 2.1959 | 1.948 | 1.8776 | 1.25 | 0.78776 | 0.46122
|  | FRIOCKHEIM | EE |  |  |  |  | 2.7541 | 2.748 | 2.7367 | 2.7204 | 2.6612 | 2.2847 | 1.9735 | 1.6806 | 1.3908 | 1.3163 | 0.51633 | -0.12653 | -0.58776 | 3.8765 | 3.8592 | 3.8408 | 3.8204 | 3.7663 | 3.4398 | 3.2143 | 3.0102 | 2.8102 | 2.8184 | 2.3939 | 2.1949 | 2.0408 | 3.1898 | 3.1735 | 3.152 | 3.1184 | 3.052 | 2.7214 | 2.449 | 2.1959 | 1.948 | 1.902 | 1.25 | 0.78776 | 0.46122
|  | FRIOCKHEIM | HT |  |  |  |  | 2.7551 | 2.751 | 2.7449 | 2.7082 | 2.6704 | 2.3194 | 2.0245 | 1.7235 | 1.5673 | 1.3796 | 0.63265 | -0.02551 | -0.42041 | 3.8755 | 3.8592 | 3.8408 | 3.8194 | 3.7673 | 3.4541 | 3.2398 | 3.0296 | 2.951 | 2.8337 | 2.3776 | 2.2184 | 2.2704 | 3.1908 | 3.1755 | 3.1582 | 3.1235 | 3.0592 | 2.748 | 2.4898 | 2.2265 | 2.1061 | 1.9449 | 1.3112 | 0.85204 | 0.63367
|  | FRIOCKHEIM | HE |  |  |  |  | 2.7551 | 2.749 | 2.7398 | 2.7092 | 2.6388 | 2.2449 | 1.9163 | 1.6704 | 1.4582 | 1.2653 | 0.68265 | 0.18673 | -0.097959 | 3.8755 | 3.8592 | 3.8398 | 3.8184 | 3.7653 | 3.4296 | 3.198 | 3.0663 | 2.9561 | 2.8469 | 2.4959 | 2.4592 | 2.4163 | 3.1908 | 3.1745 | 3.1551 | 3.1092 | 3.0347 | 2.6929 | 2.4092 | 2.2071 | 2.0408 | 1.8776 | 1.3878 | 1.0694 | 0.88571
|  | FRIOCKHEIM | FB |  |  |  |  | 2.8112 | 2.8418 | 2.8592 | 2.8571 | 2.8429 | 2.549 | 2.5214 | 2.4878 | 2.4276 | 2.3837 | 2.1714 | 1.8041 | 1.4 | 3.9173 | 3.9286 | 3.9265 | 3.9112 | 3.8908 | 3.5388 | 3.4918 | 3.4602 | 3.4031 | 3.3592 | 3.2296 | 2.9235 | 2.4378 | 3.2429 | 3.2602 | 3.2653 | 3.2561 | 3.2337 | 2.9235 | 2.8755 | 2.8418 | 2.7816 | 2.7602 | 2.5816 | 2.2133 | 1.8837
| KINTORE | FYVIE | MINIMUM HEADROOM | NJ 76759 37635 | NO | YES | 0.484 | 3.1059 | 3.0304 | 2.9447 | 2.8498 | 2.7896 | 2.6437 | 2.462 | 2.1733 | 2.0529 | 1.9151 | 1.2784 | 0.83551 | 0.44163 | 3.3182 | 3.2488 | 3.1814 | 3.1151 | 3.0947 | 3.011 | 2.9243 | 2.6202 | 2.561 | 2.4773 | 2.0896 | 2.0794 | 2.1314 | 3.2457 | 3.1692 | 3.0855 | 2.9794 | 2.9427 | 2.7967 | 2.6416 | 2.1753 | 2.06 | 1.9437 | 1.3845 | 1.0876 | 0.92122
|  | FYVIE | EE |  |  |  |  | 3.1161 | 3.0304 | 2.9529 | 2.8712 | 2.8192 | 2.6906 | 2.5233 | 2.2906 | 2.1029 | 1.9529 | 1.2784 | 0.83551 | 0.49163 | 3.3284 | 3.2488 | 3.1865 | 3.1273 | 3.1039 | 3.0304 | 2.9427 | 2.7488 | 2.6273 | 2.5324 | 2.1845 | 2.1427 | 2.1314 | 3.2549 | 3.1692 | 3.0927 | 2.9967 | 2.961 | 2.8284 | 2.6804 | 2.359 | 2.1467 | 2.0131 | 1.3855 | 1.1243 | 0.96
|  | FYVIE | HT |  |  |  |  | 3.111 | 3.0386 | 2.9447 | 2.8549 | 2.8059 | 2.659 | 2.5029 | 2.1733 | 2.0529 | 1.9151 | 1.3824 | 0.87122 | 0.44163 | 3.3233 | 3.2529 | 3.1814 | 3.1151 | 3.0947 | 3.011 | 2.9243 | 2.6202 | 2.561 | 2.4773 | 2.0896 | 2.0794 | 2.1488 | 3.2508 | 3.1743 | 3.0855 | 2.9824 | 2.9488 | 2.7967 | 2.6539 | 2.1753 | 2.06 | 1.9437 | 1.3845 | 1.0876 | 0.92122
|  | FYVIE | HE |  |  |  |  | 3.1059 | 3.0335 | 2.9508 | 2.8498 | 2.7896 | 2.6437 | 2.462 | 2.2998 | 2.211 | 2.0651 | 1.7171 | 1.1539 | 0.80286 | 3.3182 | 3.2488 | 3.1855 | 3.1192 | 3.0978 | 3.0212 | 2.9294 | 2.8569 | 2.8529 | 2.7651 | 2.5529 | 2.5069 | 2.4498 | 3.2457 | 3.1712 | 3.0916 | 2.9794 | 2.9427 | 2.7988 | 2.6416 | 2.4957 | 2.458 | 2.3263 | 2.011 | 1.6876 | 1.4804
|  | FYVIE | FB |  |  |  |  | 3.208 | 3.1773 | 3.1324 | 3.0906 | 3.058 | 3.0212 | 2.9712 | 2.9324 | 2.8743 | 2.8324 | 2.6171 | 2.2906 | 2.1784 | 3.4059 | 3.3682 | 3.3202 | 3.2876 | 3.2498 | 3.2141 | 3.162 | 3.1345 | 3.0784 | 3.0376 | 2.9039 | 2.6069 | 2.4498 | 3.3447 | 3.3131 | 3.2682 | 3.2284 | 3.1753 | 3.1324 | 3.0712 | 3.0161 | 2.9661 | 2.9161 | 2.7161 | 2.3559 | 2.3049
| GRUDIE BRIDGE | GARBAT FOREST | MINIMUM HEADROOM | NH 41255 67993 | YES | NO | 0 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146
|  | GARBAT FOREST | EE |  |  |  |  | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146
|  | GARBAT FOREST | HT |  |  |  |  | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146
|  | GARBAT FOREST | HE |  |  |  |  | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146
|  | GARBAT FOREST | FB |  |  |  |  | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.11494 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.10798 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146
| STORNOWAY | GISLA | MINIMUM HEADROOM | NB 12846 25823 | YES | YES | 0.097 | -0.55204 | 1.6735 | 1.6541 | 1.6235 | 1.5837 | 1.548 | 1.5031 | 1.4571 | 1.4041 | 1.3806 | 1.251 | 1.1806 | 1.1214 | -0.62347 | 1.6112 | 1.601 | 1.5878 | 1.5633 | 1.548 | 1.5153 | 1.4908 | 1.4571 | 1.4439 | 1.3449 | 1.3357 | 1.3418 | -0.68673 | 1.5439 | 1.5316 | 1.5153 | 1.4765 | 1.4469 | 1.4 | 1.3602 | 1.3337 | 1.3133 | 1.2041 | 1.152 | 1.1143
|  | GISLA | EE |  |  |  |  | -0.55204 | 1.6847 | 1.6541 | 1.6245 | 1.5867 | 1.5592 | 1.5041 | 1.4592 | 1.4051 | 1.3816 | 1.251 | 1.1806 | 1.1286 | -0.62347 | 1.6214 | 1.601 | 1.5888 | 1.5643 | 1.549 | 1.5153 | 1.4918 | 1.4582 | 1.4449 | 1.3612 | 1.351 | 1.3582 | -0.68673 | 1.5551 | 1.5316 | 1.5153 | 1.4796 | 1.448 | 1.401 | 1.3602 | 1.3347 | 1.3143 | 1.2041 | 1.1541 | 1.1276
|  | GISLA | HT |  |  |  |  | -0.55204 | 1.6735 | 1.6561 | 1.6255 | 1.5878 | 1.548 | 1.5071 | 1.4622 | 1.4092 | 1.3878 | 1.2602 | 1.1847 | 1.1214 | -0.62347 | 1.6112 | 1.602 | 1.5878 | 1.5643 | 1.548 | 1.5153 | 1.4918 | 1.4571 | 1.4439 | 1.3449 | 1.3357 | 1.3418 | -0.68673 | 1.5439 | 1.5347 | 1.5163 | 1.4796 | 1.45 | 1.4041 | 1.3643 | 1.3378 | 1.3184 | 1.2061 | 1.152 | 1.1143
|  | GISLA | HE |  |  |  |  | -0.55204 | 1.6837 | 1.6551 | 1.6235 | 1.5837 | 1.5582 | 1.5031 | 1.4571 | 1.4041 | 1.3806 | 1.2684 | 1.1847 | 1.1459 | -0.62347 | 1.6214 | 1.601 | 1.5878 | 1.5633 | 1.548 | 1.5153 | 1.4908 | 1.4571 | 1.4439 | 1.3612 | 1.348 | 1.3439 | -0.68673 | 1.5551 | 1.5327 | 1.5153 | 1.4765 | 1.4469 | 1.4 | 1.3602 | 1.3337 | 1.3133 | 1.2153 | 1.1541 | 1.1255
|  | GISLA | FB |  |  |  |  | -0.53367 | 1.7112 | 1.7041 | 1.6786 | 1.6643 | 1.6531 | 1.6398 | 1.6184 | 1.6112 | 1.5888 | 1.5061 | 1.4051 | 1.3704 | -0.61837 | 1.6337 | 1.6296 | 1.6122 | 1.602 | 1.598 | 1.5867 | 1.5673 | 1.5633 | 1.5439 | 1.4837 | 1.3908 | 1.3592 | -0.67245 | 1.5755 | 1.5735 | 1.5551 | 1.5429 | 1.5357 | 1.5224 | 1.502 | 1.4969 | 1.4765 | 1.401 | 1.2888 | 1.2704
| ALNESS | GLASTULLICH | MINIMUM HEADROOM | NH 78509 76508 | YES | NO | 0.165 | -0.79082 | -0.77959 | -0.76429 | -0.78571 | -0.80408 | -0.91837 | -1.1204 | -1.3827 | -1.7173 | -1.9449 | -2.1878 | -2.4204 | -2.6388 | 0.10612 | 0.10816 | 0.1102 | 0.1 | 0.07449 | -0.022449 | -0.2 | -0.42755 | -0.71735 | -0.91837 | -1.0143 | -1.002 | -0.98061 | -0.31939 | -0.31633 | -0.31327 | -0.34082 | -0.38367 | -0.48265 | -0.6949 | -0.95816 | -1.2847 | -1.5122 | -1.6908 | -1.8286 | -1.9204
|  | GLASTULLICH | EE |  |  |  |  | -0.79082 | -0.77857 | -0.76429 | -0.77857 | -0.79388 | -0.86429 | -0.91531 | -1.0449 | -1.2592 | -1.5337 | -2.1878 | -2.4204 | -2.6388 | 0.10612 | 0.10816 | 0.11122 | 0.1 | 0.07551 | 0.055102 | 0.011224 | -0.080612 | -0.25408 | -0.49694 | -0.99796 | -1.002 | -0.98061 | -0.31939 | -0.31633 | -0.31224 | -0.33673 | -0.37551 | -0.41531 | -0.47449 | -0.59388 | -0.79898 | -1.0765 | -1.6908 | -1.8286 | -1.9204
|  | GLASTULLICH | HT |  |  |  |  | -0.7898 | -0.77755 | -0.76429 | -0.77857 | -0.7949 | -0.91837 | -1.1204 | -1.3827 | -1.7173 | -1.9449 | -2.1224 | -2.3337 | -2.6337 | 0.10612 | 0.10816 | 0.1102 | 0.1 | 0.07449 | -0.022449 | -0.2 | -0.42755 | -0.71735 | -0.91837 | -1.0143 | -0.98367 | -0.96122 | -0.31939 | -0.31633 | -0.31327 | -0.33571 | -0.37653 | -0.48265 | -0.6949 | -0.95816 | -1.2847 | -1.5122 | -1.6653 | -1.7847 | -1.9143
|  | GLASTULLICH | HE |  |  |  |  | -0.7898 | -0.77959 | -0.76429 | -0.78571 | -0.80408 | -0.86633 | -0.93673 | -1.0765 | -1.3133 | -1.6347 | -2.1316 | -2.4153 | -2.5633 | 0.10612 | 0.10816 | 0.1102 | 0.1 | 0.07449 | 0.055102 | 0.013265 | -0.090816 | -0.28265 | -0.56735 | -0.9898 | -0.99796 | -0.95918 | -0.31939 | -0.31633 | -0.31327 | -0.34082 | -0.38367 | -0.41531 | -0.48265 | -0.61429 | -0.84184 | -1.1602 | -1.652 | -1.8071 | -1.8612
|  | GLASTULLICH | FB |  |  |  |  | -0.76122 | -0.72857 | -0.7051 | -0.68673 | -0.68469 | -0.69592 | -0.69694 | -0.71429 | -0.75816 | -0.87449 | -1.6347 | -1.8296 | -1.8796 | 0.13163 | 0.14286 | 0.14796 | 0.15204 | 0.15102 | 0.13673 | 0.12755 | 0.1102 | 0.039796 | -0.082653 | -0.82959 | -0.94898 | -0.97857 | -0.29082 | -0.27143 | -0.26122 | -0.25408 | -0.25918 | -0.27551 | -0.28571 | -0.30306 | -0.37449 | -0.50204 | -1.299 | -1.4602 | -1.4867
| SHIN | GLEDFIELD | MINIMUM HEADROOM | NH 58876 90837 | YES | NO | 0.377 | 2.2838 | 2.2725 | 2.2521 | 2.2072 | 2.145 | 1.9429 | 1.7389 | 1.5858 | 1.498 | 1.4062 | 1.196 | 1.0164 | 0.85314 | 1.719 | 1.7118 | 1.6996 | 1.6945 | 1.6802 | 1.471 | 1.3067 | 1.1832 | 1.1363 | 1.0985 | 1.0353 | 1.0353 | 0.9761 | 1.6213 | 1.611 | 1.5937 | 1.5733 | 1.5417 | 1.3386 | 1.1917 | 1.061 | 0.99982 | 0.92737 | 0.7539 | 0.65901 | 0.58248
|  | GLEDFIELD | EE |  |  |  |  | 2.2838 | 2.2746 | 2.2542 | 2.2113 | 2.1511 | 2.095 | 2.0144 | 1.7919 | 1.6103 | 1.4582 | 1.196 | 1.0164 | 0.87967 | 1.719 | 1.7128 | 1.7016 | 1.6955 | 1.6802 | 1.6506 | 1.6026 | 1.4036 | 1.2618 | 1.1363 | 1.0496 | 1.0485 | 1.0506 | 1.6223 | 1.611 | 1.5947 | 1.5774 | 1.5447 | 1.4886 | 1.4437 | 1.2274 | 1.0927 | 0.96615 | 0.7539 | 0.65901 | 0.60697
|  | GLEDFIELD | HT |  |  |  |  | 2.2838 | 2.2725 | 2.2531 | 2.2113 | 2.1521 | 1.9429 | 1.7389 | 1.5858 | 1.498 | 1.4225 | 1.2633 | 1.0521 | 0.85314 | 1.719 | 1.7118 | 1.7016 | 1.6955 | 1.6802 | 1.471 | 1.3067 | 1.1832 | 1.1363 | 1.0985 | 1.0353 | 1.0353 | 1.0455 | 1.6213 | 1.611 | 1.5937 | 1.5774 | 1.5468 | 1.3386 | 1.1917 | 1.061 | 0.99982 | 0.93554 | 0.78043 | 0.67125 | 0.58248
|  | GLEDFIELD | HE |  |  |  |  | 2.2838 | 2.2776 | 2.2521 | 2.2072 | 2.145 | 2.0909 | 2.0093 | 1.7684 | 1.5623 | 1.4062 | 1.246 | 1.0399 | 0.9062 | 1.719 | 1.719 | 1.6996 | 1.6945 | 1.6802 | 1.6526 | 1.6036 | 1.3985 | 1.2281 | 1.1036 | 1.0506 | 1.0475 | 1.023 | 1.6213 | 1.6161 | 1.5937 | 1.5733 | 1.5417 | 1.4845 | 1.4376 | 1.2233 | 1.0539 | 0.92737 | 0.77839 | 0.66105 | 0.59064
|  | GLEDFIELD | FB |  |  |  |  | 2.3093 | 2.3133 | 2.3093 | 2.2909 | 2.2695 | 2.245 | 2.2184 | 2.1817 | 2.0521 | 1.9389 | 1.6184 | 1.5286 | 1.494 | 1.7424 | 1.7434 | 1.7455 | 1.7414 | 1.7414 | 1.722 | 1.7026 | 1.6751 | 1.5373 | 1.42 | 1.1577 | 1.0557 | 0.9761 | 1.6447 | 1.6488 | 1.6519 | 1.6468 | 1.6417 | 1.6223 | 1.6029 | 1.5702 | 1.4355 | 1.3325 | 1.0672 | 0.94472 | 0.92737
| FORT AUGUSTUS | GLEN LAOGH | MINIMUM HEADROOM | NH 27430 00910 | YES | YES | 0 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432
|  | GLEN LAOGH | EE |  |  |  |  | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432
|  | GLEN LAOGH | HT |  |  |  |  | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432
|  | GLEN LAOGH | HE |  |  |  |  | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432
|  | GLEN LAOGH | FB |  |  |  |  | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10084 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432 | 0.10432
| KINLOCHLEVEN | GLENCOE | MINIMUM HEADROOM | NN 10658 58797 | YES | YES | 0.104 | 1.1684 | 1.1633 | 1.151 | 1.1214 | 1.1041 | 0.91429 | 0.74898 | 0.63673 | 0.53878 | 0.44898 | 0.29082 | 0.13061 | 0.028571 | 1.6878 | 1.6867 | 1.6816 | 1.6755 | 1.6643 | 1.4541 | 1.3061 | 1.2173 | 1.1561 | 1.1296 | 1.0735 | 1.0724 | 1.0163 | 1.499 | 1.4929 | 1.4847 | 1.4551 | 1.4184 | 1.2041 | 1.0663 | 0.95816 | 0.87347 | 0.81122 | 0.71837 | 0.61429 | 0.53776
|  | GLENCOE | EE |  |  |  |  | 1.1684 | 1.1633 | 1.151 | 1.1265 | 1.1112 | 1.0184 | 0.94184 | 0.75816 | 0.60306 | 0.49184 | 0.29082 | 0.13061 | 0.035714 | 1.6878 | 1.6867 | 1.6827 | 1.6755 | 1.6653 | 1.6429 | 1.5939 | 1.4143 | 1.2673 | 1.1592 | 1.0878 | 1.0816 | 1.0888 | 1.499 | 1.4929 | 1.4847 | 1.4582 | 1.4245 | 1.3755 | 1.3194 | 1.1143 | 0.96122 | 0.84796 | 0.71837 | 0.61429 | 0.55306
|  | GLENCOE | HT |  |  |  |  | 1.1694 | 1.1643 | 1.1531 | 1.1276 | 1.1102 | 0.91429 | 0.74898 | 0.63673 | 0.53878 | 0.48265 | 0.33673 | 0.16633 | 0.028571 | 1.6878 | 1.6867 | 1.6827 | 1.6755 | 1.6653 | 1.4541 | 1.3061 | 1.2173 | 1.1561 | 1.1296 | 1.0735 | 1.0724 | 1.0847 | 1.499 | 1.4939 | 1.4857 | 1.4582 | 1.4235 | 1.2041 | 1.0663 | 0.95816 | 0.87347 | 0.82959 | 0.74592 | 0.62857 | 0.53776
|  | GLENCOE | HE |  |  |  |  | 1.1694 | 1.1633 | 1.151 | 1.1214 | 1.1041 | 1.0184 | 0.93163 | 0.72755 | 0.56837 | 0.44898 | 0.32857 | 0.1398 | 0.029592 | 1.6878 | 1.6867 | 1.6816 | 1.6755 | 1.6643 | 1.6408 | 1.5918 | 1.3918 | 1.2367 | 1.1316 | 1.0878 | 1.0827 | 1.0735 | 1.499 | 1.4939 | 1.4847 | 1.4551 | 1.4184 | 1.3765 | 1.3112 | 1.0878 | 0.92551 | 0.81122 | 0.7449 | 0.62551 | 0.55612
|  | GLENCOE | FB |  |  |  |  | 1.201 | 1.2173 | 1.2306 | 1.2286 | 1.2194 | 1.2133 | 1.202 | 1.1776 | 1.0643 | 0.97245 | 0.76531 | 0.62653 | 0.57959 | 1.7 | 1.7071 | 1.7133 | 1.7122 | 1.7071 | 1.701 | 1.6969 | 1.6776 | 1.5194 | 1.4061 | 1.1867 | 1.1194 | 1.0163 | 1.5173 | 1.5296 | 1.5367 | 1.5347 | 1.5224 | 1.5163 | 1.5071 | 1.4867 | 1.349 | 1.2459 | 1.0194 | 0.94796 | 0.93367
| DUNOON | GLENDARUEL | MINIMUM HEADROOM | NN 03067 59147 | YES | YES | 0.023 | 0.29109 | 0.29007 | 0.28752 | 0.28446 | 0.2819 | 0.27527 | 0.27323 | 0.2666 | 0.25894 | 0.25741 | 0.24415 | 0.23292 | 0.22527 | 0.28672 | 0.28519 | 0.28264 | 0.28162 | 0.28059 | 0.27498 | 0.27396 | 0.26886 | 0.26325 | 0.26325 | 0.24794 | 0.24641 | 0.24386 | 0.29018 | 0.28865 | 0.28559 | 0.28355 | 0.2815 | 0.27487 | 0.27283 | 0.2662 | 0.26008 | 0.25906 | 0.2463 | 0.23814 | 0.23304
|  | GLENDARUEL | EE |  |  |  |  | 0.29109 | 0.29007 | 0.28752 | 0.28497 | 0.28241 | 0.27578 | 0.27425 | 0.2666 | 0.25946 | 0.25843 | 0.24415 | 0.23292 | 0.22629 | 0.28672 | 0.28519 | 0.28264 | 0.28162 | 0.28059 | 0.27549 | 0.27396 | 0.26886 | 0.26325 | 0.26325 | 0.24998 | 0.24947 | 0.25202 | 0.29018 | 0.28865 | 0.28559 | 0.28406 | 0.28201 | 0.27538 | 0.27334 | 0.2662 | 0.26008 | 0.25906 | 0.2463 | 0.23814 | 0.23559
|  | GLENDARUEL | HT |  |  |  |  | 0.29109 | 0.29007 | 0.28803 | 0.28446 | 0.28292 | 0.27629 | 0.27425 | 0.26813 | 0.26099 | 0.26048 | 0.24772 | 0.2365 | 0.22578 | 0.28672 | 0.28519 | 0.28264 | 0.28162 | 0.28059 | 0.27498 | 0.27396 | 0.26886 | 0.26376 | 0.26376 | 0.24794 | 0.24641 | 0.25151 | 0.29018 | 0.28865 | 0.2861 | 0.28355 | 0.28252 | 0.27589 | 0.27385 | 0.26773 | 0.26161 | 0.26059 | 0.24783 | 0.24069 | 0.23559
|  | GLENDARUEL | HE |  |  |  |  | 0.29109 | 0.29007 | 0.28752 | 0.28446 | 0.2819 | 0.27527 | 0.27323 | 0.2666 | 0.25894 | 0.25741 | 0.2467 | 0.23394 | 0.22527 | 0.28672 | 0.28519 | 0.28264 | 0.28162 | 0.28059 | 0.27498 | 0.27396 | 0.26886 | 0.26325 | 0.26325 | 0.24998 | 0.24845 | 0.24845 | 0.29018 | 0.28865 | 0.28559 | 0.28406 | 0.2815 | 0.27487 | 0.27283 | 0.26671 | 0.26059 | 0.25906 | 0.24783 | 0.23865 | 0.23304
|  | GLENDARUEL | FB |  |  |  |  | 0.29415 | 0.29466 | 0.29313 | 0.2916 | 0.28905 | 0.28803 | 0.2865 | 0.28394 | 0.28241 | 0.28139 | 0.26864 | 0.25894 | 0.25282 | 0.28978 | 0.2908 | 0.28774 | 0.2857 | 0.28468 | 0.28417 | 0.28213 | 0.27906 | 0.27753 | 0.27549 | 0.26376 | 0.25202 | 0.24386 | 0.29375 | 0.29426 | 0.2912 | 0.28967 | 0.28814 | 0.28763 | 0.28508 | 0.28355 | 0.2815 | 0.27997 | 0.26722 | 0.25446 | 0.2514
| ABERNETHY | GLENDEVON | MINIMUM HEADROOM | NO 00101 02760 | YES | YES | 1.18 | 2.9737 | 2.9451 | 2.9074 | 2.8349 | 2.84 | 2.7829 | 2.7329 | 2.6727 | 2.6033 | 2.5676 | 2.4533 | 2.3747 | 2.3278 | 2.9576 | 2.9331 | 2.9127 | 2.8709 | 2.8586 | 2.8178 | 2.7739 | 2.73 | 2.6668 | 2.628 | 2.478 | 2.4984 | 2.4943 | 2.9835 | 2.9651 | 2.9376 | 2.8825 | 2.8682 | 2.8111 | 2.7611 | 2.7019 | 2.6539 | 2.6141 | 2.4815 | 2.4539 | 2.4305
|  | GLENDEVON | EE |  |  |  |  | 2.9809 | 2.9523 | 2.9472 | 2.9033 | 2.889 | 2.8523 | 2.788 | 2.7227 | 2.6441 | 2.6125 | 2.4543 | 2.4105 | 2.4054 | 2.9617 | 2.9351 | 2.927 | 2.8943 | 2.8811 | 2.8545 | 2.7913 | 2.7423 | 2.68 | 2.6423 | 2.5147 | 2.526 | 2.5525 | 2.9876 | 2.9692 | 2.9672 | 2.9284 | 2.9162 | 2.8805 | 2.7998 | 2.7356 | 2.657 | 2.6213 | 2.4927 | 2.4825 | 2.4978
|  | GLENDEVON | HT |  |  |  |  | 2.9737 | 2.9451 | 2.9074 | 2.8349 | 2.84 | 2.7829 | 2.7329 | 2.689 | 2.6349 | 2.5911 | 2.4605 | 2.4115 | 2.3768 | 2.9586 | 2.9331 | 2.9127 | 2.8709 | 2.8586 | 2.8178 | 2.7841 | 2.7433 | 2.6831 | 2.6392 | 2.478 | 2.4984 | 2.5402 | 2.9835 | 2.9651 | 2.9376 | 2.8825 | 2.8682 | 2.8111 | 2.7641 | 2.7162 | 2.6774 | 2.6305 | 2.4815 | 2.4662 | 2.4662
|  | GLENDEVON | HE |  |  |  |  | 2.9737 | 2.9482 | 2.9298 | 2.8747 | 2.8625 | 2.8176 | 2.739 | 2.6727 | 2.6033 | 2.5676 | 2.4533 | 2.3747 | 2.3278 | 2.9576 | 2.9362 | 2.9209 | 2.8841 | 2.8719 | 2.8443 | 2.7739 | 2.73 | 2.6668 | 2.628 | 2.5035 | 2.4994 | 2.4943 | 2.9845 | 2.9662 | 2.9539 | 2.909 | 2.8968 | 2.857 | 2.7611 | 2.7019 | 2.6539 | 2.6141 | 2.4917 | 2.4539 | 2.4305
|  | GLENDEVON | FB |  |  |  |  | 3.0411 | 3.0482 | 3.0451 | 3.04 | 3.039 | 3.0135 | 2.9941 | 2.9513 | 2.9145 | 2.8951 | 2.7645 | 2.6258 | 2.6145 | 3.0015 | 3.0015 | 2.9892 | 2.9882 | 2.98 | 2.9535 | 2.9321 | 2.8954 | 2.88 | 2.8535 | 2.7198 | 2.577 | 2.5311 | 3.0427 | 3.0539 | 3.056 | 3.0549 | 3.057 | 3.0274 | 3.0111 | 2.9682 | 2.9396 | 2.9162 | 2.7784 | 2.6529 | 2.6458
| FORT AUGUSTUS | GLENDOE | MINIMUM HEADROOM | NH 40060 08894 | YES | YES | 0.493 | 7.6471 | 7.6522 | 7.6451 | 7.638 | 7.6216 | 7.4563 | 7.3451 | 7.2818 | 7.2329 | 7.2206 | 7.1635 | 7.1104 | 7.0716 | 7.2221 | 7.2262 | 7.2191 | 7.2211 | 7.2089 | 7.0762 | 6.9895 | 6.9221 | 6.8885 | 6.8844 | 6.8477 | 6.8221 | 6.7854 | 7.4974 | 7.4984 | 7.4892 | 7.4831 | 7.4647 | 7.3464 | 7.2698 | 7.2107 | 7.1729 | 7.1647 | 7.0831 | 7.0627 | 7.0321
|  | GLENDOE | EE |  |  |  |  | 7.6471 | 7.6522 | 7.6451 | 7.639 | 7.6247 | 7.5941 | 7.5757 | 7.4135 | 7.3196 | 7.2471 | 7.1635 | 7.1104 | 7.0747 | 7.2221 | 7.2262 | 7.2191 | 7.2211 | 7.2089 | 7.1987 | 7.1874 | 7.064 | 6.9711 | 6.9068 | 6.8477 | 6.8232 | 6.8109 | 7.4974 | 7.4984 | 7.4892 | 7.4831 | 7.4658 | 7.4505 | 7.4362 | 7.3209 | 7.2372 | 7.1831 | 7.0923 | 7.0627 | 7.0321
|  | GLENDOE | HT |  |  |  |  | 7.6482 | 7.6533 | 7.6461 | 7.639 | 7.6237 | 7.4563 | 7.3451 | 7.2818 | 7.2329 | 7.2206 | 7.1665 | 7.1176 | 7.0716 | 7.2221 | 7.2262 | 7.2201 | 7.2221 | 7.2089 | 7.0762 | 6.9895 | 6.9221 | 6.8885 | 6.8844 | 6.8477 | 6.8426 | 6.8374 | 7.4984 | 7.4984 | 7.4903 | 7.4831 | 7.4658 | 7.3464 | 7.2698 | 7.2107 | 7.1729 | 7.1647 | 7.0831 | 7.0852 | 7.0566
|  | GLENDOE | HE |  |  |  |  | 7.6482 | 7.6533 | 7.6461 | 7.638 | 7.6216 | 7.5961 | 7.5747 | 7.3971 | 7.2971 | 7.2267 | 7.1767 | 7.1257 | 7.0931 | 7.2221 | 7.2262 | 7.2201 | 7.2211 | 7.2089 | 7.1997 | 7.1874 | 7.0487 | 6.9517 | 6.8885 | 6.8528 | 6.8415 | 6.8201 | 7.4984 | 7.4984 | 7.4903 | 7.4831 | 7.4647 | 7.4505 | 7.4362 | 7.3096 | 7.2209 | 7.1678 | 7.0984 | 7.0882 | 7.0515
|  | GLENDOE | FB |  |  |  |  | 7.6676 | 7.6665 | 7.6686 | 7.6676 | 7.6676 | 7.6655 | 7.6594 | 7.6573 | 7.5359 | 7.4573 | 7.3063 | 7.2543 | 7.241 | 7.2364 | 7.2334 | 7.2354 | 7.2354 | 7.2313 | 7.2303 | 7.2201 | 7.2181 | 7.1119 | 7.0395 | 6.8926 | 6.8221 | 6.7854 | 7.5137 | 7.5086 | 7.5107 | 7.5056 | 7.5025 | 7.4964 | 7.4872 | 7.4852 | 7.3933 | 7.3311 | 7.2117 | 7.1321 | 7.126
| BRACO | GLENEAGLES | MINIMUM HEADROOM | NN 91540 11582 | NO | YES | 1.076 | 11.1127 | 11.4684 | 11.3643 | 11.0367 | 10.9265 | 10.3847 | 9.5051 | 8.5408 | 6.7898 | 6.1765 | 3.2776 | 0.0081633 | -2.6898 | 14.0412 | 13.8137 | 13.7545 | 13.4718 | 13.3769 | 13.0106 | 12.3188 | 11.5331 | 9.8024 | 9.2912 | 6.8514 | 3.9933 | 1.2473 | 13.1239 | 12.9127 | 12.8453 | 12.5565 | 12.4606 | 12.0065 | 11.1596 | 10.2351 | 8.3259 | 7.7269 | 4.8484 | 1.4402 | -1.5435
|  | GLENEAGLES | EE |  |  |  |  | 11.1137 | 11.4694 | 11.3643 | 11.0408 | 10.9459 | 10.4418 | 9.7306 | 8.8582 | 7.7612 | 7.248 | 4.5898 | 1.0765 | -0.34796 | 14.0422 | 13.8157 | 13.7555 | 13.481 | 13.3882 | 13.0555 | 12.5198 | 11.8055 | 10.8331 | 10.4331 | 8.6606 | 5.5841 | 4.6627 | 13.1239 | 12.9147 | 12.8453 | 12.5616 | 12.4749 | 12.0514 | 11.3871 | 10.5535 | 9.4361 | 8.9718 | 6.6127 | 3.0229 | 1.6871
|  | GLENEAGLES | HT |  |  |  |  | 11.1137 | 11.4724 | 11.3857 | 11.0408 | 10.9408 | 10.3847 | 9.5051 | 8.5408 | 7.2327 | 6.7061 | 4.2439 | 0.46224 | -2.1224 | 14.0412 | 13.8137 | 13.7555 | 13.4718 | 13.3769 | 13.0106 | 12.3188 | 11.5331 | 10.3627 | 9.9453 | 8.0535 | 4.7208 | 2.5749 | 13.1249 | 12.9147 | 12.8586 | 12.5586 | 12.4688 | 12.0065 | 11.1596 | 10.2351 | 8.8953 | 8.4167 | 6.1116 | 2.2055 | -0.52204
|  | GLENEAGLES | HE |  |  |  |  | 11.1127 | 11.4684 | 11.3724 | 11.0367 | 10.9265 | 10.4 | 9.5959 | 8.5704 | 6.7898 | 6.1765 | 3.2776 | 0.0081633 | -2.6898 | 14.0412 | 13.8137 | 13.7545 | 13.478 | 13.382 | 13.0392 | 12.4545 | 11.5759 | 9.8024 | 9.2912 | 6.8514 | 3.9933 | 1.2473 | 13.1239 | 12.9127 | 12.8504 | 12.5565 | 12.4606 | 12.0198 | 11.282 | 10.2576 | 8.3259 | 7.7269 | 4.8484 | 1.4402 | -1.5435
|  | GLENEAGLES | FB |  |  |  |  | 11.2422 | 11.7469 | 11.7612 | 11.4816 | 11.4663 | 11.4031 | 11.201 | 10.9133 | 10.1816 | 9.9316 | 8.5765 | 6.9449 | 5.9735 | 14.1382 | 14.1065 | 14.0912 | 13.7218 | 13.6759 | 13.6086 | 13.3596 | 13.0514 | 12.3045 | 12.0086 | 10.8616 | 9.3137 | 8.1065 | 13.2463 | 13.228 | 13.2147 | 12.931 | 12.9086 | 12.8453 | 12.6106 | 12.2963 | 11.5137 | 11.2371 | 9.9861 | 8.1269 | 7.3973
| RANNOCH | GLENETIVE | MINIMUM HEADROOM | NN 25850 54886 | YES | YES | 0 | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.27441 | 0.23359 | 0.20604 | 0.19584 | 0.19584 | 0.19073 | 0.18971 | 0.18563 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.23516 | 0.18516 | 0.15251 | 0.13924 | 0.13924 | 0.13414 | 0.13312 | 0.1321 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.26091 | 0.21907 | 0.1905 | 0.1803 | 0.1803 | 0.17519 | 0.17315 | 0.17009
|  | GLENETIVE | EE |  |  |  |  | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.27645 | 0.23461 | 0.20604 | 0.19073 | 0.19073 | 0.18869 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.24027 | 0.18822 | 0.15353 | 0.13414 | 0.13312 | 0.13312 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.26397 | 0.22111 | 0.19152 | 0.17519 | 0.17315 | 0.17111
|  | GLENETIVE | HT |  |  |  |  | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.27441 | 0.23359 | 0.20604 | 0.19584 | 0.19584 | 0.19073 | 0.18971 | 0.18563 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.23516 | 0.18516 | 0.15251 | 0.13924 | 0.13924 | 0.13414 | 0.13312 | 0.1321 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.26091 | 0.21907 | 0.1905 | 0.1803 | 0.1803 | 0.17519 | 0.17315 | 0.17009
|  | GLENETIVE | HE |  |  |  |  | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.34278 | 0.26829 | 0.22339 | 0.19686 | 0.19073 | 0.19073 | 0.19073 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.23006 | 0.17598 | 0.14129 | 0.13414 | 0.13312 | 0.13312 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.25581 | 0.20989 | 0.18234 | 0.17519 | 0.17315 | 0.17315
|  | GLENETIVE | FB |  |  |  |  | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.3438 | 0.28869 | 0.25502 | 0.19788 | 0.19788 | 0.19073 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.32088 | 0.25455 | 0.21169 | 0.13924 | 0.13924 | 0.1321 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.33234 | 0.27621 | 0.2405 | 0.18132 | 0.17417 | 0.17417
| FORT WILLIAM | GLENUIG | MINIMUM HEADROOM | NM 67224 77119 | YES | NO | 0 | 0.075143 | 0.073102 | 0.075143 | 0.068 | 0.063918 | 0.058816 | 0.055755 | 0.049633 | 0.046571 | 0.040449 | 0.035347 | 0.024122 | 0.022082 | 0.073286 | 0.073286 | 0.073286 | 0.070224 | 0.068184 | 0.065122 | 0.064102 | 0.061041 | 0.05798 | 0.055939 | 0.050837 | 0.048796 | 0.047776 | 0.076765 | 0.075745 | 0.075745 | 0.069622 | 0.066561 | 0.061459 | 0.059418 | 0.055337 | 0.051255 | 0.048194 | 0.042071 | 0.035949 | 0.033908
|  | GLENUIG | EE |  |  |  |  | 0.083306 | 0.073102 | 0.075143 | 0.068 | 0.064939 | 0.058816 | 0.055755 | 0.050653 | 0.047592 | 0.04249 | 0.035347 | 0.024122 | 0.023102 | 0.081449 | 0.073286 | 0.074306 | 0.070224 | 0.069204 | 0.065122 | 0.064102 | 0.061041 | 0.05798 | 0.055939 | 0.050837 | 0.049816 | 0.049816 | 0.082888 | 0.075745 | 0.076765 | 0.070643 | 0.067582 | 0.06248 | 0.059418 | 0.056357 | 0.053296 | 0.048194 | 0.042071 | 0.035949 | 0.034929
|  | GLENUIG | HT |  |  |  |  | 0.083306 | 0.078204 | 0.075143 | 0.068 | 0.064939 | 0.059837 | 0.056776 | 0.051673 | 0.048612 | 0.04351 | 0.037388 | 0.027184 | 0.023102 | 0.081449 | 0.076347 | 0.074306 | 0.070224 | 0.069204 | 0.065122 | 0.064102 | 0.061041 | 0.05798 | 0.055939 | 0.050837 | 0.048796 | 0.048796 | 0.082888 | 0.078806 | 0.076765 | 0.070643 | 0.067582 | 0.0635 | 0.060439 | 0.057378 | 0.053296 | 0.049214 | 0.045133 | 0.03799 | 0.035949
|  | GLENUIG | HE |  |  |  |  | 0.083306 | 0.073102 | 0.075143 | 0.068 | 0.063918 | 0.058816 | 0.055755 | 0.049633 | 0.046571 | 0.040449 | 0.035347 | 0.027184 | 0.022082 | 0.081449 | 0.073286 | 0.073286 | 0.070224 | 0.068184 | 0.065122 | 0.064102 | 0.061041 | 0.05798 | 0.055939 | 0.050837 | 0.049816 | 0.048796 | 0.082888 | 0.075745 | 0.075745 | 0.069622 | 0.066561 | 0.061459 | 0.059418 | 0.055337 | 0.051255 | 0.048194 | 0.043092 | 0.03799 | 0.033908
|  | GLENUIG | FB |  |  |  |  | 0.075143 | 0.077184 | 0.076163 | 0.074122 | 0.073102 | 0.075143 | 0.073102 | 0.065959 | 0.063918 | 0.062898 | 0.055755 | 0.050653 | 0.047592 | 0.073286 | 0.075327 | 0.073286 | 0.073286 | 0.072265 | 0.073286 | 0.072265 | 0.066143 | 0.064102 | 0.063082 | 0.056959 | 0.052878 | 0.047776 | 0.076765 | 0.078806 | 0.076765 | 0.076765 | 0.074724 | 0.076765 | 0.074724 | 0.068602 | 0.065541 | 0.065541 | 0.058398 | 0.052276 | 0.052276
| BRORA | GOLSPIE | MINIMUM HEADROOM | NC 82996 00240 | YES | NO | 0.251 | 0.98469 | 0.98673 | 0.98265 | 0.95816 | 0.90408 | 0.64796 | 0.24082 | -0.084694 | -0.27041 | -0.31429 | -0.57449 | -0.82245 | -1 | 1.7704 | 1.7745 | 1.7724 | 1.7622 | 1.7439 | 1.401 | 1.0153 | 0.72041 | 0.58163 | 0.56429 | 0.46735 | 0.42857 | 0.40714 | 1.4643 | 1.4663 | 1.4622 | 1.4276 | 1.3735 | 1.0857 | 0.71122 | 0.42143 | 0.26633 | 0.23265 | 0.069388 | -0.11633 | -0.22653
|  | GOLSPIE | EE |  |  |  |  | 0.98571 | 0.98673 | 0.98265 | 0.95918 | 0.90612 | 0.85 | 0.75714 | 0.50306 | 0.090816 | -0.20204 | -0.57449 | -0.82245 | -0.96837 | 1.7704 | 1.7745 | 1.7724 | 1.7622 | 1.7459 | 1.7265 | 1.6898 | 1.3582 | 0.96327 | 0.67755 | 0.48061 | 0.43673 | 0.44286 | 1.4643 | 1.4663 | 1.4622 | 1.4286 | 1.3735 | 1.3265 | 1.2663 | 1.002 | 0.61939 | 0.34286 | 0.069388 | -0.11633 | -0.2102
|  | GOLSPIE | HT |  |  |  |  | 0.98469 | 0.98776 | 0.98571 | 0.95816 | 0.90408 | 0.64796 | 0.24082 | -0.084694 | -0.27041 | -0.31429 | -0.52755 | -0.80306 | -1 | 1.7714 | 1.7745 | 1.7724 | 1.7622 | 1.7439 | 1.401 | 1.0153 | 0.72041 | 0.58163 | 0.56429 | 0.46735 | 0.42857 | 0.44388 | 1.4643 | 1.4663 | 1.4633 | 1.4276 | 1.3735 | 1.0857 | 0.71122 | 0.42143 | 0.26633 | 0.23265 | 0.082653 | -0.10102 | -0.22653
|  | GOLSPIE | HE |  |  |  |  | 0.98571 | 0.98776 | 0.98571 | 0.9602 | 0.90714 | 0.84592 | 0.75306 | 0.46735 | 0.014286 | -0.3 | -0.52347 | -0.79592 | -0.89184 | 1.7724 | 1.7745 | 1.7724 | 1.7622 | 1.7449 | 1.7265 | 1.6898 | 1.3214 | 0.89082 | 0.58776 | 0.48571 | 0.43878 | 0.46122 | 1.4643 | 1.4663 | 1.4622 | 1.4286 | 1.3745 | 1.3235 | 1.2653 | 0.96429 | 0.54898 | 0.25408 | 0.095918 | -0.10204 | -0.14694
|  | GOLSPIE | FB |  |  |  |  | 1.0143 | 1.0286 | 1.0388 | 1.0265 | 1.0173 | 1.0031 | 0.97143 | 0.94898 | 0.74796 | 0.52551 | -0.10204 | -0.24082 | -0.29796 | 1.7878 | 1.7939 | 1.7969 | 1.7908 | 1.7929 | 1.7827 | 1.7592 | 1.7439 | 1.4714 | 1.1786 | 0.57857 | 0.47143 | 0.40714 | 1.4827 | 1.4949 | 1.498 | 1.4786 | 1.4663 | 1.4531 | 1.4184 | 1.4 | 1.1755 | 0.90816 | 0.33469 | 0.21633 | 0.19388
| BURGHMUIR | GOODLYBURN | MINIMUM HEADROOM | NO 10084 24586 | NO | YES | 1.654 | 2.5233 | 2.459 | 2.3723 | 2.1641 | 1.9458 | 1.5284 | 0.14983 | -1.3308 | -3.7859 | -4.3369 | -8.894 | -17.7206 | -24.5379 | 4.8483 | 4.8473 | 4.8065 | 4.7299 | 4.631 | 4.4187 | 3.0024 | 1.1422 | -1.7201 | -2.3303 | -6.5374 | -15.9507 | -23.6711 | 3.8853 | 3.8169 | 3.7149 | 3.5526 | 3.3628 | 3.0118 | 1.4771 | -0.17287 | -3.0749 | -3.677 | -8.6657 | -18.8974 | -27.028
|  | GOODLYBURN | EE |  |  |  |  | 2.5233 | 2.459 | 2.3723 | 2.1641 | 1.9458 | 1.5437 | 0.58759 | -0.75731 | -2.7869 | -3.29 | -7.5838 | -15.9002 | -19.6951 | 4.8524 | 4.8473 | 4.8116 | 4.7432 | 4.6432 | 4.4432 | 3.5412 | 1.885 | -0.47925 | -1.0292 | -4.8537 | -13.5578 | -17.5578 | 3.8853 | 3.8169 | 3.7149 | 3.5526 | 3.3628 | 3.022 | 2.0077 | 0.52815 | -1.8321 | -2.4065 | -7.0576 | -16.5239 | -20.7433
|  | GOODLYBURN | HT |  |  |  |  | 2.5376 | 2.4947 | 2.4141 | 2.1845 | 1.9519 | 1.5284 | 0.14983 | -1.3308 | -3.7859 | -4.3369 | -8.894 | -17.7206 | -24.5379 | 4.8503 | 4.8503 | 4.8065 | 4.7299 | 4.631 | 4.4187 | 3.0024 | 1.1697 | -1.7201 | -2.3303 | -6.5374 | -15.9507 | -23.6711 | 3.9016 | 3.8547 | 3.7628 | 3.5761 | 3.371 | 3.0118 | 1.4771 | -0.17287 | -3.0749 | -3.677 | -8.6657 | -18.8974 | -27.028
|  | GOODLYBURN | HE |  |  |  |  | 2.5304 | 2.4784 | 2.3978 | 2.1764 | 1.9498 | 1.5958 | 0.63759 | -1.1991 | -1.5604 | -2.4889 | -8.2379 | -15.7359 | -22.9655 | 4.8483 | 4.8473 | 4.8105 | 4.7381 | 4.6401 | 4.4371 | 3.4687 | 1.1422 | 0.7881 | -0.28027 | -6.5231 | -14.919 | -23.4946 | 3.8924 | 3.8384 | 3.7455 | 3.5669 | 3.3679 | 3.0557 | 2.0077 | -0.11777 | -0.42695 | -1.4841 | -8.2535 | -17.0851 | -25.7167
|  | GOODLYBURN | FB |  |  |  |  | 2.6692 | 2.6151 | 2.607 | 2.5896 | 2.5264 | 2.4029 | 1.8223 | 1.1743 | -0.28588 | -0.77772 | -2.1838 | -4.5359 | -7.3502 | 4.9371 | 4.9167 | 4.934 | 4.9544 | 4.9442 | 4.8861 | 4.2616 | 3.5605 | 1.8371 | 1.1463 | -0.85476 | -3.9874 | -7.2782 | 4.0281 | 3.9588 | 3.9506 | 3.9241 | 3.8649 | 3.7679 | 3.0904 | 2.323 | 0.56182 | -0.00042245 | -1.4923 | -5.0321 | -7.2545
| CHARLESTON | GOURDIE | MINIMUM HEADROOM | NO 34573 32203 | YES | YES | 3.691 | 1.4085 | 1.1871 | 0.99319 | 0.71972 | 0.42788 | 0.13809 | -0.015996 | -0.21498 | -0.36191 | -0.3711 | -0.6711 | -0.89151 | -1.067 | 1.6731 | 1.3833 | 1.1252 | 0.82313 | 0.42619 | 0.043535 | -0.036057 | -0.14014 | -0.20647 | -0.21565 | -0.39626 | -0.37687 | -0.3983 | 1.7138 | 1.4974 | 1.2995 | 1.0413 | 0.73112 | 0.39948 | 0.28418 | 0.16173 | 0.062749 | 0.056627 | -0.18113 | -0.33317 | -0.44031
|  | GOURDIE | EE |  |  |  |  | 1.5544 | 1.1881 | 1.0075 | 0.78809 | 0.50033 | 0.15135 | 0.057473 | -0.085384 | -0.24865 | -0.23844 | -0.666 | -0.8762 | -1.067 | 1.8425 | 1.3833 | 1.1333 | 0.85884 | 0.46088 | 0.058841 | -0.010547 | -0.089118 | -0.17483 | -0.16871 | -0.36259 | -0.37381 | -0.3983 | 1.8474 | 1.4974 | 1.3066 | 1.0811 | 0.77193 | 0.42397 | 0.32499 | 0.21581 | 0.12295 | 0.13826 | -0.17501 | -0.31378 | -0.44031
|  | GOURDIE | HT |  |  |  |  | 1.4697 | 1.1983 | 0.99319 | 0.71972 | 0.42788 | 0.33502 | 0.21768 | 0.018698 | -0.1211 | -0.20987 | -0.65579 | -0.83436 | -0.95987 | 1.7435 | 1.3986 | 1.1252 | 0.82313 | 0.42619 | 0.38537 | 0.30986 | 0.20272 | 0.098637 | -0.021771 | -0.39626 | -0.37687 | -0.34116 | 1.7679 | 1.5097 | 1.2995 | 1.0413 | 0.73112 | 0.66071 | 0.55765 | 0.41275 | 0.31785 | 0.22908 | -0.17501 | -0.28215 | -0.34746
|  | GOURDIE | HE |  |  |  |  | 1.4085 | 1.1871 | 1.0044 | 0.76053 | 0.46666 | 0.13809 | -0.015996 | -0.21498 | -0.36191 | -0.3711 | -0.6711 | -0.89151 | -1.0191 | 1.6731 | 1.3844 | 1.1303 | 0.84456 | 0.44864 | 0.043535 | -0.036057 | -0.14014 | -0.20647 | -0.21565 | -0.36769 | -0.37687 | -0.39524 | 1.7138 | 1.4974 | 1.3046 | 1.0638 | 0.75459 | 0.39948 | 0.28418 | 0.16173 | 0.062749 | 0.056627 | -0.18113 | -0.33317 | -0.42297
|  | GOURDIE | FB |  |  |  |  | 1.9024 | 1.5758 | 1.3279 | 1.1769 | 0.9289 | 0.61666 | 0.44931 | 0.30237 | 0.21666 | 0.1789 | -0.019057 | -0.33538 | -0.41702 | 2.2109 | 1.8211 | 1.4803 | 1.2803 | 0.93027 | 0.52007 | 0.29047 | 0.14558 | 0.095576 | 0.061902 | -0.089118 | -0.31667 | -0.3932 | 2.1648 | 1.8801 | 1.627 | 1.4668 | 1.1985 | 0.86785 | 0.69132 | 0.55561 | 0.50152 | 0.46581 | 0.30969 | 0.0086673 | -0.032149
| BOAT OF GARTEN | GRANTOWN | MINIMUM HEADROOM | NJ 03670 26311 | NO | YES | 0.777 | 4.8706 | 4.892 | 4.8767 | 4.8349 | 4.6747 | 4.2104 | 4.0043 | 3.6992 | 3.4247 | 3.1818 | 2.4471 | 1.8727 | 1.6073 | 7.4941 | 7.4859 | 7.4696 | 7.4451 | 7.4002 | 7.0227 | 6.8859 | 6.6788 | 6.4645 | 6.3135 | 5.7563 | 5.5951 | 5.5951 | 6.3492 | 6.3502 | 6.3288 | 6.2859 | 6.2227 | 5.788 | 5.6012 | 5.3227 | 5.0798 | 4.8614 | 4.1706 | 3.7767 | 3.6584
|  | GRANTOWN | EE |  |  |  |  | 4.8706 | 4.892 | 4.8767 | 4.8461 | 4.6951 | 4.2257 | 4.0369 | 3.7604 | 3.4359 | 3.2227 | 2.4471 | 1.8727 | 1.6073 | 7.4941 | 7.4859 | 7.4696 | 7.4461 | 7.4022 | 7.0257 | 6.8931 | 6.7033 | 6.4645 | 6.3135 | 5.8002 | 5.5951 | 5.5951 | 6.3492 | 6.3502 | 6.3288 | 6.2859 | 6.2339 | 5.7982 | 5.6278 | 5.3767 | 5.0798 | 4.8798 | 4.1706 | 3.7767 | 3.6584
|  | GRANTOWN | HT |  |  |  |  | 4.8747 | 4.8941 | 4.8818 | 4.8482 | 4.6951 | 4.2798 | 4.0849 | 3.8237 | 3.5043 | 3.29 | 2.5186 | 2.1094 | 1.7155 | 7.4951 | 7.4859 | 7.4706 | 7.4482 | 7.4012 | 7.0482 | 6.9155 | 6.7431 | 6.5073 | 6.3482 | 5.7563 | 5.7563 | 5.838 | 6.3522 | 6.3512 | 6.3329 | 6.29 | 6.2339 | 5.838 | 5.6645 | 5.4329 | 5.1349 | 4.9318 | 4.189 | 3.9308 | 3.7604
|  | GRANTOWN | HE |  |  |  |  | 4.8737 | 4.8941 | 4.8818 | 4.8349 | 4.6747 | 4.2104 | 4.0043 | 3.6992 | 3.4247 | 3.1818 | 2.6237 | 2.1961 | 1.9002 | 7.4941 | 7.4859 | 7.4706 | 7.4451 | 7.4002 | 7.0227 | 6.8859 | 6.6788 | 6.5073 | 6.3461 | 5.9318 | 5.8839 | 5.8237 | 6.3512 | 6.3512 | 6.3318 | 6.3022 | 6.2227 | 5.788 | 5.6012 | 5.3227 | 5.0818 | 4.8614 | 4.3216 | 4.0818 | 3.9247
|  | GRANTOWN | FB |  |  |  |  | 4.9676 | 5.0267 | 5.0614 | 5.0614 | 5.0298 | 4.9951 | 4.9247 | 4.839 | 4.7533 | 4.8033 | 4.4288 | 3.988 | 3.3727 | 7.5655 | 7.5951 | 7.6053 | 7.5941 | 7.5829 | 7.5471 | 7.4829 | 7.4155 | 7.3329 | 7.3686 | 7.0431 | 6.54 | 5.7114 | 6.4431 | 6.4859 | 6.5012 | 6.4982 | 6.49 | 6.4747 | 6.4155 | 6.3329 | 6.2461 | 6.289 | 5.9196 | 5.4369 | 4.8951
| SHETLAND | GREMISTA | MINIMUM HEADROOM | HU4646842756 | NO | YES | 0 | 19.9241 | 19.1037 | 18.1873 | 17.1394 | 16.1476 | 14.9537 | 13.7618 | 12.5812 | 12.0608 | 11.671 | 10.2312 | 9.0924 | 8.5088 | 18.5302 | 17.6924 | 16.7741 | 15.9057 | 15.0486 | 14.0669 | 13.0955 | 12.1445 | 11.8782 | 11.5894 | 10.5894 | 10.1435 | 9.8455 | 19.6169 | 18.8914 | 18.0873 | 17.1924 | 16.3016 | 15.2241 | 14.1792 | 13.1353 | 12.7312 | 12.3914 | 10.6435 | 9.2241 | 8.8547
|  | GREMISTA | EE |  |  |  |  | 19.9496 | 19.1047 | 18.1884 | 17.1496 | 16.1527 | 14.9537 | 13.768 | 12.5965 | 12.0873 | 11.6914 | 10.2578 | 9.1476 | 8.5833 | 18.5547 | 17.6945 | 16.7751 | 15.918 | 15.0608 | 14.068 | 13.1118 | 12.1608 | 11.9027 | 11.5945 | 10.6731 | 10.1669 | 9.8455 | 19.6424 | 18.8914 | 18.0884 | 17.1976 | 16.3047 | 15.2241 | 14.1792 | 13.1404 | 12.7435 | 12.3935 | 10.6873 | 9.2241 | 8.8547
|  | GREMISTA | HT |  |  |  |  | 19.9343 | 19.119 | 18.2016 | 17.1476 | 16.1537 | 15.068 | 14.0027 | 12.822 | 12.2333 | 11.7169 | 10.2312 | 9.0924 | 8.5088 | 18.5424 | 17.7006 | 16.7782 | 15.9057 | 15.0486 | 14.1812 | 13.3455 | 12.3863 | 12.0547 | 11.619 | 10.5894 | 10.1435 | 10.2108 | 19.6292 | 18.9006 | 18.0965 | 17.1965 | 16.3067 | 15.3435 | 14.42 | 13.372 | 12.9027 | 12.4139 | 10.6435 | 9.2629 | 9.1006
|  | GREMISTA | HE |  |  |  |  | 19.9241 | 19.1037 | 18.1873 | 17.1394 | 16.1476 | 14.9598 | 13.7618 | 12.5812 | 12.0608 | 11.671 | 10.3322 | 9.3455 | 8.8139 | 18.5302 | 17.6924 | 16.7741 | 15.9129 | 15.0516 | 14.0669 | 13.0955 | 12.1445 | 11.8782 | 11.5894 | 10.722 | 10.5353 | 10.5578 | 19.6169 | 18.8914 | 18.0873 | 17.1924 | 16.3016 | 15.2322 | 14.1812 | 13.1353 | 12.7312 | 12.3914 | 10.8353 | 9.9935 | 9.8027
|  | GREMISTA | FB |  |  |  |  | 20.1618 | 19.4149 | 18.6302 | 18.0006 | 17.2618 | 16.4792 | 15.6782 | 14.7976 | 14.6292 | 14.4618 | 13.4659 | 12.2424 | 11.5251 | 18.722 | 17.9251 | 17.0935 | 16.4435 | 15.6965 | 14.8924 | 14.0904 | 13.1935 | 13.068 | 12.918 | 12.1618 | 11.171 | 9.8567 | 19.8322 | 19.1792 | 18.4843 | 17.9078 | 17.2098 | 16.4843 | 15.722 | 14.8833 | 14.7312 | 14.5741 | 13.6771 | 11.7384 | 10.7639
| WILLOWDALE | GREYFRIARS | MINIMUM HEADROOM | NJ 94327 07070 | NO | NO | 4.685 | 11.135 | 11.0044 | 10.6401 | 10.3626 | 10.0707 | 9.5228 | 9.1534 | 8.5687 | 8.3085 | 7.8095 | 5.1064 | 2.7064 | 1.5432 | 13.2528 | 13.114 | 12.7497 | 12.5028 | 12.1895 | 11.7405 | 11.4018 | 10.8252 | 10.5926 | 10.0732 | 8.2099 | 5.5987 | 1.714 | 12.4762 | 12.3609 | 12.0058 | 11.7477 | 11.4405 | 10.9334 | 10.5844 | 9.9956 | 9.763 | 9.2528 | 6.8885 | 4.7426 | 3.7497
|  | GREYFRIARS | EE |  |  |  |  | 11.135 | 11.0871 | 10.7034 | 10.4258 | 10.135 | 9.5228 | 9.1534 | 8.5687 | 8.3085 | 7.8911 | 5.1064 | 2.7064 | 1.5432 | 13.2609 | 13.1722 | 12.8058 | 12.562 | 12.2518 | 11.7405 | 11.4018 | 10.8252 | 10.5926 | 10.1793 | 8.2099 | 6.4732 | 5.1395 | 12.4762 | 12.416 | 12.0446 | 11.7885 | 11.4864 | 10.9334 | 10.5844 | 9.9956 | 9.763 | 9.3538 | 6.8885 | 4.7426 | 3.7497
|  | GREYFRIARS | HT |  |  |  |  | 11.1462 | 11.0044 | 10.6401 | 10.3626 | 10.0707 | 9.5809 | 9.282 | 8.6718 | 8.4034 | 7.8095 | 5.4646 | 3.4309 | 2.8677 | 13.2609 | 13.114 | 12.7497 | 12.5028 | 12.1895 | 11.7671 | 11.4834 | 10.8915 | 10.6599 | 10.0732 | 8.665 | 7.5456 | 7.2415 | 12.4875 | 12.3609 | 12.0058 | 11.7477 | 11.4405 | 10.9895 | 10.6977 | 10.0895 | 9.8466 | 9.2528 | 7.2222 | 5.4915 | 5.0558
|  | GREYFRIARS | HE |  |  |  |  | 11.1381 | 11.0962 | 10.8095 | 10.6218 | 10.334 | 9.8983 | 9.6003 | 8.9697 | 8.6544 | 8.3115 | 5.8166 | 4.3656 | 3.5758 | 13.263 | 13.1752 | 12.8548 | 12.6518 | 12.3405 | 11.9028 | 11.6099 | 10.9824 | 10.6834 | 10.3456 | 8.3079 | 7.1313 | 6.0609 | 12.4773 | 12.4201 | 12.114 | 11.9232 | 11.6211 | 11.1885 | 10.8946 | 10.265 | 9.9671 | 9.6344 | 7.3854 | 6.2171 | 5.5671
|  | GREYFRIARS | FB |  |  |  |  | 11.2075 | 11.2707 | 11.232 | 11.1513 | 11.1473 | 10.9993 | 10.8646 | 10.586 | 10.2636 | 10.0911 | 8.6166 | 5.9105 | 3.9687 | 13.2528 | 13.2211 | 13.0864 | 12.9354 | 12.8426 | 12.6079 | 12.3813 | 12.0222 | 11.6191 | 11.3579 | 9.3793 | 5.5987 | 1.714 | 12.5436 | 12.5956 | 12.5436 | 12.4497 | 12.4364 | 12.3038 | 12.1793 | 11.9058 | 11.5885 | 11.4201 | 9.9915 | 7.3956 | 5.6793
| SHETLAND | GUTCHER | MINIMUM HEADROOM | HU5453899599 | YES | YES | 0.427 | 0.12044 | 0.11432 | 0.11024 | 0.084731 | 0.0582 | 0.03269 | 0.0010571 | -0.01629 | -0.033637 | -0.046902 | -0.10609 | -0.15302 | -0.19078 | 0.29596 | 0.29391 | 0.29391 | 0.29085 | 0.28269 | 0.27657 | 0.2633 | 0.24596 | 0.24187 | 0.23371 | 0.18881 | 0.19085 | 0.1684 | 0.16432 | 0.16228 | 0.15922 | 0.148 | 0.13065 | 0.11432 | 0.090853 | 0.062282 | 0.047996 | 0.037792 | -0.014249 | -0.013229 | -0.030576
|  | GUTCHER | EE |  |  |  |  | 0.12044 | 0.11534 | 0.11024 | 0.086771 | 0.067384 | 0.03371 | 0.0010571 | -0.00098367 | -0.033637 | -0.046902 | -0.10609 | -0.15302 | -0.18772 | 0.29596 | 0.29493 | 0.29493 | 0.29187 | 0.28983 | 0.27657 | 0.2633 | 0.25718 | 0.24187 | 0.23371 | 0.198 | 0.198 | 0.19698 | 0.16636 | 0.16228 | 0.15922 | 0.14902 | 0.13983 | 0.11534 | 0.090853 | 0.073506 | 0.047996 | 0.037792 | -0.014249 | -0.010167 | -0.020371
|  | GUTCHER | HT |  |  |  |  | 0.12044 | 0.11636 | 0.11024 | 0.087792 | 0.069424 | 0.040853 | 0.011261 | -0.01629 | -0.020371 | -0.035678 | -0.087718 | -0.14588 | -0.19078 | 0.29596 | 0.29698 | 0.29391 | 0.29085 | 0.28983 | 0.27759 | 0.26534 | 0.2582 | 0.24289 | 0.23473 | 0.18881 | 0.19085 | 0.19493 | 0.16636 | 0.16636 | 0.16024 | 0.14902 | 0.14391 | 0.11738 | 0.094935 | 0.079629 | 0.05718 | 0.044935 | -0.0081265 | -0.011188 | -0.027514
|  | GUTCHER | HE |  |  |  |  | 0.12044 | 0.11432 | 0.11024 | 0.084731 | 0.0582 | 0.03269 | 0.0041184 | -0.0050653 | -0.027514 | -0.04282 | -0.087718 | -0.14486 | -0.18364 | 0.29596 | 0.29391 | 0.29493 | 0.29187 | 0.28269 | 0.27759 | 0.26534 | 0.24596 | 0.24187 | 0.23575 | 0.198 | 0.19187 | 0.18371 | 0.16432 | 0.1633 | 0.16228 | 0.148 | 0.13065 | 0.11432 | 0.092894 | 0.062282 | 0.051057 | 0.040853 | -0.0040449 | -0.013229 | -0.030576
|  | GUTCHER | FB |  |  |  |  | 0.13779 | 0.13473 | 0.13575 | 0.13473 | 0.13269 | 0.12759 | 0.12147 | 0.1184 | 0.11432 | 0.10616 | 0.074527 | 0.022486 | 0.0061592 | 0.3133 | 0.31024 | 0.31228 | 0.31228 | 0.31228 | 0.3082 | 0.30106 | 0.29698 | 0.29289 | 0.28371 | 0.25616 | 0.19902 | 0.1684 | 0.18575 | 0.18371 | 0.18473 | 0.18677 | 0.18983 | 0.18473 | 0.17759 | 0.17555 | 0.16942 | 0.16228 | 0.13065 | 0.065343 | 0.05922
| THURSO | HALKIRK | MINIMUM HEADROOM | ND 13246 58223 | YES | NO | 0.273 | 5.385 | 6.1176 | 6.0808 | 6.0186 | 5.9124 | 5.7431 | 5.5502 | 5.3043 | 5.0655 | 4.9329 | 4.5492 | 4.2033 | 3.9441 | 5.6068 | 6.9186 | 6.9022 | 6.8808 | 6.842 | 6.7461 | 6.6369 | 6.5604 | 6.4798 | 6.4135 | 6.2645 | 6.24 | 6.1114 | 5.575 | 6.5931 | 6.5624 | 6.5043 | 6.4431 | 6.3073 | 6.1553 | 6.0033 | 5.8216 | 5.7155 | 5.4298 | 5.2359 | 5.0798
|  | HALKIRK | EE |  |  |  |  | 5.385 | 6.1176 | 6.0808 | 6.0237 | 5.9247 | 5.7859 | 5.5818 | 5.3492 | 5.1206 | 5.0012 | 4.5492 | 4.2033 | 3.9441 | 5.6068 | 6.9186 | 6.9022 | 6.8818 | 6.8431 | 6.8012 | 6.7186 | 6.6084 | 6.4961 | 6.4257 | 6.2645 | 6.2522 | 6.2318 | 5.575 | 6.5931 | 6.5635 | 6.5094 | 6.4492 | 6.3553 | 6.2114 | 6.0318 | 5.8584 | 5.7604 | 5.4298 | 5.2359 | 5.0798
|  | HALKIRK | HT |  |  |  |  | 5.385 | 6.1186 | 6.0808 | 6.0257 | 5.9329 | 5.7431 | 5.5502 | 5.3798 | 5.2145 | 5.0757 | 4.7747 | 4.3553 | 3.9492 | 5.6068 | 6.9186 | 6.9022 | 6.8818 | 6.8441 | 6.7461 | 6.6369 | 6.5604 | 6.4798 | 6.4135 | 6.3359 | 6.3471 | 6.2604 | 5.575 | 6.5941 | 6.5635 | 6.5084 | 6.4553 | 6.3073 | 6.1553 | 6.0267 | 5.8992 | 5.791 | 5.6053 | 5.342 | 5.0839
|  | HALKIRK | HE |  |  |  |  | 5.3871 | 6.1186 | 6.0808 | 6.0186 | 5.9124 | 5.7686 | 5.5584 | 5.3043 | 5.0655 | 4.9329 | 4.641 | 4.2676 | 4.0155 | 5.6099 | 6.9196 | 6.9022 | 6.8808 | 6.842 | 6.8012 | 6.7237 | 6.5992 | 6.49 | 6.4135 | 6.2676 | 6.24 | 6.19 | 5.576 | 6.5941 | 6.5624 | 6.5043 | 6.4431 | 6.3471 | 6.1961 | 6.0033 | 5.8216 | 5.7155 | 5.4737 | 5.2665 | 5.1063
|  | HALKIRK | FB |  |  |  |  | 5.432 | 6.1931 | 6.1849 | 6.1859 | 6.1624 | 6.1308 | 6.0869 | 6.0829 | 5.9951 | 5.9227 | 5.5522 | 5.3298 | 5.2492 | 5.6364 | 6.9604 | 6.9502 | 6.9594 | 6.941 | 6.9206 | 6.8808 | 6.8614 | 6.7757 | 6.7043 | 6.4584 | 6.2492 | 6.1114 | 5.6158 | 6.6563 | 6.6461 | 6.6482 | 6.6257 | 6.6002 | 6.5594 | 6.541 | 6.4522 | 6.3808 | 6.0961 | 5.8747 | 5.842
| ABERNETHY | HARBOUR | MINIMUM HEADROOM | NO 11948 22049 | NO | YES | 2.03 | 18.0206 | 17.9635 | 17.8767 | 17.7033 | 17.4084 | 16.8186 | 15.6563 | 14.0655 | 10.6992 | 9.6686 | 4.8757 | -1.1804 | -6.9018 | 19.7339 | 19.6971 | 19.6349 | 19.541 | 19.3931 | 19.1084 | 17.9237 | 16.2859 | 12.4135 | 11.3716 | 6.4716 | -0.24878 | -6.9529 | 19.1829 | 19.1247 | 19.0512 | 18.9053 | 18.6788 | 17.9941 | 16.6951 | 14.942 | 10.9543 | 9.8318 | 4.4849 | -2.6008 | -9.4396
|  | HARBOUR | EE |  |  |  |  | 18.0216 | 17.9655 | 17.8982 | 17.742 | 17.4655 | 16.8563 | 16.0635 | 14.5778 | 12.7441 | 12.188 | 8.4431 | 1.9124 | -0.99776 | 19.7349 | 19.7012 | 19.6502 | 19.5655 | 19.4196 | 19.1165 | 18.388 | 16.938 | 14.9808 | 14.5206 | 11.3829 | 4.4288 | 1.3961 | 19.1839 | 19.1247 | 19.0645 | 18.9329 | 18.7206 | 18.0104 | 17.1676 | 15.5778 | 13.5022 | 12.9635 | 9.1604 | 1.6859 | -1.5488
|  | HARBOUR | HT |  |  |  |  | 18.0216 | 17.9645 | 17.8767 | 17.7033 | 17.4084 | 16.8186 | 15.6563 | 14.0839 | 11.938 | 11.3165 | 7.4594 | 0.38184 | -5.0498 | 19.7339 | 19.6971 | 19.6349 | 19.541 | 19.3931 | 19.1084 | 17.9237 | 16.3543 | 13.9737 | 13.4461 | 10.04 | 2.4063 | -3.7284 | 19.1839 | 19.1257 | 19.0512 | 18.9053 | 18.6788 | 17.9941 | 16.6951 | 14.991 | 12.5063 | 11.8951 | 7.9022 | -0.29367 | -6.7467
|  | HARBOUR | HE |  |  |  |  | 18.0206 | 17.9635 | 17.8839 | 17.7124 | 17.439 | 16.8604 | 15.9665 | 14.0655 | 10.6992 | 9.6686 | 4.8757 | -1.1804 | -6.9018 | 19.7349 | 19.7002 | 19.6431 | 19.5533 | 19.4084 | 19.1237 | 18.2757 | 16.2859 | 12.4135 | 11.3716 | 6.4716 | -0.24878 | -6.9529 | 19.1829 | 19.1257 | 19.0533 | 18.9104 | 18.7022 | 18.0216 | 17.0614 | 14.942 | 10.9543 | 9.8318 | 4.4849 | -2.6008 | -9.4396
|  | HARBOUR | FB |  |  |  |  | 18.0829 | 18.092 | 18.0951 | 18.0196 | 17.9798 | 17.8829 | 17.4288 | 16.8594 | 15.6257 | 15.2349 | 13.3982 | 10.9992 | 8.8941 | 19.7686 | 19.7788 | 19.7818 | 19.738 | 19.7043 | 19.6247 | 19.1084 | 18.4859 | 17.1043 | 16.6227 | 14.79 | 12.3278 | 9.9573 | 19.2369 | 19.242 | 19.2349 | 19.1727 | 19.1308 | 19.038 | 18.5084 | 17.8665 | 16.3329 | 15.8043 | 13.8676 | 10.7788 | 9.1206
| ARDMORE | HARRIS GRID | MINIMUM HEADROOM | NG 13500 94249 | YES | YES | 0 | 35.398 | 35.2255 | 35.2235 | 35.2153 | 35.2051 | 35.1867 | 35.1735 | 35.1551 | 35.1449 | 35.1316 | 35.098 | 35.0898 | 35.0663 | 32.6939 | 32.5204 | 32.5224 | 32.5204 | 32.5194 | 32.5194 | 32.5112 | 32.5061 | 32.5051 | 32.4949 | 32.4633 | 32.4582 | 32.4633 | 34.0459 | 33.8765 | 33.8755 | 33.8714 | 33.8653 | 33.8551 | 33.8449 | 33.8306 | 33.8235 | 33.8122 | 33.7806 | 33.7643 | 33.752
|  | HARRIS GRID | EE |  |  |  |  | 35.398 | 35.3888 | 35.2235 | 35.2153 | 35.2051 | 35.1878 | 35.1735 | 35.1551 | 35.1449 | 35.1316 | 35.098 | 35.0898 | 35.0663 | 32.6939 | 32.6878 | 32.5224 | 32.5204 | 32.5194 | 32.5194 | 32.5112 | 32.5061 | 32.5051 | 32.4949 | 32.4653 | 32.4633 | 32.4684 | 34.0459 | 34.0367 | 33.8755 | 33.8714 | 33.8653 | 33.8571 | 33.8449 | 33.8306 | 33.8235 | 33.8133 | 33.7806 | 33.7663 | 33.7531
|  | HARRIS GRID | HT |  |  |  |  | 35.398 | 35.2255 | 35.2245 | 35.2173 | 35.2092 | 35.1898 | 35.1776 | 35.1592 | 35.15 | 35.1367 | 35.1112 | 35.0959 | 35.0663 | 32.6939 | 32.5204 | 32.5235 | 32.5214 | 32.5224 | 32.5204 | 32.5133 | 32.5071 | 32.5071 | 32.4959 | 32.4633 | 32.4582 | 32.4653 | 34.0459 | 33.8765 | 33.8765 | 33.8724 | 33.8684 | 33.8571 | 33.848 | 33.8347 | 33.8276 | 33.8163 | 33.7827 | 33.7643 | 33.752
|  | HARRIS GRID | HE |  |  |  |  | 35.398 | 35.3908 | 35.2235 | 35.2153 | 35.2071 | 35.1867 | 35.1735 | 35.1561 | 35.1459 | 35.1316 | 35.1112 | 35.0939 | 35.0704 | 32.6939 | 32.6908 | 32.5224 | 32.5204 | 32.5204 | 32.5194 | 32.5112 | 32.5061 | 32.5051 | 32.4949 | 32.4673 | 32.4622 | 32.4633 | 34.0459 | 34.0398 | 33.8755 | 33.8714 | 33.8663 | 33.8551 | 33.8449 | 33.8316 | 33.8245 | 33.8122 | 33.7867 | 33.7673 | 33.7541
|  | HARRIS GRID | FB |  |  |  |  | 35.4031 | 35.4031 | 35.399 | 35.2337 | 35.2357 | 35.2347 | 35.2316 | 35.2276 | 35.2255 | 35.2245 | 35.2 | 35.1684 | 35.1561 | 32.7 | 32.699 | 32.6969 | 32.5296 | 32.5316 | 32.5306 | 32.5286 | 32.5276 | 32.5255 | 32.5235 | 32.5112 | 32.4786 | 32.4663 | 34.051 | 34.051 | 34.0459 | 33.8847 | 33.8888 | 33.8857 | 33.8847 | 33.8837 | 33.8816 | 33.8816 | 33.8531 | 33.8143 | 33.8061
| DYCE | HARVEST AVENUE | MINIMUM HEADROOM | NJ 86978 11769 | NO | YES | 0.158 | 19.5208 | 19.5137 | 19.5127 | 19.4953 | 19.3892 | 19.3259 | 19.2963 | 19.2422 | 19.2076 | 19.1576 | 19.028 | 18.9157 | 18.8565 | 19.7035 | 19.6984 | 19.6933 | 19.6892 | 19.5831 | 19.529 | 19.5157 | 19.4718 | 19.4382 | 19.4024 | 19.3004 | 19.2392 | 19.2229 | 19.7831 | 19.7769 | 19.7759 | 19.7657 | 19.5208 | 19.3688 | 19.3443 | 19.2269 | 19.1412 | 19.0433 | 18.7616 | 18.53 | 18.4708
|  | HARVEST AVENUE | EE |  |  |  |  | 19.5208 | 19.5137 | 19.5127 | 19.4973 | 19.3943 | 19.3259 | 19.3065 | 19.2463 | 19.2137 | 19.1576 | 19.028 | 18.9157 | 18.8565 | 19.7045 | 19.6994 | 19.6933 | 19.6902 | 19.5841 | 19.529 | 19.5198 | 19.4718 | 19.4494 | 19.4024 | 19.3004 | 19.2392 | 19.2229 | 19.7841 | 19.7769 | 19.7759 | 19.7688 | 19.5239 | 19.3688 | 19.3576 | 19.2269 | 19.1749 | 19.0433 | 18.7616 | 18.53 | 18.4708
|  | HARVEST AVENUE | HT |  |  |  |  | 19.5208 | 19.5147 | 19.5137 | 19.4994 | 19.3953 | 19.3361 | 19.3065 | 19.2586 | 19.2076 | 19.1759 | 19.0331 | 18.9443 | 18.8861 | 19.7045 | 19.7004 | 19.6943 | 19.6902 | 19.5841 | 19.5361 | 19.5178 | 19.479 | 19.4382 | 19.4147 | 19.3045 | 19.2494 | 19.2473 | 19.7841 | 19.778 | 19.778 | 19.7698 | 19.5249 | 19.3922 | 19.3576 | 19.2494 | 19.1412 | 19.0861 | 18.778 | 18.5769 | 18.5504
|  | HARVEST AVENUE | HE |  |  |  |  | 19.5208 | 19.5147 | 19.5127 | 19.4953 | 19.3892 | 19.3494 | 19.2963 | 19.2422 | 19.2116 | 19.1576 | 19.0953 | 19.0504 | 19.0249 | 19.7035 | 19.6984 | 19.6933 | 19.6892 | 19.5831 | 19.5565 | 19.5157 | 19.4739 | 19.4586 | 19.4106 | 19.3524 | 19.3576 | 19.3688 | 19.7831 | 19.7769 | 19.7769 | 19.7657 | 19.5208 | 19.4535 | 19.3443 | 19.228 | 19.1984 | 19.0657 | 18.928 | 18.9116 | 18.9004
|  | HARVEST AVENUE | FB |  |  |  |  | 19.532 | 19.5341 | 19.5269 | 19.5157 | 19.5106 | 19.4106 | 19.4004 | 19.3984 | 19.3892 | 19.38 | 19.3351 | 19.2912 | 19.1759 | 19.7106 | 19.7116 | 19.7035 | 19.6984 | 19.6912 | 19.5892 | 19.581 | 19.581 | 19.5749 | 19.5667 | 19.5422 | 19.5147 | 19.4106 | 19.7912 | 19.7912 | 19.7861 | 19.779 | 19.7759 | 19.5167 | 19.5076 | 19.5055 | 19.4994 | 19.4861 | 19.4514 | 19.4014 | 19.0963
| THURSO | HASTIGROW | MINIMUM HEADROOM | ND 26576 60773 | YES | NO | 0.452 | 0.19147 | 0.14759 | 0.12412 | 0.0016735 | -0.15445 | -0.51363 | -0.75139 | -1.1759 | -1.4963 | -1.6412 | -2.2963 | -2.7698 | -3.2147 | 0.82718 | 0.80984 | 0.78739 | 0.76494 | 0.71596 | 0.48331 | 0.39453 | 0.12922 | 0.13841 | 0.040449 | -0.35649 | -0.33404 | -0.30853 | 0.56494 | 0.53127 | 0.49453 | 0.43535 | 0.32208 | 0.038408 | -0.14527 | -0.48506 | -0.6922 | -0.81771 | -1.3463 | -1.6493 | -1.8606
|  | HASTIGROW | EE |  |  |  |  | 0.19147 | 0.14759 | 0.12412 | 0.014939 | -0.12792 | -0.35445 | -0.67384 | -1.1432 | -1.4963 | -1.6412 | -2.2963 | -2.7698 | -3.2147 | 0.82718 | 0.80984 | 0.78739 | 0.76494 | 0.71698 | 0.64453 | 0.54147 | 0.268 | 0.14045 | 0.046571 | -0.35649 | -0.33404 | -0.29731 | 0.56494 | 0.53127 | 0.49453 | 0.44249 | 0.34045 | 0.17208 | -0.055469 | -0.43812 | -0.6922 | -0.81771 | -1.3463 | -1.6493 | -1.8269
|  | HASTIGROW | HT |  |  |  |  | 0.19147 | 0.14759 | 0.12514 | 0.01902 | -0.11976 | -0.51363 | -0.75139 | -1.1759 | -1.3096 | -1.4728 | -2.0106 | -2.5769 | -3.2096 | 0.8282 | 0.80984 | 0.78841 | 0.76698 | 0.71902 | 0.48331 | 0.39453 | 0.12922 | 0.13841 | 0.040449 | -0.34935 | -0.32894 | -0.30853 | 0.56494 | 0.53229 | 0.49657 | 0.44657 | 0.34453 | 0.038408 | -0.14527 | -0.48506 | -0.56567 | -0.70547 | -1.1626 | -1.5259 | -1.8606
|  | HASTIGROW | HE |  |  |  |  | 0.19147 | 0.14759 | 0.12412 | 0.0016735 | -0.15445 | -0.38812 | -0.732 | -1.0749 | -1.3636 | -1.4942 | -1.6657 | -2.4177 | -2.9147 | 0.8282 | 0.81086 | 0.78841 | 0.76494 | 0.71596 | 0.64249 | 0.53841 | 0.43127 | 0.46902 | 0.38637 | 0.20065 | 0.17106 | 0.12208 | 0.56494 | 0.53229 | 0.49759 | 0.43535 | 0.32208 | 0.14759 | -0.085061 | -0.32384 | -0.44527 | -0.55343 | -0.76873 | -1.1749 | -1.5034
|  | HASTIGROW | FB |  |  |  |  | 0.25269 | 0.268 | 0.27208 | 0.26188 | 0.23024 | 0.21596 | 0.1578 | 0.11392 | 0.054735 | -0.0013878 | -0.2371 | -0.56669 | -0.67384 | 0.87412 | 0.88229 | 0.87922 | 0.88024 | 0.86086 | 0.83637 | 0.78433 | 0.75473 | 0.69453 | 0.64555 | 0.5231 | 0.25678 | 0.12208 | 0.62004 | 0.63943 | 0.64453 | 0.63943 | 0.6129 | 0.58739 | 0.53433 | 0.49657 | 0.43637 | 0.41086 | 0.22616 | -0.099347 | -0.14322
| STRICHEN | HATTON | MINIMUM HEADROOM | NK 06441 37348 | NO | YES | 0.237 | 4.7553 | 4.5941 | 4.4165 | 4.1971 | 3.9941 | 3.6227 | 3.3278 | 2.9757 | 2.6124 | 2.3298 | 1.3033 | 0.4002 | -0.33959 | 5.8043 | 5.6788 | 5.5696 | 5.4471 | 5.3594 | 5.2176 | 5.1716 | 5.0349 | 4.8798 | 4.7329 | 4.2951 | 4.2196 | 4.0757 | 5.3053 | 5.1553 | 5.0124 | 4.8604 | 4.7104 | 4.4186 | 4.2635 | 3.9716 | 3.6706 | 3.4298 | 2.6186 | 2.1176 | 1.7359
|  | HATTON | EE |  |  |  |  | 4.7798 | 4.5941 | 4.4165 | 4.1971 | 4.0002 | 3.6441 | 3.3543 | 3.0063 | 2.6512 | 2.3839 | 1.3033 | 0.4002 | -0.25694 | 5.8247 | 5.6788 | 5.5696 | 5.4471 | 5.3645 | 5.2216 | 5.1757 | 5.0471 | 4.9043 | 4.7706 | 4.3482 | 4.239 | 4.1441 | 5.3237 | 5.1553 | 5.0124 | 4.8635 | 4.7155 | 4.4288 | 4.2798 | 4.0002 | 3.7165 | 3.489 | 2.6186 | 2.1176 | 1.8073
|  | HATTON | HT |  |  |  |  | 4.7655 | 4.6012 | 4.4278 | 4.2135 | 4.0043 | 3.6747 | 3.3665 | 2.989 | 2.6145 | 2.3298 | 1.4104 | 0.49102 | -0.33959 | 5.8124 | 5.6829 | 5.5706 | 5.4482 | 5.3594 | 5.2318 | 5.1818 | 5.0349 | 4.8798 | 4.7329 | 4.2951 | 4.2369 | 4.241 | 5.3145 | 5.1573 | 5.0186 | 4.8696 | 4.7145 | 4.4492 | 4.2808 | 3.9716 | 3.6706 | 3.4298 | 2.6604 | 2.1257 | 1.7359
|  | HATTON | HE |  |  |  |  | 4.7553 | 4.5951 | 4.4206 | 4.1971 | 3.9941 | 3.6227 | 3.3278 | 2.9757 | 2.6124 | 2.342 | 1.4869 | 0.59918 | 0.04 | 5.8043 | 5.6788 | 5.5696 | 5.4471 | 5.3614 | 5.2176 | 5.1716 | 5.039 | 4.8961 | 4.7635 | 4.3522 | 4.2196 | 4.0757 | 5.3053 | 5.1553 | 5.0145 | 4.8604 | 4.7104 | 4.4186 | 4.2635 | 3.9778 | 3.6869 | 3.4584 | 2.7135 | 2.192 | 1.8859
|  | HATTON | FB |  |  |  |  | 4.9094 | 4.8033 | 4.6778 | 4.5747 | 4.4543 | 4.3124 | 4.2237 | 4.1339 | 4.0502 | 3.9614 | 3.4818 | 2.9961 | 2.8461 | 5.938 | 5.8584 | 5.7716 | 5.6931 | 5.6278 | 5.5145 | 5.4471 | 5.3676 | 5.3002 | 5.2298 | 4.9665 | 4.5084 | 4.2155 | 5.4655 | 5.3849 | 5.289 | 5.1941 | 5.1104 | 4.99 | 4.9135 | 4.8298 | 4.7451 | 4.6553 | 4.292 | 3.7482 | 3.6553
| PERSLEY | HAUDAGAIN | MINIMUM HEADROOM | NJ 91425 09066 | NO | NO | 3.379 | 10.6801 | 10.6495 | 10.6608 | 10.622 | 10.2893 | 10.1108 | 9.8067 | 9.4434 | 9.1536 | 8.8679 | 6.6863 | 4.773 | 3.6975 | 11.7852 | 11.7648 | 11.7659 | 11.6067 | 11.4434 | 11.3291 | 11.0781 | 10.8108 | 10.5893 | 10.3822 | 9.172 | 8.2648 | 7.1118 | 11.3556 | 11.3097 | 11.2965 | 11.2618 | 10.9342 | 10.772 | 10.4873 | 10.1454 | 9.874 | 9.6077 | 7.6505 | 6.0261 | 5.0995
|  | HAUDAGAIN | EE |  |  |  |  | 10.6801 | 10.6495 | 10.6608 | 10.622 | 10.2893 | 10.1108 | 9.8067 | 9.4434 | 9.1536 | 8.8679 | 6.6863 | 4.773 | 3.6975 | 11.7852 | 11.7648 | 11.7659 | 11.7444 | 11.4434 | 11.3291 | 11.0944 | 10.8108 | 10.5893 | 10.3822 | 9.172 | 8.2648 | 7.5893 | 11.3556 | 11.3097 | 11.2965 | 11.2618 | 10.9342 | 10.772 | 10.4873 | 10.1454 | 9.874 | 9.6077 | 7.6505 | 6.0261 | 5.0995
|  | HAUDAGAIN | HT |  |  |  |  | 10.6954 | 10.6812 | 10.7087 | 10.6659 | 10.3342 | 10.1597 | 9.825 | 9.4954 | 9.2199 | 8.925 | 6.8985 | 5.3087 | 4.6097 | 11.7863 | 11.7659 | 11.7679 | 11.7454 | 11.4465 | 11.3444 | 11.0781 | 10.8159 | 10.6077 | 10.4026 | 9.4159 | 8.8873 | 8.6403 | 11.371 | 11.3403 | 11.3434 | 11.3026 | 10.972 | 10.8159 | 10.5005 | 10.1873 | 9.9301 | 9.6577 | 7.8679 | 6.5414 | 5.975
|  | HAUDAGAIN | HE |  |  |  |  | 10.6852 | 10.6587 | 10.673 | 10.6332 | 10.2995 | 10.1526 | 9.8608 | 9.5771 | 9.3036 | 9.0414 | 7.6067 | 6.4516 | 5.5679 | 11.7873 | 11.7669 | 11.771 | 11.7475 | 11.4485 | 11.3403 | 11.1005 | 10.8597 | 10.6352 | 10.4056 | 9.5883 | 9.0005 | 8.3873 | 11.3618 | 11.3179 | 11.3087 | 11.271 | 10.9414 | 10.8046 | 10.5261 | 10.2546 | 9.9914 | 9.7373 | 8.4638 | 7.4791 | 6.724
|  | HAUDAGAIN | FB |  |  |  |  | 10.7842 | 10.821 | 10.8801 | 10.6516 | 10.6352 | 10.6056 | 10.5597 | 10.4995 | 10.4118 | 10.323 | 9.6077 | 8.0608 | 6.6301 | 11.8414 | 11.8505 | 11.8577 | 11.6067 | 11.5659 | 11.5077 | 11.425 | 11.3373 | 11.222 | 11.1056 | 10.271 | 8.7148 | 7.1118 | 11.4577 | 11.4801 | 11.5087 | 11.2648 | 11.2454 | 11.2118 | 11.1618 | 11.0995 | 11.0077 | 10.921 | 10.1873 | 8.4016 | 7.374
| WILLOWDALE | HAYTON | MINIMUM HEADROOM | NJ 92753 08909 | NO | NO | 0.26 | 18.9243 | 18.9376 | 18.9437 | 18.9263 | 18.8784 | 18.7518 | 18.5957 | 18.4294 | 18.2192 | 18.0314 | 16.5478 | 15.21 | 14.358 | 18.7151 | 18.7294 | 18.7406 | 18.7386 | 18.7222 | 18.661 | 18.558 | 18.5284 | 18.411 | 18.3008 | 17.5753 | 16.5324 | 15.109 | 18.9003 | 18.8911 | 18.8758 | 18.8472 | 18.8023 | 18.6952 | 18.5544 | 18.4911 | 18.3126 | 18.1544 | 16.7901 | 15.637 | 14.9748
|  | HAYTON | EE |  |  |  |  | 18.9243 | 18.9376 | 18.9437 | 18.9263 | 18.8784 | 18.7518 | 18.5957 | 18.4508 | 18.2682 | 18.0967 | 16.6427 | 15.21 | 14.358 | 18.7151 | 18.7294 | 18.7406 | 18.7386 | 18.7222 | 18.661 | 18.558 | 18.5457 | 18.4314 | 18.3161 | 17.5753 | 16.9386 | 16.2998 | 18.9003 | 18.8911 | 18.8758 | 18.8472 | 18.8023 | 18.6952 | 18.5544 | 18.4942 | 18.333 | 18.1779 | 16.7901 | 15.637 | 14.9748
|  | HAYTON | HT |  |  |  |  | 18.9314 | 18.9539 | 18.9641 | 18.9386 | 18.8998 | 18.7865 | 18.5967 | 18.4294 | 18.2192 | 18.0314 | 16.5478 | 15.4355 | 14.9222 | 18.7161 | 18.7324 | 18.7406 | 18.7396 | 18.7243 | 18.6722 | 18.558 | 18.5365 | 18.411 | 18.3008 | 17.8202 | 17.5467 | 17.3427 | 18.9136 | 18.9156 | 18.9085 | 18.8799 | 18.8207 | 18.7268 | 18.5656 | 18.4911 | 18.3126 | 18.1544 | 16.986 | 16.0503 | 15.6013
|  | HAYTON | HE |  |  |  |  | 18.9263 | 18.9447 | 18.9498 | 18.9324 | 18.8876 | 18.7784 | 18.6365 | 18.5182 | 18.358 | 18.2161 | 17.0855 | 16.2722 | 15.5406 | 18.7161 | 18.7335 | 18.7427 | 18.7406 | 18.7284 | 18.6743 | 18.5784 | 18.5712 | 18.4671 | 18.362 | 17.7549 | 17.1916 | 16.5702 | 18.9064 | 18.9003 | 18.886 | 18.8574 | 18.8166 | 18.7238 | 18.5993 | 18.5636 | 18.4228 | 18.2932 | 17.2983 | 16.4809 | 15.8646
|  | HAYTON | FB |  |  |  |  | 18.9722 | 19.0243 | 19.059 | 19.0671 | 19.059 | 19.0437 | 19.0243 | 18.9518 | 18.8784 | 18.7988 | 18.3722 | 17.4335 | 16.5559 | 18.7294 | 18.7569 | 18.7692 | 18.7743 | 18.7498 | 18.6916 | 18.6243 | 18.5284 | 18.4324 | 18.3253 | 17.8518 | 16.5324 | 15.109 | 18.9738 | 19.0177 | 19.0411 | 19.0452 | 19.0207 | 18.9972 | 18.9789 | 18.9166 | 18.8564 | 18.787 | 18.4585 | 17.2248 | 16.6626
| BRORA | HELMSDALE | MINIMUM HEADROOM | ND 02372 15376 | YES | NO | 0.022 | 0.29388 | 0.2898 | 0.28878 | 0.26224 | 0.22551 | 0.12653 | 0.029592 | -0.041837 | -0.095918 | -0.1551 | -0.28776 | -0.44082 | -0.5898 | 0.71939 | 0.71633 | 0.71429 | 0.70612 | 0.70306 | 0.60408 | 0.53265 | 0.48571 | 0.44898 | 0.43469 | 0.37551 | 0.35918 | 0.27755 | 0.56633 | 0.5551 | 0.54286 | 0.50918 | 0.47449 | 0.37755 | 0.28878 | 0.2449 | 0.18673 | 0.13878 | 0.029592 | -0.044898 | -0.11735
|  | HELMSDALE | EE |  |  |  |  | 0.29388 | 0.29082 | 0.2898 | 0.26531 | 0.22959 | 0.19388 | 0.13673 | 0.032653 | -0.061224 | -0.13673 | -0.28776 | -0.44082 | -0.57857 | 0.71939 | 0.71633 | 0.71531 | 0.70714 | 0.70408 | 0.68878 | 0.65612 | 0.57245 | 0.49796 | 0.4449 | 0.38469 | 0.37347 | 0.35714 | 0.56735 | 0.5551 | 0.54388 | 0.51122 | 0.47857 | 0.43776 | 0.38673 | 0.30612 | 0.22143 | 0.15204 | 0.029592 | -0.044898 | -0.10306
|  | HELMSDALE | HT |  |  |  |  | 0.29388 | 0.2898 | 0.28878 | 0.26429 | 0.22959 | 0.12653 | 0.029592 | -0.041837 | -0.095918 | -0.14082 | -0.26224 | -0.40714 | -0.5898 | 0.71939 | 0.71633 | 0.71429 | 0.70714 | 0.70408 | 0.60408 | 0.53265 | 0.48571 | 0.44898 | 0.43469 | 0.37551 | 0.36837 | 0.36939 | 0.56633 | 0.5551 | 0.54286 | 0.5102 | 0.47755 | 0.37755 | 0.28878 | 0.2449 | 0.18673 | 0.1449 | 0.039796 | -0.042857 | -0.11735
|  | HELMSDALE | HE |  |  |  |  | 0.29388 | 0.2898 | 0.28878 | 0.26224 | 0.22551 | 0.19286 | 0.13367 | 0.021429 | -0.076531 | -0.1551 | -0.25714 | -0.41633 | -0.56633 | 0.71939 | 0.71633 | 0.71429 | 0.70612 | 0.70306 | 0.68776 | 0.65612 | 0.56429 | 0.48571 | 0.43469 | 0.38776 | 0.37041 | 0.34082 | 0.56633 | 0.5551 | 0.54286 | 0.50918 | 0.47449 | 0.43571 | 0.38367 | 0.29694 | 0.20612 | 0.13878 | 0.04898 | -0.034694 | -0.09898
|  | HELMSDALE | FB |  |  |  |  | 0.30714 | 0.31327 | 0.31939 | 0.31837 | 0.31429 | 0.29388 | 0.28571 | 0.26327 | 0.19796 | 0.1398 | -0.0071429 | -0.10408 | -0.1449 | 0.72857 | 0.73265 | 0.73673 | 0.73878 | 0.73673 | 0.72755 | 0.72449 | 0.71122 | 0.63673 | 0.58163 | 0.45816 | 0.35918 | 0.27755 | 0.57959 | 0.57653 | 0.57653 | 0.56633 | 0.55102 | 0.53163 | 0.52245 | 0.50102 | 0.43776 | 0.38265 | 0.23061 | 0.13878 | 0.11939
| INVERNESS | HILTON | MINIMUM HEADROOM | NH 67326 43262 | NO | NO | 6.821 | 7.3975 | 7.0557 | 6.6761 | 6.0291 | 5.7383 | 4.1445 | 2.7424 | 1.4394 | 0.43731 | -0.3484 | -3.5668 | -6.3964 | -8.127 | 9.8969 | 9.7561 | 9.7122 | 9.5336 | 9.404 | 8.6275 | 7.8469 | 7.1449 | 6.6632 | 6.2918 | 4.9112 | 4.3857 | 2.8112 | 9.2551 | 9.0438 | 8.8183 | 8.3561 | 8.0887 | 6.9081 | 5.7765 | 4.7336 | 3.9612 | 3.3836 | 0.88466 | -1.1878 | -2.4235
|  | HILTON | EE |  |  |  |  | 7.3996 | 7.0608 | 6.6761 | 6.0291 | 5.7526 | 4.6465 | 3.4485 | 2.0445 | 0.70976 | -0.3484 | -3.5484 | -6.3964 | -8.127 | 9.8969 | 9.7581 | 9.7132 | 9.5357 | 9.4153 | 9.1 | 8.6224 | 7.8051 | 7.0224 | 6.3826 | 5.0449 | 4.3857 | 3.7867 | 9.2551 | 9.0459 | 8.8183 | 8.3571 | 8.101 | 7.3469 | 6.4622 | 5.3489 | 4.2857 | 3.4051 | 0.88466 | -1.1878 | -2.4235
|  | HILTON | HT |  |  |  |  | 7.3975 | 7.0567 | 6.6781 | 6.0332 | 5.7383 | 4.1445 | 2.7424 | 1.4394 | 0.43731 | -0.3382 | -3.5668 | -6.3474 | -8.1045 | 9.9 | 9.7561 | 9.7122 | 9.5336 | 9.404 | 8.6275 | 7.8469 | 7.1449 | 6.6632 | 6.2918 | 4.9112 | 4.5949 | 4.5296 | 9.2551 | 9.0438 | 8.8194 | 8.3561 | 8.0887 | 6.9081 | 5.7765 | 4.7336 | 3.9612 | 3.3836 | 0.90302 | -0.99289 | -2.1409
|  | HILTON | HE |  |  |  |  | 7.3975 | 7.0557 | 6.6761 | 6.0342 | 5.7536 | 4.6455 | 3.5608 | 2.1098 | 0.74853 | -0.29126 | -2.9076 | -5.4576 | -6.7984 | 9.9 | 9.7571 | 9.7122 | 9.5347 | 9.4112 | 9.0734 | 8.6408 | 7.7816 | 6.9642 | 6.3204 | 5.1428 | 4.5336 | 3.8612 | 9.2561 | 9.0459 | 8.8204 | 8.3581 | 8.0979 | 7.3377 | 6.5367 | 5.3826 | 4.2969 | 3.4265 | 1.3571 | -0.43881 | -1.4
|  | HILTON | FB |  |  |  |  | 7.6598 | 7.5822 | 7.27 | 6.922 | 7.0067 | 6.8904 | 6.5077 | 6.0618 | 5.5628 | 5.0302 | 3.3067 | 1.3485 | 0.41486 | 10.0163 | 10.0142 | 9.9081 | 9.801 | 9.8642 | 9.7316 | 9.5163 | 9.2459 | 8.7357 | 8.2051 | 6.5336 | 4.4928 | 2.8112 | 9.4887 | 9.4612 | 9.2673 | 9.0153 | 9.0724 | 8.9489 | 8.6479 | 8.2959 | 7.8275 | 7.3214 | 5.701 | 3.6255 | 3.0969
| ARBROATH | HUME STREET | MINIMUM HEADROOM | NO 64067 41180 | NO | YES | 0.454 | 15.2602 | 15.1929 | 15.1622 | 15.0786 | 14.9765 | 14.4704 | 14.1194 | 13.6398 | 13.0031 | 12.7418 | 10.2092 | 8.1051 | 6.7796 | 16.5157 | 16.4637 | 16.4443 | 16.4137 | 16.3514 | 16.0024 | 15.7708 | 15.3882 | 14.8239 | 14.6912 | 12.9565 | 11.878 | 11.18 | 16.0718 | 15.9484 | 15.8943 | 15.8157 | 15.6994 | 15.4065 | 15.1014 | 14.631 | 13.9943 | 13.7729 | 11.4973 | 9.7545 | 8.6759
|  | HUME STREET | EE |  |  |  |  | 15.2602 | 15.2092 | 15.1755 | 15.0867 | 14.9888 | 14.4837 | 14.1214 | 13.6429 | 13.0143 | 12.7418 | 10.2092 | 8.1051 | 6.7796 | 16.5157 | 16.4739 | 16.4535 | 16.4218 | 16.3637 | 16.0229 | 15.7912 | 15.4157 | 14.8616 | 14.6912 | 12.9565 | 11.878 | 11.18 | 16.0718 | 15.9678 | 15.9035 | 15.8239 | 15.7076 | 15.4096 | 15.1137 | 14.6412 | 14.0086 | 13.7729 | 11.4973 | 9.7545 | 8.6759
|  | HUME STREET | HT |  |  |  |  | 15.2643 | 15.1929 | 15.1622 | 15.0786 | 14.9765 | 14.5571 | 14.2316 | 13.7653 | 13.1633 | 12.8837 | 10.602 | 8.6398 | 7.4255 | 16.5188 | 16.4637 | 16.4443 | 16.4137 | 16.3514 | 16.0647 | 15.8382 | 15.4718 | 14.931 | 14.7514 | 13.1371 | 12.3127 | 11.9637 | 16.0739 | 15.9484 | 15.8943 | 15.8157 | 15.6994 | 15.4565 | 15.2086 | 14.7504 | 14.131 | 13.8902 | 11.8453 | 10.2749 | 9.3667
|  | HUME STREET | HE |  |  |  |  | 15.2643 | 15.2112 | 15.1939 | 15.1041 | 14.9949 | 14.4704 | 14.1194 | 13.6398 | 13.0031 | 12.8214 | 11.1663 | 9.25 | 8.7347 | 16.5178 | 16.4759 | 16.4596 | 16.431 | 16.3698 | 16.0024 | 15.7708 | 15.3882 | 14.8239 | 14.7229 | 13.5086 | 12.3922 | 12.282 | 16.0739 | 15.9688 | 15.9178 | 15.8361 | 15.7137 | 15.4065 | 15.1014 | 14.631 | 13.9943 | 13.8443 | 12.3443 | 10.7218 | 10.3912
|  | HUME STREET | FB |  |  |  |  | 15.3245 | 15.3163 | 15.3898 | 15.402 | 15.4255 | 15.4061 | 15.3112 | 15.2439 | 15.2255 | 15.0735 | 13.999 | 12.2071 | 10.4827 | 16.5473 | 16.5341 | 16.58 | 16.5739 | 16.5749 | 16.5596 | 16.48 | 16.4076 | 16.3524 | 16.1576 | 14.9351 | 13.2412 | 11.3116 | 16.1402 | 16.0871 | 16.1514 | 16.1484 | 16.1698 | 16.1555 | 16.0514 | 15.9627 | 15.9412 | 15.8545 | 14.728 | 12.5973 | 11.3014
| KEITH 2 | HUNTLY | MINIMUM HEADROOM | NJ 52762 39217 | NO | YES | 1.002 | 7.4847 | 7.1449 | 6.7785 | 6.3938 | 6.2163 | 5.949 | 5.65 | 5.3418 | 5.0132 | 4.7132 | 3.603 | 2.4938 | 1.7132 | 8.753 | 8.3694 | 7.9857 | 7.5908 | 7.4745 | 7.3612 | 7.2387 | 7.1245 | 7.003 | 6.8806 | 6.4336 | 6.0265 | 5.902 | 8.3209 | 8.0015 | 7.6668 | 7.2668 | 7.1372 | 6.9484 | 6.7086 | 6.5076 | 6.2627 | 6.0178 | 5.0709 | 4.1893 | 3.7607
|  | HUNTLY | EE |  |  |  |  | 7.5969 | 7.1459 | 6.803 | 6.4296 | 6.2551 | 5.9898 | 5.6908 | 5.3867 | 5.0418 | 4.7449 | 3.603 | 2.4938 | 1.8306 | 8.8745 | 8.3694 | 7.9938 | 7.6041 | 7.4867 | 7.3714 | 7.253 | 7.1408 | 7.0183 | 6.8816 | 6.4377 | 6.0265 | 5.902 | 8.426 | 8.0015 | 7.6821 | 7.2719 | 7.1597 | 6.9688 | 6.7382 | 6.5423 | 6.276 | 6.026 | 5.0709 | 4.1893 | 3.7607
|  | HUNTLY | HT |  |  |  |  | 7.5296 | 7.1592 | 6.7785 | 6.3938 | 6.2163 | 5.949 | 5.6724 | 5.4143 | 5.1163 | 4.8449 | 3.7653 | 2.5938 | 1.7132 | 8.802 | 8.3836 | 7.9857 | 7.5908 | 7.4745 | 7.3612 | 7.2387 | 7.1245 | 7.003 | 6.8867 | 6.4336 | 6.1194 | 6.0132 | 8.3627 | 8.0158 | 7.6668 | 7.2668 | 7.1372 | 6.9484 | 6.728 | 6.5433 | 6.3025 | 6.0913 | 5.227 | 4.3515 | 3.7882
|  | HUNTLY | HE |  |  |  |  | 7.4847 | 7.1449 | 6.7949 | 6.4092 | 6.2265 | 5.9622 | 5.65 | 5.3418 | 5.0132 | 4.7132 | 3.8592 | 2.902 | 2.3336 | 8.753 | 8.3694 | 7.9908 | 7.599 | 7.4816 | 7.3673 | 7.2408 | 7.1275 | 7.0143 | 6.8806 | 6.5347 | 6.3592 | 6.1796 | 8.3209 | 8.0015 | 7.675 | 7.278 | 7.1433 | 6.9525 | 6.7086 | 6.5076 | 6.2627 | 6.0178 | 5.2923 | 4.6291 | 4.2219
|  | HUNTLY | FB |  |  |  |  | 7.9081 | 7.5877 | 7.249 | 6.902 | 6.7275 | 6.5592 | 6.453 | 6.3561 | 6.2745 | 6.2632 | 5.7745 | 5.1408 | 4.6898 | 9.199 | 8.8245 | 8.4255 | 8.0632 | 7.8387 | 7.6969 | 7.5969 | 7.5173 | 7.4653 | 7.4459 | 7.1755 | 6.6867 | 6.1 | 8.727 | 8.428 | 8.1056 | 7.7505 | 7.5535 | 7.3984 | 7.3076 | 7.2168 | 7.1464 | 7.1229 | 6.7525 | 6.1178 | 5.8107
| BRIDGE OF DUN | INCHBARE | MINIMUM HEADROOM | NO 60684 65379 | YES | NO | 0.492 | 1.6794 | 1.6784 | 1.6651 | 1.662 | 1.6539 | 1.6406 | 1.6202 | 1.5927 | 1.5671 | 1.559 | 1.512 | 1.4957 | 1.3988 | 1.8166 | 1.8125 | 1.8023 | 1.7962 | 1.7901 | 1.7819 | 1.7677 | 1.7483 | 1.7309 | 1.7228 | 1.6697 | 1.6768 | 1.5646 | 1.7873 | 1.7842 | 1.774 | 1.7689 | 1.7618 | 1.7516 | 1.7383 | 1.7148 | 1.6955 | 1.6842 | 1.6404 | 1.6383 | 1.5414
|  | INCHBARE | EE |  |  |  |  | 1.6794 | 1.6784 | 1.6651 | 1.662 | 1.6549 | 1.6416 | 1.6222 | 1.5978 | 1.5763 | 1.5651 | 1.512 | 1.5018 | 1.3988 | 1.8166 | 1.8125 | 1.8023 | 1.7962 | 1.7901 | 1.783 | 1.7687 | 1.7483 | 1.7319 | 1.7248 | 1.6799 | 1.683 | 1.5646 | 1.7873 | 1.7842 | 1.774 | 1.7689 | 1.7618 | 1.7546 | 1.7393 | 1.7189 | 1.6985 | 1.6904 | 1.6444 | 1.6424 | 1.5414
|  | INCHBARE | HT |  |  |  |  | 1.6794 | 1.6804 | 1.6661 | 1.6671 | 1.6539 | 1.6437 | 1.6243 | 1.5998 | 1.5773 | 1.5671 | 1.5131 | 1.4998 | 1.4947 | 1.8166 | 1.8156 | 1.8034 | 1.8023 | 1.7901 | 1.7819 | 1.7677 | 1.7483 | 1.7319 | 1.7238 | 1.6697 | 1.683 | 1.7013 | 1.7873 | 1.7873 | 1.774 | 1.774 | 1.7618 | 1.7546 | 1.7404 | 1.7189 | 1.6985 | 1.6883 | 1.6404 | 1.6383 | 1.6424
|  | INCHBARE | HE |  |  |  |  | 1.6794 | 1.6804 | 1.6651 | 1.6651 | 1.6539 | 1.6406 | 1.6202 | 1.5927 | 1.5671 | 1.559 | 1.512 | 1.4957 | 1.4804 | 1.8166 | 1.8156 | 1.8034 | 1.8013 | 1.7901 | 1.7819 | 1.7677 | 1.7483 | 1.7309 | 1.7228 | 1.6779 | 1.6768 | 1.6656 | 1.7873 | 1.7873 | 1.774 | 1.774 | 1.7618 | 1.7516 | 1.7383 | 1.7148 | 1.6955 | 1.6842 | 1.6485 | 1.6414 | 1.6353
|  | INCHBARE | FB |  |  |  |  | 1.6947 | 1.6967 | 1.6988 | 1.6927 | 1.6896 | 1.6773 | 1.6712 | 1.66 | 1.6569 | 1.6529 | 1.61 | 1.5631 | 1.5498 | 1.8248 | 1.8238 | 1.8248 | 1.8207 | 1.8166 | 1.8044 | 1.7962 | 1.786 | 1.784 | 1.7789 | 1.7432 | 1.684 | 1.6483 | 1.7975 | 1.7985 | 1.7985 | 1.7944 | 1.7934 | 1.7802 | 1.775 | 1.7638 | 1.7628 | 1.7597 | 1.725 | 1.6791 | 1.673
| DUNOON | INNELLAN | MINIMUM HEADROOM | NS 15129 70875 | YES | YES | 0.012 | 1.8378 | 0.57245 | 0.56531 | 0.55204 | 0.46531 | 0.41224 | 0.31939 | 0.25306 | 0.10714 | -0.039796 | -0.35408 | -0.65612 | -0.83061 | 2.0219 | 0.64235 | 0.63724 | 0.63724 | 0.60051 | 0.5852 | 0.54745 | 0.52806 | 0.43214 | 0.27092 | 0.17092 | 0.12704 | 0.091327 | 1.9559 | 0.66505 | 0.65689 | 0.6426 | 0.57832 | 0.52219 | 0.47423 | 0.42832 | 0.25383 | 0.071173 | -0.12883 | -0.34413 | -0.46046
|  | INNELLAN | EE |  |  |  |  | 1.8388 | 1.8367 | 0.56531 | 0.5551 | 0.5398 | 0.42347 | 0.34286 | 0.27959 | 0.1551 | 0.005102 | -0.35408 | -0.65612 | -0.83061 | 2.023 | 2.0128 | 0.63724 | 0.63827 | 0.62806 | 0.58724 | 0.55357 | 0.53622 | 0.47194 | 0.35459 | 0.20867 | 0.12704 | 0.091327 | 1.9559 | 1.9436 | 0.65689 | 0.6477 | 0.62423 | 0.5324 | 0.48954 | 0.44362 | 0.33138 | 0.14974 | -0.12883 | -0.34413 | -0.46046
|  | INNELLAN | HT |  |  |  |  | 1.8398 | 0.57245 | 0.56939 | 0.5551 | 0.54286 | 0.49592 | 0.41327 | 0.3551 | 0.10714 | -0.039796 | -0.31122 | -0.57653 | -0.75816 | 2.023 | 0.64235 | 0.64133 | 0.64133 | 0.63214 | 0.62092 | 0.59235 | 0.57806 | 0.43214 | 0.27092 | 0.17092 | 0.15153 | 0.17398 | 1.9559 | 0.66505 | 0.66199 | 0.64872 | 0.6273 | 0.57628 | 0.5324 | 0.48954 | 0.25383 | 0.071173 | -0.12679 | -0.28801 | -0.38699
|  | INNELLAN | HE |  |  |  |  | 1.8378 | 1.8367 | 0.56531 | 0.55204 | 0.46531 | 0.41224 | 0.31939 | 0.25306 | 0.11939 | -0.035714 | -0.30306 | -0.55204 | -0.72449 | 2.0219 | 2.0128 | 0.63724 | 0.63724 | 0.60051 | 0.5852 | 0.54745 | 0.52806 | 0.46378 | 0.33724 | 0.21684 | 0.18929 | 0.091327 | 1.9569 | 1.9436 | 0.65791 | 0.6426 | 0.57832 | 0.52219 | 0.47423 | 0.42832 | 0.30587 | 0.11913 | -0.096173 | -0.24719 | -0.38903
|  | INNELLAN | FB |  |  |  |  | 1.8602 | 1.8806 | 1.8837 | 0.61531 | 0.62041 | 0.61429 | 0.45714 | 0.44592 | 0.41429 | 0.40714 | 0.28878 | 0.065306 | -0.018367 | 2.0383 | 2.0505 | 2.0403 | 0.66378 | 0.6699 | 0.6648 | 0.58418 | 0.57602 | 0.54847 | 0.51888 | 0.4199 | 0.22602 | 0.11173 | 1.9753 | 1.9885 | 1.9855 | 0.68954 | 0.6875 | 0.6773 | 0.52015 | 0.50485 | 0.4773 | 0.44668 | 0.3273 | 0.10791 | 0.066071
| KEITH 2 | INSCH | MINIMUM HEADROOM | NJ 63100 28651 | NO | YES | 0.562 | 7.1979 | 6.7908 | 6.3275 | 5.7979 | 5.5653 | 5.2765 | 4.8367 | 4.4551 | 4.0296 | 3.5979 | 2.5173 | 1.4888 | 0.87242 | 8.5479 | 8.1643 | 7.7785 | 7.3683 | 7.1551 | 7.051 | 6.8143 | 6.6224 | 6.4183 | 6.1296 | 5.353 | 5.0979 | 5.0132 | 8.3096 | 7.9116 | 7.4944 | 7.0454 | 6.7535 | 6.4913 | 6.0689 | 5.7342 | 5.3648 | 4.9658 | 4.0046 | 3.274 | 2.9301
|  | INSCH | EE |  |  |  |  | 7.2969 | 6.7908 | 6.3285 | 5.8092 | 5.5806 | 5.3296 | 4.9132 | 4.5316 | 4.1081 | 3.7398 | 2.5173 | 1.4888 | 0.94896 | 8.6418 | 8.1643 | 7.7867 | 7.3785 | 7.1673 | 7.0581 | 6.8255 | 6.6224 | 6.4183 | 6.1398 | 5.4204 | 5.1245 | 5.1571 | 8.4024 | 7.9116 | 7.5148 | 7.0525 | 6.7658 | 6.525 | 6.125 | 5.776 | 5.3974 | 5.0566 | 4.0046 | 3.274 | 2.9882
|  | INSCH | HT |  |  |  |  | 7.2367 | 6.7969 | 6.3275 | 5.7979 | 5.5683 | 5.352 | 4.9694 | 4.652 | 4.2449 | 3.8816 | 2.8183 | 1.6551 | 0.87242 | 8.5867 | 8.1755 | 7.7785 | 7.3683 | 7.1551 | 7.0694 | 6.8336 | 6.6632 | 6.4571 | 6.1939 | 5.353 | 5.0979 | 5.2347 | 8.3463 | 7.9228 | 7.5117 | 7.0454 | 6.7535 | 6.5433 | 6.1495 | 5.8658 | 5.4974 | 5.1658 | 4.1566 | 3.3525 | 2.9301
|  | INSCH | HE |  |  |  |  | 7.1979 | 6.7959 | 6.3408 | 5.801 | 5.5653 | 5.2765 | 4.8367 | 4.4551 | 4.0296 | 3.5979 | 2.8 | 1.8816 | 1.2388 | 8.5479 | 8.1643 | 7.7857 | 7.3755 | 7.1632 | 7.051 | 6.8143 | 6.6439 | 6.4357 | 6.1296 | 5.5439 | 5.4877 | 5.3449 | 8.3096 | 7.9147 | 7.4944 | 7.0474 | 6.7556 | 6.4913 | 6.0689 | 5.7342 | 5.3648 | 4.9658 | 4.2229 | 3.6433 | 3.2199
|  | INSCH | FB |  |  |  |  | 7.603 | 7.2847 | 6.7775 | 6.4836 | 6.2296 | 6.0051 | 5.8316 | 5.7663 | 5.6673 | 5.5316 | 4.7622 | 3.8296 | 3.3806 | 8.8959 | 8.5908 | 8.0581 | 7.7969 | 7.5785 | 7.3857 | 7.2296 | 7.1775 | 7.0857 | 6.949 | 6.4102 | 5.5969 | 5.0132 | 8.68 | 8.3963 | 7.7842 | 7.5107 | 7.325 | 7.1209 | 6.9423 | 6.9005 | 6.7913 | 6.5944 | 5.8495 | 4.876 | 4.5566
| BURGHMUIR | INVERALMOND | MINIMUM HEADROOM | NO 08721 25807 | NO | YES | 14.469 | 5.8612 | 5.7816 | 5.7449 | 5.6224 | 5.5184 | 5.199 | 4.9316 | 4.7316 | 4.5857 | 4.3163 | 3.6286 | 3.1071 | 2.7582 | 5.8673 | 5.7755 | 5.7357 | 5.598 | 5.4847 | 5.3388 | 5.1867 | 5.1204 | 5.0755 | 5.001 | 4.3469 | 3.8439 | 3.5031 | 5.7194 | 5.6245 | 5.5908 | 5.4531 | 5.3347 | 5.1816 | 5.0306 | 4.9531 | 4.899 | 4.8041 | 4.4939 | 4.0724 | 3.7224
|  | INVERALMOND | EE |  |  |  |  | 5.8633 | 5.7816 | 5.7449 | 5.6224 | 5.5184 | 5.199 | 4.9449 | 4.7316 | 4.5857 | 4.3163 | 3.6286 | 3.1071 | 2.7582 | 5.8704 | 5.7755 | 5.7357 | 5.598 | 5.4847 | 5.3388 | 5.1867 | 5.1204 | 5.0755 | 5.001 | 4.3469 | 3.8439 | 3.5031 | 5.7214 | 5.6245 | 5.5908 | 5.4531 | 5.3347 | 5.1816 | 5.0326 | 4.9531 | 4.899 | 4.8041 | 4.4939 | 4.0724 | 3.7224
|  | INVERALMOND | HT |  |  |  |  | 5.8622 | 5.7826 | 5.7449 | 5.6224 | 5.5184 | 5.2306 | 5.0082 | 4.799 | 4.6408 | 4.3265 | 3.6561 | 3.1398 | 2.9388 | 5.8694 | 5.7765 | 5.7357 | 5.598 | 5.4847 | 5.3867 | 5.3235 | 5.2531 | 5.1786 | 5.0326 | 4.3755 | 3.8755 | 3.6816 | 5.7204 | 5.6265 | 5.5908 | 5.4531 | 5.3347 | 5.2194 | 5.1377 | 5.0571 | 4.9796 | 4.8306 | 4.5041 | 4.1051 | 3.9041
|  | INVERALMOND | HE |  |  |  |  | 5.8612 | 5.7816 | 5.7449 | 5.6224 | 5.5184 | 5.2388 | 4.9316 | 4.7571 | 4.601 | 4.4122 | 3.8173 | 3.7582 | 3.5214 | 5.8673 | 5.7755 | 5.7357 | 5.598 | 5.4847 | 5.352 | 5.1888 | 5.1296 | 5.0816 | 5.0245 | 4.5337 | 4.4796 | 4.251 | 5.7194 | 5.6245 | 5.5908 | 5.4531 | 5.3347 | 5.1959 | 5.0306 | 4.9633 | 4.9051 | 4.8357 | 4.5653 | 4.5377 | 4.452
|  | INVERALMOND | FB |  |  |  |  | 5.8684 | 5.8469 | 5.8173 | 5.6877 | 5.6204 | 5.5235 | 5.4153 | 5.2694 | 5.2051 | 5.0847 | 4.5663 | 4.0918 | 3.4653 | 5.8755 | 5.85 | 5.8163 | 5.6724 | 5.6 | 5.4877 | 5.3857 | 5.2541 | 5.2306 | 5.1959 | 5.0173 | 4.7939 | 4.1796 | 5.7265 | 5.7041 | 5.6775 | 5.5184 | 5.4571 | 5.3418 | 5.2449 | 5.1286 | 5.1041 | 5.0602 | 4.8571 | 4.6112 | 4.4255
| CLACHAN | INVERARAY | MINIMUM HEADROOM | NN 09172 09746 | YES | YES | 0.003 | 1.9592 | 1.7673 | 1.6459 | 1.5704 | 1.4786 | 1.2806 | 1.1959 | 1.1194 | 0.99388 | 0.86531 | 0.41531 | 0.38061 | 0.39184 | 2.0995 | 1.8321 | 1.675 | 1.7878 | 1.7531 | 1.649 | 1.5663 | 1.498 | 1.3714 | 1.2357 | 0.79286 | 0.7602 | 0.78367 | 2.0651 | 1.8293 | 1.6906 | 1.7112 | 1.6735 | 1.4622 | 1.3888 | 1.3163 | 1.1908 | 1.0316 | 0.55714 | 0.51327 | 0.53163
|  | INVERARAY | EE |  |  |  |  | 1.9592 | 1.9663 | 1.7714 | 1.6939 | 1.5663 | 1.2857 | 1.2602 | 1.1357 | 1.0194 | 0.98571 | 0.41531 | 0.38061 | 0.41122 | 2.0995 | 2.1046 | 1.8332 | 1.948 | 1.7847 | 1.6541 | 1.6306 | 1.5122 | 1.4 | 1.3653 | 0.79898 | 0.7602 | 0.79184 | 2.0651 | 2.0732 | 1.8334 | 1.8551 | 1.7112 | 1.4673 | 1.4459 | 1.3316 | 1.2184 | 1.1837 | 0.55714 | 0.51327 | 0.54694
|  | INVERARAY | HT |  |  |  |  | 1.9592 | 1.7673 | 1.6459 | 1.5704 | 1.55 | 1.2969 | 1.1959 | 1.1714 | 1.0071 | 0.86531 | 0.43265 | 0.39184 | 0.39184 | 2.0995 | 1.8321 | 1.675 | 1.7878 | 1.7612 | 1.6633 | 1.5663 | 1.5439 | 1.3806 | 1.2357 | 0.80612 | 0.76837 | 0.78367 | 2.0651 | 1.8293 | 1.6906 | 1.7112 | 1.6888 | 1.4776 | 1.3888 | 1.3643 | 1.1908 | 1.0316 | 0.57245 | 0.52551 | 0.53163
|  | INVERARAY | HE |  |  |  |  | 1.9592 | 1.9663 | 1.7714 | 1.6939 | 1.5153 | 1.2806 | 1.2561 | 1.1194 | 0.99388 | 0.96429 | 0.41633 | 0.45408 | 0.43163 | 2.0995 | 2.1046 | 1.8332 | 1.948 | 1.7531 | 1.649 | 1.6276 | 1.498 | 1.3714 | 1.3429 | 0.79286 | 0.83061 | 0.8102 | 2.0651 | 2.0732 | 1.8334 | 1.8531 | 1.6735 | 1.4622 | 1.4429 | 1.3163 | 1.1908 | 1.1633 | 0.55714 | 0.58776 | 0.56837
|  | INVERARAY | FB |  |  |  |  | 1.9878 | 1.9796 | 1.9837 | 1.8357 | 1.4786 | 1.3673 | 1.3276 | 1.3214 | 1.3265 | 1.3214 | 1.1714 | 0.93776 | 0.92347 | 2.1168 | 2.1097 | 2.1138 | 2.1133 | 1.8388 | 1.7245 | 1.6786 | 1.6714 | 1.6745 | 1.6643 | 1.4694 | 1.1388 | 1.1204 | 2.0834 | 2.0814 | 2.0885 | 2.0112 | 1.6816 | 1.55 | 1.5051 | 1.499 | 1.5051 | 1.5 | 1.3163 | 1.0296 | 1.0204
| LUNANHEAD | INVERARITY | MINIMUM HEADROOM | NO 44549 44200 | YES | YES | 0 | 0.29592 | 0.2898 | 0.28367 | 0.26837 | 0.24082 | 0.044898 | -0.16122 | -0.2051 | -0.27347 | -0.36939 | -0.58265 | -0.63061 | -0.68878 | 0.45 | 0.44592 | 0.44184 | 0.43469 | 0.42653 | 0.25306 | 0.060204 | 0.023469 | -0.031633 | -0.13673 | -0.32857 | -0.31429 | -0.29286 | 0.30918 | 0.30204 | 0.29286 | 0.28265 | 0.25918 | 0.066327 | -0.13571 | -0.17653 | -0.23469 | -0.3449 | -0.54388 | -0.55 | -0.55612
|  | INVERARITY | EE |  |  |  |  | 0.29592 | 0.29082 | 0.28469 | 0.27245 | 0.2449 | 0.20408 | 0.17755 | -0.02449 | -0.22755 | -0.27653 | -0.57041 | -0.61939 | -0.66327 | 0.45 | 0.44592 | 0.44184 | 0.43469 | 0.42755 | 0.41224 | 0.39898 | 0.21429 | 0.005102 | -0.034694 | -0.29184 | -0.28163 | -0.26939 | 0.30918 | 0.30204 | 0.29286 | 0.28469 | 0.26224 | 0.22857 | 0.20408 | 0.0071429 | -0.20408 | -0.24694 | -0.52551 | -0.52347 | -0.52551
|  | INVERARITY | HT |  |  |  |  | 0.29694 | 0.2898 | 0.28469 | 0.27143 | 0.24592 | 0.044898 | -0.16122 | -0.2051 | -0.27347 | -0.36939 | -0.58265 | -0.63061 | -0.68878 | 0.45 | 0.44592 | 0.44184 | 0.43469 | 0.42857 | 0.25306 | 0.060204 | 0.023469 | -0.031633 | -0.13673 | -0.32857 | -0.31429 | -0.29286 | 0.30918 | 0.30204 | 0.29388 | 0.28469 | 0.26327 | 0.066327 | -0.13571 | -0.17653 | -0.23469 | -0.3449 | -0.54388 | -0.55 | -0.55612
|  | INVERARITY | HE |  |  |  |  | 0.29694 | 0.29082 | 0.28367 | 0.26837 | 0.24082 | 0.19796 | 0.17143 | 0.13367 | 0.1051 | 0.066327 | -0.0091837 | -0.073469 | -0.13673 | 0.45 | 0.44694 | 0.44184 | 0.43469 | 0.42653 | 0.4102 | 0.39796 | 0.38571 | 0.36837 | 0.3449 | 0.30102 | 0.28673 | 0.27551 | 0.30918 | 0.30204 | 0.29286 | 0.28265 | 0.25918 | 0.22449 | 0.19898 | 0.16939 | 0.13367 | 0.1 | 0.031633 | 0.011224 | -0.018367
|  | INVERARITY | FB |  |  |  |  | 0.31224 | 0.3102 | 0.30714 | 0.3051 | 0.29694 | 0.28776 | 0.27551 | 0.25612 | 0.24592 | 0.22755 | 0.13776 | 0.058163 | -0.26122 | 0.4602 | 0.45816 | 0.45612 | 0.45612 | 0.45102 | 0.44694 | 0.44082 | 0.43265 | 0.42959 | 0.41939 | 0.37449 | 0.31633 | -0.045918 | 0.32449 | 0.31837 | 0.31633 | 0.31531 | 0.30612 | 0.29898 | 0.28776 | 0.26939 | 0.2602 | 0.2449 | 0.16327 | 0.080612 | -0.23673
| INVERNESS | INVERARNIE | MINIMUM HEADROOM | NH 68830 34971 | YES | NO | 0.749 | 1.1366 | 1.1284 | 1.1141 | 1.0876 | 1.0539 | 0.99374 | 0.96721 | 0.91517 | 0.86517 | 0.83456 | 0.72843 | 0.61211 | 0.50904 | 1.307 | 1.3029 | 1.2937 | 1.2866 | 1.2713 | 1.2427 | 1.2192 | 1.1866 | 1.1621 | 1.1509 | 1.1029 | 1.108 | 1.1019 | 1.2897 | 1.2825 | 1.2713 | 1.2529 | 1.2244 | 1.1774 | 1.1417 | 1.0917 | 1.0519 | 1.0386 | 0.98251 | 0.91619 | 0.85292
|  | INVERARNIE | EE |  |  |  |  | 1.1376 | 1.1284 | 1.1141 | 1.0907 | 1.0631 | 0.99884 | 0.98149 | 0.92945 | 0.88047 | 0.85088 | 0.72843 | 0.61211 | 0.50904 | 1.309 | 1.3039 | 1.2937 | 1.2866 | 1.2723 | 1.2427 | 1.2192 | 1.1866 | 1.1621 | 1.1519 | 1.1152 | 1.1141 | 1.1019 | 1.2907 | 1.2825 | 1.2713 | 1.2539 | 1.2295 | 1.1815 | 1.1468 | 1.1029 | 1.0631 | 1.0386 | 0.98251 | 0.91619 | 0.85292
|  | INVERARNIE | HT |  |  |  |  | 1.1386 | 1.1295 | 1.1172 | 1.0927 | 1.0641 | 1.0141 | 0.96721 | 0.93762 | 0.89068 | 0.86313 | 0.77027 | 0.63966 | 0.52537 | 1.309 | 1.3029 | 1.2937 | 1.2866 | 1.2713 | 1.2448 | 1.2213 | 1.1886 | 1.1621 | 1.1539 | 1.1029 | 1.108 | 1.1172 | 1.2917 | 1.2835 | 1.2733 | 1.255 | 1.2305 | 1.1907 | 1.155 | 1.109 | 1.0662 | 1.0488 | 1.0019 | 0.92843 | 0.86823
|  | INVERARNIE | HE |  |  |  |  | 1.1366 | 1.1295 | 1.1182 | 1.0876 | 1.0539 | 0.99374 | 0.97129 | 0.91517 | 0.86517 | 0.83456 | 0.76211 | 0.62843 | 0.55496 | 1.307 | 1.3029 | 1.2958 | 1.2866 | 1.2713 | 1.2427 | 1.2213 | 1.1876 | 1.1631 | 1.1509 | 1.1162 | 1.1152 | 1.1152 | 1.2897 | 1.2835 | 1.2744 | 1.2529 | 1.2244 | 1.1774 | 1.1417 | 1.0917 | 1.0519 | 1.056 | 0.99986 | 0.92537 | 0.88353
|  | INVERARNIE | FB |  |  |  |  | 1.157 | 1.156 | 1.155 | 1.1488 | 1.1346 | 1.1203 | 1.108 | 1.0978 | 1.0795 | 1.0703 | 0.97129 | 0.92639 | 0.90088 | 1.3244 | 1.3213 | 1.3203 | 1.3182 | 1.3152 | 1.3019 | 1.2937 | 1.2846 | 1.2703 | 1.2631 | 1.206 | 1.1641 | 1.1458 | 1.307 | 1.307 | 1.305 | 1.3009 | 1.2897 | 1.2784 | 1.2682 | 1.259 | 1.2407 | 1.2335 | 1.1529 | 1.0835 | 1.0744
| FIDDES | INVERBERVIE | MINIMUM HEADROOM | NO 82850 72935 | NO | NO | 0.446 | 3.4611 | 3.3183 | 3.157 | 2.9948 | 2.9213 | 2.7101 | 2.3917 | 2.0764 | 1.6642 | 1.4693 | 0.30296 | -0.43582 | -0.995 | 4.0989 | 3.9295 | 3.756 | 3.5815 | 3.553 | 3.4846 | 3.3876 | 3.2958 | 3.1723 | 3.0815 | 2.5244 | 2.4795 | 2.2866 | 4.0264 | 3.8856 | 3.7274 | 3.5672 | 3.5305 | 3.3642 | 3.1203 | 2.904 | 2.5856 | 2.4091 | 1.4152 | 0.92642 | 0.53357
|  | INVERBERVIE | EE |  |  |  |  | 3.5121 | 3.3183 | 3.1713 | 2.9948 | 2.9417 | 2.7509 | 2.5223 | 2.2897 | 1.9713 | 1.7805 | 0.30296 | -0.43582 | -0.995 | 4.1611 | 3.9295 | 3.756 | 3.5815 | 3.555 | 3.4907 | 3.4244 | 3.353 | 3.2448 | 3.1621 | 2.5244 | 2.4795 | 2.2866 | 4.0744 | 3.8856 | 3.7274 | 3.5672 | 3.5448 | 3.3928 | 3.2101 | 3.0295 | 2.7968 | 2.6244 | 1.4152 | 0.92642 | 0.53357
|  | INVERBERVIE | HT |  |  |  |  | 3.4815 | 3.3274 | 3.1866 | 3.0152 | 2.9499 | 2.7438 | 2.3917 | 2.0764 | 1.6642 | 1.4693 | 0.51418 | -0.21949 | -0.77358 | 4.1223 | 3.9366 | 3.7713 | 3.5907 | 3.553 | 3.4846 | 3.3876 | 3.2958 | 3.1723 | 3.0815 | 2.6642 | 2.6774 | 2.7081 | 4.0448 | 3.8948 | 3.7581 | 3.5836 | 3.5489 | 3.3846 | 3.1203 | 2.904 | 2.5856 | 2.4091 | 1.6183 | 1.156 | 0.76418
|  | INVERBERVIE | HE |  |  |  |  | 3.4611 | 3.3203 | 3.157 | 2.9958 | 2.9213 | 2.7101 | 2.4346 | 2.1805 | 1.8489 | 1.6479 | 0.71622 | -0.19092 | -0.60317 | 4.0989 | 3.9295 | 3.757 | 3.5907 | 3.553 | 3.4866 | 3.4121 | 3.3438 | 3.2428 | 3.1509 | 2.7795 | 2.653 | 2.504 | 4.0264 | 3.8856 | 3.7305 | 3.5672 | 3.5305 | 3.3642 | 3.1519 | 2.9509 | 2.704 | 2.5387 | 1.7887 | 1.1825 | 0.905
|  | INVERBERVIE | FB |  |  |  |  | 3.7142 | 3.5856 | 3.4499 | 3.3438 | 3.2825 | 3.1866 | 3.1305 | 3.055 | 2.9438 | 2.8999 | 2.4223 | 1.4825 | 1.2825 | 4.353 | 4.1785 | 3.9968 | 3.8754 | 3.7785 | 3.6887 | 3.6417 | 3.5897 | 3.5325 | 3.505 | 3.3009 | 2.7499 | 2.4234 | 4.2621 | 4.1407 | 4.0101 | 3.9111 | 3.8193 | 3.7264 | 3.6876 | 3.6254 | 3.5346 | 3.4876 | 3.0846 | 2.2407 | 2.1397
| GRUDIE BRIDGE | INVERBROOM | MINIMUM HEADROOM | NH 17885 84667 | YES | NO | 0.012 | 0.10641 | 0.10335 | 0.099265 | 0.095184 | 0.090082 | 0.079878 | 0.071714 | 0.058449 | 0.052327 | 0.045184 | 0.020694 | 0.0013061 | -0.01298 | 0.12106 | 0.11698 | 0.11494 | 0.11392 | 0.10984 | 0.10882 | 0.10065 | 0.090449 | 0.087388 | 0.077184 | 0.049633 | 0.051673 | 0.057796 | 0.11271 | 0.10965 | 0.10557 | 0.10251 | 0.099449 | 0.093327 | 0.082102 | 0.069857 | 0.065776 | 0.056592 | 0.035163 | 0.021898 | 0.013735
|  | INVERBROOM | EE |  |  |  |  | 0.10641 | 0.10335 | 0.099265 | 0.097224 | 0.093143 | 0.079878 | 0.073755 | 0.059469 | 0.055388 | 0.045184 | 0.020694 | 0.0043673 | -0.011959 | 0.12208 | 0.11698 | 0.11494 | 0.11392 | 0.11188 | 0.10882 | 0.10065 | 0.090449 | 0.089429 | 0.077184 | 0.055755 | 0.057796 | 0.06698 | 0.11373 | 0.10965 | 0.10557 | 0.10455 | 0.10047 | 0.093327 | 0.084143 | 0.070878 | 0.068837 | 0.056592 | 0.035163 | 0.024959 | 0.020878
|  | INVERBROOM | HT |  |  |  |  | 0.10641 | 0.10335 | 0.099265 | 0.097224 | 0.093143 | 0.083959 | 0.074776 | 0.06049 | 0.056408 | 0.047224 | 0.024776 | 0.0033469 | -0.01298 | 0.12208 | 0.11698 | 0.11596 | 0.11392 | 0.11188 | 0.10984 | 0.10065 | 0.090449 | 0.088408 | 0.078204 | 0.049633 | 0.051673 | 0.059837 | 0.11373 | 0.10965 | 0.10557 | 0.10353 | 0.10047 | 0.096388 | 0.085163 | 0.071898 | 0.068837 | 0.057612 | 0.038224 | 0.021898 | 0.015776
|  | INVERBROOM | HE |  |  |  |  | 0.10641 | 0.10335 | 0.099265 | 0.095184 | 0.090082 | 0.079878 | 0.071714 | 0.058449 | 0.052327 | 0.046204 | 0.027837 | 0.0013061 | -0.011959 | 0.12106 | 0.11698 | 0.11596 | 0.11392 | 0.10984 | 0.10882 | 0.10065 | 0.090449 | 0.087388 | 0.078204 | 0.055755 | 0.055755 | 0.059837 | 0.11271 | 0.10965 | 0.10557 | 0.10251 | 0.099449 | 0.093327 | 0.082102 | 0.069857 | 0.065776 | 0.056592 | 0.039245 | 0.021898 | 0.013735
|  | INVERBROOM | FB |  |  |  |  | 0.11253 | 0.11559 | 0.11457 | 0.11253 | 0.11151 | 0.11151 | 0.10947 | 0.10335 | 0.099265 | 0.10131 | 0.081918 | 0.064571 | 0.056408 | 0.1282 | 0.13024 | 0.12514 | 0.12616 | 0.12412 | 0.12412 | 0.1231 | 0.11698 | 0.10984 | 0.10882 | 0.091469 | 0.072082 | 0.057796 | 0.1219 | 0.12394 | 0.1219 | 0.1219 | 0.11782 | 0.11884 | 0.11578 | 0.11067 | 0.10761 | 0.10659 | 0.089245 | 0.066796 | 0.065776
| FORT AUGUSTUS | INVERGARRY | MINIMUM HEADROOM | NH 29862 01000 | YES | YES | 0.036 | 0.7 | 0.69694 | 0.6949 | 0.68367 | 0.67959 | 0.65306 | 0.64082 | 0.62347 | 0.60816 | 0.5898 | 0.56327 | 0.54796 | 0.52551 | 0.79694 | 0.79592 | 0.79082 | 0.78776 | 0.78571 | 0.77449 | 0.76633 | 0.75714 | 0.74388 | 0.73163 | 0.70306 | 0.70612 | 0.68878 | 0.74694 | 0.74388 | 0.74082 | 0.73163 | 0.72755 | 0.7051 | 0.69286 | 0.67959 | 0.66224 | 0.6449 | 0.61531 | 0.59592 | 0.58163
|  | INVERGARRY | EE |  |  |  |  | 0.7 | 0.69694 | 0.6949 | 0.68367 | 0.68163 | 0.65306 | 0.64184 | 0.62755 | 0.6102 | 0.59388 | 0.57551 | 0.54796 | 0.52857 | 0.79694 | 0.79592 | 0.79082 | 0.78878 | 0.78776 | 0.77449 | 0.76633 | 0.75816 | 0.7449 | 0.73265 | 0.7102 | 0.70612 | 0.70816 | 0.74694 | 0.74388 | 0.74082 | 0.73163 | 0.72959 | 0.7051 | 0.69388 | 0.68163 | 0.66429 | 0.64796 | 0.61531 | 0.59592 | 0.58776
|  | INVERGARRY | HT |  |  |  |  | 0.70102 | 0.69694 | 0.69592 | 0.68367 | 0.68061 | 0.65918 | 0.64694 | 0.63061 | 0.6102 | 0.59796 | 0.56327 | 0.5602 | 0.52551 | 0.79796 | 0.79592 | 0.79184 | 0.78878 | 0.78571 | 0.77449 | 0.76735 | 0.75714 | 0.74388 | 0.73265 | 0.70306 | 0.71327 | 0.70918 | 0.74694 | 0.74388 | 0.74184 | 0.73163 | 0.72857 | 0.70918 | 0.69694 | 0.68367 | 0.66429 | 0.65102 | 0.62143 | 0.6051 | 0.58265
|  | INVERGARRY | HE |  |  |  |  | 0.70102 | 0.69898 | 0.69592 | 0.68367 | 0.67959 | 0.6551 | 0.64082 | 0.62347 | 0.60816 | 0.5898 | 0.58265 | 0.55102 | 0.52755 | 0.79796 | 0.79898 | 0.79184 | 0.78776 | 0.78571 | 0.77449 | 0.76633 | 0.75714 | 0.74388 | 0.73163 | 0.71122 | 0.70612 | 0.69796 | 0.74694 | 0.74592 | 0.74184 | 0.73163 | 0.72755 | 0.70612 | 0.69286 | 0.67959 | 0.66224 | 0.6449 | 0.62041 | 0.59796 | 0.58163
|  | INVERGARRY | FB |  |  |  |  | 0.71837 | 0.71633 | 0.71327 | 0.71429 | 0.7102 | 0.70408 | 0.70204 | 0.70102 | 0.6898 | 0.69184 | 0.6602 | 0.63265 | 0.61735 | 0.81429 | 0.8102 | 0.8051 | 0.80816 | 0.80306 | 0.79694 | 0.79388 | 0.78878 | 0.78061 | 0.77857 | 0.74592 | 0.71429 | 0.68878 | 0.76735 | 0.76327 | 0.75714 | 0.75918 | 0.7551 | 0.74796 | 0.7449 | 0.74082 | 0.73061 | 0.73265 | 0.69796 | 0.66531 | 0.65612
| ALNESS | INVERGORDON | MINIMUM HEADROOM | NH 70756 69177 | NO | NO | 3.173 | 7.2858 | 7.1777 | 7.1552 | 7.1022 | 6.7205 | 6.0583 | 5.3409 | 4.142 | 3.2032 | 2.4879 | 0.73687 | 0.097069 | -0.40599 | 7.0318 | 6.9869 | 6.9797 | 6.9736 | 6.8889 | 6.346 | 5.6032 | 4.5879 | 3.7746 | 3.2542 | 2.1593 | 2.0348 | 1.9083 | 4.8241 | 4.7292 | 4.72 | 4.6986 | 4.3659 | 3.7598 | 3.069 | 2.0506 | 1.2068 | 0.5884 | -0.83711 | -1.3759 | -1.6963
|  | INVERGORDON | EE |  |  |  |  | 7.2869 | 7.1797 | 7.1563 | 7.1032 | 6.7205 | 6.4695 | 6.2103 | 5.4909 | 4.6767 | 3.7297 | 0.96748 | 0.097069 | -0.40599 | 7.0318 | 6.9869 | 6.9797 | 6.9736 | 6.8889 | 6.8348 | 6.6838 | 6.146 | 5.3981 | 4.446 | 2.4022 | 2.0348 | 1.9083 | 4.8241 | 4.7302 | 4.7221 | 4.6986 | 4.3659 | 4.17 | 3.97 | 3.3292 | 2.5251 | 1.6537 | -0.65242 | -1.3759 | -1.6963
|  | INVERGORDON | HT |  |  |  |  | 7.2858 | 7.1777 | 7.1552 | 7.1042 | 6.7236 | 6.0583 | 5.3409 | 4.142 | 3.2032 | 2.4879 | 0.73687 | 0.11136 | -0.37742 | 7.0318 | 6.9879 | 6.9807 | 6.9756 | 6.892 | 6.346 | 5.6032 | 4.5879 | 3.7746 | 3.2542 | 2.1593 | 2.0583 | 2.0083 | 4.8251 | 4.7292 | 4.72 | 4.6986 | 4.369 | 3.7598 | 3.069 | 2.0506 | 1.2068 | 0.5884 | -0.83711 | -1.3136 | -1.6136
|  | INVERGORDON | HE |  |  |  |  | 7.2869 | 7.1807 | 7.1563 | 7.1022 | 6.7205 | 6.4838 | 6.2144 | 5.4205 | 4.6001 | 3.5093 | 1.2032 | 0.45931 | 0.17156 | 7.0318 | 6.9889 | 6.9807 | 6.9756 | 6.892 | 6.8307 | 6.6797 | 6.0348 | 5.2705 | 4.1603 | 2.4675 | 2.1532 | 2.0869 | 4.8251 | 4.7292 | 4.72 | 4.6986 | 4.368 | 4.1823 | 3.9751 | 3.2364 | 2.421 | 1.467 | -0.40752 | -0.90548 | -1.1208
|  | INVERGORDON | FB |  |  |  |  | 7.3134 | 7.2552 | 7.2532 | 7.2491 | 7.2369 | 6.8899 | 6.7879 | 6.643 | 6.3073 | 5.8787 | 2.7185 | 1.9501 | 1.6563 | 7.0532 | 7.0267 | 7.0318 | 7.0318 | 7.0379 | 6.9522 | 6.9144 | 6.8634 | 6.4797 | 5.9277 | 2.9236 | 2.2358 | 1.9205 | 4.8506 | 4.7925 | 4.7853 | 4.7843 | 4.7813 | 4.4884 | 4.418 | 4.3241 | 3.9802 | 3.5353 | 0.48431 | -0.17997 | -0.29936
| FORT WILLIAM | INVERLOCHY | MINIMUM HEADROOM | NN 11653 74987 | NO | NO | 6.429 | 0.87324 | 0.9212 | 15.463 | 15.2457 | 15.0794 | 14.0824 | 13.2671 | 12.5069 | 11.8324 | 11.659 | 10.76 | 9.8345 | 9.3273 | 3.0385 | 3.06 | 16.8773 | 16.663 | 16.5222 | 15.8845 | 15.4161 | 14.8171 | 14.313 | 14.0947 | 13.3447 | 12.912 | 12.6875 | 2.2788 | 2.2891 | 16.4722 | 16.3385 | 16.2324 | 15.4161 | 14.6671 | 13.9457 | 13.3365 | 13.1753 | 12.5171 | 11.9865 | 11.6008
|  | INVERLOCHY | EE |  |  |  |  | 0.87324 | 0.9212 | 15.463 | 15.2457 | 15.0875 | 14.6294 | 14.1487 | 13.36 | 12.6457 | 12.0008 | 10.76 | 9.8345 | 9.3314 | 3.0385 | 3.06 | 16.8773 | 16.663 | 16.5222 | 16.2487 | 16.0896 | 15.5008 | 14.9549 | 14.4049 | 13.3671 | 12.912 | 12.6936 | 2.2788 | 2.2891 | 16.4722 | 16.3385 | 16.2375 | 15.9232 | 15.5426 | 14.8232 | 14.1579 | 13.5222 | 12.5171 | 11.9865 | 11.6763
|  | INVERLOCHY | HT |  |  |  |  | 0.87324 | 0.92222 | 15.4641 | 15.2467 | 15.0794 | 14.0824 | 13.2671 | 12.5069 | 11.8324 | 11.659 | 10.911 | 9.9651 | 9.3273 | 3.0385 | 3.06 | 16.8773 | 16.6651 | 16.5232 | 15.8845 | 15.4161 | 14.8171 | 14.313 | 14.0947 | 13.3447 | 12.9406 | 12.8549 | 2.2788 | 2.2911 | 16.4732 | 16.3385 | 16.2324 | 15.4161 | 14.6671 | 13.9457 | 13.3365 | 13.1753 | 12.5824 | 12.011 | 11.6008
|  | INVERLOCHY | HE |  |  |  |  | 0.87324 | 0.9212 | 15.4641 | 15.2498 | 15.0896 | 14.5957 | 14.1702 | 13.3661 | 12.6334 | 11.8926 | 11.0232 | 10.3202 | 9.8783 | 3.0385 | 3.06 | 16.8773 | 16.6651 | 16.5243 | 16.2375 | 16.0947 | 15.4783 | 14.9069 | 14.3477 | 13.5294 | 13.3773 | 13.2181 | 2.2788 | 2.2901 | 16.4732 | 16.3406 | 16.2375 | 15.9049 | 15.5579 | 14.809 | 14.1151 | 13.409 | 12.6559 | 12.1936 | 11.9243
|  | INVERLOCHY | FB |  |  |  |  | 0.98752 | 1.0732 | 15.6681 | 15.5926 | 15.5845 | 15.5855 | 15.4845 | 15.3396 | 14.9508 | 14.6294 | 13.0712 | 12.3559 | 11.8528 | 3.1059 | 3.1569 | 16.9916 | 16.8355 | 16.7926 | 16.762 | 16.6804 | 16.5059 | 16.159 | 15.8457 | 14.3926 | 13.4896 | 12.6875 | 2.3595 | 2.4115 | 16.611 | 16.5416 | 16.5385 | 16.5375 | 16.4569 | 16.3518 | 15.9467 | 15.5926 | 14.1804 | 13.5549 | 13.3487
| PORT ANN | INVERNEIL | MINIMUM HEADROOM | NR 84790 80580 | YES | YES | 0.064 | 2.2143 | 2.2112 | 2.2082 | 2.1867 | 2.1663 | 2.1041 | 2.0592 | 2.0173 | 1.9735 | 1.949 | 1.8816 | 1.8235 | 1.7704 | 2.5214 | 2.5214 | 2.5235 | 2.499 | 2.4755 | 2.4429 | 2.4102 | 2.3684 | 2.3459 | 2.3041 | 2.2102 | 2.1959 | 2.2 | 2.3959 | 2.3898 | 2.3816 | 2.352 | 2.3265 | 2.2806 | 2.2337 | 2.1888 | 2.1633 | 2.1235 | 2.0296 | 1.999 | 1.9898
|  | INVERNEIL | EE |  |  |  |  | 2.2143 | 2.2133 | 2.2082 | 2.1867 | 2.1663 | 2.1286 | 2.099 | 2.0378 | 1.998 | 1.9714 | 1.8816 | 1.8255 | 1.7847 | 2.5214 | 2.5224 | 2.5235 | 2.499 | 2.4755 | 2.4459 | 2.4163 | 2.3684 | 2.35 | 2.3082 | 2.2286 | 2.2173 | 2.2235 | 2.3959 | 2.3898 | 2.3816 | 2.352 | 2.3265 | 2.2888 | 2.249 | 2.1888 | 2.1735 | 2.1327 | 2.0429 | 2.0184 | 2.0112
|  | INVERNEIL | HT |  |  |  |  | 2.2143 | 2.2122 | 2.2112 | 2.1918 | 2.1704 | 2.1041 | 2.0592 | 2.0173 | 1.9735 | 1.949 | 1.8878 | 1.8245 | 1.7704 | 2.5214 | 2.5224 | 2.5235 | 2.499 | 2.4755 | 2.4429 | 2.4102 | 2.3847 | 2.3459 | 2.3041 | 2.2102 | 2.1959 | 2.2051 | 2.3959 | 2.3898 | 2.3827 | 2.3541 | 2.3276 | 2.2806 | 2.2337 | 2.1959 | 2.1633 | 2.1235 | 2.0296 | 1.999 | 1.9908
|  | INVERNEIL | HE |  |  |  |  | 2.2143 | 2.2112 | 2.2102 | 2.1878 | 2.1663 | 2.1286 | 2.0857 | 2.0347 | 1.9827 | 1.9541 | 1.8929 | 1.8235 | 1.7776 | 2.5214 | 2.5214 | 2.5235 | 2.499 | 2.4755 | 2.4449 | 2.4143 | 2.3867 | 2.3459 | 2.3041 | 2.2286 | 2.2092 | 2.2 | 2.3959 | 2.3898 | 2.3816 | 2.352 | 2.3265 | 2.2888 | 2.2429 | 2.202 | 2.1663 | 2.1255 | 2.0449 | 2.0102 | 1.9898
|  | INVERNEIL | FB |  |  |  |  | 2.2306 | 2.2327 | 2.2367 | 2.2337 | 2.2357 | 2.2327 | 2.2214 | 2.2102 | 2.1969 | 2.1847 | 2.1051 | 2.0367 | 1.998 | 2.5388 | 2.5439 | 2.5449 | 2.5296 | 2.5204 | 2.5082 | 2.4867 | 2.4776 | 2.4633 | 2.4398 | 2.3469 | 2.248 | 2.2051 | 2.4133 | 2.4133 | 2.4092 | 2.3959 | 2.3888 | 2.3776 | 2.3571 | 2.3469 | 2.3316 | 2.3112 | 2.2102 | 2.0929 | 2.0694
| INVERNESS | INVERNESS | MINIMUM HEADROOM | NH 65302 42625 | NO | NO | 4.547 | 3.6604 | 3.491 | 3.2665 | 2.942 | 2.843 | 2.095 | 1.4777 | 0.84811 | 0.2828 | -0.2274 | -2.2345 | -3.6243 | -4.4621 | 5.8063 | 5.6399 | 5.5369 | 5.4195 | 5.4634 | 5.1257 | 4.845 | 4.5512 | 4.3012 | 4.0542 | 3.2634 | 3.0665 | 2.6542 | 4.4884 | 4.1731 | 3.9547 | 3.6884 | 3.667 | 3.0456 | 2.5568 | 2.0507 | 1.6027 | 1.1874 | -0.39832 | -1.3585 | -1.9197
|  | INVERNESS | EE |  |  |  |  | 3.6614 | 3.491 | 3.2665 | 2.942 | 2.843 | 2.3746 | 1.6226 | 0.88791 | 0.2828 | -0.16618 | -2.2345 | -3.6243 | -4.4621 | 5.8073 | 5.641 | 5.5389 | 5.4267 | 5.4675 | 5.294 | 4.9593 | 4.6032 | 4.3206 | 4.0869 | 3.3104 | 3.0665 | 2.8348 | 4.4884 | 4.1731 | 3.9547 | 3.6884 | 3.6721 | 3.2721 | 2.6721 | 2.0854 | 1.6027 | 1.2333 | -0.39832 | -1.3585 | -1.9197
|  | INVERNESS | HT |  |  |  |  | 3.6624 | 3.4971 | 3.2767 | 2.9512 | 2.843 | 2.095 | 1.4777 | 0.84811 | 0.29403 | -0.2274 | -2.1335 | -3.459 | -4.2386 | 5.8073 | 5.6399 | 5.5369 | 5.4257 | 5.4634 | 5.1257 | 4.845 | 4.5512 | 4.3012 | 4.0542 | 3.2634 | 3.1695 | 3.2144 | 4.4925 | 4.1782 | 3.9609 | 3.6935 | 3.667 | 3.0456 | 2.5568 | 2.0507 | 1.6098 | 1.1874 | -0.3524 | -1.2504 | -1.7289
|  | INVERNESS | HE |  |  |  |  | 3.6604 | 3.491 | 3.2706 | 2.9461 | 2.843 | 2.295 | 1.6267 | 0.90933 | 0.30729 | -0.12638 | -1.8284 | -3.0621 | -3.6417 | 5.8063 | 5.643 | 5.5389 | 5.4195 | 5.4695 | 5.243 | 4.9522 | 4.5971 | 4.3083 | 4.0838 | 3.3716 | 3.1512 | 3.0522 | 4.4905 | 4.1772 | 3.9619 | 3.6945 | 3.6772 | 3.1996 | 2.6762 | 2.0976 | 1.6129 | 1.2568 | -0.10954 | -0.94526 | -1.2626
|  | INVERNESS | FB |  |  |  |  | 3.7971 | 3.742 | 3.5716 | 3.3746 | 3.3471 | 3.294 | 3.0246 | 2.7481 | 2.5124 | 2.3859 | 1.391 | 0.4328 | -0.061073 | 5.9308 | 5.8971 | 5.8042 | 5.7114 | 5.7093 | 5.6491 | 5.4848 | 5.3583 | 5.1675 | 5.0318 | 4.2838 | 3.3767 | 2.6542 | 4.6619 | 4.6078 | 4.4394 | 4.2558 | 4.2456 | 4.1823 | 3.919 | 3.7078 | 3.4813 | 3.3456 | 2.3956 | 1.3711 | 1.0915
| KINTORE | INVERURIE | MINIMUM HEADROOM | NJ 75665 21688 | NO | YES | 3.209 | 11.5923 | 10.7372 | 9.8923 | 8.8861 | 7.4994 | 5.3076 | 2.928 | 1.2555 | -0.71896 | -1.5598 | -7.2792 | -11.4506 | -14.8057 | 15.4759 | 14.9004 | 14.4045 | 13.8453 | 12.5474 | 11.1086 | 9.3729 | 8.2606 | 6.4545 | 5.8566 | 1.2198 | -1.5261 | -4.1649 | 13.9117 | 13.2137 | 12.5851 | 11.8035 | 10.5525 | 8.7392 | 6.6933 | 5.1555 | 3.0494 | 2.1831 | -3.3812 | -7.3128 | -10.5486
|  | INVERURIE | EE |  |  |  |  | 11.6055 | 10.7719 | 9.9208 | 8.8923 | 7.5504 | 5.3076 | 2.928 | 1.2841 | -0.11284 | -0.85263 | -6.4628 | -10.7455 | -12.9669 | 15.4943 | 14.9157 | 14.4372 | 13.88 | 12.5912 | 11.1086 | 9.4014 | 8.528 | 7.479 | 7.0606 | 3.1678 | 0.44124 | -0.98222 | 13.9219 | 13.2321 | 12.6014 | 11.8066 | 10.5872 | 8.7392 | 6.6933 | 5.2984 | 3.93 | 3.2208 | -2.0383 | -6.2537 | -8.2598
|  | INVERURIE | HT |  |  |  |  | 11.5923 | 10.7372 | 9.8923 | 8.8861 | 7.4994 | 6.2688 | 4.6168 | 2.8555 | 0.729 | -1.0945 | -6.8169 | -11.4506 | -14.8057 | 15.4821 | 14.9004 | 14.4045 | 13.8453 | 12.5474 | 12.1157 | 11.2372 | 10.2912 | 8.478 | 6.8576 | 2.4739 | -0.50263 | -2.8751 | 13.9137 | 13.2137 | 12.5851 | 11.8035 | 10.5525 | 9.63 | 8.2351 | 6.6698 | 4.5382 | 2.8953 | -2.6108 | -7.1322 | -10.3934
|  | INVERURIE | HE |  |  |  |  | 11.5933 | 10.7749 | 9.9259 | 8.9351 | 7.5943 | 5.4514 | 3.079 | 1.2555 | -0.71896 | -1.5598 | -7.2792 | -11.2394 | -14.3394 | 15.4759 | 14.9127 | 14.428 | 13.8708 | 12.5821 | 11.1219 | 9.3729 | 8.2606 | 6.4545 | 5.8566 | 1.2198 | -1.5261 | -4.1649 | 13.9117 | 13.2341 | 12.6096 | 11.8331 | 10.6117 | 8.8361 | 6.7739 | 5.1555 | 3.0494 | 2.1831 | -3.3812 | -7.3128 | -10.5486
|  | INVERURIE | FB |  |  |  |  | 11.9249 | 11.3168 | 10.727 | 10.0525 | 9.5494 | 8.3392 | 6.677 | 4.7831 | 4.0382 | 3.7045 | 1.3484 | -2.0353 | -3.6312 | 15.6525 | 15.1719 | 14.7504 | 14.3096 | 13.7443 | 12.778 | 11.3484 | 9.6647 | 8.9474 | 8.6372 | 6.8004 | 3.9902 | 2.0402 | 14.2106 | 13.6821 | 13.2127 | 12.6841 | 12.227 | 11.2004 | 9.6219 | 7.8004 | 7.0229 | 6.6759 | 4.5596 | 1.0249 | -0.30671
| BROADFORD | KALNAKIL | MINIMUM HEADROOM | NG 69146 53941 | YES | YES | 0.009 | 2.5367 | 2.5296 | 2.5194 | 2.499 | 2.4704 | 2.4459 | 2.4173 | 2.3816 | 2.3796 | 2.3531 | 2.2949 | 2.2633 | 2.2316 | 2.3597 | 2.3577 | 2.3546 | 2.3474 | 2.327 | 2.3148 | 2.2964 | 2.2689 | 2.2638 | 2.2423 | 2.1893 | 2.1913 | 2.2015 | 2.4416 | 2.4385 | 2.4304 | 2.412 | 2.3865 | 2.3671 | 2.3406 | 2.311 | 2.2997 | 2.2753 | 2.2191 | 2.213 | 2.2059
|  | KALNAKIL | EE |  |  |  |  | 2.5367 | 2.5296 | 2.5194 | 2.5 | 2.4714 | 2.4469 | 2.4194 | 2.3837 | 2.3816 | 2.3551 | 2.2949 | 2.2653 | 2.2367 | 2.3597 | 2.3577 | 2.3546 | 2.3474 | 2.327 | 2.3148 | 2.2974 | 2.2709 | 2.2648 | 2.2423 | 2.2015 | 2.2015 | 2.2148 | 2.4416 | 2.4385 | 2.4304 | 2.412 | 2.3875 | 2.3681 | 2.3426 | 2.313 | 2.2997 | 2.2773 | 2.2242 | 2.2191 | 2.2171
|  | KALNAKIL | HT |  |  |  |  | 2.5367 | 2.5296 | 2.5194 | 2.5 | 2.4714 | 2.449 | 2.4204 | 2.3857 | 2.3837 | 2.3582 | 2.2949 | 2.2633 | 2.2316 | 2.3597 | 2.3577 | 2.3546 | 2.3474 | 2.327 | 2.3148 | 2.2964 | 2.2699 | 2.2638 | 2.2423 | 2.1893 | 2.1913 | 2.2015 | 2.4416 | 2.4385 | 2.4304 | 2.413 | 2.3875 | 2.3691 | 2.3436 | 2.313 | 2.3028 | 2.2793 | 2.2191 | 2.213 | 2.2059
|  | KALNAKIL | HE |  |  |  |  | 2.5398 | 2.5296 | 2.5194 | 2.499 | 2.4704 | 2.4459 | 2.4173 | 2.3816 | 2.3796 | 2.3531 | 2.302 | 2.2684 | 2.2408 | 2.3628 | 2.3577 | 2.3546 | 2.3474 | 2.327 | 2.3148 | 2.2964 | 2.2689 | 2.2638 | 2.2423 | 2.2015 | 2.2005 | 2.2026 | 2.4446 | 2.4385 | 2.4304 | 2.412 | 2.3865 | 2.3671 | 2.3406 | 2.311 | 2.2997 | 2.2753 | 2.2273 | 2.2202 | 2.211
|  | KALNAKIL | FB |  |  |  |  | 2.55 | 2.548 | 2.5408 | 2.5357 | 2.5224 | 2.5184 | 2.5031 | 2.5 | 2.4847 | 2.4755 | 2.4245 | 2.3714 | 2.3561 | 2.373 | 2.3719 | 2.3689 | 2.3689 | 2.3617 | 2.3587 | 2.3454 | 2.3423 | 2.3281 | 2.3179 | 2.276 | 2.2311 | 2.2179 | 2.4579 | 2.4559 | 2.4497 | 2.4446 | 2.4314 | 2.4283 | 2.413 | 2.411 | 2.3967 | 2.3875 | 2.3416 | 2.2844 | 2.2783
| DUNOON | KAMES | MINIMUM HEADROOM | NR 96305 71237 | YES | YES | 0.22 | 1.9204 | 1.9347 | 1.9337 | 1.9071 | 1.6439 | 1.5327 | 1.3857 | 1.3388 | 1.1969 | 1.0908 | 0.79796 | 0.55 | 0.47041 | 2.1454 | 2.1464 | 2.1474 | 2.1444 | 1.8352 | 1.777 | 1.6209 | 1.5893 | 1.4526 | 1.3505 | 1.0944 | 0.89133 | 0.86786 | 2.0957 | 2.1059 | 2.1099 | 2.1008 | 1.8538 | 1.761 | 1.5997 | 1.5569 | 1.4334 | 1.3344 | 1.0467 | 0.80179 | 0.74974
|  | KAMES | EE |  |  |  |  | 1.9276 | 1.9357 | 1.9347 | 1.9092 | 1.8867 | 1.6071 | 1.4745 | 1.3949 | 1.2459 | 1.1714 | 0.79796 | 0.55 | 0.47041 | 2.1505 | 2.1474 | 2.1485 | 2.1474 | 2.1444 | 1.8587 | 1.7179 | 1.6495 | 1.5066 | 1.4393 | 1.0954 | 0.89133 | 0.86786 | 2.0987 | 2.1069 | 2.111 | 2.1059 | 2.1018 | 1.8406 | 1.6977 | 1.6212 | 1.4926 | 1.4232 | 1.0467 | 0.80179 | 0.74974
|  | KAMES | HT |  |  |  |  | 1.9204 | 1.9357 | 1.9337 | 1.9082 | 1.8857 | 1.5327 | 1.3857 | 1.3388 | 1.1969 | 1.0908 | 0.81939 | 0.60918 | 0.56122 | 2.1454 | 2.1464 | 2.1474 | 2.1444 | 2.1403 | 1.777 | 1.6209 | 1.5893 | 1.4526 | 1.3505 | 1.0944 | 0.94133 | 0.97806 | 2.0957 | 2.1059 | 2.1099 | 2.1008 | 2.0967 | 1.761 | 1.5997 | 1.5569 | 1.4334 | 1.3344 | 1.0722 | 0.87321 | 0.85077
|  | KAMES | HE |  |  |  |  | 1.9276 | 1.9347 | 1.9347 | 1.9071 | 1.8847 | 1.6041 | 1.4653 | 1.3765 | 1.249 | 1.1163 | 0.98469 | 0.86122 | 0.7898 | 2.1505 | 2.1464 | 2.1485 | 2.1444 | 2.1413 | 1.8556 | 1.7128 | 1.6362 | 1.5168 | 1.3872 | 1.2913 | 1.2281 | 1.2046 | 2.0987 | 2.1059 | 2.111 | 2.1028 | 2.0977 | 1.8344 | 1.6885 | 1.6018 | 1.4967 | 1.3671 | 1.2538 | 1.1436 | 1.0855
|  | KAMES | FB |  |  |  |  | 1.9429 | 1.9571 | 1.9663 | 1.952 | 1.6439 | 1.6276 | 1.6255 | 1.6163 | 1.5949 | 1.5755 | 1.5031 | 1.3602 | 1.1337 | 2.1638 | 2.1658 | 2.174 | 2.1668 | 1.8352 | 1.8209 | 1.8179 | 1.8097 | 1.7923 | 1.774 | 1.7056 | 1.573 | 1.2995 | 2.1099 | 2.1232 | 2.1365 | 2.1406 | 1.8538 | 1.8436 | 1.8457 | 1.8395 | 1.8222 | 1.8048 | 1.7242 | 1.5865 | 1.3589
| KEITH 2 | KEITH | MINIMUM HEADROOM | NJ 43925 50405 | NO | YES | 1.132 | 6.8537 | 6.6914 | 6.519 | 6.4659 | 6.3884 | 6.122 | 5.9904 | 5.6557 | 5.4016 | 4.9894 | 3.9108 | 3.3945 | 3.0945 | 6.0873 | 5.9894 | 5.772 | 5.7363 | 5.6618 | 5.5108 | 5.4139 | 5.1751 | 4.9006 | 4.4424 | 3.2955 | 3.0455 | 2.8496 | 6.8062 | 6.4664 | 6.2685 | 6.1552 | 5.9603 | 5.5623 | 5.393 | 5.0001 | 4.7195 | 4.2654 | 3.1277 | 2.8583 | 2.7705
|  | KEITH | EE |  |  |  |  | 6.8822 | 6.6914 | 6.519 | 6.471 | 6.3955 | 6.1506 | 6.0241 | 5.6833 | 5.472 | 5.0771 | 3.9108 | 3.3945 | 3.0945 | 6.121 | 5.9894 | 5.772 | 5.7414 | 5.6659 | 5.521 | 5.4282 | 5.1914 | 4.9435 | 4.4894 | 3.369 | 3.0782 | 2.9006 | 6.8215 | 6.4664 | 6.2685 | 6.1593 | 5.9603 | 5.5777 | 5.4174 | 5.0134 | 4.7664 | 4.3154 | 3.194 | 2.8889 | 2.7787
|  | KEITH | HT |  |  |  |  | 6.8659 | 6.6924 | 6.5231 | 6.4659 | 6.3884 | 6.122 | 5.9976 | 5.7108 | 5.4016 | 4.9894 | 3.9373 | 3.5149 | 3.2496 | 6.1027 | 5.9904 | 5.7751 | 5.7363 | 5.6618 | 5.5108 | 5.4139 | 5.2363 | 4.9006 | 4.4424 | 3.2955 | 3.0455 | 2.9873 | 6.8134 | 6.4685 | 6.2695 | 6.1552 | 5.9603 | 5.5623 | 5.4195 | 5.0674 | 4.7195 | 4.2654 | 3.1277 | 2.8583 | 2.7705
|  | KEITH | HE |  |  |  |  | 6.8537 | 6.6924 | 6.5231 | 6.468 | 6.3914 | 6.1414 | 5.9904 | 5.6557 | 5.4455 | 5.1016 | 4.2496 | 3.7802 | 3.5241 | 6.0873 | 5.9894 | 5.7751 | 5.7394 | 5.6639 | 5.521 | 5.4169 | 5.1751 | 4.9445 | 4.5353 | 3.6608 | 3.3914 | 3.2608 | 6.8062 | 6.4674 | 6.2695 | 6.1583 | 5.9613 | 5.5756 | 5.393 | 5.0001 | 4.7634 | 4.3583 | 3.494 | 3.2164 | 3.0868
|  | KEITH | FB |  |  |  |  | 6.9761 | 6.7853 | 6.7057 | 6.669 | 6.5904 | 6.5649 | 6.519 | 6.4078 | 6.2822 | 6.3241 | 5.572 | 4.4476 | 3.7333 | 6.2169 | 6.0833 | 5.9527 | 5.8935 | 5.8149 | 5.7894 | 5.7404 | 5.6618 | 5.5761 | 5.5598 | 4.872 | 3.719 | 2.8496 | 6.9011 | 6.5205 | 6.4083 | 6.3338 | 6.1562 | 6.1011 | 6.0123 | 5.8317 | 5.6368 | 5.6613 | 4.7562 | 3.5899 | 3.0348
| KINTORE | KEMNAY | MINIMUM HEADROOM | NJ 73180 16804 | NO | YES | 0.22 | 10.8439 | 10.7969 | 10.7663 | 10.6347 | 10.3398 | 9.9133 | 9.4378 | 9.2653 | 9.0153 | 8.7857 | 7.4939 | 6.7255 | 6.0776 | 11.4163 | 11.3888 | 11.3653 | 11.3051 | 11.0643 | 10.7704 | 10.4571 | 10.4214 | 10.3143 | 10.2255 | 9.398 | 9.3306 | 9.1082 | 11.2281 | 11.1872 | 11.1474 | 11.0668 | 10.7944 | 10.4199 | 10.0148 | 9.8587 | 9.6617 | 9.4781 | 8.3587 | 7.8281 | 7.4311
|  | KEMNAY | EE |  |  |  |  | 10.8469 | 10.8061 | 10.802 | 10.6918 | 10.3939 | 9.948 | 9.4694 | 9.2827 | 9.0265 | 8.8031 | 7.4939 | 6.7286 | 6.1949 | 11.4173 | 11.3939 | 11.3776 | 11.3286 | 11.0837 | 10.7796 | 10.4684 | 10.4286 | 10.3194 | 10.2296 | 9.4429 | 9.3357 | 9.2122 | 11.2301 | 11.1923 | 11.1709 | 11.1036 | 10.8281 | 10.4423 | 10.0332 | 9.8658 | 9.6648 | 9.4852 | 8.3587 | 7.8393 | 7.5097
|  | KEMNAY | HT |  |  |  |  | 10.8439 | 10.7969 | 10.7663 | 10.6347 | 10.3398 | 10.1102 | 9.8724 | 9.7102 | 9.35 | 8.8714 | 7.5561 | 6.7255 | 6.0776 | 11.4163 | 11.3888 | 11.3653 | 11.3051 | 11.0643 | 10.9653 | 10.8694 | 10.8388 | 10.6133 | 10.2776 | 9.398 | 9.3306 | 9.3133 | 11.2281 | 11.1872 | 11.1474 | 11.0668 | 10.7944 | 10.6189 | 10.4413 | 10.3281 | 10.0148 | 9.5607 | 8.3883 | 7.8281 | 7.4311
|  | KEMNAY | HE |  |  |  |  | 10.849 | 10.8031 | 10.7857 | 10.6602 | 10.3612 | 9.9133 | 9.4378 | 9.2653 | 9.0153 | 8.7857 | 7.6541 | 6.9306 | 6.5092 | 11.4173 | 11.3929 | 11.3745 | 11.3184 | 11.0755 | 10.7704 | 10.4571 | 10.4214 | 10.3143 | 10.2255 | 9.4582 | 9.3541 | 9.2276 | 11.2311 | 11.1923 | 11.1617 | 11.0852 | 10.8066 | 10.4199 | 10.0148 | 9.8587 | 9.6617 | 9.4781 | 8.475 | 7.9668 | 7.7026
|  | KEMNAY | FB |  |  |  |  | 10.9459 | 10.9724 | 10.9847 | 10.9643 | 10.8653 | 10.6663 | 10.4 | 10.0663 | 9.9622 | 9.9082 | 9.4398 | 8.7306 | 8.5204 | 11.4724 | 11.4898 | 11.4867 | 11.4673 | 11.3724 | 11.1612 | 10.8959 | 10.5776 | 10.501 | 10.4612 | 10.0918 | 9.4388 | 9.1082 | 11.3097 | 11.3342 | 11.3362 | 11.3148 | 11.2219 | 11.0097 | 10.7505 | 10.4556 | 10.3689 | 10.3219 | 9.8679 | 9.2138 | 9.1077
| TAYNUILT | KENMORE | MINIMUM HEADROOM | NN 00325 34042 | YES | YES | 0 | 0.86224 | 0.85816 | 0.85408 | 0.85102 | 0.84592 | 0.83776 | 0.82653 | 0.81224 | 0.79898 | 0.80102 | 0.77653 | 0.76122 | 0.75102 | 0.90918 | 0.90408 | 0.90102 | 0.90204 | 0.89694 | 0.89592 | 0.88878 | 0.87653 | 0.86224 | 0.86531 | 0.83571 | 0.83571 | 0.8398 | 0.89184 | 0.88469 | 0.88061 | 0.87857 | 0.87347 | 0.86837 | 0.85612 | 0.8449 | 0.83163 | 0.83265 | 0.81122 | 0.79898 | 0.79388
|  | KENMORE | EE |  |  |  |  | 0.86224 | 0.85816 | 0.8551 | 0.85102 | 0.84592 | 0.83776 | 0.82857 | 0.81224 | 0.8 | 0.80102 | 0.77653 | 0.76122 | 0.75612 | 0.90918 | 0.90408 | 0.90306 | 0.90204 | 0.89694 | 0.89694 | 0.89082 | 0.87653 | 0.86224 | 0.86531 | 0.84082 | 0.84082 | 0.84796 | 0.89286 | 0.88469 | 0.88265 | 0.87857 | 0.87347 | 0.86837 | 0.85816 | 0.8449 | 0.83265 | 0.83265 | 0.81122 | 0.80102 | 0.79796
|  | KENMORE | HT |  |  |  |  | 0.86327 | 0.86224 | 0.8551 | 0.85204 | 0.84694 | 0.84082 | 0.82959 | 0.81633 | 0.80306 | 0.8051 | 0.78061 | 0.76122 | 0.75204 | 0.90918 | 0.90714 | 0.90204 | 0.90204 | 0.89694 | 0.89694 | 0.88878 | 0.87653 | 0.86224 | 0.86531 | 0.83571 | 0.83571 | 0.8398 | 0.89286 | 0.88878 | 0.88163 | 0.87959 | 0.87347 | 0.87041 | 0.85816 | 0.84694 | 0.83469 | 0.83571 | 0.81327 | 0.79898 | 0.79388
|  | KENMORE | HE |  |  |  |  | 0.86327 | 0.86224 | 0.85408 | 0.85204 | 0.84592 | 0.83776 | 0.82653 | 0.81327 | 0.79898 | 0.80204 | 0.78163 | 0.76122 | 0.75102 | 0.90918 | 0.90714 | 0.90102 | 0.90204 | 0.89694 | 0.89592 | 0.88878 | 0.87653 | 0.86224 | 0.86531 | 0.84184 | 0.83878 | 0.8398 | 0.89184 | 0.88878 | 0.88061 | 0.87959 | 0.87347 | 0.86837 | 0.85612 | 0.84592 | 0.83163 | 0.83367 | 0.81531 | 0.8 | 0.79388
|  | KENMORE | FB |  |  |  |  | 0.87143 | 0.86735 | 0.87041 | 0.86735 | 0.86531 | 0.86429 | 0.86122 | 0.85918 | 0.85714 | 0.85102 | 0.83878 | 0.81735 | 0.81429 | 0.91837 | 0.91224 | 0.91531 | 0.91224 | 0.91122 | 0.91122 | 0.90714 | 0.90408 | 0.9 | 0.89286 | 0.87959 | 0.85408 | 0.84694 | 0.9 | 0.8949 | 0.89796 | 0.89184 | 0.89184 | 0.89184 | 0.88673 | 0.88367 | 0.88265 | 0.87347 | 0.86327 | 0.83878 | 0.83776
| STRATHLEVEN | KEPCULLOCH | MINIMUM HEADROOM | NS 53864 91598 | NO | YES | 1.179 | 2.4815 | 2.4785 | 2.4305 | 10.6184 | 10.5602 | 10.1643 | 10.001 | 9.7622 | 9.6102 | 9.5071 | 8.8469 | 8.4714 | 8.1418 | 3.4463 | 3.4331 | 3.4096 | 11.1827 | 11.1541 | 10.7602 | 10.6429 | 10.448 | 10.3367 | 10.2786 | 9.802 | 9.7163 | 9.6653 | 3.2731 | 3.266 | 3.2221 | 11.1821 | 11.1464 | 10.7291 | 10.5862 | 10.3638 | 10.2301 | 10.1413 | 9.5546 | 9.2883 | 9.0699
|  | KEPCULLOCH | EE |  |  |  |  | 2.4866 | 2.4928 | 2.457 | 10.6592 | 10.6163 | 10.3806 | 10.0806 | 9.9398 | 9.7908 | 9.6827 | 9.0796 | 8.7714 | 8.5204 | 3.4473 | 3.4382 | 3.4178 | 11.1969 | 11.1735 | 10.9337 | 10.6673 | 10.5582 | 10.4429 | 10.3582 | 9.9051 | 9.8143 | 9.7429 | 3.2772 | 3.2741 | 3.2405 | 11.2158 | 11.1587 | 10.9352 | 10.6383 | 10.5138 | 10.3791 | 10.276 | 9.723 | 9.4964 | 9.324
|  | KEPCULLOCH | HT |  |  |  |  | 2.4815 | 2.4785 | 2.4305 | 10.6184 | 10.5602 | 10.1643 | 10.001 | 9.7622 | 9.6102 | 9.5071 | 8.8469 | 8.4714 | 8.1418 | 3.4463 | 3.4331 | 3.4096 | 11.1827 | 11.1541 | 10.7602 | 10.6429 | 10.448 | 10.3367 | 10.2786 | 9.802 | 9.7163 | 9.6653 | 3.2731 | 3.266 | 3.2221 | 11.1821 | 11.1464 | 10.7291 | 10.5862 | 10.3638 | 10.2301 | 10.1413 | 9.5546 | 9.2883 | 9.0699
|  | KEPCULLOCH | HE |  |  |  |  | 2.4856 | 2.4917 | 2.456 | 10.6694 | 10.6337 | 10.398 | 10.2102 | 9.95 | 9.7959 | 9.7235 | 9.3398 | 9.0122 | 8.7204 | 3.4473 | 3.4382 | 3.4167 | 11.198 | 11.1714 | 10.9337 | 10.7704 | 10.5459 | 10.4245 | 10.3745 | 10.1439 | 10.0347 | 9.9214 | 3.2762 | 3.2731 | 3.2405 | 11.2199 | 11.1709 | 10.9393 | 10.7597 | 10.5128 | 10.3699 | 10.3097 | 9.975 | 9.7301 | 9.5189
|  | KEPCULLOCH | FB |  |  |  |  | 2.5234 | 2.5632 | 2.5591 | 10.799 | 10.7571 | 10.7418 | 10.6735 | 10.6194 | 10.5408 | 10.4704 | 10.2327 | 9.7296 | 9.0449 | 3.4739 | 3.4892 | 3.481 | 11.2969 | 11.2592 | 11.2316 | 11.1694 | 11.1296 | 11.0571 | 11.0031 | 10.8204 | 10.3969 | 9.7031 | 3.3037 | 3.3211 | 3.3119 | 11.327 | 11.2883 | 11.2577 | 11.2036 | 11.1801 | 11.1046 | 11.0372 | 10.826 | 10.3117 | 9.7372
| TAYNUILT | KERRERA | MINIMUM HEADROOM | NM 82340 27997 | YES | YES | 0 | 0.28869 | 0.28665 | 0.28563 | 0.27543 | 0.27237 | 0.27033 | 0.26318 | 0.2591 | 0.254 | 0.24788 | 0.23665 | 0.22747 | 0.22237 | 0.28312 | 0.2821 | 0.2821 | 0.27496 | 0.27292 | 0.27292 | 0.26884 | 0.26476 | 0.26271 | 0.25659 | 0.24639 | 0.24537 | 0.24639 | 0.28744 | 0.28744 | 0.2854 | 0.27621 | 0.27213 | 0.26907 | 0.26193 | 0.25683 | 0.25274 | 0.24458 | 0.23336 | 0.23132 | 0.2303
|  | KERRERA | EE |  |  |  |  | 0.28869 | 0.28869 | 0.28563 | 0.27645 | 0.27237 | 0.27135 | 0.26318 | 0.2591 | 0.254 | 0.24788 | 0.23665 | 0.22747 | 0.22339 | 0.28312 | 0.28516 | 0.2821 | 0.27496 | 0.27292 | 0.27292 | 0.26884 | 0.26476 | 0.26271 | 0.25659 | 0.24639 | 0.24843 | 0.25149 | 0.28744 | 0.2905 | 0.2854 | 0.27621 | 0.27213 | 0.26907 | 0.26193 | 0.25683 | 0.25274 | 0.24458 | 0.23336 | 0.23336 | 0.23234
|  | KERRERA | HT |  |  |  |  | 0.28869 | 0.28869 | 0.28563 | 0.27747 | 0.27339 | 0.27135 | 0.26522 | 0.26216 | 0.25706 | 0.24992 | 0.24278 | 0.23053 | 0.22237 | 0.28312 | 0.28516 | 0.2821 | 0.27598 | 0.27292 | 0.27292 | 0.26884 | 0.26476 | 0.26271 | 0.25659 | 0.25047 | 0.24537 | 0.24945 | 0.28744 | 0.2905 | 0.2854 | 0.27723 | 0.27213 | 0.26907 | 0.26295 | 0.25785 | 0.25479 | 0.24662 | 0.23948 | 0.23132 | 0.23132
|  | KERRERA | HE |  |  |  |  | 0.28869 | 0.28869 | 0.28563 | 0.27543 | 0.27339 | 0.27033 | 0.26318 | 0.2591 | 0.254 | 0.24992 | 0.23971 | 0.22951 | 0.22339 | 0.28312 | 0.28516 | 0.2821 | 0.27496 | 0.27496 | 0.27292 | 0.26884 | 0.26476 | 0.26271 | 0.25659 | 0.24639 | 0.24741 | 0.24741 | 0.28744 | 0.2905 | 0.2854 | 0.27621 | 0.27315 | 0.26907 | 0.26295 | 0.25683 | 0.25377 | 0.2456 | 0.2354 | 0.23336 | 0.2303
|  | KERRERA | FB |  |  |  |  | 0.30094 | 0.28665 | 0.28971 | 0.29176 | 0.29073 | 0.28869 | 0.28869 | 0.28461 | 0.28053 | 0.27951 | 0.26829 | 0.2591 | 0.25604 | 0.29537 | 0.2821 | 0.28414 | 0.28312 | 0.28312 | 0.28006 | 0.28006 | 0.27598 | 0.27292 | 0.27292 | 0.26271 | 0.25149 | 0.24639 | 0.29764 | 0.28744 | 0.28846 | 0.28846 | 0.2854 | 0.28438 | 0.28234 | 0.27621 | 0.27315 | 0.27315 | 0.25989 | 0.24764 | 0.2456
| GRUDIE BRIDGE | KERRY FALLS | MINIMUM HEADROOM | NG 82909 71978 | YES | NO | 0.561 | 1.9531 | 1.9429 | 1.9204 | 1.8684 | 1.8255 | 1.5684 | 1.2408 | 0.95408 | 0.81633 | 0.76429 | 0.58469 | 0.42449 | 0.27959 | 1.9204 | 1.9122 | 1.8969 | 1.8673 | 1.8327 | 1.6265 | 1.299 | 1.0286 | 0.91837 | 0.89898 | 0.81939 | 0.82245 | 0.83571 | 1.8551 | 1.8531 | 1.8429 | 1.8122 | 1.7776 | 1.5265 | 1.2857 | 1.0214 | 0.89694 | 0.86633 | 0.67551 | 0.60306 | 0.4949
|  | KERRY FALLS | EE |  |  |  |  | 1.9531 | 1.9429 | 1.9204 | 1.8714 | 1.8327 | 1.7347 | 1.6857 | 1.4194 | 1.1163 | 0.84796 | 0.58469 | 0.42449 | 0.31122 | 1.9204 | 1.9122 | 1.8969 | 1.8673 | 1.8327 | 1.7898 | 1.7592 | 1.55 | 1.251 | 0.99082 | 0.83163 | 0.83571 | 0.85 | 1.8551 | 1.8531 | 1.8429 | 1.8133 | 1.7796 | 1.6898 | 1.6551 | 1.3949 | 1.1163 | 0.92245 | 0.67857 | 0.60816 | 0.51531
|  | KERRY FALLS | HT |  |  |  |  | 1.9541 | 1.9439 | 1.9224 | 1.8714 | 1.8327 | 1.5684 | 1.2408 | 0.95408 | 0.81633 | 0.77653 | 0.6398 | 0.45306 | 0.27959 | 1.9204 | 1.9122 | 1.898 | 1.8673 | 1.8327 | 1.6265 | 1.299 | 1.0286 | 0.91837 | 0.89898 | 0.81939 | 0.82245 | 0.84082 | 1.8561 | 1.8531 | 1.8449 | 1.8143 | 1.7796 | 1.5265 | 1.2857 | 1.0214 | 0.89694 | 0.86633 | 0.67551 | 0.61224 | 0.4949
|  | KERRY FALLS | HE |  |  |  |  | 1.9551 | 1.9449 | 1.9224 | 1.8684 | 1.8255 | 1.7357 | 1.6786 | 1.3918 | 1.0449 | 0.76429 | 0.63265 | 0.44796 | 0.34592 | 1.9214 | 1.9133 | 1.898 | 1.8673 | 1.8337 | 1.7898 | 1.7612 | 1.5347 | 1.1837 | 0.91122 | 0.83673 | 0.83673 | 0.83571 | 1.8582 | 1.8541 | 1.8449 | 1.8122 | 1.7776 | 1.6908 | 1.652 | 1.3735 | 1.0694 | 0.86633 | 0.69898 | 0.60306 | 0.52551
|  | KERRY FALLS | FB |  |  |  |  | 1.9786 | 1.9776 | 1.9724 | 1.9531 | 1.9316 | 1.9112 | 1.8847 | 1.8684 | 1.6898 | 1.4857 | 1.0071 | 0.89082 | 0.86531 | 1.9398 | 1.9347 | 1.9286 | 1.9143 | 1.898 | 1.8827 | 1.8592 | 1.8449 | 1.6888 | 1.4582 | 0.96224 | 0.86837 | 0.84184 | 1.8969 | 1.899 | 1.901 | 1.8939 | 1.8939 | 1.8745 | 1.8388 | 1.8163 | 1.6388 | 1.4408 | 1.0071 | 0.86122 | 0.84286
| TAYNUILT | KILCHRENAN | MINIMUM HEADROOM | NN 03495 23835 | YES | YES | 0.046 | 0.26633 | 0.1398 | 0.022449 | 0.0030612 | -0.012245 | -0.045918 | -0.070408 | -0.082653 | -0.1051 | -0.12755 | -0.17653 | -0.21224 | -0.24184 | 0.42245 | 0.30816 | 0.20306 | 0.19796 | 0.1898 | 0.16633 | 0.15612 | 0.13878 | 0.11633 | 0.093878 | 0.056122 | 0.058163 | 0.044898 | 0.25816 | 0.11735 | -0.011224 | -0.020408 | -0.035714 | -0.067347 | -0.086735 | -0.11122 | -0.14082 | -0.16531 | -0.2051 | -0.21429 | -0.23571
|  | KILCHRENAN | EE |  |  |  |  | 0.26633 | 0.26224 | 0.12857 | 0.0030612 | -0.011224 | -0.042857 | -0.070408 | -0.079592 | -0.1051 | -0.12653 | -0.17653 | -0.21224 | -0.23673 | 0.42245 | 0.41837 | 0.29898 | 0.19796 | 0.1898 | 0.16837 | 0.15612 | 0.1398 | 0.11633 | 0.094898 | 0.062245 | 0.066327 | 0.07449 | 0.25816 | 0.2551 | 0.10714 | -0.020408 | -0.034694 | -0.063265 | -0.084694 | -0.11122 | -0.14082 | -0.16224 | -0.19184 | -0.21429 | -0.22245
|  | KILCHRENAN | HT |  |  |  |  | 0.26633 | 0.1398 | 0.022449 | 0.0091837 | -0.005102 | -0.033673 | -0.057143 | -0.082653 | -0.090816 | -0.11122 | -0.15612 | -0.20102 | -0.24184 | 0.42245 | 0.30816 | 0.20306 | 0.2 | 0.19184 | 0.16939 | 0.15816 | 0.14082 | 0.12041 | 0.097959 | 0.056122 | 0.058163 | 0.07449 | 0.25918 | 0.11735 | -0.011224 | -0.016327 | -0.028571 | -0.056122 | -0.077551 | -0.09898 | -0.12755 | -0.15306 | -0.20306 | -0.20714 | -0.23061
|  | KILCHRENAN | HE |  |  |  |  | 0.26633 | 0.26327 | 0.13061 | 0.0030612 | -0.012245 | -0.045918 | -0.069388 | -0.078571 | -0.10408 | -0.12755 | -0.16122 | -0.20408 | -0.23061 | 0.42245 | 0.41837 | 0.29898 | 0.19796 | 0.1898 | 0.16633 | 0.15612 | 0.13878 | 0.11633 | 0.093878 | 0.064286 | 0.061224 | 0.057143 | 0.25918 | 0.25612 | 0.10816 | -0.020408 | -0.035714 | -0.067347 | -0.086735 | -0.11122 | -0.14082 | -0.16531 | -0.2051 | -0.21429 | -0.23571
|  | KILCHRENAN | FB |  |  |  |  | 0.28061 | 0.27755 | 0.27857 | 0.1551 | 0.038776 | 0.035714 | 0.028571 | 0.021429 | 0.013265 | 0.011224 | -0.027551 | -0.063265 | -0.07551 | 0.43571 | 0.43163 | 0.43061 | 0.32143 | 0.21939 | 0.21429 | 0.20714 | 0.19184 | 0.17857 | 0.17449 | 0.12755 | 0.077551 | 0.044898 | 0.27653 | 0.27449 | 0.27449 | 0.14082 | 0.016327 | 0.013265 | 0.0061224 | -0.0040816 | -0.014286 | -0.015306 | -0.060204 | -0.10816 | -0.11327
| STRATHLEVEN | KILLEARN | MINIMUM HEADROOM | NS 51313 86758 | YES | YES | 0.456 | -0.98571 | -1.0224 | -1.098 | -1.2245 | -1.3459 | -1.5582 | -1.7969 | -2.0449 | -2.2643 | -2.4806 | -3.1337 | -3.9337 | -4.5857 | -0.31939 | -0.33776 | -0.37347 | -0.41531 | -0.46939 | -0.53776 | -0.61429 | -0.72449 | -0.80306 | -0.88469 | -1.0898 | -1.1786 | -1.2684 | -0.56837 | -0.60102 | -0.67857 | -0.75 | -0.84592 | -0.99796 | -1.1745 | -1.3663 | -1.5316 | -1.698 | -2.1602 | -2.6888 | -3.1102
|  | KILLEARN | EE |  |  |  |  | -0.97857 | -1.0061 | -1.0602 | -1.151 | -1.25 | -1.4296 | -1.6398 | -1.8806 | -2.0939 | -2.2857 | -2.9847 | -3.5398 | -4.0765 | -0.31633 | -0.32959 | -0.35714 | -0.3898 | -0.43571 | -0.49184 | -0.56531 | -0.66939 | -0.7449 | -0.83878 | -1.0898 | -1.0755 | -1.1857 | -0.56327 | -0.58776 | -0.65 | -0.7 | -0.77857 | -0.91122 | -1.0663 | -1.2531 | -1.4122 | -1.5633 | -2.101 | -2.4112 | -2.7612
|  | KILLEARN | HT |  |  |  |  | -0.98571 | -1.0224 | -1.098 | -1.2245 | -1.3459 | -1.5582 | -1.7969 | -2.0449 | -2.2643 | -2.4806 | -3.1337 | -3.9337 | -4.5857 | -0.31939 | -0.33776 | -0.37347 | -0.41531 | -0.46939 | -0.53776 | -0.61429 | -0.72449 | -0.80306 | -0.88469 | -1.051 | -1.1786 | -1.2684 | -0.56837 | -0.60102 | -0.67857 | -0.75 | -0.84592 | -0.99796 | -1.1745 | -1.3663 | -1.5316 | -1.698 | -2.1602 | -2.6888 | -3.1102
|  | KILLEARN | HE |  |  |  |  | -0.97959 | -1.0061 | -1.0643 | -1.148 | -1.2408 | -1.4214 | -1.6398 | -1.8745 | -2.0847 | -2.2837 | -2.801 | -3.4949 | -4.0051 | -0.31633 | -0.33061 | -0.3602 | -0.3898 | -0.44184 | -0.49592 | -0.56837 | -0.67449 | -0.75 | -0.84388 | -0.94082 | -1.0765 | -1.2133 | -0.56327 | -0.58878 | -0.6551 | -0.69796 | -0.77551 | -0.9051 | -1.0673 | -1.25 | -1.4071 | -1.5622 | -1.9214 | -2.3857 | -2.7306
|  | KILLEARN | FB |  |  |  |  | -0.92857 | -0.92245 | -0.94796 | -0.97143 | -1.0112 | -1.0827 | -1.1704 | -1.2459 | -1.3571 | -1.4327 | -1.8837 | -2.3408 | -2.7061 | -0.2898 | -0.28776 | -0.29694 | -0.31429 | -0.32755 | -0.37347 | -0.42755 | -0.46327 | -0.53163 | -0.57245 | -0.82245 | -1.0357 | -1.2357 | -0.52143 | -0.51735 | -0.5398 | -0.57347 | -0.60306 | -0.64694 | -0.71939 | -0.77755 | -0.86633 | -0.92857 | -1.2888 | -1.698 | -1.8939
| KILLIN | KILLIN TOWN | MINIMUM HEADROOM | NN 56931 32662 | YES | YES | 0.131 | 1.7622 | 1.7622 | 1.7592 | 1.7429 | 1.7306 | 1.6898 | 1.6582 | 1.6204 | 1.5684 | 1.5245 | 1.4112 | 1.2806 | 1.1551 | 2.0199 | 2.0158 | 2.0087 | 1.9964 | 1.9883 | 1.9689 | 1.9321 | 1.9077 | 1.874 | 1.8403 | 1.7474 | 1.727 | 1.6515 | 2.0855 | 2.0834 | 2.0742 | 2.0497 | 2.0212 | 1.9844 | 1.9324 | 1.8957 | 1.8508 | 1.814 | 1.7038 | 1.6385 | 1.6008
|  | KILLIN TOWN | EE |  |  |  |  | 1.7643 | 1.7633 | 1.7612 | 1.7439 | 1.7347 | 1.6959 | 1.6633 | 1.6276 | 1.5776 | 1.5367 | 1.4112 | 1.2929 | 1.2031 | 2.0209 | 2.0168 | 2.0087 | 1.9995 | 1.9903 | 1.973 | 1.9362 | 1.9148 | 1.8811 | 1.8495 | 1.775 | 1.7434 | 1.7189 | 2.0865 | 2.0834 | 2.0742 | 2.0497 | 2.0222 | 1.9865 | 1.9344 | 1.8997 | 1.8508 | 1.8181 | 1.712 | 1.6589 | 1.6283
|  | KILLIN TOWN | HT |  |  |  |  | 1.7622 | 1.7622 | 1.7592 | 1.7429 | 1.7306 | 1.6939 | 1.6612 | 1.6245 | 1.5745 | 1.5316 | 1.4153 | 1.2806 | 1.1551 | 2.0199 | 2.0158 | 2.0087 | 1.9964 | 1.9883 | 1.9689 | 1.9321 | 1.9077 | 1.874 | 1.8403 | 1.7474 | 1.727 | 1.7199 | 2.0855 | 2.0834 | 2.0753 | 2.0508 | 2.0222 | 1.9885 | 1.9375 | 1.9008 | 1.8559 | 1.8212 | 1.7038 | 1.6385 | 1.6008
|  | KILLIN TOWN | HE |  |  |  |  | 1.7653 | 1.7643 | 1.7612 | 1.7439 | 1.7316 | 1.6898 | 1.6582 | 1.6204 | 1.5684 | 1.5245 | 1.4357 | 1.2939 | 1.2031 | 2.0209 | 2.0168 | 2.0087 | 1.9995 | 1.9903 | 1.973 | 1.9372 | 1.9138 | 1.8811 | 1.8474 | 1.776 | 1.7362 | 1.7015 | 2.0875 | 2.0834 | 2.0753 | 2.0497 | 2.0212 | 1.9844 | 1.9324 | 1.8957 | 1.862 | 1.814 | 1.7191 | 1.6538 | 1.6171
|  | KILLIN TOWN | FB |  |  |  |  | 1.7837 | 1.7949 | 1.8051 | 1.8051 | 1.8082 | 1.7929 | 1.7898 | 1.7786 | 1.7633 | 1.7388 | 1.6582 | 1.549 | 1.4888 | 2.0352 | 2.0403 | 2.0393 | 2.0362 | 2.0291 | 2.0158 | 2.0117 | 1.9974 | 1.977 | 1.9546 | 1.8628 | 1.7444 | 1.6515 | 2.0977 | 2.1018 | 2.1048 | 2.0967 | 2.0865 | 2.0702 | 2.0651 | 2.0487 | 2.0293 | 2.0028 | 1.9048 | 1.7875 | 1.761
| TAYNUILT | KILMELFORD | MINIMUM HEADROOM | NM 84056 14437 | YES | YES | 0.323 | -2.0784 | -2.1182 | -2.1438 | -2.1825 | -2.254 | -2.3621 | -2.4438 | 1.5501 | 1.4736 | 1.4062 | 1.2685 | 1.1011 | 1.0389 | -1.707 | -1.7642 | -1.7703 | -1.7754 | -2.0427 | -2.1856 | -2.254 | 1.6716 | 1.5777 | 1.4226 | 1.1328 | 1.0216 | 0.99707 | -1.7682 | -1.8233 | -1.8417 | -1.8652 | -2.1284 | -2.304 | -2.3866 | 1.5501 | 1.4409 | 1.2777 | 1.0124 | 0.85013 | 0.80625
|  | KILMELFORD | EE |  |  |  |  | -2.0784 | -2.0866 | -2.1438 | -2.1825 | -2.254 | -2.3621 | -2.4438 | 1.5501 | 1.4736 | 1.4062 | 1.2685 | 1.1011 | 1.0389 | -1.707 | -1.7101 | -1.7693 | -1.7733 | -1.9438 | -2.1784 | -2.2468 | 1.6971 | 1.5777 | 1.4226 | 1.1491 | 1.0216 | 0.99707 | -1.7672 | -1.7825 | -1.8417 | -1.8642 | -2.0427 | -2.2999 | -2.3652 | 1.5634 | 1.4409 | 1.2777 | 1.0124 | 0.85013 | 0.80625
|  | KILMELFORD | HT |  |  |  |  | -2.0784 | -2.1182 | -2.1356 | -2.1733 | -2.2438 | -2.3397 | -2.4142 | 1.593 | 1.5154 | 1.446 | 1.2777 | 1.1593 | 1.1348 | -1.706 | -1.7642 | -1.7703 | -1.7733 | -1.9448 | -2.1631 | -2.2448 | 1.7236 | 1.5981 | 1.4409 | 1.1328 | 1.0675 | 1.1083 | -1.7682 | -1.8233 | -1.8397 | -1.8591 | -2.0376 | -2.2733 | -2.3703 | 1.6114 | 1.4828 | 1.3134 | 1.0277 | 0.92972 | 0.92462
|  | KILMELFORD | HE |  |  |  |  | -2.0754 | -2.0866 | -2.1417 | -2.1825 | -2.254 | -2.358 | -2.4264 | 1.5695 | 1.5175 | 1.4491 | 1.3603 | 1.2736 | 1.2032 | -1.704 | -1.7091 | -1.7703 | -1.7754 | -1.9458 | -2.1856 | -2.254 | 1.6716 | 1.6277 | 1.4909 | 1.2532 | 1.2736 | 1.246 | -1.7642 | -1.7846 | -1.8417 | -1.8652 | -2.0427 | -2.304 | -2.3866 | 1.5501 | 1.495 | 1.3624 | 1.144 | 1.1307 | 1.0787
|  | KILMELFORD | FB |  |  |  |  | -2.0591 | -2.0519 | -2.054 | -2.0897 | -2.1825 | -2.1927 | -2.2213 | 1.8614 | 1.845 | 1.842 | 1.7838 | 1.746 | 1.6511 | -1.6907 | -1.6866 | -1.6927 | -1.7468 | -2.0427 | -2.0519 | -2.105 | 1.9756 | 1.944 | 1.9287 | 1.8318 | 1.6991 | 1.4409 | -1.7417 | -1.7366 | -1.754 | -1.7958 | -2.1284 | -2.1366 | -2.1876 | 1.896 | 1.8767 | 1.8716 | 1.8052 | 1.6971 | 1.4287
| TAYNUILT | KILNINVER | MINIMUM HEADROOM | NM 83049 22251 | YES | YES | 0.305 | -0.88061 | -0.93469 | -0.9551 | -0.97857 | -1.1337 | -1.3602 | -1.4755 | -1.6418 | -1.7888 | -1.8653 | -2.2031 | -2.4541 | -2.5653 | -0.44388 | -0.50102 | -0.52959 | -0.54388 | -0.82449 | -0.98367 | -1.0867 | -1.2398 | -1.3684 | -1.4571 | -1.7796 | -1.9224 | -1.9296 | -0.57449 | -0.64388 | -0.66224 | -0.67857 | -0.85408 | -1.0541 | -1.1388 | -1.2898 | -1.4214 | -1.4929 | -1.8255 | -2.0194 | -2.0878
|  | KILNINVER | EE |  |  |  |  | -0.88061 | -0.89796 | -0.9551 | -0.97857 | -1.1265 | -1.352 | -1.4745 | -1.6265 | -1.7888 | -1.8643 | -2.2031 | -2.4541 | -2.5653 | -0.44184 | -0.47041 | -0.52755 | -0.54388 | -0.7551 | -0.97857 | -1.0776 | -1.2112 | -1.3684 | -1.449 | -1.7765 | -1.9224 | -1.9296 | -0.57347 | -0.5949 | -0.66224 | -0.67857 | -0.8398 | -1.0541 | -1.1357 | -1.2714 | -1.4214 | -1.4888 | -1.8255 | -2.0194 | -2.0878
|  | KILNINVER | HT |  |  |  |  | -0.87959 | -0.93469 | -0.94898 | -0.96531 | -1.1163 | -1.3214 | -1.4449 | -1.5684 | -1.7327 | -1.8153 | -2.1286 | -2.2867 | -2.4061 | -0.44184 | -0.50102 | -0.52857 | -0.54388 | -0.75612 | -0.96327 | -1.0745 | -1.1857 | -1.348 | -1.4347 | -1.7796 | -1.7939 | -1.7602 | -0.57347 | -0.64388 | -0.65816 | -0.66939 | -0.83265 | -1.0276 | -1.1173 | -1.2276 | -1.3786 | -1.4551 | -1.799 | -1.8765 | -1.9153
|  | KILNINVER | HE |  |  |  |  | -0.88061 | -0.89796 | -0.95102 | -0.97755 | -1.1276 | -1.3602 | -1.4755 | -1.6418 | -1.7602 | -1.8653 | -2.0133 | -2.1561 | -2.2357 | -0.44388 | -0.47143 | -0.52959 | -0.54388 | -0.75714 | -0.98367 | -1.0867 | -1.2398 | -1.3429 | -1.4571 | -1.6061 | -1.5969 | -1.5663 | -0.57449 | -0.5949 | -0.65918 | -0.67857 | -0.84184 | -1.0367 | -1.1388 | -1.2898 | -1.3949 | -1.4929 | -1.6418 | -1.7133 | -1.7561
|  | KILNINVER | FB |  |  |  |  | -0.85204 | -0.83367 | -0.83367 | -0.87143 | -1.1337 | -1.148 | -1.1602 | -1.1806 | -1.1908 | -1.2143 | -1.3041 | -1.4367 | -1.6745 | -0.41939 | -0.42245 | -0.4449 | -0.4898 | -0.82449 | -0.85306 | -0.87449 | -0.90816 | -0.92347 | -0.96224 | -1.0847 | -1.2235 | -1.501 | -0.54184 | -0.53265 | -0.5398 | -0.59184 | -0.85408 | -0.87041 | -0.88469 | -0.9051 | -0.91735 | -0.94286 | -1.048 | -1.2051 | -1.4286
| BEAULY | KILTARLITY | MINIMUM HEADROOM | NH 50271 41265 | YES | NO | 0.566 | 4.7265 | 4.7173 | 4.6888 | 4.6582 | 4.5939 | 4.4918 | 4.3776 | 4.2694 | 4.1531 | 4.0704 | 3.8092 | 3.5898 | 3.3561 | 5.2163 | 5.2122 | 5.1959 | 5.1837 | 5.15 | 5.1082 | 5.0122 | 4.9439 | 4.8571 | 4.7949 | 4.5735 | 4.5837 | 4.6265 | 4.5806 | 4.5673 | 4.5449 | 4.5071 | 4.4541 | 4.3949 | 4.298 | 4.2112 | 4.1122 | 4.0429 | 3.8286 | 3.6806 | 3.5633
|  | KILTARLITY | EE |  |  |  |  | 4.7265 | 4.7173 | 4.6888 | 4.6633 | 4.6031 | 4.4959 | 4.399 | 4.2939 | 4.1816 | 4.1071 | 3.8092 | 3.5898 | 3.3776 | 5.2173 | 5.2122 | 5.1959 | 5.1837 | 5.151 | 5.1133 | 5.0184 | 4.9469 | 4.8582 | 4.7949 | 4.6102 | 4.6214 | 4.6684 | 4.5806 | 4.5673 | 4.5449 | 4.5112 | 4.4612 | 4.4 | 4.3112 | 4.2255 | 4.1316 | 4.0684 | 3.8286 | 3.6827 | 3.5898
|  | KILTARLITY | HT |  |  |  |  | 4.7265 | 4.7184 | 4.6908 | 4.6643 | 4.602 | 4.5133 | 4.3949 | 4.2949 | 4.1867 | 4.1122 | 3.8867 | 3.6418 | 3.3561 | 5.2163 | 5.2122 | 5.1969 | 5.1837 | 5.15 | 5.1082 | 5.0122 | 4.9439 | 4.8571 | 4.798 | 4.5735 | 4.5837 | 4.6265 | 4.5806 | 4.5684 | 4.5469 | 4.5122 | 4.4612 | 4.4082 | 4.3082 | 4.2255 | 4.1337 | 4.0714 | 3.8796 | 3.7173 | 3.5633
|  | KILTARLITY | HE |  |  |  |  | 4.7265 | 4.7194 | 4.6929 | 4.6582 | 4.5939 | 4.4918 | 4.3776 | 4.2694 | 4.1531 | 4.0704 | 3.8582 | 3.5929 | 3.4092 | 5.2163 | 5.2122 | 5.1969 | 5.1837 | 5.15 | 5.1133 | 5.0173 | 4.9459 | 4.8582 | 4.799 | 4.6122 | 4.6173 | 4.6316 | 4.5806 | 4.5704 | 4.548 | 4.5071 | 4.4541 | 4.3949 | 4.298 | 4.2112 | 4.1122 | 4.0429 | 3.8592 | 3.6806 | 3.5643
|  | KILTARLITY | FB |  |  |  |  | 4.7653 | 4.7724 | 4.7755 | 4.7663 | 4.7551 | 4.7367 | 4.7092 | 4.6653 | 4.6388 | 4.598 | 4.4194 | 4.2245 | 4.1602 | 5.248 | 5.251 | 5.248 | 5.2469 | 5.2449 | 5.2306 | 5.1969 | 5.1592 | 5.1378 | 5.0827 | 4.9163 | 4.7367 | 4.6847 | 4.6153 | 4.6204 | 4.6204 | 4.6153 | 4.6102 | 4.5898 | 4.548 | 4.5071 | 4.4827 | 4.4449 | 4.3071 | 4.1122 | 4.0847
| REDMOSS | KINCORTH | MINIMUM HEADROOM | NJ 94445 03252 | NO | NO | 6.72 | 0.46847 | 0.011331 | -0.70602 | -1.0499 | -1.4683 | -1.6764 | -1.9213 | -2.1132 | -2.3407 | -2.6223 | -4.0479 | -5.2387 | -5.9142 | 1.4465 | 1.0271 | 0.26184 | -0.099384 | -0.52693 | -0.60142 | -0.67285 | -0.75347 | -0.85755 | -0.97591 | -1.6198 | -2.1494 | -2.728 | 0.6621 | 0.2325 | -0.4879 | -0.82668 | -1.2246 | -1.341 | -1.4593 | -1.5655 | -1.6961 | -1.8379 | -2.9593 | -3.9899 | -4.5767
|  | KINCORTH | EE |  |  |  |  | 0.53888 | 0.011331 | -0.64887 | -0.98969 | -1.4244 | -1.6091 | -1.8723 | -2.0723 | -2.3407 | -2.605 | -4.0479 | -5.2387 | -5.9142 | 1.5231 | 1.0333 | 0.29245 | -0.068771 | -0.49632 | -0.57387 | -0.65347 | -0.72693 | -0.84122 | -0.95959 | -1.6198 | -2.1494 | -2.5443 | 0.73454 | 0.2325 | -0.44199 | -0.77668 | -1.1757 | -1.295 | -1.4216 | -1.5389 | -1.691 | -1.8287 | -2.9593 | -3.9899 | -4.5767
|  | KINCORTH | HT |  |  |  |  | 0.48684 | 0.015412 | -0.70602 | -1.0499 | -1.4683 | -1.6764 | -1.9213 | -2.1132 | -2.3407 | -2.6223 | -4.0407 | -5.0142 | -5.5213 | 1.4761 | 1.0384 | 0.26184 | -0.099384 | -0.52693 | -0.60142 | -0.67285 | -0.75347 | -0.85551 | -0.97591 | -1.5729 | -1.8422 | -1.9984 | 0.68659 | 0.23761 | -0.4879 | -0.82668 | -1.2246 | -1.341 | -1.4593 | -1.5655 | -1.6961 | -1.8379 | -2.9328 | -3.7277 | -4.1318
|  | KINCORTH | HE |  |  |  |  | 0.46847 | 0.017453 | -0.67642 | -1.0325 | -1.4642 | -1.6376 | -1.8713 | -2.0111 | -2.257 | -2.4948 | -3.5428 | -4.2448 | -4.6744 | 1.4465 | 1.0271 | 0.27715 | -0.09122 | -0.51877 | -0.59326 | -0.67285 | -0.73204 | -0.85755 | -0.96877 | -1.4341 | -1.7422 | -1.9933 | 0.6621 | 0.2325 | -0.46137 | -0.81137 | -1.2114 | -1.3195 | -1.4369 | -1.5287 | -1.6634 | -1.7859 | -2.5114 | -3.0808 | -3.4246
|  | KINCORTH | FB |  |  |  |  | 0.79092 | 0.545 | 0.046024 | -0.28051 | -0.66826 | -0.89479 | -1.0315 | -1.1744 | -1.2795 | -1.3774 | -1.8499 | -2.9203 | -3.8081 | 1.7057 | 1.4394 | 0.89245 | 0.54143 | 0.1098 | -0.13714 | -0.28102 | -0.40142 | -0.46163 | -0.53306 | -0.80244 | -1.7331 | -2.728 | 0.94781 | 0.70189 | 0.19883 | -0.12566 | -0.50423 | -0.71239 | -0.84097 | -0.96341 | -1.043 | -1.1155 | -1.4328 | -2.3328 | -2.9675
| FORT WILLIAM | KINGAIRLOCH | MINIMUM HEADROOM | NM 76917 56652 | YES | NO | 0.046 | 0.038359 | 0.031216 | 0.031216 | 0.028155 | 0.028155 | 0.022033 | 0.016931 | 0.013869 | 0.012849 | 0.0077469 | 0.0036653 | -0.00041633 | -0.0024571 | 0.042624 | 0.035482 | 0.035482 | 0.033441 | 0.033441 | 0.029359 | 0.025278 | 0.021196 | 0.022216 | 0.018135 | 0.016094 | 0.015073 | 0.016094 | 0.046104 | 0.03488 | 0.03692 | 0.032839 | 0.032839 | 0.024676 | 0.022635 | 0.018553 | 0.018553 | 0.015492 | 0.008349 | 0.0052878 | 0.0042673
|  | KINGAIRLOCH | EE |  |  |  |  | 0.038359 | 0.031216 | 0.031216 | 0.028155 | 0.029176 | 0.022033 | 0.016931 | 0.01489 | 0.012849 | 0.0087673 | 0.0036653 | -0.00041633 | -0.00041633 | 0.042624 | 0.035482 | 0.035482 | 0.033441 | 0.033441 | 0.029359 | 0.025278 | 0.023237 | 0.022216 | 0.018135 | 0.016094 | 0.015073 | 0.018135 | 0.046104 | 0.03488 | 0.03692 | 0.033859 | 0.032839 | 0.025696 | 0.023655 | 0.020594 | 0.018553 | 0.015492 | 0.008349 | 0.0052878 | 0.0063082
|  | KINGAIRLOCH | HT |  |  |  |  | 0.038359 | 0.031216 | 0.031216 | 0.028155 | 0.029176 | 0.024073 | 0.017951 | 0.013869 | 0.012849 | 0.0087673 | 0.0067265 | 0.0016245 | -0.0024571 | 0.042624 | 0.035482 | 0.035482 | 0.033441 | 0.033441 | 0.03038 | 0.025278 | 0.021196 | 0.022216 | 0.019155 | 0.017114 | 0.016094 | 0.017114 | 0.046104 | 0.03488 | 0.03692 | 0.032839 | 0.032839 | 0.026716 | 0.024676 | 0.018553 | 0.018553 | 0.015492 | 0.01141 | 0.008349 | 0.0042673
|  | KINGAIRLOCH | HE |  |  |  |  | 0.038359 | 0.031216 | 0.031216 | 0.028155 | 0.028155 | 0.022033 | 0.016931 | 0.01489 | 0.012849 | 0.0077469 | 0.0057061 | 0.00060408 | -0.0014367 | 0.042624 | 0.035482 | 0.035482 | 0.033441 | 0.033441 | 0.029359 | 0.025278 | 0.023237 | 0.022216 | 0.018135 | 0.017114 | 0.016094 | 0.017114 | 0.046104 | 0.03488 | 0.03692 | 0.032839 | 0.032839 | 0.024676 | 0.022635 | 0.020594 | 0.018553 | 0.015492 | 0.01039 | 0.0073286 | 0.0052878
|  | KINGAIRLOCH | FB |  |  |  |  | 0.038359 | 0.038359 | 0.033257 | 0.034278 | 0.034278 | 0.034278 | 0.031216 | 0.029176 | 0.029176 | 0.029176 | 0.018971 | 0.013869 | 0.012849 | 0.042624 | 0.042624 | 0.037522 | 0.038543 | 0.038543 | 0.038543 | 0.034461 | 0.033441 | 0.033441 | 0.03242 | 0.024257 | 0.020176 | 0.016094 | 0.046104 | 0.046104 | 0.038961 | 0.039982 | 0.039982 | 0.039982 | 0.03692 | 0.0359 | 0.033859 | 0.032839 | 0.022635 | 0.016512 | 0.016512
| DYCE | KINGSEAT | MINIMUM HEADROOM | NJ 89545 19709 | NO | YES | 1.8 | 9.4656 | 9.337 | 9.1145 | 8.8227 | 8.3513 | 7.4309 | 6.6248 | 6.1748 | 5.6829 | 5.3809 | 3.8227 | 2.9656 | 2.4737 | 10.3645 | 10.2962 | 10.2166 | 10.1217 | 9.7043 | 9.085 | 8.5901 | 8.4105 | 8.1962 | 7.9309 | 6.6829 | 6.5023 | 6.4666 | 10.1027 | 9.9915 | 9.8323 | 9.6037 | 9.2027 | 8.3088 | 7.6425 | 7.2762 | 6.8619 | 6.5343 | 5.1231 | 4.5129 | 4.2303
|  | KINGSEAT | EE |  |  |  |  | 9.4707 | 9.3401 | 9.185 | 8.9533 | 8.4727 | 7.5452 | 6.7829 | 6.3421 | 5.8707 | 5.6227 | 3.8227 | 2.9676 | 2.487 | 10.3676 | 10.3043 | 10.2482 | 10.1666 | 9.7554 | 9.1033 | 8.6196 | 8.436 | 8.1962 | 8.0207 | 6.739 | 6.5023 | 6.4666 | 10.1058 | 9.9925 | 9.8843 | 9.6996 | 9.2894 | 8.3884 | 7.7527 | 7.3874 | 6.9619 | 6.7201 | 5.1231 | 4.5231 | 4.2303
|  | KINGSEAT | HT |  |  |  |  | 9.4656 | 9.337 | 9.1145 | 8.8227 | 8.3513 | 7.8207 | 7.4645 | 7.0543 | 6.3911 | 5.7196 | 3.8737 | 2.9656 | 2.4737 | 10.3645 | 10.2962 | 10.2166 | 10.1217 | 9.7043 | 9.4421 | 9.2727 | 9.0686 | 8.6227 | 8.0901 | 6.6829 | 6.5023 | 6.5809 | 10.1027 | 9.9915 | 9.8323 | 9.6037 | 9.2027 | 8.6303 | 8.3231 | 7.9935 | 7.417 | 6.8017 | 5.1292 | 4.5129 | 4.2435
|  | KINGSEAT | HE |  |  |  |  | 9.4717 | 9.339 | 9.139 | 8.8503 | 8.3554 | 7.4309 | 6.6248 | 6.1748 | 5.6829 | 5.3809 | 3.9645 | 3.2768 | 2.8594 | 10.3686 | 10.3033 | 10.2339 | 10.1441 | 9.7268 | 9.085 | 8.5901 | 8.4105 | 8.2094 | 7.9309 | 6.9084 | 6.8186 | 6.687 | 10.1058 | 9.9915 | 9.8537 | 9.6282 | 9.2129 | 8.3088 | 7.6425 | 7.2762 | 6.8619 | 6.5343 | 5.3058 | 4.8782 | 4.6119
|  | KINGSEAT | FB |  |  |  |  | 9.6278 | 9.5748 | 9.4952 | 9.3727 | 9.1717 | 8.7299 | 8.1799 | 7.5196 | 7.2809 | 7.2839 | 6.5339 | 5.6543 | 5.187 | 10.4594 | 10.4319 | 10.3941 | 10.3503 | 10.1554 | 9.7972 | 9.2911 | 8.6717 | 8.586 | 8.5717 | 8.0268 | 7.3105 | 6.7758 | 10.2405 | 10.2037 | 10.1303 | 10.0548 | 9.8731 | 9.4945 | 9.0088 | 8.4303 | 8.2548 | 8.2609 | 7.6078 | 6.7599 | 6.2211
| BOAT OF GARTEN | KINGUSSIE | MINIMUM HEADROOM | NH 75429 00426 | NO | YES | 1.594 | 1.889 | 1.7961 | 1.7073 | 1.6247 | 1.5145 | 1.3114 | 1.0941 | 0.94612 | 0.72367 | 0.56551 | -0.031429 | -0.51612 | -0.90592 | 1.5349 | 1.4869 | 1.4257 | 1.338 | 1.2176 | 1.0961 | 0.94 | 0.94408 | 0.80224 | 0.66449 | 0.13898 | 0.1349 | 0.21959 | 1.6936 | 1.5946 | 1.5374 | 1.4742 | 1.3568 | 1.1905 | 1.0038 | 0.96296 | 0.78439 | 0.62827 | 0.015 | -0.16663 | -0.26663
|  | KINGUSSIE | EE |  |  |  |  | 1.889 | 1.7961 | 1.7073 | 1.6359 | 1.5288 | 1.3237 | 1.1237 | 1.0114 | 0.79816 | 0.6451 | -0.031429 | -0.51612 | -0.88755 | 1.5349 | 1.4869 | 1.4267 | 1.34 | 1.2176 | 1.0992 | 0.94204 | 0.9451 | 0.80327 | 0.66653 | 0.13898 | 0.1349 | 0.21959 | 1.6936 | 1.5966 | 1.5374 | 1.4823 | 1.367 | 1.1987 | 1.0211 | 0.98745 | 0.81194 | 0.6548 | 0.015 | -0.16663 | -0.26663
|  | KINGUSSIE | HT |  |  |  |  | 1.891 | 1.7971 | 1.7094 | 1.638 | 1.5278 | 1.3482 | 1.1349 | 1.0349 | 0.83898 | 0.68388 | 0.17163 | -0.37327 | -0.90592 | 1.5359 | 1.4869 | 1.4267 | 1.34 | 1.2176 | 1.0961 | 0.94 | 0.94408 | 0.80224 | 0.66449 | 0.2298 | 0.24102 | 0.31857 | 1.6946 | 1.5946 | 1.5385 | 1.4834 | 1.366 | 1.214 | 1.0272 | 0.99561 | 0.82418 | 0.66602 | 0.16908 | -0.0084694 | -0.21663
|  | KINGUSSIE | HE |  |  |  |  | 1.89 | 1.7971 | 1.7073 | 1.6247 | 1.5145 | 1.3114 | 1.0941 | 0.94612 | 0.72367 | 0.56551 | 0.16245 | -0.39776 | -0.76918 | 1.5359 | 1.4869 | 1.4257 | 1.338 | 1.2176 | 1.0982 | 0.94 | 0.9451 | 0.80224 | 0.66755 | 0.30531 | 0.28694 | 0.29102 | 1.6946 | 1.5946 | 1.5374 | 1.4742 | 1.3568 | 1.1905 | 1.0038 | 0.96296 | 0.78439 | 0.62827 | 0.215 | 0.01398 | -0.15745
|  | KINGUSSIE | FB |  |  |  |  | 1.9839 | 1.9533 | 1.9308 | 1.9145 | 1.8604 | 1.8288 | 1.7655 | 1.6696 | 1.5931 | 1.5206 | 1.2665 | 0.84918 | 0.72776 | 1.6022 | 1.5829 | 1.5594 | 1.5257 | 1.4573 | 1.4227 | 1.3696 | 1.2818 | 1.2073 | 1.1288 | 0.93592 | 0.56551 | 0.45429 | 1.7864 | 1.7487 | 1.713 | 1.7028 | 1.6589 | 1.6242 | 1.565 | 1.4762 | 1.4028 | 1.3283 | 1.0966 | 0.65786 | 0.60582
| TAYNUILT | KINLOCH | MINIMUM HEADROOM | NM 52465 27215 | YES | YES | 0.993 | -0.87387 | -0.93407 | -0.94836 | -0.96978 | -1.1657 | -1.3545 | -1.4371 | -1.6157 | -1.732 | -1.8953 | -2.2035 | -2.4228 | -2.4943 | -0.63203 | -0.69631 | -0.7004 | -0.7004 | -0.93611 | -1.0382 | -1.0922 | -1.2514 | -1.329 | -1.4871 | -1.7494 | -1.8728 | -1.8698 | -0.77999 | -0.85448 | -0.8606 | -0.87284 | -1.0892 | -1.2637 | -1.3371 | -1.4749 | -1.5759 | -1.732 | -2.0218 | -2.2004 | -2.2392
|  | KINLOCH | EE |  |  |  |  | -0.86978 | -0.87999 | -0.94836 | -0.96774 | -1.129 | -1.3473 | -1.4371 | -1.6014 | -1.732 | -1.8953 | -2.2035 | -2.4228 | -2.4943 | -0.62897 | -0.63815 | -0.7004 | -0.7004 | -0.83305 | -1.0351 | -1.0882 | -1.2239 | -1.329 | -1.4871 | -1.7484 | -1.8728 | -1.8698 | -0.77693 | -0.78305 | -0.8606 | -0.87182 | -1.0279 | -1.2565 | -1.3086 | -1.4586 | -1.5759 | -1.732 | -2.0218 | -2.2004 | -2.2392
|  | KINLOCH | HT |  |  |  |  | -0.86978 | -0.93407 | -0.94121 | -0.95856 | -1.1177 | -1.3157 | -1.4106 | -1.5422 | -1.6739 | -1.8433 | -2.1422 | -2.3126 | -2.3871 | -0.62897 | -0.69631 | -0.69938 | -0.69938 | -0.82999 | -1.0167 | -1.082 | -1.1922 | -1.3055 | -1.4626 | -1.7494 | -1.8086 | -1.7637 | -0.77693 | -0.85448 | -0.85652 | -0.8657 | -1.0198 | -1.2279 | -1.3157 | -1.4116 | -1.53 | -1.6933 | -1.983 | -2.1075 | -2.133
|  | KINLOCH | HE |  |  |  |  | -0.87387 | -0.87897 | -0.94427 | -0.96978 | -1.1341 | -1.3545 | -1.4361 | -1.6157 | -1.7004 | -1.8137 | -2.0484 | -2.1361 | -2.2351 | -0.63203 | -0.63815 | -0.69836 | -0.69938 | -0.83101 | -1.0382 | -1.0922 | -1.2514 | -1.3096 | -1.4106 | -1.6269 | -1.5943 | -1.6188 | -0.77999 | -0.78203 | -0.85958 | -0.87284 | -1.029 | -1.2637 | -1.3371 | -1.4749 | -1.5473 | -1.6545 | -1.881 | -1.9188 | -1.9871
|  | KINLOCH | FB |  |  |  |  | -0.84836 | -0.83407 | -0.83815 | -0.88101 | -1.1657 | -1.1677 | -1.2014 | -1.2065 | -1.2198 | -1.2218 | -1.3106 | -1.3575 | -1.6361 | -0.61264 | -0.60346 | -0.61366 | -0.66468 | -0.93611 | -0.93815 | -0.97591 | -0.98509 | -0.99938 | -1.0055 | -1.079 | -1.1514 | -1.4422 | -0.75856 | -0.74223 | -0.74529 | -0.80448 | -1.0892 | -1.0933 | -1.1279 | -1.133 | -1.1473 | -1.1514 | -1.233 | -1.3116 | -1.5708
| TUMMEL BRIDGE | KINLOCH RANNOCH | MINIMUM HEADROOM | NN 65927 58500 | YES | YES | 0.09 | 0.0061224 | 0.010204 | 0.0071429 | 0.005102 | -0.0030612 | -0.017347 | -0.032653 | -0.055102 | -0.067347 | -0.083673 | -0.11531 | -0.1449 | -0.16939 | -0.016327 | -0.020408 | -0.031633 | -0.040816 | -0.061224 | -0.071429 | -0.086735 | -0.11122 | -0.11633 | -0.13469 | -0.18367 | -0.18673 | -0.17755 | 0.039796 | 0.036735 | 0.026531 | 0.018367 | -0.0071429 | -0.018367 | -0.035714 | -0.061224 | -0.069388 | -0.090816 | -0.13878 | -0.1602 | -0.15612
|  | KINLOCH RANNOCH | EE |  |  |  |  | 0.0061224 | 0.010204 | 0.0071429 | 0.005102 | -0.0020408 | -0.014286 | -0.030612 | -0.05102 | -0.062245 | -0.076531 | -0.10714 | -0.1449 | -0.16939 | -0.016327 | -0.020408 | -0.031633 | -0.040816 | -0.061224 | -0.071429 | -0.086735 | -0.11122 | -0.11633 | -0.13469 | -0.17551 | -0.17755 | -0.17143 | 0.039796 | 0.036735 | 0.026531 | 0.018367 | -0.0061224 | -0.017347 | -0.034694 | -0.060204 | -0.069388 | -0.087755 | -0.13878 | -0.15816 | -0.15102
|  | KINLOCH RANNOCH | HT |  |  |  |  | 0.0081633 | 0.011224 | 0.0091837 | 0.0071429 | 0.0010204 | -0.011224 | -0.026531 | -0.046939 | -0.055102 | -0.07449 | -0.11531 | -0.13673 | -0.16735 | -0.016327 | -0.020408 | -0.031633 | -0.040816 | -0.061224 | -0.070408 | -0.084694 | -0.1102 | -0.11531 | -0.13367 | -0.18367 | -0.18673 | -0.17755 | 0.040816 | 0.036735 | 0.027551 | 0.018367 | -0.005102 | -0.015306 | -0.032653 | -0.058163 | -0.063265 | -0.086735 | -0.13673 | -0.1602 | -0.15612
|  | KINLOCH RANNOCH | HE |  |  |  |  | 0.0081633 | 0.011224 | 0.0091837 | 0.005102 | -0.0030612 | -0.017347 | -0.032653 | -0.055102 | -0.067347 | -0.083673 | -0.096939 | -0.14286 | -0.16837 | -0.016327 | -0.020408 | -0.031633 | -0.040816 | -0.061224 | -0.070408 | -0.084694 | -0.1102 | -0.11531 | -0.13367 | -0.17347 | -0.17857 | -0.17755 | 0.040816 | 0.036735 | 0.027551 | 0.018367 | -0.0071429 | -0.018367 | -0.035714 | -0.061224 | -0.069388 | -0.090816 | -0.13265 | -0.15816 | -0.15306
|  | KINLOCH RANNOCH | FB |  |  |  |  | 0.023469 | 0.021429 | 0.029592 | 0.028571 | 0.028571 | 0.029592 | 0.02551 | 0.015306 | 0.015306 | 0.016327 | -0.015306 | -0.053061 | -0.065306 | -0.0071429 | -0.013265 | -0.015306 | -0.02551 | -0.036735 | -0.036735 | -0.046939 | -0.061224 | -0.063265 | -0.070408 | -0.10918 | -0.15102 | -0.16837 | 0.052041 | 0.043878 | 0.043878 | 0.036735 | 0.027551 | 0.02551 | 0.016327 | 0.0020408 | 0 | -0.0081633 | -0.043878 | -0.093878 | -0.10306
| GRUDIE BRIDGE | KINLOCHEWE | MINIMUM HEADROOM | NH 03723 62321 | YES | NO | 0.18 | 0.16429 | 0.16429 | 0.1602 | 0.15102 | 0.1398 | 0.10408 | 0.085714 | 0.062245 | 0.031633 | 0.02449 | -0.029592 | -0.07551 | -0.12755 | 0.44898 | 0.44592 | 0.43776 | 0.43367 | 0.42449 | 0.4051 | 0.39592 | 0.37959 | 0.3602 | 0.33469 | 0.27551 | 0.28061 | 0.27857 | 0.34082 | 0.3398 | 0.33265 | 0.32347 | 0.31224 | 0.28163 | 0.26531 | 0.24388 | 0.21837 | 0.19286 | 0.14592 | 0.14184 | 0.1102
|  | KINLOCHEWE | EE |  |  |  |  | 0.16531 | 0.16429 | 0.1602 | 0.15306 | 0.1449 | 0.10408 | 0.091837 | 0.067347 | 0.035714 | 0.028571 | -0.029592 | -0.07551 | -0.12041 | 0.44898 | 0.44694 | 0.43878 | 0.43571 | 0.42551 | 0.4051 | 0.39694 | 0.37959 | 0.3602 | 0.33469 | 0.29082 | 0.29592 | 0.31531 | 0.34184 | 0.34082 | 0.33265 | 0.32347 | 0.31531 | 0.28163 | 0.26939 | 0.24694 | 0.22143 | 0.19694 | 0.14592 | 0.14184 | 0.11939
|  | KINLOCHEWE | HT |  |  |  |  | 0.16531 | 0.16429 | 0.1602 | 0.15306 | 0.14286 | 0.11429 | 0.092857 | 0.070408 | 0.038776 | 0.031633 | -0.016327 | -0.068367 | -0.12755 | 0.44898 | 0.44592 | 0.43776 | 0.43571 | 0.42449 | 0.40612 | 0.39592 | 0.37959 | 0.3602 | 0.33469 | 0.27551 | 0.28061 | 0.3 | 0.34082 | 0.3398 | 0.33265 | 0.32347 | 0.31327 | 0.28776 | 0.26939 | 0.24898 | 0.22245 | 0.19592 | 0.15102 | 0.14388 | 0.1102
|  | KINLOCHEWE | HE |  |  |  |  | 0.16429 | 0.16531 | 0.16224 | 0.15102 | 0.1398 | 0.10612 | 0.085714 | 0.062245 | 0.031633 | 0.02449 | -0.017347 | -0.07449 | -0.11939 | 0.44898 | 0.44694 | 0.4398 | 0.43367 | 0.42449 | 0.40612 | 0.39592 | 0.38061 | 0.3602 | 0.33469 | 0.2898 | 0.29388 | 0.29796 | 0.34082 | 0.34082 | 0.33265 | 0.32347 | 0.31224 | 0.28163 | 0.26531 | 0.24388 | 0.21837 | 0.19286 | 0.15102 | 0.14184 | 0.11837
|  | KINLOCHEWE | FB |  |  |  |  | 0.18367 | 0.18367 | 0.18878 | 0.18673 | 0.18878 | 0.18673 | 0.17551 | 0.17245 | 0.16224 | 0.15918 | 0.1102 | 0.067347 | 0.052041 | 0.46224 | 0.4602 | 0.45816 | 0.45306 | 0.45 | 0.44694 | 0.43469 | 0.42551 | 0.41327 | 0.40918 | 0.36224 | 0.31633 | 0.27857 | 0.35714 | 0.3551 | 0.35612 | 0.35408 | 0.35102 | 0.34796 | 0.33878 | 0.33061 | 0.31633 | 0.31735 | 0.26327 | 0.21837 | 0.21429
| KINLOCHLEVEN | KINLOCHLEVEN | MINIMUM HEADROOM | NN 19285 62002 | NO | YES | 0.07 | 2.1255 | 2.1367 | 2.1439 | 2.1286 | 2.1041 | 1.9316 | 1.7735 | 1.6582 | 1.601 | 1.5806 | 1.5143 | 1.4643 | 1.4092 | 2.0612 | 2.0541 | 2.0429 | 2.0184 | 1.9939 | 1.8643 | 1.7561 | 1.6878 | 1.6316 | 1.5918 | 1.499 | 1.4929 | 1.5051 | 2.2122 | 2.2204 | 2.2255 | 2.2194 | 2.2112 | 2.0265 | 1.9031 | 1.8082 | 1.7571 | 1.7408 | 1.6949 | 1.6612 | 1.6337
|  | KINLOCHLEVEN | EE |  |  |  |  | 2.1255 | 2.1367 | 2.1439 | 2.1286 | 2.1041 | 2.0724 | 2.0337 | 1.8714 | 1.7163 | 1.6306 | 1.5153 | 1.4663 | 1.448 | 2.0612 | 2.0541 | 2.0429 | 2.0184 | 1.9939 | 1.9684 | 1.9276 | 1.798 | 1.6929 | 1.6112 | 1.5173 | 1.5092 | 1.5255 | 2.2122 | 2.2204 | 2.2255 | 2.2194 | 2.2112 | 2.1837 | 2.15 | 1.999 | 1.8612 | 1.7806 | 1.6949 | 1.6643 | 1.6622
|  | KINLOCHLEVEN | HT |  |  |  |  | 2.1265 | 2.1367 | 2.1459 | 2.1286 | 2.1041 | 1.9316 | 1.7735 | 1.6582 | 1.601 | 1.5806 | 1.5224 | 1.4643 | 1.4092 | 2.0612 | 2.0541 | 2.0439 | 2.0184 | 1.9939 | 1.8643 | 1.7561 | 1.6878 | 1.6316 | 1.5918 | 1.499 | 1.4929 | 1.5082 | 2.2133 | 2.2204 | 2.2265 | 2.2194 | 2.2112 | 2.0265 | 1.9031 | 1.8082 | 1.7571 | 1.7408 | 1.701 | 1.6612 | 1.6337
|  | KINLOCHLEVEN | HE |  |  |  |  | 2.1265 | 2.1367 | 2.1449 | 2.1306 | 2.1082 | 2.0765 | 2.0296 | 1.8418 | 1.6765 | 1.5857 | 1.5143 | 1.4643 | 1.4388 | 2.0612 | 2.0541 | 2.0429 | 2.0184 | 1.9939 | 1.9694 | 1.9286 | 1.7888 | 1.6786 | 1.598 | 1.5194 | 1.5092 | 1.5051 | 2.2133 | 2.2204 | 2.2265 | 2.2214 | 2.2143 | 2.1847 | 2.1459 | 1.9745 | 1.8276 | 1.7439 | 1.6969 | 1.6684 | 1.652
|  | KINLOCHLEVEN | FB |  |  |  |  | 2.151 | 2.1653 | 2.1827 | 2.1786 | 2.1755 | 2.1643 | 2.1663 | 2.152 | 2.0459 | 1.949 | 1.7367 | 1.6684 | 1.6439 | 2.0806 | 2.0735 | 2.0714 | 2.0551 | 2.0469 | 2.0327 | 2.0255 | 2.0031 | 1.9051 | 1.8327 | 1.6439 | 1.552 | 1.5112 | 2.2327 | 2.2459 | 2.2561 | 2.2602 | 2.2694 | 2.2633 | 2.2633 | 2.25 | 2.1276 | 2.0378 | 1.8327 | 1.7724 | 1.7612
| FORT WILLIAM | KINLOCHMOIDART | MINIMUM HEADROOM | NM 71407 72091 | YES | NO | 0 | 0.9602 | 0.95102 | 0.95 | 0.94898 | 0.94286 | 0.9398 | 0.93367 | 0.93265 | 0.92857 | 0.92857 | 0.92041 | 0.91429 | 0.91122 | 0.97347 | 0.96327 | 0.96327 | 0.96224 | 0.95816 | 0.95714 | 0.95408 | 0.95204 | 0.94898 | 0.95 | 0.94184 | 0.9449 | 0.9449 | 0.96633 | 0.95714 | 0.95816 | 0.95612 | 0.94898 | 0.94694 | 0.94184 | 0.94082 | 0.93673 | 0.93776 | 0.93163 | 0.92755 | 0.92449
|  | KINLOCHMOIDART | EE |  |  |  |  | 0.9602 | 0.95102 | 0.95 | 0.95 | 0.94388 | 0.94082 | 0.93367 | 0.93265 | 0.92857 | 0.92857 | 0.92041 | 0.91429 | 0.91122 | 0.97347 | 0.96327 | 0.96327 | 0.96224 | 0.95918 | 0.95816 | 0.95408 | 0.95204 | 0.94898 | 0.95 | 0.94388 | 0.9449 | 0.9449 | 0.96633 | 0.95714 | 0.95816 | 0.95612 | 0.95102 | 0.94796 | 0.94184 | 0.94082 | 0.93673 | 0.93776 | 0.93163 | 0.92755 | 0.92551
|  | KINLOCHMOIDART | HT |  |  |  |  | 0.9602 | 0.95102 | 0.95 | 0.95 | 0.94388 | 0.9398 | 0.93469 | 0.93367 | 0.92959 | 0.92857 | 0.92245 | 0.91735 | 0.91122 | 0.97347 | 0.96327 | 0.96327 | 0.96224 | 0.95918 | 0.95714 | 0.95408 | 0.95204 | 0.95 | 0.95102 | 0.94184 | 0.94592 | 0.9449 | 0.96633 | 0.95714 | 0.95816 | 0.95612 | 0.95102 | 0.94694 | 0.94286 | 0.94184 | 0.93776 | 0.93878 | 0.93163 | 0.92959 | 0.92449
|  | KINLOCHMOIDART | HE |  |  |  |  | 0.9602 | 0.95102 | 0.95 | 0.94898 | 0.94286 | 0.9398 | 0.93469 | 0.93265 | 0.92857 | 0.92857 | 0.92245 | 0.91735 | 0.91327 | 0.97347 | 0.96327 | 0.96327 | 0.96224 | 0.95816 | 0.95816 | 0.95408 | 0.95204 | 0.94898 | 0.95102 | 0.94388 | 0.94592 | 0.94592 | 0.96633 | 0.95714 | 0.95816 | 0.95612 | 0.94898 | 0.94796 | 0.94388 | 0.94082 | 0.93673 | 0.93776 | 0.93367 | 0.92959 | 0.92653
|  | KINLOCHMOIDART | FB |  |  |  |  | 0.9602 | 0.96122 | 0.95408 | 0.95612 | 0.95408 | 0.95204 | 0.95204 | 0.95204 | 0.94796 | 0.95204 | 0.93878 | 0.93571 | 0.93367 | 0.97347 | 0.97347 | 0.96633 | 0.96837 | 0.96837 | 0.96429 | 0.96531 | 0.96327 | 0.95918 | 0.96224 | 0.95204 | 0.94796 | 0.94694 | 0.96633 | 0.96735 | 0.96122 | 0.96224 | 0.96224 | 0.95918 | 0.95918 | 0.95816 | 0.95408 | 0.95714 | 0.94388 | 0.94184 | 0.94082
| ELGIN | KINLOSS | MINIMUM HEADROOM | NJ 06695 61740 | NO | YES | 0.09 | 11.2153 | 11.2173 | 11.2041 | 11.1714 | 10.9429 | 10.7163 | 10.5602 | 10.351 | 10.2316 | 10.0224 | 9.5796 | 9.102 | 8.8776 | 11.5745 | 11.5776 | 11.5724 | 11.5643 | 11.3439 | 11.1602 | 11.0704 | 10.8806 | 10.8112 | 10.6316 | 10.3439 | 10.1724 | 10.1235 | 11.1628 | 11.1628 | 11.1495 | 11.1281 | 10.9913 | 10.8842 | 10.7801 | 10.6577 | 10.575 | 10.4383 | 10.0964 | 9.7077 | 9.5566
|  | KINLOSS | EE |  |  |  |  | 11.2153 | 11.2184 | 11.2041 | 11.1888 | 10.9429 | 10.7163 | 10.5602 | 10.3643 | 10.2327 | 10.049 | 9.5796 | 9.102 | 8.8776 | 11.5745 | 11.5776 | 11.5745 | 11.5643 | 11.3459 | 11.1612 | 11.0704 | 10.9224 | 10.85 | 10.699 | 10.4051 | 10.1724 | 10.1235 | 11.1628 | 11.1628 | 11.1505 | 11.1281 | 10.9913 | 10.8842 | 10.7801 | 10.6628 | 10.575 | 10.4546 | 10.1005 | 9.7077 | 9.5566
|  | KINLOSS | HT |  |  |  |  | 11.2153 | 11.2184 | 11.2061 | 11.1745 | 10.9459 | 10.7449 | 10.602 | 10.351 | 10.2316 | 10.0224 | 9.6102 | 9.1888 | 8.8969 | 11.5745 | 11.5776 | 11.5724 | 11.5643 | 11.3439 | 11.1857 | 11.102 | 10.8806 | 10.8112 | 10.6316 | 10.3439 | 10.2112 | 10.1816 | 11.1628 | 11.1628 | 11.1505 | 11.1301 | 10.9944 | 10.8974 | 10.8026 | 10.6577 | 10.577 | 10.4383 | 10.0964 | 9.7832 | 9.5923
|  | KINLOSS | HE |  |  |  |  | 11.2153 | 11.2173 | 11.2051 | 11.1714 | 10.9459 | 10.7204 | 10.5724 | 10.3724 | 10.2612 | 10.0612 | 9.7755 | 9.4684 | 9.3194 | 11.5745 | 11.5776 | 11.5724 | 11.5643 | 11.3439 | 11.1602 | 11.0786 | 10.9214 | 10.8684 | 10.6959 | 10.5235 | 10.5051 | 10.4959 | 11.1628 | 11.1628 | 11.1495 | 11.1281 | 10.9934 | 10.8872 | 10.7872 | 10.6648 | 10.5893 | 10.4597 | 10.2699 | 10.0536 | 9.9434
|  | KINLOSS | FB |  |  |  |  | 11.2469 | 11.2673 | 11.2786 | 11.2673 | 11.2643 | 11.2408 | 11.2214 | 11.2031 | 11.1633 | 11.1449 | 10.9418 | 10.3357 | 9.9837 | 11.5888 | 11.598 | 11.6051 | 11.5959 | 11.5918 | 11.5796 | 11.5561 | 11.5408 | 11.5143 | 11.5031 | 11.3204 | 10.7163 | 10.2959 | 11.1801 | 11.1944 | 11.1995 | 11.1913 | 11.1832 | 11.1709 | 11.1413 | 11.1291 | 11.1026 | 11.0934 | 10.9689 | 10.5352 | 10.3434
| BRACO | KIPPEN | MINIMUM HEADROOM | NS 66376 95628 | NO | YES | 0.422 | 3.5202 | 3.4967 | 3.4263 | 3.3202 | 3.1835 | 2.7539 | 2.4151 | 2.2529 | 1.9182 | 1.6284 | 0.72531 | -0.062449 | -0.78592 | 3.0518 | 3.0284 | 2.9743 | 2.9151 | 2.7967 | 2.4396 | 2.1702 | 2.1508 | 1.8998 | 1.6855 | 1.06 | 1.0569 | 1.1222 | 3.2712 | 3.2406 | 3.1559 | 3.0927 | 2.9896 | 2.5896 | 2.2937 | 2.1692 | 1.8722 | 1.6182 | 0.83755 | 0.32939 | -0.12878
|  | KIPPEN | EE |  |  |  |  | 3.5212 | 3.508 | 3.4427 | 3.3416 | 3.209 | 2.7773 | 2.4447 | 2.3345 | 2.0161 | 1.7151 | 0.8498 | 0.21918 | -0.2951 | 3.0549 | 3.0335 | 2.9824 | 2.9212 | 2.8039 | 2.4396 | 2.1794 | 2.1773 | 1.9294 | 1.6906 | 1.1682 | 1.1835 | 1.2437 | 3.2753 | 3.2498 | 3.1702 | 3.1161 | 3.0049 | 2.6069 | 2.311 | 2.2365 | 1.9549 | 1.6845 | 0.9549 | 0.55184 | 0.23551
|  | KIPPEN | HT |  |  |  |  | 3.5202 | 3.4967 | 3.4263 | 3.3202 | 3.1835 | 2.7539 | 2.4151 | 2.2529 | 1.9182 | 1.6284 | 0.72531 | -0.062449 | -0.78592 | 3.0518 | 3.0284 | 2.9743 | 2.9151 | 2.7967 | 2.4457 | 2.1865 | 2.1508 | 1.8998 | 1.6855 | 1.06 | 1.0569 | 1.1222 | 3.2712 | 3.2406 | 3.1559 | 3.0927 | 2.9896 | 2.5896 | 2.2937 | 2.1692 | 1.8722 | 1.6182 | 0.83755 | 0.32939 | -0.12878
|  | KIPPEN | HE |  |  |  |  | 3.5243 | 3.511 | 3.4498 | 3.3447 | 3.208 | 2.8457 | 2.4273 | 2.2967 | 2.0416 | 1.7263 | 1.1437 | 0.42429 | -0.13388 | 3.0559 | 3.0335 | 2.9845 | 2.9212 | 2.8029 | 2.511 | 2.1702 | 2.159 | 1.9794 | 1.7345 | 1.3539 | 1.3386 | 1.3345 | 3.2763 | 3.2518 | 3.1784 | 3.1192 | 3.0039 | 2.6712 | 2.2988 | 2.2059 | 1.9886 | 1.7059 | 1.21 | 0.73653 | 0.35694
|  | KIPPEN | FB |  |  |  |  | 3.5804 | 3.5998 | 3.5906 | 3.5733 | 3.5202 | 3.4427 | 3.3804 | 3.2824 | 3.1998 | 3.11 | 2.7437 | 2.1763 | 1.3927 | 3.1059 | 3.108 | 3.0937 | 3.0865 | 3.0406 | 2.9743 | 2.9233 | 2.8345 | 2.7631 | 2.6814 | 2.4876 | 2.0906 | 1.4406 | 3.3416 | 3.3488 | 3.3345 | 3.3069 | 3.2661 | 3.212 | 3.1559 | 3.0641 | 2.9876 | 2.9049 | 2.5835 | 1.9937 | 1.3947
| THURSO | KIRKWALL | MINIMUM HEADROOM | HY 44669 10987 | NO | NO | 2.953 | 5.1684 | 4.6338 | 4.0246 | 2.6756 | 2.2705 | 1.7491 | -0.0019592 | -2.002 | -5.7275 | -6.6428 | -14.153 | -20.5275 | -25.9173 | 8.898 | 8.246 | 7.5664 | 6.2195 | 5.9093 | 5.5868 | 4.3562 | 2.9654 | -1.2173 | -2.0795 | -9.1826 | -16.3867 | -22.8622 | 7.6491 | 7.0582 | 6.446 | 5.1062 | 4.7429 | 4.2562 | 2.598 | 0.71743 | -3.4622 | -4.3295 | -12.0387 | -19.4907 | -25.9346
|  | KIRKWALL | EE |  |  |  |  | 5.3674 | 4.6338 | 4.0246 | 2.6838 | 2.2868 | 1.7552 | 0.66335 | -0.92951 | -3.5611 | -3.9795 | -10.3897 | -16.452 | -18.9101 | 9.1205 | 8.246 | 7.5674 | 6.2205 | 5.9093 | 5.5868 | 4.7868 | 3.6031 | 1.4297 | 0.996 | -4.4979 | -11.2897 | -14.0591 | 7.8521 | 7.0582 | 6.446 | 5.1103 | 4.7531 | 4.2562 | 3.2154 | 1.6746 | -0.81012 | -1.2377 | -7.3438 | -14.3856 | -17.1367
|  | KIRKWALL | HT |  |  |  |  | 5.247 | 4.6664 | 4.0256 | 2.6756 | 2.2705 | 1.7674 | -0.0019592 | -2.002 | -5.7275 | -6.6428 | -11.4734 | -18.1346 | -23.4234 | 8.9858 | 8.2797 | 7.5674 | 6.2195 | 5.9123 | 5.6358 | 4.3562 | 2.9715 | 0.032735 | -0.97237 | -5.9683 | -13.5275 | -19.4122 | 7.7307 | 7.0909 | 6.446 | 5.1062 | 4.7429 | 4.2878 | 2.598 | 0.71743 | -2.7979 | -3.7387 | -8.7346 | -16.5346 | -22.6989
|  | KIRKWALL | HE |  |  |  |  | 5.1684 | 4.647 | 4.0287 | 2.6919 | 2.2889 | 1.7491 | 0.56845 | -1.4591 | -5.7101 | -6.4816 | -14.153 | -20.5275 | -25.9173 | 8.898 | 8.2542 | 7.5664 | 6.2215 | 5.9133 | 5.596 | 4.7031 | 2.9654 | -1.2173 | -2.0795 | -9.1826 | -16.3867 | -22.8622 | 7.6491 | 7.0705 | 6.4491 | 5.1164 | 4.7552 | 4.2572 | 3.1154 | 1.0236 | -3.4622 | -4.3295 | -12.0387 | -19.4907 | -25.9346
|  | KIRKWALL | FB |  |  |  |  | 5.9562 | 5.4654 | 4.9389 | 4.3807 | 3.7899 | 3.4399 | 2.8297 | 2.1072 | 0.946 | 0.57151 | -2.2662 | -6.7367 | -8.9693 | 9.7256 | 9.0817 | 8.4164 | 7.7307 | 7.0348 | 6.6195 | 5.8593 | 4.9838 | 3.5715 | 3.1062 | 0.7909 | -3.5173 | -6.5438 | 8.4358 | 7.8889 | 7.3174 | 6.7042 | 6.095 | 5.7225 | 5.0103 | 4.1644 | 2.7582 | 2.3082 | -0.30196 | -5.2479 | -7.1009
| BROADFORD | KISHORNHILL | MINIMUM HEADROOM | NG 88304 40591 | YES | YES | 0.689 | -0.15094 | -0.15502 | -0.1591 | -0.16624 | -0.17645 | -0.29482 | -0.36624 | -0.42441 | -0.45196 | -0.46318 | -0.49073 | -0.52033 | -0.51624 | -0.073388 | -0.07849 | -0.07951 | -0.085633 | -0.092776 | -0.19278 | -0.25808 | -0.31012 | -0.33053 | -0.33971 | -0.35706 | -0.3591 | -0.36012 | -0.082571 | -0.086653 | -0.089714 | -0.093796 | -0.099918 | -0.21624 | -0.28665 | -0.34278 | -0.36522 | -0.37543 | -0.39278 | -0.404 | -0.41522
|  | KISHORNHILL | EE |  |  |  |  | -0.15094 | -0.15502 | -0.15808 | -0.16624 | -0.17441 | -0.18869 | -0.1989 | -0.31829 | -0.39482 | -0.4489 | -0.49073 | -0.52033 | -0.51216 | -0.073388 | -0.07849 | -0.07951 | -0.085633 | -0.091755 | -0.099918 | -0.10502 | -0.2091 | -0.27033 | -0.32237 | -0.35196 | -0.35298 | -0.34992 | -0.082571 | -0.086653 | -0.089714 | -0.093796 | -0.099918 | -0.1091 | -0.11522 | -0.23155 | -0.30604 | -0.36114 | -0.39278 | -0.404 | -0.41012
|  | KISHORNHILL | HT |  |  |  |  | -0.15094 | -0.15502 | -0.15808 | -0.16624 | -0.17441 | -0.29482 | -0.36624 | -0.42441 | -0.45196 | -0.46216 | -0.48563 | -0.51522 | -0.51624 | -0.073388 | -0.07849 | -0.07951 | -0.085633 | -0.092776 | -0.19278 | -0.25808 | -0.31012 | -0.33053 | -0.33971 | -0.35706 | -0.3591 | -0.35094 | -0.082571 | -0.086653 | -0.089714 | -0.093796 | -0.099918 | -0.21624 | -0.28665 | -0.34278 | -0.36522 | -0.37543 | -0.39278 | -0.404 | -0.41522
|  | KISHORNHILL | HE |  |  |  |  | -0.15094 | -0.15502 | -0.1591 | -0.16522 | -0.17645 | -0.18971 | -0.1989 | -0.33053 | -0.41114 | -0.46318 | -0.48461 | -0.51624 | -0.51216 | -0.073388 | -0.07849 | -0.07951 | -0.084612 | -0.091755 | -0.10094 | -0.10604 | -0.21931 | -0.28461 | -0.33665 | -0.35094 | -0.354 | -0.35604 | -0.082571 | -0.086653 | -0.089714 | -0.093796 | -0.098898 | -0.1091 | -0.11522 | -0.24482 | -0.32237 | -0.37441 | -0.38971 | -0.40196 | -0.41012
|  | KISHORNHILL | FB |  |  |  |  | -0.14073 | -0.14482 | -0.14073 | -0.14686 | -0.15094 | -0.15298 | -0.15706 | -0.16114 | -0.24992 | -0.30604 | -0.41114 | -0.43155 | -0.43767 | -0.059102 | -0.066245 | -0.065224 | -0.069306 | -0.072367 | -0.074408 | -0.081551 | -0.086653 | -0.16624 | -0.21931 | -0.32441 | -0.34482 | -0.36012 | -0.074408 | -0.076449 | -0.075429 | -0.07849 | -0.07951 | -0.083592 | -0.084612 | -0.088694 | -0.17747 | -0.23563 | -0.33767 | -0.35706 | -0.3591
| BROADFORD | KYLE | MINIMUM HEADROOM | NG 76499 27247 | NO | YES | 0.088 | 4.6582 | 6.3512 | 6.342 | 6.3216 | 6.3063 | 5.9492 | 5.5043 | 4.9818 | 4.4553 | 4.1288 | 3.7308 | 3.5961 | 3.4635 | 4.7031 | 6.39 | 6.3859 | 6.3829 | 6.3716 | 6.0818 | 5.7288 | 5.2533 | 4.7247 | 4.3818 | 4.0522 | 4.0492 | 3.9869 | 4.5184 | 6.2104 | 6.2022 | 6.1757 | 6.1349 | 5.7931 | 5.391 | 4.9145 | 4.4267 | 4.1176 | 3.7696 | 3.6951 | 3.6165
|  | KYLE | EE |  |  |  |  | 4.6582 | 6.3512 | 6.342 | 6.3227 | 6.3063 | 6.2482 | 6.1737 | 5.8033 | 5.3716 | 4.8849 | 3.7308 | 3.5961 | 3.5033 | 4.7051 | 6.39 | 6.3859 | 6.3839 | 6.3716 | 6.3492 | 6.3073 | 6.0339 | 5.6971 | 5.2073 | 4.0624 | 4.0563 | 4.0584 | 4.5204 | 6.2104 | 6.2022 | 6.1767 | 6.1349 | 6.0869 | 6.0431 | 5.6859 | 5.2961 | 4.841 | 3.7696 | 3.6951 | 3.6431
|  | KYLE | HT |  |  |  |  | 4.6592 | 6.3522 | 6.3431 | 6.3237 | 6.3084 | 5.9492 | 5.5043 | 4.9818 | 4.4553 | 4.1288 | 3.7655 | 3.6022 | 3.4635 | 4.7051 | 6.39 | 6.3859 | 6.3839 | 6.3716 | 6.0818 | 5.7288 | 5.2533 | 4.7247 | 4.3818 | 4.0522 | 4.0492 | 4.0696 | 4.5204 | 6.2104 | 6.2033 | 6.1767 | 6.1359 | 5.7931 | 5.391 | 4.9145 | 4.4267 | 4.1176 | 3.7808 | 3.6982 | 3.6165
|  | KYLE | HE |  |  |  |  | 4.6582 | 6.3522 | 6.3431 | 6.3216 | 6.3104 | 6.2553 | 6.1757 | 5.7829 | 5.2941 | 4.7339 | 3.7594 | 3.6084 | 3.5196 | 4.7031 | 6.39 | 6.3859 | 6.3829 | 6.3716 | 6.3512 | 6.3073 | 6.0216 | 5.6288 | 5.0522 | 4.0676 | 4.0553 | 4.0492 | 4.5184 | 6.2104 | 6.2033 | 6.1757 | 6.138 | 6.09 | 6.0431 | 5.6635 | 5.2227 | 4.6982 | 3.7849 | 3.7002 | 3.6471
|  | KYLE | FB |  |  |  |  | 4.6908 | 6.4022 | 6.4145 | 6.4216 | 6.4206 | 6.4155 | 6.4104 | 6.392 | 6.139 | 5.8788 | 4.2471 | 4.1216 | 4.0839 | 4.7276 | 6.4267 | 6.4247 | 6.4288 | 6.4227 | 6.4155 | 6.4063 | 6.3818 | 6.1614 | 5.8951 | 4.1869 | 4.0543 | 3.9869 | 4.5408 | 6.2441 | 6.2502 | 6.2482 | 6.2329 | 6.2237 | 6.2104 | 6.1849 | 5.9553 | 5.6849 | 4.0869 | 3.9788 | 3.9645
| LAIRG | LAIRG | MINIMUM HEADROOM | NC 58798 07111 | YES | NO | 0.141 | -0.30102 | -0.30714 | 1.9357 | 1.8878 | 1.8459 | 1.6184 | 1.4378 | 1.3 | 1.1959 | 1.0939 | 0.62041 | 0.33878 | 0.18061 | 0.17857 | 0.18163 | 2.4296 | 2.4163 | 2.3908 | 2.2347 | 2.1082 | 2.0286 | 1.9694 | 1.9235 | 1.5939 | 1.5102 | 1.502 | -0.010204 | -0.016327 | 2.2255 | 2.1918 | 2.1429 | 1.9806 | 1.8571 | 1.7541 | 1.6745 | 1.5735 | 1.1112 | 0.90816 | 0.8102
|  | LAIRG | EE |  |  |  |  | -0.30102 | -0.3051 | 1.9357 | 1.8949 | 1.8571 | 1.7571 | 1.6969 | 1.4643 | 1.2816 | 1.1602 | 0.62041 | 0.33878 | 0.18061 | 0.17857 | 0.18265 | 2.4296 | 2.4173 | 2.3918 | 2.3633 | 2.3184 | 2.1745 | 2.05 | 1.9551 | 1.5939 | 1.5102 | 1.502 | -0.010204 | -0.016327 | 2.2255 | 2.1969 | 2.149 | 2.102 | 2.0429 | 1.8796 | 1.7378 | 1.6204 | 1.1112 | 0.90816 | 0.8102
|  | LAIRG | HT |  |  |  |  | -0.30102 | -0.30714 | 1.9367 | 1.8949 | 1.8571 | 1.6184 | 1.4378 | 1.3 | 1.1959 | 1.1153 | 0.85204 | 0.58673 | 0.34694 | 0.17857 | 0.18163 | 2.4296 | 2.4173 | 2.3918 | 2.2347 | 2.1082 | 2.0286 | 1.9694 | 1.9235 | 1.8061 | 1.802 | 1.8296 | -0.010204 | -0.016327 | 2.2255 | 2.1969 | 2.151 | 1.9806 | 1.8571 | 1.7541 | 1.6745 | 1.5837 | 1.3633 | 1.2184 | 1.0776
|  | LAIRG | HE |  |  |  |  | -0.29184 | -0.30714 | 1.9367 | 1.8878 | 1.8459 | 1.752 | 1.6724 | 1.4153 | 1.2204 | 1.0939 | 0.82143 | 0.58265 | 0.43163 | 0.18673 | 0.18163 | 2.4296 | 2.4163 | 2.3908 | 2.3622 | 2.3173 | 2.1531 | 2.0224 | 1.9286 | 1.8184 | 1.798 | 1.7622 | -0.0020408 | -0.016327 | 2.2255 | 2.1918 | 2.1429 | 2.1 | 2.0306 | 1.8449 | 1.6959 | 1.5735 | 1.351 | 1.201 | 1.0969
|  | LAIRG | FB |  |  |  |  | -0.26735 | -0.26122 | 1.9929 | 1.9847 | 1.9714 | 1.9541 | 1.9296 | 1.9122 | 1.752 | 1.6673 | 1.3041 | 1.1653 | 1.1224 | 0.20306 | 0.20816 | 2.4602 | 2.4592 | 2.4592 | 2.448 | 2.4235 | 2.4102 | 2.2786 | 2.1867 | 1.9408 | 1.8082 | 1.7173 | 0.020408 | 0.023469 | 2.2745 | 2.2684 | 2.2612 | 2.2459 | 2.2194 | 2.2041 | 2.0888 | 1.998 | 1.7112 | 1.5602 | 1.5429
| MYBSTER 1 | LATHERON | MINIMUM HEADROOM | ND 19924 33627 | YES | NO | 0.068 | 1.1796 | 1.1776 | 1.1837 | 1.1429 | 1.0857 | 0.89286 | 0.72245 | 0.58367 | 0.45918 | 0.32551 | -0.036735 | -0.4551 | -0.77143 | 1.7765 | 1.7765 | 1.7837 | 1.7684 | 1.7571 | 1.6224 | 1.5398 | 1.45 | 1.402 | 1.3612 | 1.2449 | 1.2122 | 1.0806 | 1.4622 | 1.4531 | 1.4541 | 1.4051 | 1.3602 | 1.2235 | 1.1092 | 0.98469 | 0.90204 | 0.8 | 0.57245 | 0.35408 | 0.18469
|  | LATHERON | EE |  |  |  |  | 1.1796 | 1.1776 | 1.1837 | 1.148 | 1.0959 | 0.97959 | 0.87755 | 0.67959 | 0.50816 | 0.37143 | -0.036735 | -0.4551 | -0.77041 | 1.7765 | 1.7765 | 1.7837 | 1.7694 | 1.7571 | 1.7153 | 1.6878 | 1.5469 | 1.4551 | 1.3796 | 1.2633 | 1.2633 | 1.2296 | 1.4622 | 1.4531 | 1.4551 | 1.4102 | 1.3684 | 1.3 | 1.2296 | 1.0592 | 0.94286 | 0.82959 | 0.57245 | 0.35408 | 0.2
|  | LATHERON | HT |  |  |  |  | 1.1796 | 1.1776 | 1.1837 | 1.1459 | 1.0959 | 0.89286 | 0.72245 | 0.58367 | 0.45918 | 0.36939 | 0.11224 | -0.35 | -0.77143 | 1.7765 | 1.7765 | 1.7837 | 1.7684 | 1.7571 | 1.6224 | 1.5398 | 1.45 | 1.402 | 1.3663 | 1.2449 | 1.251 | 1.2663 | 1.4622 | 1.4531 | 1.4541 | 1.4071 | 1.3684 | 1.2235 | 1.1092 | 0.98469 | 0.90204 | 0.82551 | 0.63061 | 0.40612 | 0.20714
|  | LATHERON | HE |  |  |  |  | 1.1796 | 1.1776 | 1.1847 | 1.1429 | 1.0857 | 0.97245 | 0.86633 | 0.65306 | 0.47551 | 0.32551 | 0.083673 | -0.38776 | -0.69694 | 1.7765 | 1.7765 | 1.7847 | 1.7684 | 1.7582 | 1.7153 | 1.6847 | 1.5327 | 1.4367 | 1.3612 | 1.2633 | 1.25 | 1.1918 | 1.4622 | 1.4531 | 1.4551 | 1.4051 | 1.3602 | 1.2959 | 1.2204 | 1.0398 | 0.91837 | 0.8 | 0.62449 | 0.36531 | 0.18469
|  | LATHERON | FB |  |  |  |  | 1.2184 | 1.2408 | 1.2531 | 1.2592 | 1.2531 | 1.2153 | 1.2112 | 1.1724 | 1.0786 | 1.0112 | 0.72857 | 0.50918 | 0.42755 | 1.8041 | 1.8194 | 1.8235 | 1.8306 | 1.8296 | 1.8082 | 1.7959 | 1.7724 | 1.6694 | 1.6133 | 1.4122 | 1.2122 | 1.0806 | 1.5031 | 1.5143 | 1.5184 | 1.5204 | 1.5143 | 1.4827 | 1.4673 | 1.4316 | 1.3347 | 1.2837 | 1.0622 | 0.85 | 0.81531
| FIDDES | LAURENCEKIRK | MINIMUM HEADROOM | NO 70915 71028 | NO | NO | 2.738 | 7.6182 | 7.4172 | 7.1468 | 6.7346 | 6.2315 | 5.2386 | 4.2876 | 3.7458 | 3.1611 | 2.7774 | 0.22844 | -0.76441 | -1.4318 | 8.7325 | 8.5958 | 8.4672 | 8.254 | 7.7009 | 7.0417 | 6.3774 | 6.1703 | 5.9458 | 5.6948 | 3.9591 | 3.8305 | 3.6672 | 8.1136 | 7.9239 | 7.732 | 7.3922 | 6.9351 | 6.1147 | 5.3065 | 4.8759 | 4.4045 | 4.0902 | 1.9085 | 1.2259 | 0.76773
|  | LAURENCEKIRK | EE |  |  |  |  | 7.6356 | 7.4468 | 7.2142 | 6.8009 | 6.3182 | 5.3193 | 4.3886 | 3.8142 | 3.2968 | 2.9325 | 0.22844 | -0.76441 | -1.4318 | 8.756 | 8.6101 | 8.4886 | 8.2795 | 7.7254 | 7.055 | 6.3927 | 6.1703 | 5.9825 | 5.7284 | 4.0346 | 3.8305 | 3.6672 | 8.1269 | 7.9575 | 7.7779 | 7.4392 | 6.9943 | 6.1708 | 5.3769 | 4.9106 | 4.5096 | 4.1912 | 1.9085 | 1.2259 | 0.76773
|  | LAURENCEKIRK | HT |  |  |  |  | 7.6254 | 7.4172 | 7.1468 | 6.7346 | 6.2315 | 5.7499 | 5.1274 | 4.5376 | 3.6244 | 2.7774 | 0.28967 | -0.70421 | -1.3654 | 8.7407 | 8.5958 | 8.4672 | 8.254 | 7.7009 | 7.5274 | 7.2305 | 6.9284 | 6.3693 | 5.6948 | 3.9591 | 3.8376 | 3.8978 | 8.1188 | 7.9239 | 7.732 | 7.3922 | 6.9351 | 6.5657 | 6.0657 | 5.6116 | 4.8545 | 4.0902 | 1.9157 | 1.2463 | 0.87283
|  | LAURENCEKIRK | HE |  |  |  |  | 7.6182 | 7.4438 | 7.205 | 6.7723 | 6.2764 | 5.2386 | 4.2876 | 3.7458 | 3.1611 | 2.8305 | 0.83865 | -0.35115 | -0.98788 | 8.7325 | 8.607 | 8.4846 | 8.2723 | 7.7193 | 7.0417 | 6.3774 | 6.1754 | 5.9458 | 5.7244 | 4.2591 | 4.1091 | 3.954 | 8.1136 | 7.9545 | 7.7688 | 7.4177 | 6.9657 | 6.1147 | 5.3065 | 4.8759 | 4.4045 | 4.1249 | 2.3677 | 1.6075 | 1.1881
|  | LAURENCEKIRK | FB |  |  |  |  | 7.7795 | 7.6846 | 7.5815 | 7.2019 | 6.9284 | 6.3978 | 5.6529 | 5.0162 | 4.9131 | 4.8162 | 3.9805 | 2.6142 | 1.9978 | 8.858 | 8.7672 | 8.6682 | 8.4427 | 8.2009 | 7.7244 | 7.0999 | 6.4529 | 6.3907 | 6.3182 | 5.6938 | 4.8397 | 4.3478 | 8.2626 | 8.1698 | 8.0657 | 7.7463 | 7.4892 | 7.0351 | 6.3902 | 5.8218 | 5.7575 | 5.6636 | 4.9269 | 3.6555 | 3.3177
| STORNOWAY | LAXAY | MINIMUM HEADROOM | NB 33424 21925 | YES | YES | 0.071 | -0.68265 | -0.69796 | 6.4757 | 6.438 | 6.3839 | 6.2502 | 6.1308 | 5.99 | 5.8767 | 5.7788 | 5.5165 | 5.2237 | 5.0114 | -0.11429 | -0.11837 | 7.0665 | 7.0522 | 7.04 | 6.99 | 6.9502 | 6.8859 | 6.8512 | 6.7971 | 6.6686 | 6.6451 | 6.5318 | -0.31327 | -0.32959 | 6.8431 | 6.7982 | 6.7522 | 6.6778 | 6.5961 | 6.489 | 6.4094 | 6.3267 | 6.1186 | 5.9247 | 5.7778
|  | LAXAY | EE |  |  |  |  | -0.67959 | -0.69694 | 6.4757 | 6.442 | 6.3941 | 6.2522 | 6.141 | 6.0033 | 5.8859 | 5.7961 | 5.5165 | 5.2237 | 5.0165 | -0.1102 | -0.11633 | 7.0665 | 7.0543 | 7.041 | 6.991 | 6.9533 | 6.888 | 6.8553 | 6.8002 | 6.6849 | 6.6808 | 6.6624 | -0.31224 | -0.32959 | 6.8431 | 6.8012 | 6.7594 | 6.6798 | 6.6033 | 6.4971 | 6.4165 | 6.338 | 6.1186 | 5.9288 | 5.7798
|  | LAXAY | HT |  |  |  |  | -0.68265 | -0.69796 | 6.4798 | 6.4431 | 6.3961 | 6.2676 | 6.1543 | 6.0186 | 5.9073 | 5.8216 | 5.6257 | 5.3063 | 5.0114 | -0.11429 | -0.11837 | 7.0665 | 7.0522 | 7.04 | 6.991 | 6.9533 | 6.889 | 6.8553 | 6.8033 | 6.6686 | 6.6512 | 6.6788 | -0.31327 | -0.32959 | 6.8431 | 6.8012 | 6.7604 | 6.689 | 6.6094 | 6.5063 | 6.4298 | 6.3522 | 6.1757 | 5.9727 | 5.7778
|  | LAXAY | HE |  |  |  |  | -0.68163 | -0.69592 | 6.4788 | 6.438 | 6.3839 | 6.2502 | 6.1308 | 5.99 | 5.8767 | 5.7788 | 5.6012 | 5.2308 | 5.0216 | -0.11122 | -0.11633 | 7.0676 | 7.0533 | 7.04 | 6.99 | 6.9502 | 6.8859 | 6.8512 | 6.7971 | 6.69 | 6.6451 | 6.6206 | -0.31327 | -0.32959 | 6.8451 | 6.7982 | 6.7522 | 6.6778 | 6.5961 | 6.489 | 6.4094 | 6.3267 | 6.1706 | 5.9247 | 5.79
|  | LAXAY | FB |  |  |  |  | -0.63673 | -0.62143 | 6.5869 | 6.5757 | 6.5757 | 6.5584 | 6.5471 | 6.5155 | 6.5114 | 6.5012 | 6.3267 | 6.1165 | 6.0543 | -0.077551 | -0.072449 | 7.1298 | 7.1206 | 7.1216 | 7.1053 | 7.092 | 7.0645 | 7.0298 | 7.0206 | 6.8767 | 6.6584 | 6.5318 | -0.27449 | -0.26837 | 6.9329 | 6.9196 | 6.9165 | 6.8992 | 6.8869 | 6.8543 | 6.8196 | 6.8084 | 6.6686 | 6.4573 | 6.4267
| COUPAR ANGUS | LEOCH | MINIMUM HEADROOM | NO 35945 36287 | YES | NO | 0.516 | -2.1469 | -2.1949 | -2.2347 | -2.2878 | -2.3531 | -2.5459 | -2.7439 | -2.9398 | -3.098 | -3.2724 | -3.9939 | -4.6143 | -5.0622 | -1.1163 | -1.151 | -1.1796 | -1.1949 | -1.2255 | -1.3143 | -1.4143 | -1.4949 | -1.498 | -1.5847 | -1.9745 | -2.0296 | -2.1388 | -1.6673 | -1.7194 | -1.7755 | -1.8224 | -1.8531 | -2.0082 | -2.1663 | -2.3204 | -2.3663 | -2.5092 | -3.1714 | -3.4918 | -3.7582
|  | LEOCH | EE |  |  |  |  | -2.1469 | -2.1949 | -2.2347 | -2.2878 | -2.3469 | -2.5388 | -2.7439 | -2.9398 | -3.098 | -3.2724 | -3.9939 | -4.6143 | -5.0622 | -1.1163 | -1.15 | -1.1796 | -1.1949 | -1.2255 | -1.3143 | -1.4143 | -1.4949 | -1.498 | -1.5837 | -1.9745 | -2.0296 | -2.1388 | -1.6673 | -1.7194 | -1.7755 | -1.8224 | -1.85 | -2.0051 | -2.1663 | -2.3204 | -2.3663 | -2.5092 | -3.1714 | -3.4918 | -3.7582
|  | LEOCH | HT |  |  |  |  | -2.1469 | -2.1918 | -2.2286 | -2.2724 | -2.3306 | -2.5102 | -2.702 | -2.8878 | -3.0398 | -3.2122 | -3.8357 | -4.4888 | -4.9765 | -1.1163 | -1.151 | -1.1796 | -1.1949 | -1.2235 | -1.3092 | -1.4082 | -1.4908 | -1.4918 | -1.5847 | -1.8622 | -1.8908 | -1.8643 | -1.6673 | -1.7184 | -1.7724 | -1.8133 | -1.8439 | -1.9918 | -2.1459 | -2.2939 | -2.3357 | -2.4796 | -2.9786 | -3.3102 | -3.5276
|  | LEOCH | HE |  |  |  |  | -2.1469 | -2.1939 | -2.2316 | -2.2867 | -2.3531 | -2.5459 | -2.7388 | -2.9316 | -3.0827 | -3.2582 | -3.7847 | -4.4041 | -4.7612 | -1.1163 | -1.151 | -1.1786 | -1.1949 | -1.2245 | -1.3133 | -1.4143 | -1.4949 | -1.4949 | -1.5816 | -1.8163 | -1.9092 | -2.002 | -1.6673 | -1.7184 | -1.7724 | -1.8214 | -1.8531 | -2.0082 | -2.1643 | -2.3153 | -2.3582 | -2.502 | -2.9337 | -3.2735 | -3.4673
|  | LEOCH | FB |  |  |  |  | -2.0929 | -2.0949 | -2.1143 | -2.1265 | -2.1571 | -2.1633 | -2.1878 | -2.2255 | -2.2653 | -2.3153 | -2.548 | -2.8857 | -3.0265 | -1.0653 | -1.0724 | -1.0878 | -1.0867 | -1.1031 | -1.1388 | -1.1888 | -1.2276 | -1.2765 | -1.3449 | -1.501 | -1.8765 | -2.1235 | -1.601 | -1.6112 | -1.6347 | -1.6357 | -1.6582 | -1.699 | -1.749 | -1.7898 | -1.8204 | -1.8847 | -2.0531 | -2.452 | -2.5245
| NAIRN | LETHEN | MINIMUM HEADROOM | NH 92307 50795 | YES | YES | 0.255 | 2.9873 | 2.9853 | 2.9761 | 2.9343 | 2.869 | 2.8118 | 2.7241 | 2.6659 | 2.5812 | 2.5118 | 2.2914 | 2.0771 | 1.9159 | 3.212 | 3.2131 | 3.2039 | 3.1784 | 3.1539 | 3.1151 | 3.0773 | 3.0457 | 2.9988 | 2.9641 | 2.7794 | 2.8049 | 2.7998 | 3.1461 | 3.1471 | 3.1329 | 3.0931 | 3.0533 | 2.9778 | 2.9186 | 2.8645 | 2.7849 | 2.7278 | 2.5492 | 2.439 | 2.339
|  | LETHEN | EE |  |  |  |  | 2.9884 | 2.9853 | 2.9761 | 2.9343 | 2.8873 | 2.8118 | 2.7424 | 2.6904 | 2.6108 | 2.5435 | 2.2914 | 2.0771 | 1.922 | 3.2131 | 3.2131 | 3.2039 | 3.1784 | 3.1559 | 3.1151 | 3.0794 | 3.0508 | 3.0008 | 2.9692 | 2.8182 | 2.8376 | 2.8467 | 3.1461 | 3.1471 | 3.1329 | 3.0931 | 3.0655 | 2.9778 | 2.9186 | 2.8798 | 2.8043 | 2.7512 | 2.5492 | 2.4431 | 2.3778
|  | LETHEN | HT |  |  |  |  | 2.9873 | 2.9863 | 2.9782 | 2.9353 | 2.8904 | 2.8486 | 2.7598 | 2.7088 | 2.6312 | 2.569 | 2.3731 | 2.1343 | 1.9159 | 3.212 | 3.2131 | 3.2049 | 3.1784 | 3.1559 | 3.1324 | 3.0794 | 3.0549 | 3.0029 | 2.9743 | 2.7794 | 2.8049 | 2.8682 | 3.1461 | 3.1471 | 3.1349 | 3.0941 | 3.0676 | 3.0176 | 2.9298 | 2.89 | 2.8155 | 2.7645 | 2.5798 | 2.4614 | 2.3737
|  | LETHEN | HE |  |  |  |  | 2.9873 | 2.9873 | 2.9771 | 2.9353 | 2.869 | 2.8159 | 2.7241 | 2.6659 | 2.5812 | 2.5118 | 2.3506 | 2.1149 | 1.9598 | 3.212 | 3.2131 | 3.2039 | 3.1896 | 3.1539 | 3.1294 | 3.0773 | 3.0457 | 2.9988 | 2.9641 | 2.8222 | 2.8335 | 2.7998 | 3.1461 | 3.1471 | 3.1329 | 3.1022 | 3.0533 | 2.9961 | 2.9329 | 2.8645 | 2.7849 | 2.7278 | 2.5767 | 2.439 | 2.339
|  | LETHEN | FB |  |  |  |  | 3.0261 | 3.0373 | 3.0424 | 3.0404 | 3.0241 | 2.9965 | 2.9792 | 2.9516 | 2.9251 | 2.9078 | 2.7945 | 2.6465 | 2.6016 | 3.2427 | 3.2518 | 3.2508 | 3.2498 | 3.2427 | 3.2233 | 3.211 | 3.1876 | 3.1631 | 3.1508 | 3.0406 | 2.8876 | 2.7998 | 3.1737 | 3.1808 | 3.1839 | 3.1818 | 3.1737 | 3.1553 | 3.1441 | 3.1196 | 3.0941 | 3.0808 | 2.9308 | 2.7849 | 2.7696
| GRUDIE BRIDGE | LETTEREWE | MINIMUM HEADROOM | NG 93546 70082 | YES | NO | 0 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942
|  | LETTEREWE | EE |  |  |  |  | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942
|  | LETTEREWE | HT |  |  |  |  | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942
|  | LETTEREWE | HE |  |  |  |  | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942
|  | LETTEREWE | FB |  |  |  |  | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942
| ELGIN | LHANBRYDE | MINIMUM HEADROOM | NJ 27940 61640 | NO | YES | 0.364 | 4.8602 | 4.7959 | 4.7306 | 4.6959 | 4.6531 | 4.5592 | 4.4316 | 4.3082 | 4.1735 | 4.0827 | 3.6622 | 3.3622 | 3.102 | 5.4286 | 5.398 | 5.3704 | 5.3602 | 5.3347 | 5.3041 | 5.2408 | 5.1816 | 5.1194 | 5.0724 | 4.9031 | 4.8796 | 4.6837 | 5.2378 | 5.1694 | 5.1102 | 5.0959 | 5.05 | 4.9786 | 4.8673 | 4.7663 | 4.65 | 4.5704 | 4.2286 | 4.0633 | 3.8969
|  | LHANBRYDE | EE |  |  |  |  | 4.8643 | 4.8 | 4.7551 | 4.7163 | 4.6755 | 4.5827 | 4.4459 | 4.3173 | 4.1827 | 4.0888 | 3.6622 | 3.3622 | 3.102 | 5.4306 | 5.4 | 5.3827 | 5.3694 | 5.3449 | 5.3133 | 5.2469 | 5.1929 | 5.1245 | 5.0745 | 4.9031 | 4.9327 | 4.8643 | 5.2418 | 5.1724 | 5.1255 | 5.1122 | 5.0653 | 4.9939 | 4.8786 | 4.7724 | 4.6571 | 4.5776 | 4.2286 | 4.0633 | 3.8969
|  | LHANBRYDE | HT |  |  |  |  | 4.8602 | 4.7959 | 4.7306 | 4.6959 | 4.6531 | 4.5592 | 4.4408 | 4.3316 | 4.2133 | 4.1204 | 3.8296 | 3.4439 | 3.1388 | 5.4286 | 5.398 | 5.3704 | 5.3602 | 5.3347 | 5.3041 | 5.2408 | 5.1827 | 5.1245 | 5.0776 | 4.9959 | 4.9663 | 4.9449 | 5.2378 | 5.1694 | 5.1102 | 5.0959 | 5.05 | 4.9786 | 4.8714 | 4.7806 | 4.6755 | 4.5949 | 4.3765 | 4.1214 | 3.9265
|  | LHANBRYDE | HE |  |  |  |  | 4.8612 | 4.7969 | 4.7449 | 4.7071 | 4.6673 | 4.5704 | 4.4316 | 4.3082 | 4.1735 | 4.0827 | 3.752 | 3.4684 | 3.2592 | 5.4296 | 5.399 | 5.3776 | 5.3643 | 5.3378 | 5.3082 | 5.2408 | 5.1816 | 5.1194 | 5.0724 | 4.9204 | 4.952 | 4.8714 | 5.2388 | 5.1694 | 5.1204 | 5.1051 | 5.0592 | 4.9857 | 4.8673 | 4.7663 | 4.65 | 4.5704 | 4.2888 | 4.1367 | 3.9949
|  | LHANBRYDE | FB |  |  |  |  | 4.9133 | 4.8735 | 4.8582 | 4.8714 | 4.8571 | 4.8408 | 4.8082 | 4.7806 | 4.7245 | 4.6878 | 4.4592 | 4.2378 | 4.1153 | 5.4571 | 5.4408 | 5.4357 | 5.4367 | 5.4214 | 5.4051 | 5.3694 | 5.349 | 5.301 | 5.2612 | 5.0735 | 4.8796 | 4.6837 | 5.2806 | 5.25 | 5.2296 | 5.2214 | 5.2041 | 5.1816 | 5.1449 | 5.1163 | 5.0806 | 5.0378 | 4.8224 | 4.5959 | 4.5347
| FORT WILLIAM | LIDDESDALE | MINIMUM HEADROOM | NM 78116 59480 | YES | NO | 0 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10167 | 0.099633 | 0.095551 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.094714 | 0.093694 | 0.088592 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.099214 | 0.093092 | 0.093092
|  | LIDDESDALE | EE |  |  |  |  | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10167 | 0.099633 | 0.10167 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.095735 | 0.093694 | 0.095735 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10023 | 0.098194 | 0.10023
|  | LIDDESDALE | HT |  |  |  |  | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10167 | 0.099633 | 0.099633 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.094714 | 0.093694 | 0.093694 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.099214 | 0.098194 | 0.097173
|  | LIDDESDALE | HE |  |  |  |  | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10167 | 0.099633 | 0.10065 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.095735 | 0.093694 | 0.094714 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10023 | 0.098194 | 0.098194
|  | LIDDESDALE | FB |  |  |  |  | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.095551 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.088592 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.10636 | 0.093092 | 0.093092
| KEITH 1 | LIMEHILLOCKS | MINIMUM HEADROOM | NJ 52093 50703 | YES | YES | 0.101 | -0.37143 | -0.36633 | -0.36735 | -0.38163 | -0.39082 | -0.43878 | -0.48469 | -0.55 | -0.59082 | -0.62041 | -1.0163 | -1.0398 | -1.0296 | 0.30204 | 0.29388 | 0.28163 | 0.26327 | 0.24694 | 0.20102 | 0.16429 | 0.10204 | 0.072449 | 0.020408 | -0.38673 | -0.38163 | -0.37449 | 0.070408 | 0.068367 | 0.065306 | 0.044898 | 0.031633 | -0.018367 | -0.065306 | -0.13571 | -0.17449 | -0.22959 | -0.62653 | -0.62653 | -0.61837
|  | LIMEHILLOCKS | EE |  |  |  |  | -0.36429 | -0.36633 | -0.36429 | -0.37653 | -0.38469 | -0.42959 | -0.47041 | -0.53776 | -0.56939 | -0.59694 | -1.0163 | -1.0398 | -1.0296 | 0.31122 | 0.29388 | 0.28265 | 0.26531 | 0.25204 | 0.20612 | 0.17143 | 0.10714 | 0.077551 | 0.02551 | -0.38673 | -0.38163 | -0.37449 | 0.082653 | 0.068367 | 0.066327 | 0.04898 | 0.035714 | -0.012245 | -0.053061 | -0.12551 | -0.16122 | -0.21429 | -0.62653 | -0.62653 | -0.61837
|  | LIMEHILLOCKS | HT |  |  |  |  | -0.36429 | -0.36633 | -0.36735 | -0.38163 | -0.39082 | -0.43673 | -0.48061 | -0.54184 | -0.56837 | -0.61939 | -0.74592 | -0.77857 | -0.80408 | 0.31122 | 0.29388 | 0.28163 | 0.26327 | 0.24694 | 0.20102 | 0.16429 | 0.10204 | 0.073469 | 0.020408 | -0.11429 | -0.1 | -0.059184 | 0.081633 | 0.068367 | 0.065306 | 0.044898 | 0.031633 | -0.017347 | -0.061224 | -0.13061 | -0.16224 | -0.21837 | -0.36224 | -0.36939 | -0.37041
|  | LIMEHILLOCKS | HE |  |  |  |  | -0.37143 | -0.36429 | -0.36429 | -0.37857 | -0.39082 | -0.43878 | -0.48469 | -0.55 | -0.59082 | -0.62041 | -0.71939 | -0.78571 | -0.84286 | 0.30204 | 0.29592 | 0.28265 | 0.26531 | 0.25 | 0.20408 | 0.16633 | 0.1051 | 0.072449 | 0.020408 | -0.089796 | -0.1 | -0.12449 | 0.070408 | 0.071429 | 0.066327 | 0.046939 | 0.031633 | -0.018367 | -0.065306 | -0.13571 | -0.17449 | -0.22959 | -0.35102 | -0.37143 | -0.40612
|  | LIMEHILLOCKS | FB |  |  |  |  | -0.33265 | -0.32347 | -0.31939 | -0.30714 | -0.30408 | -0.32245 | -0.33265 | -0.35918 | -0.39082 | -0.39796 | -0.51327 | -0.65204 | -0.7 | 0.33469 | 0.33061 | 0.31837 | 0.31939 | 0.31224 | 0.28367 | 0.26429 | 0.22449 | 0.18673 | 0.17755 | 0.032653 | -0.13673 | -0.22959 | 0.11531 | 0.11429 | 0.11429 | 0.11837 | 0.11735 | 0.093878 | 0.080612 | 0.046939 | 0.011224 | 0.0020408 | -0.13061 | -0.2898 | -0.30306
| ARDMORE | LOCH CARNAN | MINIMUM HEADROOM | NF 83230 42735 | NO | YES | 0.034 | 6.5115 | 6.5023 | 6.4982 | 6.4819 | 6.4676 | 6.4502 | 6.436 | 6.4125 | 6.3972 | 6.3768 | 6.337 | 6.3298 | 6.3166 | 6.1007 | 6.0986 | 6.1017 | 6.0976 | 6.0966 | 6.0915 | 6.0874 | 6.0792 | 6.0751 | 6.069 | 6.0558 | 6.0547 | 6.0558 | 6.5453 | 6.5351 | 6.5321 | 6.5178 | 6.5045 | 6.4892 | 6.476 | 6.4545 | 6.4402 | 6.4219 | 6.3851 | 6.3698 | 6.3627
|  | LOCH CARNAN | EE |  |  |  |  | 6.5115 | 6.5023 | 6.4982 | 6.4839 | 6.4686 | 6.4502 | 6.436 | 6.4125 | 6.3982 | 6.3788 | 6.337 | 6.3298 | 6.3207 | 6.1007 | 6.0986 | 6.1017 | 6.0996 | 6.0966 | 6.0915 | 6.0884 | 6.0792 | 6.0751 | 6.069 | 6.0578 | 6.0568 | 6.0588 | 6.5453 | 6.5351 | 6.5321 | 6.5188 | 6.5056 | 6.4892 | 6.477 | 6.4545 | 6.4423 | 6.4229 | 6.3862 | 6.3719 | 6.3688
|  | LOCH CARNAN | HT |  |  |  |  | 6.5115 | 6.5043 | 6.4982 | 6.4849 | 6.4686 | 6.4513 | 6.438 | 6.4145 | 6.4002 | 6.3809 | 6.3421 | 6.3298 | 6.3166 | 6.1007 | 6.1007 | 6.1017 | 6.0996 | 6.0966 | 6.0915 | 6.0884 | 6.0792 | 6.0762 | 6.069 | 6.0558 | 6.0547 | 6.0568 | 6.5464 | 6.5382 | 6.5331 | 6.5188 | 6.5045 | 6.4892 | 6.478 | 6.4556 | 6.4433 | 6.4239 | 6.3851 | 6.3698 | 6.3637
|  | LOCH CARNAN | HE |  |  |  |  | 6.5115 | 6.5043 | 6.4982 | 6.4819 | 6.4676 | 6.4502 | 6.436 | 6.4125 | 6.3972 | 6.3768 | 6.3462 | 6.3319 | 6.3176 | 6.1007 | 6.1007 | 6.1017 | 6.0976 | 6.0966 | 6.0915 | 6.0874 | 6.0792 | 6.0751 | 6.069 | 6.0588 | 6.0558 | 6.0558 | 6.5464 | 6.5372 | 6.5331 | 6.5178 | 6.5045 | 6.4892 | 6.476 | 6.4545 | 6.4402 | 6.4219 | 6.3913 | 6.3719 | 6.3627
|  | LOCH CARNAN | FB |  |  |  |  | 6.5227 | 6.5196 | 6.5176 | 6.5084 | 6.5023 | 6.4992 | 6.49 | 6.487 | 6.4737 | 6.4645 | 6.4288 | 6.388 | 6.3717 | 6.1098 | 6.1088 | 6.1119 | 6.1088 | 6.1078 | 6.1078 | 6.1047 | 6.1027 | 6.0996 | 6.0966 | 6.0853 | 6.066 | 6.0578 | 6.5566 | 6.5545 | 6.5504 | 6.5433 | 6.5351 | 6.5311 | 6.5219 | 6.5188 | 6.5056 | 6.4964 | 6.4596 | 6.4127 | 6.4056
| GRUDIE BRIDGE | LOCH GLASCARNOCH | MINIMUM HEADROOM | NH 31620 71996 | YES | NO | 0.023 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546
|  | LOCH GLASCARNOCH | EE |  |  |  |  | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546
|  | LOCH GLASCARNOCH | HT |  |  |  |  | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546
|  | LOCH GLASCARNOCH | HE |  |  |  |  | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546
|  | LOCH GLASCARNOCH | FB |  |  |  |  | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.58796 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.54398 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546 | 0.56546
| FORT WILLIAM | LOCHALINE | MINIMUM HEADROOM | NM 67939 45444 | YES | NO | 0.74 | -0.5058 | -0.50376 | -0.50682 | -0.51804 | -0.53641 | -0.5609 | -0.58335 | -0.60682 | -0.62416 | -0.63845 | -0.70682 | -0.73641 | -0.75273 | -0.62518 | -0.62212 | -0.62416 | -0.62824 | -0.63539 | -0.64151 | -0.65478 | -0.66192 | -0.67824 | -0.68641 | -0.73437 | -0.73641 | -0.74253 | -0.53845 | -0.53743 | -0.53845 | -0.54865 | -0.56192 | -0.58233 | -0.60069 | -0.61702 | -0.63437 | -0.64763 | -0.68437 | -0.69661 | -0.71804
|  | LOCHALINE | EE |  |  |  |  | -0.5058 | -0.50376 | -0.5058 | -0.51804 | -0.53641 | -0.55886 | -0.58029 | -0.59763 | -0.62416 | -0.62927 | -0.70478 | -0.73029 | -0.74457 | -0.62518 | -0.62212 | -0.62416 | -0.62824 | -0.63539 | -0.64049 | -0.65478 | -0.6609 | -0.67824 | -0.68437 | -0.72722 | -0.73131 | -0.72824 | -0.53845 | -0.53743 | -0.53845 | -0.54865 | -0.5609 | -0.58233 | -0.59661 | -0.60988 | -0.62518 | -0.63437 | -0.68437 | -0.69661 | -0.71192
|  | LOCHALINE | HT |  |  |  |  | -0.5058 | -0.50273 | -0.50682 | -0.51804 | -0.53539 | -0.55376 | -0.57722 | -0.59457 | -0.62314 | -0.62824 | -0.70682 | -0.73641 | -0.75171 | -0.62518 | -0.62212 | -0.62416 | -0.62824 | -0.63539 | -0.64151 | -0.65478 | -0.6609 | -0.67824 | -0.68539 | -0.73437 | -0.73641 | -0.73335 | -0.53743 | -0.53641 | -0.53743 | -0.54865 | -0.5609 | -0.5762 | -0.59253 | -0.6058 | -0.62314 | -0.63131 | -0.67722 | -0.69253 | -0.716
|  | LOCHALINE | HE |  |  |  |  | -0.5058 | -0.50171 | -0.50682 | -0.51804 | -0.53641 | -0.5609 | -0.58335 | -0.60682 | -0.6211 | -0.63845 | -0.70171 | -0.73233 | -0.75273 | -0.62518 | -0.62212 | -0.62416 | -0.62824 | -0.63539 | -0.64151 | -0.65478 | -0.66192 | -0.67824 | -0.68641 | -0.72722 | -0.73539 | -0.74253 | -0.53743 | -0.53539 | -0.53743 | -0.54865 | -0.56192 | -0.58233 | -0.60069 | -0.61702 | -0.63437 | -0.64763 | -0.68233 | -0.69661 | -0.71804
|  | LOCHALINE | FB |  |  |  |  | -0.48947 | -0.48845 | -0.48743 | -0.48845 | -0.48845 | -0.49355 | -0.50784 | -0.50988 | -0.51702 | -0.53437 | -0.57722 | -0.64661 | -0.66804 | -0.61498 | -0.616 | -0.616 | -0.61498 | -0.616 | -0.61804 | -0.62416 | -0.62416 | -0.62722 | -0.63743 | -0.66192 | -0.71396 | -0.73947 | -0.52518 | -0.5262 | -0.5262 | -0.5262 | -0.52722 | -0.53029 | -0.53641 | -0.53845 | -0.53947 | -0.54763 | -0.57212 | -0.6262 | -0.63641
| GRUDIE BRIDGE | LOCHCARRON | MINIMUM HEADROOM | NG 91944 41839 | YES | NO | 0.037 | 1.8612 | 1.8561 | 1.8551 | 1.8286 | 1.7969 | 1.3531 | 0.75408 | 0.022449 | -0.70612 | -1.1776 | -2.552 | -2.7337 | -2.849 | 2.0209 | 2.0148 | 2.0097 | 2.0005 | 1.9923 | 1.5679 | 0.9352 | 0.17296 | -0.59337 | -1.0658 | -2.4668 | -2.4556 | -2.4883 | 1.9763 | 1.9681 | 1.964 | 1.9446 | 1.9242 | 1.4783 | 0.89362 | 0.18342 | -0.50842 | -0.9574 | -2.2819 | -2.3645 | -2.4186
|  | LOCHCARRON | EE |  |  |  |  | 1.8612 | 1.8561 | 1.8551 | 1.8306 | 1.8061 | 1.7592 | 1.7173 | 1.2622 | 0.66327 | -0.082653 | -2.1939 | -2.7337 | -2.8357 | 2.0209 | 2.0148 | 2.0097 | 2.0005 | 1.9944 | 1.9709 | 1.9352 | 1.5485 | 0.91888 | 0.13622 | -2.0087 | -2.4515 | -2.4444 | 1.9763 | 1.9702 | 1.964 | 1.9446 | 1.9293 | 1.8773 | 1.8385 | 1.4069 | 0.85893 | 0.13852 | -1.8962 | -2.3645 | -2.4054
|  | LOCHCARRON | HT |  |  |  |  | 1.8612 | 1.8592 | 1.8551 | 1.8337 | 1.8051 | 1.3531 | 0.75408 | 0.022449 | -0.70612 | -1.1776 | -2.552 | -2.7082 | -2.849 | 2.0209 | 2.0158 | 2.0097 | 2.0015 | 1.9934 | 1.5679 | 0.9352 | 0.17296 | -0.59337 | -1.0658 | -2.4668 | -2.4556 | -2.4372 | 1.9763 | 1.9702 | 1.9651 | 1.9477 | 1.9283 | 1.4783 | 0.89362 | 0.18342 | -0.50842 | -0.9574 | -2.2819 | -2.3564 | -2.4186
|  | LOCHCARRON | HE |  |  |  |  | 1.8612 | 1.8571 | 1.8602 | 1.8286 | 1.7969 | 1.7582 | 1.7071 | 1.2041 | 0.53673 | -0.32245 | -2.1541 | -2.7122 | -2.8133 | 2.0209 | 2.0148 | 2.0158 | 2.0005 | 1.9923 | 1.9709 | 1.9342 | 1.4944 | 0.78929 | -0.11071 | -2.0056 | -2.4546 | -2.4617 | 1.9763 | 1.9681 | 1.9691 | 1.9446 | 1.9242 | 1.8783 | 1.8324 | 1.3855 | 0.7375 | -0.097194 | -1.8747 | -2.3513 | -2.3992
|  | LOCHCARRON | FB |  |  |  |  | 1.8898 | 1.8949 | 1.9031 | 1.9071 | 1.9 | 1.8837 | 1.8776 | 1.8684 | 1.5173 | 1.0796 | -1.4133 | -2.3031 | -2.3347 | 2.0434 | 2.0434 | 2.0454 | 2.0444 | 2.0403 | 2.023 | 2.0138 | 2.0026 | 1.6821 | 1.1974 | -1.4903 | -2.4495 | -2.4883 | 2.0038 | 2.0059 | 2.0099 | 2.0099 | 2.0038 | 1.9875 | 1.9804 | 1.9732 | 1.6395 | 1.2089 | -1.2747 | -2.139 | -2.1482
| TAYNUILT | LOCHDONHEAD | MINIMUM HEADROOM | NM 72902 34134 | YES | YES | 0.058 | 0.15816 | 0.090816 | 0.041837 | 0.013265 | -0.12959 | -0.22551 | -0.29694 | -0.47959 | -0.56429 | -0.73061 | -1.0286 | -1.0398 | -1.048 | 0.34592 | 0.27857 | 0.26837 | 0.26327 | 0.12857 | 0.042857 | 0.020408 | -0.11122 | -0.19388 | -0.3602 | -0.67143 | -0.65714 | -0.63265 | 0.20408 | 0.12347 | 0.087755 | 0.067347 | -0.078571 | -0.18265 | -0.2398 | -0.37959 | -0.45816 | -0.62245 | -0.91531 | -0.92041 | -0.91531
|  | LOCHDONHEAD | EE |  |  |  |  | 0.1602 | 0.13265 | 0.041837 | 0.013265 | -0.12959 | -0.19592 | -0.27449 | -0.4 | -0.53571 | -0.57857 | -0.98163 | -0.98878 | -1.048 | 0.34898 | 0.32245 | 0.26837 | 0.26327 | 0.12857 | 0.089796 | 0.065306 | -0.023469 | -0.14388 | -0.18571 | -0.6051 | -0.5898 | -0.63265 | 0.20714 | 0.17653 | 0.087755 | 0.067347 | -0.078571 | -0.1449 | -0.18469 | -0.29898 | -0.42347 | -0.46429 | -0.86633 | -0.86837 | -0.91531
|  | LOCHDONHEAD | HT |  |  |  |  | 0.16122 | 0.090816 | 0.047959 | 0.022449 | -0.11939 | -0.22551 | -0.29694 | -0.47959 | -0.56429 | -0.73061 | -1.0286 | -1.0398 | -0.99388 | 0.34898 | 0.27857 | 0.26939 | 0.26429 | 0.12959 | 0.042857 | 0.020408 | -0.11122 | -0.19388 | -0.3602 | -0.67143 | -0.65714 | -0.57755 | 0.20714 | 0.12347 | 0.091837 | 0.073469 | -0.072449 | -0.18265 | -0.2398 | -0.37959 | -0.45816 | -0.62245 | -0.91531 | -0.92041 | -0.87041
|  | LOCHDONHEAD | HE |  |  |  |  | 0.15816 | 0.13265 | 0.043878 | 0.021429 | -0.12245 | -0.16837 | -0.24694 | -0.31531 | -0.33367 | -0.34694 | -0.61122 | -0.64286 | -0.60918 | 0.34592 | 0.32347 | 0.26837 | 0.26429 | 0.13061 | 0.096939 | 0.067347 | 0.035714 | 0.021429 | 0.0091837 | -0.25 | -0.24796 | -0.14898 | 0.20408 | 0.17755 | 0.087755 | 0.072449 | -0.072449 | -0.12653 | -0.1898 | -0.22245 | -0.23776 | -0.25102 | -0.51122 | -0.52959 | -0.43673
|  | LOCHDONHEAD | FB |  |  |  |  | 0.16837 | 0.16327 | 0.12959 | 0.078571 | 0.082653 | 0.053061 | 0.017347 | -0.005102 | -0.013265 | -0.011224 | -0.15816 | -0.38061 | -0.39898 | 0.35714 | 0.35612 | 0.33163 | 0.28163 | 0.28367 | 0.26939 | 0.25204 | 0.24082 | 0.22857 | 0.22755 | 0.083673 | -0.13367 | -0.15306 | 0.21531 | 0.21429 | 0.17755 | 0.12143 | 0.12143 | 0.096939 | 0.068367 | 0.05 | 0.037755 | 0.038776 | -0.10612 | -0.31224 | -0.32143
| KILLIN | LOCHEARNHEAD | MINIMUM HEADROOM | NN 58766 24177 | YES | YES | 0.073 | -0.23163 | -0.22041 | -0.22449 | -0.23571 | -0.27551 | -0.30918 | -0.37041 | -0.40408 | -0.45918 | -0.51327 | -0.64184 | -0.65102 | -0.64388 | -0.65306 | -0.65714 | -0.67857 | -0.6949 | -0.72755 | -0.75 | -0.8 | -0.82653 | -0.86939 | -0.91429 | -1.0245 | -1.0163 | -0.99184 | -0.10918 | -0.10612 | -0.11633 | -0.12245 | -0.13265 | -0.15918 | -0.2051 | -0.22857 | -0.27449 | -0.31327 | -0.41327 | -0.43673 | -0.45918
|  | LOCHEARNHEAD | EE |  |  |  |  | -0.23163 | -0.21939 | -0.22041 | -0.23469 | -0.27551 | -0.30714 | -0.36735 | -0.40204 | -0.45612 | -0.51122 | -0.6102 | -0.62551 | -0.61327 | -0.65306 | -0.65612 | -0.67653 | -0.69388 | -0.72653 | -0.74898 | -0.79796 | -0.82653 | -0.86735 | -0.91327 | -0.99694 | -0.98673 | -0.96122 | -0.10918 | -0.10612 | -0.11429 | -0.12143 | -0.13163 | -0.15816 | -0.2 | -0.22551 | -0.26735 | -0.30612 | -0.39592 | -0.41224 | -0.38469
|  | LOCHEARNHEAD | HT |  |  |  |  | -0.22857 | -0.22041 | -0.22449 | -0.23367 | -0.27449 | -0.30612 | -0.36633 | -0.39898 | -0.45306 | -0.50918 | -0.64184 | -0.65102 | -0.64388 | -0.65306 | -0.65714 | -0.67857 | -0.6949 | -0.72653 | -0.75 | -0.8 | -0.82653 | -0.86939 | -0.91429 | -1.0245 | -1.0163 | -0.98776 | -0.10612 | -0.10612 | -0.11633 | -0.12143 | -0.13163 | -0.15714 | -0.20204 | -0.22755 | -0.26939 | -0.30918 | -0.41327 | -0.43673 | -0.41531
|  | LOCHEARNHEAD | HE |  |  |  |  | -0.22755 | -0.21837 | -0.22143 | -0.23571 | -0.27551 | -0.30918 | -0.37041 | -0.40408 | -0.45918 | -0.51327 | -0.61837 | -0.62959 | -0.64286 | -0.65204 | -0.65612 | -0.67755 | -0.69388 | -0.72755 | -0.74898 | -0.79898 | -0.82653 | -0.86735 | -0.91224 | -0.99898 | -0.99796 | -0.99184 | -0.1051 | -0.10612 | -0.11327 | -0.12245 | -0.13265 | -0.15918 | -0.2051 | -0.22857 | -0.27449 | -0.31327 | -0.39184 | -0.42857 | -0.45918
|  | LOCHEARNHEAD | FB |  |  |  |  | -0.20408 | -0.18571 | -0.17551 | -0.17041 | -0.17755 | -0.2 | -0.21633 | -0.2449 | -0.25816 | -0.28673 | -0.38571 | -0.49184 | -0.52245 | -0.63265 | -0.63265 | -0.63776 | -0.64592 | -0.65102 | -0.67143 | -0.68571 | -0.71327 | -0.72347 | -0.75 | -0.83469 | -0.92755 | -0.96224 | -0.083673 | -0.07551 | -0.072449 | -0.072449 | -0.067347 | -0.079592 | -0.087755 | -0.10408 | -0.11122 | -0.13163 | -0.21429 | -0.31633 | -0.33571
| LYNDHURST | LOCHEE | MINIMUM HEADROOM | NO 38065 31416 | NO | YES | 0.909 | 16.089 | 15.8869 | 15.8196 | 15.6941 | 15.5839 | 15.2471 | 14.9686 | 14.5482 | 14.4196 | 14.1471 | 12.7053 | 11.438 | 10.7196 | 17.3126 | 17.183 | 17.1453 | 17.0698 | 17.0024 | 16.783 | 16.5289 | 16.1657 | 16.0606 | 15.7953 | 14.7616 | 13.8718 | 12.5708 | 17.009 | 16.9101 | 16.8611 | 16.7631 | 16.6631 | 16.3029 | 16.0182 | 15.5692 | 15.4397 | 15.1529 | 13.7101 | 12.4815 | 11.7825
|  | LOCHEE | EE |  |  |  |  | 16.089 | 15.8869 | 15.8196 | 15.6941 | 15.5839 | 15.2471 | 14.9686 | 14.5482 | 14.4196 | 14.1471 | 12.7053 | 11.438 | 10.7196 | 17.3126 | 17.183 | 17.1453 | 17.0698 | 17.0065 | 16.783 | 16.5636 | 16.1657 | 16.0606 | 15.7953 | 14.8024 | 13.8718 | 13.1096 | 17.009 | 16.9101 | 16.8611 | 16.7723 | 16.6631 | 16.3029 | 16.0233 | 15.5692 | 15.4397 | 15.1529 | 13.7101 | 12.4815 | 11.7825
|  | LOCHEE | HT |  |  |  |  | 16.0931 | 15.8992 | 15.839 | 15.7318 | 15.5931 | 15.2798 | 15.0145 | 14.6033 | 14.4829 | 14.2033 | 12.7553 | 11.638 | 11.2002 | 17.3126 | 17.184 | 17.1453 | 17.0871 | 17.0024 | 16.8034 | 16.582 | 16.1779 | 16.0728 | 15.7983 | 14.7616 | 14.181 | 13.9626 | 17.0182 | 16.9284 | 16.8897 | 16.7948 | 16.6692 | 16.3366 | 16.0621 | 15.6162 | 15.4897 | 15.1999 | 13.7886 | 12.7274 | 12.3274
|  | LOCHEE | HE |  |  |  |  | 16.0931 | 15.8982 | 15.838 | 15.7114 | 15.6033 | 15.3073 | 14.9869 | 14.638 | 14.5369 | 14.3553 | 13.2267 | 12.589 | 12.0267 | 17.3157 | 17.1881 | 17.1514 | 17.0759 | 17.0126 | 16.8208 | 16.5289 | 16.184 | 16.0932 | 15.9096 | 14.981 | 14.6708 | 14.031 | 17.0131 | 16.9141 | 16.8692 | 16.7631 | 16.6774 | 16.3601 | 16.0182 | 15.6427 | 15.5386 | 15.3499 | 14.207 | 13.6641 | 13.1294
|  | LOCHEE | FB |  |  |  |  | 16.1604 | 16.2359 | 16.0257 | 16.0584 | 16.0114 | 15.94 | 15.8645 | 15.7839 | 15.641 | 15.5237 | 14.989 | 13.9696 | 12.9747 | 17.3269 | 17.3524 | 17.1942 | 17.1902 | 17.1238 | 17.0228 | 16.9228 | 16.8187 | 16.6677 | 16.533 | 15.7616 | 14.3116 | 12.5708 | 17.0662 | 17.0948 | 17.0152 | 16.9968 | 16.9448 | 16.905 | 16.8437 | 16.805 | 16.6407 | 16.5009 | 15.8652 | 14.5356 | 13.7223
| PORT ANN | LOCHGILPHEAD | MINIMUM HEADROOM | NR 86092 88371 | NO | YES | 1.28 | 16.1153 | 16.0112 | 15.7214 | 15.4265 | 14.9734 | 14.4683 | 13.8428 | 13.3724 | 12.8285 | 12.1796 | 10.4806 | 9.1714 | 8.6245 | 17.7173 | 17.5683 | 17.1857 | 16.899 | 16.4775 | 16.002 | 15.4214 | 15.0551 | 14.5704 | 13.8785 | 12.0438 | 11.1 | 10.7347 | 17.303 | 17.1775 | 16.8153 | 16.5051 | 16.0592 | 15.5775 | 14.9979 | 14.5816 | 14.0796 | 13.4377 | 11.7438 | 10.552 | 10.1
|  | LOCHGILPHEAD | EE |  |  |  |  | 16.1153 | 16.1479 | 15.7653 | 15.4653 | 15.0143 | 14.5 | 13.9102 | 13.4296 | 12.9581 | 12.4122 | 10.5775 | 9.1714 | 8.6245 | 17.7173 | 17.7092 | 17.1969 | 16.9194 | 16.4979 | 16.0204 | 15.4592 | 15.0877 | 14.6847 | 14.0908 | 12.3377 | 11.1 | 10.7347 | 17.303 | 17.2898 | 16.8316 | 16.5306 | 16.0857 | 15.601 | 15.0469 | 14.6214 | 14.1918 | 13.6469 | 11.9204 | 10.552 | 10.1
|  | LOCHGILPHEAD | HT |  |  |  |  | 16.1183 | 16.0112 | 15.7214 | 15.4265 | 14.9734 | 14.5071 | 13.8887 | 13.4041 | 12.8898 | 12.1796 | 10.4806 | 9.3214 | 8.8734 | 17.7183 | 17.5683 | 17.1857 | 16.899 | 16.4775 | 16.0602 | 15.5122 | 15.1132 | 14.65 | 13.8785 | 12.0438 | 11.1153 | 10.9887 | 17.3051 | 17.1775 | 16.8153 | 16.5051 | 16.0592 | 15.6234 | 15.0612 | 14.6255 | 14.1438 | 13.4377 | 11.7438 | 10.6632 | 10.349
|  | LOCHGILPHEAD | HE |  |  |  |  | 16.1163 | 16.1428 | 15.749 | 15.45 | 14.9959 | 14.4683 | 13.8428 | 13.3724 | 12.8285 | 12.35 | 10.8765 | 10.0357 | 9.6745 | 17.7183 | 17.7081 | 17.1918 | 16.9112 | 16.4898 | 16.002 | 15.4214 | 15.0551 | 14.5704 | 14.0683 | 12.5561 | 12.0194 | 11.8336 | 17.303 | 17.2887 | 16.8255 | 16.5214 | 16.0745 | 15.5775 | 14.9979 | 14.5816 | 14.0796 | 13.6081 | 12.1541 | 11.4571 | 11.1755
|  | LOCHGILPHEAD | FB |  |  |  |  | 16.2326 | 16.2785 | 16.3204 | 16.1051 | 16.0796 | 15.9081 | 15.7296 | 15.4653 | 15.1214 | 15.1041 | 13.6765 | 12.2367 | 11.1173 | 17.8163 | 17.7673 | 17.7806 | 17.5296 | 17.5092 | 17.301 | 17.0836 | 16.7806 | 16.402 | 16.352 | 14.7755 | 13.1632 | 11.7714 | 17.3826 | 17.3438 | 17.353 | 17.1204 | 17.0704 | 16.8826 | 16.6938 | 16.4398 | 16.0938 | 16.0643 | 14.6418 | 12.9408 | 12.0224
| CLACHAN | LOCHGOILHEAD | MINIMUM HEADROOM | NN 20159 01862 | YES | YES | 0.069 | 0.48265 | 0.47959 | 0.47857 | 0.47449 | 0.47041 | 0.45918 | 0.44592 | 0.42857 | 0.41122 | 0.40408 | 0.36429 | 0.35204 | 0.32755 | 0.67653 | 0.67449 | 0.67143 | 0.66735 | 0.66327 | 0.65612 | 0.64388 | 0.62041 | 0.60204 | 0.59898 | 0.5551 | 0.55714 | 0.53571 | -0.033673 | -0.039796 | -0.040816 | -0.046939 | -0.05102 | -0.063265 | -0.07551 | -0.096939 | -0.11633 | -0.12041 | -0.15612 | -0.17653 | -0.19082
|  | LOCHGOILHEAD | EE |  |  |  |  | 0.48265 | 0.48061 | 0.47857 | 0.47449 | 0.47143 | 0.4602 | 0.44694 | 0.42959 | 0.41327 | 0.40816 | 0.36429 | 0.35204 | 0.33163 | 0.67653 | 0.67449 | 0.67143 | 0.66837 | 0.66429 | 0.65612 | 0.64388 | 0.62245 | 0.60204 | 0.6 | 0.56531 | 0.56224 | 0.57347 | -0.033673 | -0.037755 | -0.040816 | -0.046939 | -0.05 | -0.062245 | -0.07449 | -0.094898 | -0.11327 | -0.11735 | -0.15612 | -0.17653 | -0.18163
|  | LOCHGOILHEAD | HT |  |  |  |  | 0.48265 | 0.47959 | 0.48061 | 0.47551 | 0.47245 | 0.46224 | 0.45204 | 0.43571 | 0.41735 | 0.4102 | 0.36939 | 0.3602 | 0.33163 | 0.67653 | 0.67449 | 0.67245 | 0.66735 | 0.66429 | 0.65612 | 0.64388 | 0.62041 | 0.60204 | 0.59898 | 0.5551 | 0.55714 | 0.57245 | -0.033673 | -0.039796 | -0.039796 | -0.046939 | -0.05102 | -0.061224 | -0.071429 | -0.092857 | -0.11224 | -0.11735 | -0.15408 | -0.17143 | -0.17857
|  | LOCHGOILHEAD | HE |  |  |  |  | 0.48367 | 0.47959 | 0.47959 | 0.47449 | 0.47041 | 0.45918 | 0.44592 | 0.42857 | 0.41122 | 0.40408 | 0.37245 | 0.3551 | 0.32755 | 0.67959 | 0.67449 | 0.67245 | 0.66837 | 0.66327 | 0.65612 | 0.64388 | 0.62041 | 0.60204 | 0.59898 | 0.56327 | 0.55918 | 0.55918 | -0.032653 | -0.039796 | -0.040816 | -0.046939 | -0.05102 | -0.063265 | -0.07551 | -0.096939 | -0.11633 | -0.12041 | -0.14898 | -0.17653 | -0.19082
|  | LOCHGOILHEAD | FB |  |  |  |  | 0.48878 | 0.49286 | 0.49184 | 0.49184 | 0.49286 | 0.4898 | 0.48776 | 0.48776 | 0.48163 | 0.47959 | 0.44796 | 0.40408 | 0.3898 | 0.68673 | 0.68776 | 0.68367 | 0.68265 | 0.68061 | 0.67653 | 0.66837 | 0.66837 | 0.6551 | 0.65102 | 0.61224 | 0.56224 | 0.53571 | -0.020408 | -0.022449 | -0.023469 | -0.02449 | -0.026531 | -0.028571 | -0.036735 | -0.035714 | -0.046939 | -0.05102 | -0.084694 | -0.13367 | -0.14082
| GRUDIE BRIDGE | LOCHINVER | MINIMUM HEADROOM | NC 09516 22243 | YES | NO | 0.236 | -0.22653 | -0.22449 | -0.23469 | -0.26327 | -0.30714 | -0.44286 | -0.57449 | -0.67245 | -0.75 | -0.82959 | -0.96939 | -1.1357 | -1.2765 | -0.11735 | -0.11735 | -0.12551 | -0.12857 | -0.14184 | -0.2551 | -0.35714 | -0.42449 | -0.47857 | -0.50612 | -0.60102 | -0.5949 | -0.64388 | -0.22245 | -0.22041 | -0.22551 | -0.24082 | -0.26224 | -0.41837 | -0.53673 | -0.59898 | -0.66224 | -0.71122 | -0.80102 | -0.88776 | -0.96735
|  | LOCHINVER | EE |  |  |  |  | -0.22653 | -0.22245 | -0.23265 | -0.2602 | -0.29796 | -0.35204 | -0.39388 | -0.55816 | -0.6898 | -0.79796 | -0.96939 | -1.1357 | -1.2571 | -0.11633 | -0.11224 | -0.12449 | -0.12857 | -0.14082 | -0.16531 | -0.20204 | -0.31429 | -0.40612 | -0.48673 | -0.57347 | -0.56939 | -0.54898 | -0.22245 | -0.21837 | -0.22449 | -0.24082 | -0.25918 | -0.30918 | -0.35714 | -0.47041 | -0.59286 | -0.68776 | -0.80102 | -0.88776 | -0.95306
|  | LOCHINVER | HT |  |  |  |  | -0.22653 | -0.22449 | -0.23367 | -0.2602 | -0.29694 | -0.44286 | -0.57449 | -0.67245 | -0.75 | -0.8051 | -0.92959 | -1.1102 | -1.2765 | -0.11735 | -0.11735 | -0.12449 | -0.12857 | -0.14082 | -0.2551 | -0.35714 | -0.42449 | -0.47857 | -0.50612 | -0.60102 | -0.5949 | -0.5602 | -0.22245 | -0.22041 | -0.22551 | -0.24082 | -0.25918 | -0.41837 | -0.53673 | -0.59898 | -0.66224 | -0.70102 | -0.79286 | -0.87143 | -0.96735
|  | LOCHINVER | HE |  |  |  |  | -0.22653 | -0.22245 | -0.23469 | -0.26327 | -0.30714 | -0.34796 | -0.40408 | -0.58469 | -0.71939 | -0.82959 | -0.92857 | -1.1122 | -1.2327 | -0.11735 | -0.11122 | -0.12551 | -0.12041 | -0.14184 | -0.16429 | -0.2051 | -0.32653 | -0.42245 | -0.50612 | -0.57143 | -0.57143 | -0.57551 | -0.22245 | -0.21735 | -0.22551 | -0.23776 | -0.26224 | -0.30816 | -0.34184 | -0.49082 | -0.61735 | -0.71122 | -0.78163 | -0.87755 | -0.95102
|  | LOCHINVER | FB |  |  |  |  | -0.20612 | -0.19388 | -0.18469 | -0.18571 | -0.1898 | -0.20306 | -0.20918 | -0.22347 | -0.32245 | -0.39592 | -0.57551 | -0.70714 | -0.74898 | -0.087755 | -0.084694 | -0.080612 | -0.078571 | -0.077551 | -0.092857 | -0.10612 | -0.12959 | -0.21633 | -0.28776 | -0.45102 | -0.56939 | -0.64388 | -0.20102 | -0.19286 | -0.18367 | -0.18265 | -0.18163 | -0.1949 | -0.20102 | -0.21633 | -0.32245 | -0.4 | -0.57041 | -0.64898 | -0.66429
| LUNANHEAD | LOCHSIDE | MINIMUM HEADROOM | NO 45151 50548 | NO | YES | 2.425 | 6 | 5.8428 | 5.7102 | 5.5142 | 5.3285 | 4.9357 | 3.7326 | 2.5051 | -0.35616 | -1.1041 | -6.5858 | -12.3449 | -17.4827 | 8.1279 | 7.983 | 7.9167 | 7.83 | 7.73 | 7.4493 | 6.0932 | 4.582 | 1.0565 | 0.19935 | -5.3211 | -11.518 | -17.4435 | 7.83 | 7.6657 | 7.581 | 7.4442 | 7.3238 | 6.8432 | 5.3473 | 3.7177 | 0.12384 | -0.79555 | -6.7496 | -13.3527 | -19.4251
|  | LOCHSIDE | EE |  |  |  |  | 6.0836 | 5.9704 | 5.7591 | 5.6275 | 5.451 | 5.0816 | 4.1826 | 3.1306 | 1.4255 | 0.94282 | -3.4868 | -9.8245 | -12.7092 | 8.2187 | 8.1147 | 7.9402 | 7.8759 | 7.7749 | 7.4963 | 6.4647 | 5.4004 | 3.3555 | 2.83 | -0.94963 | -7.3476 | -10.1415 | 7.9177 | 7.7922 | 7.6024 | 7.5157 | 7.3993 | 6.9371 | 5.7779 | 4.5698 | 2.3953 | 1.784 | -2.6609 | -9.717 | -12.8149
|  | LOCHSIDE | HT |  |  |  |  | 6.0336 | 5.8428 | 5.7102 | 5.5142 | 5.3285 | 4.9357 | 3.7326 | 2.5051 | 0.57853 | -0.16024 | -4.3368 | -11.0368 | -16.0225 | 8.1657 | 7.983 | 7.9167 | 7.83 | 7.73 | 7.4493 | 6.0932 | 4.582 | 2.3789 | 1.634 | -2.0782 | -8.917 | -14.3231 | 7.8667 | 7.6657 | 7.581 | 7.4442 | 7.3238 | 6.8432 | 5.3473 | 3.7177 | 1.4167 | 0.57588 | -3.7527 | -11.3251 | -17.1251
|  | LOCHSIDE | HE |  |  |  |  | 6 | 5.9826 | 5.754 | 5.5877 | 5.3979 | 5.0449 | 4.0908 | 2.653 | -0.35616 | -1.1041 | -6.5858 | -12.3449 | -17.4827 | 8.1279 | 8.1167 | 7.932 | 7.8596 | 7.7565 | 7.4504 | 6.3993 | 4.781 | 1.0565 | 0.19935 | -5.3211 | -11.518 | -17.4435 | 7.83 | 7.7993 | 7.5983 | 7.4881 | 7.3677 | 6.8902 | 5.7004 | 3.9596 | 0.12384 | -0.79555 | -6.7496 | -13.3527 | -19.4251
|  | LOCHSIDE | FB |  |  |  |  | 6.3704 | 6.3051 | 6.2551 | 6.1449 | 6.1112 | 6.0173 | 5.604 | 5.0887 | 3.9826 | 3.6296 | 1.9265 | -1.0398 | -3.2358 | 8.4616 | 8.3585 | 8.2932 | 8.1493 | 8.1218 | 8.0616 | 7.6075 | 7.0585 | 5.7575 | 5.2381 | 3.0759 | -0.29249 | -2.8119 | 8.1698 | 8.0667 | 7.9973 | 7.8402 | 7.8034 | 7.7463 | 7.283 | 6.7279 | 5.4616 | 4.9606 | 2.7626 | -1.2792 | -2.9578
| BRIDGE OF DUN | LOGIE PERT | MINIMUM HEADROOM | NO 67764 64427 | YES | NO | 1.073 | 3.6977 | 3.6936 | 3.6855 | 3.6773 | 3.4089 | 3.161 | 2.9722 | 2.8732 | 2.763 | 2.6824 | 2.2732 | 2.0375 | 1.9406 | 3.4345 | 3.4253 | 3.41 | 3.3926 | 3.1345 | 2.9069 | 2.7243 | 2.6263 | 2.5151 | 2.4365 | 2.0294 | 1.7855 | 1.6875 | 3.3727 | 3.3737 | 3.3707 | 3.3707 | 3.1227 | 2.8707 | 2.6778 | 2.5799 | 2.4727 | 2.386 | 1.9717 | 1.7268 | 1.6258
|  | LOGIE PERT | EE |  |  |  |  | 3.6977 | 3.6936 | 3.6855 | 3.6773 | 3.4089 | 3.2171 | 2.9885 | 2.8732 | 2.7845 | 2.7049 | 2.2732 | 2.0375 | 1.9406 | 3.4345 | 3.4253 | 3.411 | 3.3926 | 3.1355 | 2.9569 | 2.7396 | 2.6263 | 2.5334 | 2.4569 | 2.0294 | 1.7855 | 1.6875 | 3.3727 | 3.3737 | 3.3707 | 3.3707 | 3.1227 | 2.9278 | 2.6982 | 2.5799 | 2.4901 | 2.4095 | 1.9717 | 1.7268 | 1.6258
|  | LOGIE PERT | HT |  |  |  |  | 3.6977 | 3.6936 | 3.6855 | 3.6773 | 3.4089 | 3.161 | 3.0651 | 2.9385 | 2.7671 | 2.6885 | 2.2753 | 2.0692 | 1.9743 | 3.4345 | 3.4253 | 3.41 | 3.3926 | 3.1355 | 2.9069 | 2.81 | 2.6824 | 2.5181 | 2.4396 | 2.0314 | 1.8232 | 1.7232 | 3.3727 | 3.3737 | 3.3707 | 3.3707 | 3.1227 | 2.8707 | 2.7748 | 2.6472 | 2.4768 | 2.3931 | 1.9768 | 1.7646 | 1.6615
|  | LOGIE PERT | HE |  |  |  |  | 3.6977 | 3.6936 | 3.6855 | 3.6773 | 3.4089 | 3.2089 | 2.9722 | 2.9232 | 2.763 | 2.6824 | 2.4681 | 2.5018 | 2.4855 | 3.4345 | 3.4253 | 3.41 | 3.3926 | 3.1345 | 2.9487 | 2.7243 | 2.6702 | 2.5151 | 2.4365 | 2.211 | 2.2396 | 2.2192 | 3.3727 | 3.3737 | 3.3707 | 3.3707 | 3.1227 | 2.9176 | 2.6778 | 2.6299 | 2.4727 | 2.386 | 2.1697 | 2.2033 | 2.1839
|  | LOGIE PERT | FB |  |  |  |  | 3.7079 | 3.7089 | 3.6957 | 3.6926 | 3.6814 | 3.6783 | 3.6732 | 3.6589 | 3.6569 | 3.2814 | 2.9936 | 2.6845 | 2.3457 | 3.4467 | 3.4436 | 3.4263 | 3.4151 | 3.3957 | 3.3896 | 3.3783 | 3.3589 | 3.3518 | 3.0018 | 2.7202 | 2.41 | 2.0783 | 3.3829 | 3.3901 | 3.385 | 3.387 | 3.3839 | 3.3809 | 3.3788 | 3.3646 | 3.3656 | 2.9962 | 2.7033 | 2.289 | 2.038
| MILTON OF CRAIGIE | LONGHAUGH | MINIMUM HEADROOM | NO 42768 33789 | NO | NO | 5.323 | 9.6645 | 9.2002 | 8.4573 | 8.0012 | 7.5124 | 7.4584 | 7.3788 | 7.2451 | 7.1512 | 7.0267 | 5.8043 | 4.8002 | 4.14 | 12.2818 | 11.7676 | 10.9859 | 10.4869 | 9.9604 | 9.9267 | 9.8359 | 9.7318 | 9.6482 | 9.5063 | 8.8573 | 8.5237 | 8.2737 | 11.5155 | 11.0288 | 10.289 | 9.8176 | 9.3124 | 9.2788 | 9.189 | 9.0614 | 8.9982 | 8.889 | 7.738 | 6.8982 | 6.3227
|  | LONGHAUGH | EE |  |  |  |  | 9.8339 | 9.2002 | 8.4665 | 8.0114 | 7.5298 | 7.4849 | 7.4196 | 7.2451 | 7.1512 | 7.041 | 5.8043 | 4.8002 | 4.14 | 12.4696 | 11.7676 | 11.0002 | 10.4971 | 9.9686 | 9.9492 | 9.8798 | 9.7318 | 9.6482 | 9.5512 | 8.8573 | 8.5237 | 8.2737 | 11.692 | 11.0288 | 10.289 | 9.8176 | 9.3186 | 9.2931 | 9.2145 | 9.0614 | 8.9982 | 8.9033 | 7.738 | 6.8982 | 6.3227
|  | LONGHAUGH | HT |  |  |  |  | 9.7288 | 9.2237 | 8.4573 | 8.0012 | 7.5124 | 7.4584 | 7.3788 | 7.2941 | 7.2114 | 7.0267 | 6.1859 | 5.5849 | 5.2329 | 12.3563 | 11.789 | 10.9859 | 10.4869 | 9.9604 | 9.9267 | 9.8359 | 9.7512 | 9.6737 | 9.5063 | 8.9869 | 8.9155 | 8.8982 | 11.5869 | 11.0604 | 10.289 | 9.8186 | 9.3124 | 9.2788 | 9.189 | 9.1073 | 9.0502 | 8.889 | 7.9563 | 7.492 | 7.2747
|  | LONGHAUGH | HE |  |  |  |  | 9.6645 | 9.2084 | 8.4706 | 8.0063 | 7.5186 | 7.5757 | 7.5084 | 7.3451 | 7.2686 | 7.189 | 6.5155 | 5.788 | 5.3573 | 12.2818 | 11.7676 | 10.9961 | 10.4931 | 9.9665 | 10.0084 | 9.9492 | 9.8104 | 9.738 | 9.6635 | 9.1951 | 8.9053 | 8.6951 | 11.5155 | 11.039 | 10.2982 | 9.8196 | 9.3165 | 9.3533 | 9.2931 | 9.1737 | 9.1022 | 9.0329 | 8.3951 | 7.7727 | 7.4012
|  | LONGHAUGH | FB |  |  |  |  | 10.3318 | 9.9706 | 9.3665 | 9.0502 | 8.5176 | 8.2104 | 8.0339 | 7.9563 | 8.0135 | 8.0145 | 7.7329 | 6.5808 | 5.7176 | 12.9349 | 12.492 | 11.8186 | 11.4573 | 10.8737 | 10.5257 | 10.3206 | 10.2124 | 10.242 | 10.2145 | 9.8778 | 8.9849 | 8.3053 | 12.1604 | 11.7635 | 11.1349 | 10.8022 | 10.2512 | 9.9369 | 9.7573 | 9.6747 | 9.7237 | 9.7196 | 9.4288 | 8.1584 | 7.6084
| INVERNESS | LONGMAN DRIVE | MINIMUM HEADROOM | NH 67139 46770 | NO | NO | 3.852 | 10.3403 | 10.1962 | 10.2151 | 10.0948 | 9.9306 | 8.9437 | 7.7093 | 6.4115 | 5.3412 | 4.8521 | 3.42 | 1.9186 | 1.0272 | 10.2842 | 10.2551 | 10.2626 | 10.2286 | 10.1761 | 9.354 | 8.2431 | 7.0552 | 6.0872 | 5.8139 | 4.782 | 3.9812 | 3.2019 | 8.327 | 8.2689 | 8.2647 | 8.1985 | 8.1049 | 7.2799 | 6.1654 | 4.9847 | 3.9858 | 3.6449 | 2.3341 | 0.95807 | 0.011146
|  | LONGMAN DRIVE | EE |  |  |  |  | 10.3403 | 10.1962 | 10.2151 | 10.0948 | 9.9327 | 9.6334 | 9.2587 | 8.2096 | 6.9191 | 5.6995 | 3.5741 | 2.0845 | 1.6144 | 10.2842 | 10.2555 | 10.2626 | 10.2286 | 10.177 | 10.0953 | 9.9382 | 9.0346 | 7.8351 | 6.7405 | 5.2997 | 4.4041 | 4.0929 | 8.3273 | 8.2689 | 8.2647 | 8.1985 | 8.1072 | 7.9612 | 7.7252 | 6.8091 | 5.6265 | 4.5394 | 2.6411 | 1.1656 | 0.7405
|  | LONGMAN DRIVE | HT |  |  |  |  | 10.3418 | 10.1998 | 10.2193 | 10.0992 | 9.9306 | 8.9437 | 7.7093 | 6.4115 | 5.3412 | 4.8521 | 3.42 | 1.9186 | 1.0272 | 10.2848 | 10.256 | 10.2631 | 10.2295 | 10.1761 | 9.354 | 8.2431 | 7.0552 | 6.0872 | 5.8139 | 5.1101 | 4.1535 | 3.3525 | 8.3301 | 8.276 | 8.2764 | 8.2078 | 8.1127 | 7.2799 | 6.1654 | 4.9847 | 3.9858 | 3.6449 | 2.4543 | 0.95807 | 0.011146
|  | LONGMAN DRIVE | HE |  |  |  |  | 10.3427 | 10.2014 | 10.2247 | 10.1012 | 9.9426 | 9.6434 | 9.2967 | 8.1356 | 6.5923 | 5.2479 | 3.4735 | 2.4275 | 1.5373 | 10.2848 | 10.2551 | 10.2631 | 10.23 | 10.1775 | 10.0925 | 9.9343 | 8.8887 | 7.3587 | 6.0854 | 4.782 | 3.9812 | 3.2019 | 8.327 | 8.2693 | 8.2679 | 8.199 | 8.1049 | 7.9589 | 7.7275 | 6.6851 | 5.1872 | 3.9424 | 2.3341 | 1.2815 | 0.33291
|  | LONGMAN DRIVE | FB |  |  |  |  | 10.3676 | 10.2223 | 10.2435 | 10.2184 | 10.1548 | 10.0811 | 9.9072 | 9.7105 | 8.965 | 8.22 | 5.5574 | 4.7961 | 4.1538 | 10.2973 | 10.2793 | 10.2908 | 10.2807 | 10.2558 | 10.2341 | 10.1308 | 10.0072 | 9.2445 | 8.4773 | 5.9903 | 5.555 | 5.2484 | 8.3465 | 8.3044 | 8.3165 | 8.2917 | 8.2459 | 8.2111 | 8.0799 | 7.9206 | 7.1943 | 6.4752 | 4.0486 | 3.4063 | 2.9777
| ELGIN | LOSSIEMOUTH | MINIMUM HEADROOM | NJ 23203 69923 | NO | YES | 0.788 | 7.199 | 7.1684 | 7.1582 | 6.9082 | 6.6296 | 6.2592 | 5.8306 | 5.5041 | 5.1245 | 4.7673 | 3.2735 | 2.1398 | 1.4163 | 8.1378 | 8.1296 | 8.1245 | 7.9418 | 7.8194 | 7.6245 | 7.3837 | 7.251 | 7.0551 | 6.8122 | 5.8959 | 5.6796 | 5.1051 | 7.6429 | 7.6316 | 7.6255 | 7.549 | 7.351 | 7.0531 | 6.6949 | 6.4153 | 6.1031 | 5.7959 | 4.5276 | 3.649 | 3.0949
|  | LOSSIEMOUTH | EE |  |  |  |  | 7.2 | 7.1694 | 7.1582 | 7.05 | 6.6306 | 6.2592 | 5.8306 | 5.5388 | 5.1245 | 4.7673 | 3.2735 | 2.1398 | 1.4163 | 8.1378 | 8.1296 | 8.1255 | 8.0806 | 7.8224 | 7.6245 | 7.4051 | 7.2949 | 7.0602 | 6.8122 | 5.9765 | 5.6796 | 5.3612 | 7.6429 | 7.6337 | 7.6255 | 7.5745 | 7.351 | 7.0531 | 6.6949 | 6.4551 | 6.1031 | 5.7959 | 4.5276 | 3.649 | 3.0949
|  | LOSSIEMOUTH | HT |  |  |  |  | 7.2 | 7.1694 | 7.1592 | 7.0571 | 6.6388 | 6.302 | 5.8561 | 5.5643 | 5.2092 | 4.898 | 3.4235 | 2.3735 | 1.5745 | 8.1378 | 8.1296 | 8.1245 | 8.0796 | 7.8194 | 7.6459 | 7.3837 | 7.2582 | 7.0551 | 6.8367 | 5.8959 | 5.701 | 5.6429 | 7.6429 | 7.6327 | 7.6286 | 7.5806 | 7.3571 | 7.0857 | 6.701 | 6.4571 | 6.1561 | 5.8929 | 4.6398 | 3.848 | 3.2582
|  | LOSSIEMOUTH | HE |  |  |  |  | 7.199 | 7.1684 | 7.1582 | 7.05 | 6.6296 | 6.2622 | 5.8388 | 5.5041 | 5.1541 | 4.8531 | 3.6449 | 2.7571 | 2.3255 | 8.1378 | 8.1296 | 8.1255 | 8.0786 | 7.8204 | 7.6245 | 7.399 | 7.251 | 7.0663 | 6.8612 | 6.1143 | 6.0173 | 5.8235 | 7.6439 | 7.6316 | 7.6265 | 7.5735 | 7.351 | 7.0551 | 6.6959 | 6.4153 | 6.1245 | 5.8714 | 4.8398 | 4.1847 | 3.8735
|  | LOSSIEMOUTH | FB |  |  |  |  | 7.252 | 7.2612 | 7.2622 | 6.9082 | 6.8918 | 6.802 | 6.7082 | 6.6235 | 6.5245 | 6.5347 | 5.8102 | 4.8051 | 4.1602 | 8.1643 | 8.1796 | 8.1847 | 7.9418 | 7.9296 | 7.85 | 7.7633 | 7.6816 | 7.5918 | 7.6 | 6.9582 | 5.9765 | 5.1051 | 7.6929 | 7.7163 | 7.7296 | 7.549 | 7.549 | 7.5102 | 7.4276 | 7.349 | 7.2602 | 7.2765 | 6.6122 | 5.5408 | 5.099
| BROADFORD | LOWER OLLACH | MINIMUM HEADROOM | NG 51241 37001 | YES | YES | 1.072 | -0.56463 | -0.57687 | -0.58504 | -0.61055 | -0.63198 | -0.68402 | -0.71871 | -0.76769 | -0.82177 | -0.86259 | -0.96157 | -1.0514 | -1.134 | -0.37381 | -0.38198 | -0.38606 | -0.3983 | -0.40544 | -0.42687 | -0.46055 | -0.48504 | -0.51463 | -0.54524 | -0.61259 | -0.61667 | -0.64116 | -0.45034 | -0.46157 | -0.46871 | -0.49218 | -0.50544 | -0.54524 | -0.59728 | -0.63504 | -0.66157 | -0.6983 | -0.77483 | -0.83198 | -0.883
|  | LOWER OLLACH | EE |  |  |  |  | -0.56259 | -0.57483 | -0.583 | -0.60749 | -0.62585 | -0.68198 | -0.71667 | -0.76463 | -0.82075 | -0.85851 | -0.96157 | -1.0514 | -1.1105 | -0.37177 | -0.38096 | -0.38504 | -0.39728 | -0.40136 | -0.42483 | -0.45851 | -0.48198 | -0.51361 | -0.54218 | -0.59422 | -0.60647 | -0.61259 | -0.4483 | -0.46055 | -0.46769 | -0.48708 | -0.50136 | -0.5432 | -0.59626 | -0.633 | -0.65749 | -0.69116 | -0.77483 | -0.83198 | -0.86259
|  | LOWER OLLACH | HT |  |  |  |  | -0.56259 | -0.57381 | -0.58504 | -0.60749 | -0.63198 | -0.68096 | -0.71769 | -0.76259 | -0.81667 | -0.85647 | -0.94932 | -1.0452 | -1.134 | -0.37177 | -0.38096 | -0.38606 | -0.39728 | -0.40544 | -0.42483 | -0.46055 | -0.483 | -0.51463 | -0.54524 | -0.61259 | -0.61667 | -0.61463 | -0.4483 | -0.46055 | -0.46871 | -0.48912 | -0.50544 | -0.5432 | -0.59626 | -0.63198 | -0.65749 | -0.69422 | -0.77381 | -0.83198 | -0.883
|  | LOWER OLLACH | HE |  |  |  |  | -0.56463 | -0.57687 | -0.583 | -0.61055 | -0.63096 | -0.68402 | -0.71871 | -0.76769 | -0.82177 | -0.86259 | -0.9381 | -1.0452 | -1.1136 | -0.37381 | -0.38198 | -0.383 | -0.3983 | -0.40442 | -0.42687 | -0.45953 | -0.48504 | -0.51463 | -0.54422 | -0.5983 | -0.61157 | -0.63096 | -0.45034 | -0.46157 | -0.46463 | -0.49218 | -0.50442 | -0.54524 | -0.59728 | -0.63504 | -0.66157 | -0.6983 | -0.76157 | -0.83096 | -0.87279
|  | LOWER OLLACH | FB |  |  |  |  | -0.53402 | -0.54014 | -0.53606 | -0.53606 | -0.54422 | -0.55647 | -0.56565 | -0.583 | -0.59218 | -0.61361 | -0.70034 | -0.75442 | -0.78708 | -0.35034 | -0.35851 | -0.35647 | -0.35647 | -0.36463 | -0.37585 | -0.38402 | -0.40034 | -0.41361 | -0.43606 | -0.50544 | -0.58402 | -0.64116 | -0.41973 | -0.42891 | -0.42687 | -0.42687 | -0.43708 | -0.44932 | -0.45442 | -0.47075 | -0.48402 | -0.50442 | -0.583 | -0.66259 | -0.67585
| KILLIN | LUBNAIG | MINIMUM HEADROOM | NN 57455 13800 | YES | YES | 0 | 0.22376 | 0.22478 | 0.21355 | 0.21661 | 0.21559 | 0.21457 | 0.21253 | 0.21151 | 0.20743 | 0.20845 | 0.20335 | 0.20029 | 0.19824 | 0.21086 | 0.21086 | 0.19963 | 0.20065 | 0.20065 | 0.19861 | 0.19657 | 0.19657 | 0.19351 | 0.19453 | 0.18943 | 0.18739 | 0.18739 | 0.21782 | 0.21782 | 0.20761 | 0.20863 | 0.20965 | 0.20659 | 0.20455 | 0.20557 | 0.20149 | 0.20251 | 0.19741 | 0.19435 | 0.19333
|  | LUBNAIG | EE |  |  |  |  | 0.22376 | 0.22478 | 0.21355 | 0.21661 | 0.21559 | 0.21457 | 0.21253 | 0.21151 | 0.20743 | 0.20845 | 0.20335 | 0.20233 | 0.20131 | 0.21086 | 0.21086 | 0.19963 | 0.20065 | 0.20065 | 0.19861 | 0.19657 | 0.19657 | 0.19351 | 0.19453 | 0.19045 | 0.18943 | 0.19045 | 0.21782 | 0.21782 | 0.20761 | 0.20863 | 0.20965 | 0.20659 | 0.20455 | 0.20557 | 0.20149 | 0.20251 | 0.19741 | 0.19639 | 0.19639
|  | LUBNAIG | HT |  |  |  |  | 0.22376 | 0.22478 | 0.21355 | 0.21661 | 0.21559 | 0.21457 | 0.21355 | 0.21151 | 0.20743 | 0.20845 | 0.20641 | 0.20029 | 0.19824 | 0.21086 | 0.21086 | 0.19963 | 0.20065 | 0.20065 | 0.19861 | 0.19657 | 0.19657 | 0.19351 | 0.19453 | 0.18943 | 0.18739 | 0.18739 | 0.21782 | 0.21782 | 0.20761 | 0.20863 | 0.20965 | 0.20659 | 0.20455 | 0.20557 | 0.20149 | 0.20251 | 0.19741 | 0.19435 | 0.19333
|  | LUBNAIG | HE |  |  |  |  | 0.22376 | 0.22478 | 0.21355 | 0.21661 | 0.21559 | 0.21457 | 0.21253 | 0.21151 | 0.20743 | 0.20845 | 0.20335 | 0.20233 | 0.20131 | 0.21086 | 0.21086 | 0.19963 | 0.20065 | 0.20065 | 0.19861 | 0.19657 | 0.19657 | 0.19351 | 0.19453 | 0.19045 | 0.18943 | 0.18943 | 0.21782 | 0.21782 | 0.20761 | 0.20863 | 0.20965 | 0.20659 | 0.20455 | 0.20557 | 0.20149 | 0.20251 | 0.19741 | 0.19639 | 0.19537
|  | LUBNAIG | FB |  |  |  |  | 0.22376 | 0.22478 | 0.22478 | 0.22478 | 0.21967 | 0.21967 | 0.21763 | 0.21763 | 0.21559 | 0.21661 | 0.21253 | 0.20845 | 0.20845 | 0.21086 | 0.21086 | 0.21086 | 0.21086 | 0.20371 | 0.20473 | 0.20371 | 0.20371 | 0.20065 | 0.20065 | 0.19657 | 0.19351 | 0.19045 | 0.21782 | 0.21782 | 0.21884 | 0.21884 | 0.21271 | 0.21271 | 0.21169 | 0.21271 | 0.20965 | 0.20965 | 0.20557 | 0.20353 | 0.20149
| LUNANHEAD | LUNANHEAD | MINIMUM HEADROOM | NO 47042 51733 | NO | YES | 0.934 | 7.7276 | 7.6112 | 7.5796 | 7.4531 | 7.252 | 6.8857 | 6.2204 | 5.2286 | 3.2327 | 2.4235 | -0.34694 | -4.4429 | -7.9367 | 9.399 | 9.2827 | 9.2622 | 9.2286 | 9.1133 | 8.9551 | 8.2214 | 7.3622 | 5.1296 | 4.3847 | 1.6908 | -2.1592 | -5.8102 | 8.0944 | 7.8362 | 7.8036 | 7.7138 | 7.5046 | 7.1485 | 6.3628 | 5.3179 | 2.9903 | 2.2036 | -0.75663 | -5.1383 | -9.0628
|  | LUNANHEAD | EE |  |  |  |  | 7.7276 | 7.6112 | 7.5796 | 7.4663 | 7.2857 | 6.949 | 6.3408 | 5.6071 | 4.4439 | 3.9643 | 1.2112 | -2.6959 | -4.7204 | 9.401 | 9.2827 | 9.2622 | 9.2306 | 9.1173 | 8.9673 | 8.4245 | 7.7102 | 6.4816 | 6.1276 | 4.0082 | 0.42449 | -1.201 | 8.0964 | 7.8372 | 7.8036 | 7.724 | 7.5189 | 7.1974 | 6.5393 | 5.723 | 4.4209 | 3.9995 | 1.4883 | -2.6638 | -4.6495
|  | LUNANHEAD | HT |  |  |  |  | 7.7296 | 7.6153 | 7.601 | 7.4918 | 7.3143 | 6.9908 | 6.2204 | 5.4051 | 4.0143 | 3.5235 | 0.93776 | -3.3082 | -6.8531 | 9.399 | 9.2827 | 9.2633 | 9.2337 | 9.1204 | 8.9673 | 8.2214 | 7.3673 | 5.9133 | 5.5398 | 3.3 | -0.60612 | -3.8816 | 8.0964 | 7.8383 | 7.8158 | 7.7393 | 7.5434 | 7.2189 | 6.3628 | 5.4281 | 3.8832 | 3.4434 | 0.96276 | -3.6015 | -7.4291
|  | LUNANHEAD | HE |  |  |  |  | 7.7286 | 7.6133 | 7.5918 | 7.4531 | 7.252 | 6.8857 | 6.2388 | 5.2286 | 3.2327 | 2.4235 | -0.34694 | -4.4429 | -7.9367 | 9.399 | 9.2827 | 9.2633 | 9.2286 | 9.1133 | 8.9551 | 8.4102 | 7.3622 | 5.1296 | 4.3847 | 1.6908 | -2.1592 | -5.8102 | 8.0944 | 7.8362 | 7.8117 | 7.7138 | 7.5046 | 7.1485 | 6.474 | 5.3179 | 2.9903 | 2.2036 | -0.75663 | -5.1383 | -9.0628
|  | LUNANHEAD | FB |  |  |  |  | 7.8133 | 7.8255 | 7.7418 | 7.7296 | 7.701 | 7.6347 | 7.3418 | 6.9969 | 6.3724 | 6.1112 | 5.1459 | 3.5031 | 2.1612 | 9.4592 | 9.4735 | 9.3684 | 9.3633 | 9.3643 | 9.3357 | 9.0092 | 8.6082 | 7.901 | 7.5847 | 6.5092 | 4.9439 | 3.399 | 8.1934 | 8.2189 | 8.0066 | 7.9852 | 7.9566 | 7.9301 | 7.5423 | 7.0883 | 6.3515 | 6.0189 | 4.8995 | 3.0097 | 2.0495
| PORT ANN | LUSSAGIVEN | MINIMUM HEADROOM | NR 63461 86798 | YES | YES | 0 | 0.058816 | 0.046571 | 0.047592 | 0.044531 | 0.040449 | 0.032286 | 0.032286 | 0.029224 | 0.025143 | 0.022082 | 0.018 | 0.015959 | 0.010857 | 0.069204 | 0.062061 | 0.063082 | 0.061041 | 0.059 | 0.052878 | 0.055939 | 0.053898 | 0.051857 | 0.048796 | 0.045735 | 0.046755 | 0.047776 | 0.06452 | 0.054316 | 0.054316 | 0.049214 | 0.046153 | 0.03799 | 0.03901 | 0.036969 | 0.034929 | 0.031867 | 0.029827 | 0.026765 | 0.024724
|  | LUSSAGIVEN | EE |  |  |  |  | 0.058816 | 0.046571 | 0.047592 | 0.044531 | 0.040449 | 0.034327 | 0.033306 | 0.029224 | 0.026163 | 0.022082 | 0.018 | 0.015959 | 0.012898 | 0.069204 | 0.062061 | 0.063082 | 0.061041 | 0.059 | 0.054918 | 0.056959 | 0.053898 | 0.051857 | 0.048796 | 0.046755 | 0.049816 | 0.048796 | 0.06452 | 0.054316 | 0.054316 | 0.049214 | 0.046153 | 0.040031 | 0.040031 | 0.036969 | 0.035949 | 0.031867 | 0.029827 | 0.027786 | 0.025745
|  | LUSSAGIVEN | HT |  |  |  |  | 0.058816 | 0.047592 | 0.047592 | 0.048612 | 0.041469 | 0.032286 | 0.033306 | 0.030245 | 0.027184 | 0.023102 | 0.020041 | 0.01698 | 0.010857 | 0.069204 | 0.062061 | 0.063082 | 0.063082 | 0.06002 | 0.052878 | 0.055939 | 0.053898 | 0.052878 | 0.048796 | 0.045735 | 0.046755 | 0.047776 | 0.06452 | 0.054316 | 0.054316 | 0.054316 | 0.047173 | 0.03799 | 0.040031 | 0.03901 | 0.036969 | 0.032888 | 0.029827 | 0.026765 | 0.024724
|  | LUSSAGIVEN | HE |  |  |  |  | 0.058816 | 0.046571 | 0.047592 | 0.044531 | 0.040449 | 0.034327 | 0.032286 | 0.029224 | 0.025143 | 0.023102 | 0.020041 | 0.01698 | 0.011878 | 0.069204 | 0.062061 | 0.063082 | 0.061041 | 0.059 | 0.054918 | 0.055939 | 0.053898 | 0.051857 | 0.048796 | 0.046755 | 0.048796 | 0.047776 | 0.06452 | 0.054316 | 0.054316 | 0.049214 | 0.046153 | 0.040031 | 0.03901 | 0.03799 | 0.034929 | 0.031867 | 0.029827 | 0.026765 | 0.025745
|  | LUSSAGIVEN | FB |  |  |  |  | 0.058816 | 0.058816 | 0.051673 | 0.051673 | 0.048612 | 0.048612 | 0.046571 | 0.047592 | 0.044531 | 0.04249 | 0.034327 | 0.026163 | 0.025143 | 0.069204 | 0.069204 | 0.064102 | 0.064102 | 0.063082 | 0.063082 | 0.062061 | 0.06002 | 0.06002 | 0.059 | 0.053898 | 0.046755 | 0.047776 | 0.06452 | 0.06452 | 0.057378 | 0.057378 | 0.055337 | 0.055337 | 0.053296 | 0.053296 | 0.050235 | 0.049214 | 0.041051 | 0.032888 | 0.032888
| LYNDHURST | LYNDHURST | MINIMUM HEADROOM | NO 37434 32575 | NO | YES | 2.897 | 6.9839 | 7.0012 | 7.0094 | 6.9594 | 6.8788 | 6.7767 | 6.6859 | 6.5849 | 6.5257 | 6.4196 | 5.738 | 5.1839 | 4.79 | 7.5798 | 7.5971 | 7.6084 | 7.5788 | 7.5033 | 7.4431 | 7.3951 | 7.3288 | 7.3053 | 7.2247 | 6.7859 | 6.4104 | 5.9165 | 6.9058 | 6.915 | 6.9232 | 6.8844 | 6.8017 | 6.7283 | 6.6589 | 6.5701 | 6.5242 | 6.4395 | 5.8783 | 5.4007 | 5.166
|  | LYNDHURST | EE |  |  |  |  | 7.0043 | 7.0012 | 7.0094 | 6.9594 | 6.8788 | 6.7767 | 6.6859 | 6.5849 | 6.5257 | 6.4267 | 5.8033 | 5.1839 | 4.79 | 7.6073 | 7.5971 | 7.6084 | 7.5798 | 7.5033 | 7.4431 | 7.3951 | 7.3288 | 7.3053 | 7.241 | 6.7859 | 6.4104 | 6.0737 | 6.9262 | 6.915 | 6.9232 | 6.8844 | 6.8017 | 6.7283 | 6.6589 | 6.5701 | 6.5242 | 6.4395 | 5.916 | 5.4936 | 5.2426
|  | LYNDHURST | HT |  |  |  |  | 6.9941 | 7.0053 | 7.0165 | 6.9665 | 6.8829 | 6.7849 | 6.6992 | 6.6114 | 6.54 | 6.4196 | 5.738 | 5.1992 | 4.9216 | 7.59 | 7.5971 | 7.6084 | 7.5788 | 7.5053 | 7.4441 | 7.3971 | 7.3451 | 7.3084 | 7.2247 | 6.9563 | 6.6451 | 6.4778 | 6.913 | 6.9201 | 6.9293 | 6.8874 | 6.8038 | 6.7344 | 6.666 | 6.5956 | 6.5426 | 6.4426 | 5.8783 | 5.4007 | 5.166
|  | LYNDHURST | HE |  |  |  |  | 6.9839 | 7.0053 | 7.0176 | 6.9716 | 6.892 | 6.7982 | 6.7155 | 6.6288 | 6.5818 | 6.4941 | 6.0441 | 5.7482 | 5.5533 | 7.5798 | 7.5971 | 7.6094 | 7.5818 | 7.5063 | 7.4451 | 7.3971 | 7.34 | 7.3196 | 7.2573 | 7.0635 | 6.9788 | 6.7665 | 6.9058 | 6.9191 | 6.9334 | 6.8936 | 6.814 | 6.7446 | 6.6813 | 6.6058 | 6.5711 | 6.4966 | 6.1456 | 5.8977 | 5.7303
|  | LYNDHURST | FB |  |  |  |  | 7.0931 | 7.0818 | 7.0767 | 7.0686 | 7.0573 | 7.039 | 7.0257 | 7.0155 | 6.9329 | 6.9022 | 6.7206 | 6.3339 | 5.988 | 7.6992 | 7.6676 | 7.6471 | 7.6359 | 7.6227 | 7.6043 | 7.5869 | 7.5727 | 7.49 | 7.4584 | 7.2706 | 6.6359 | 5.9165 | 7.013 | 6.9956 | 6.9803 | 6.9742 | 6.965 | 6.9497 | 6.9334 | 6.9252 | 6.8436 | 6.8293 | 6.6507 | 6.2232 | 6.0385
| THURSO | LYNESS | MINIMUM HEADROOM | ND 30350 94625 | YES | NO | 0.005 | 0.19286 | 0.1898 | 0.18469 | 0.16939 | 0.1551 | -0.02449 | -0.05102 | -0.24286 | -0.2949 | -0.33163 | -0.58469 | -0.61735 | -0.63673 | 0.068367 | 0.068367 | 0.064286 | 0.061224 | 0.057143 | -0.05 | -0.062245 | -0.25102 | -0.27755 | -0.32041 | -0.54796 | -0.53469 | -0.52245 | 0.16633 | 0.16735 | 0.16122 | 0.13878 | 0.11327 | -0.067347 | -0.088776 | -0.28878 | -0.32959 | -0.36939 | -0.5949 | -0.6102 | -0.61837
|  | LYNESS | EE |  |  |  |  | 0.19286 | 0.19082 | 0.18571 | 0.17245 | 0.16122 | 0.13571 | 0.10204 | -0.095918 | -0.2949 | -0.33163 | -0.58469 | -0.61735 | -0.63163 | 0.068367 | 0.068367 | 0.064286 | 0.061224 | 0.057143 | 0.05102 | 0.043878 | -0.093878 | -0.27551 | -0.30408 | -0.54796 | -0.53469 | -0.51939 | 0.16633 | 0.16837 | 0.16122 | 0.14082 | 0.11735 | 0.09898 | 0.071429 | -0.13878 | -0.32959 | -0.36429 | -0.5949 | -0.6102 | -0.6102
|  | LYNESS | HT |  |  |  |  | 0.19286 | 0.1898 | 0.18469 | 0.17245 | 0.16122 | -0.02449 | -0.05102 | -0.24286 | -0.27857 | -0.33061 | -0.53571 | -0.57653 | -0.63673 | 0.068367 | 0.068367 | 0.064286 | 0.061224 | 0.057143 | -0.05 | -0.062245 | -0.25102 | -0.27755 | -0.32041 | -0.51735 | -0.50918 | -0.52245 | 0.16735 | 0.16735 | 0.16122 | 0.14082 | 0.11735 | -0.067347 | -0.088776 | -0.28878 | -0.31939 | -0.36939 | -0.56939 | -0.57653 | -0.61837
|  | LYNESS | HE |  |  |  |  | 0.19286 | 0.1898 | 0.18469 | 0.16939 | 0.1551 | 0.13163 | 0.096939 | 0.073469 | 0.05 | 0.026531 | -0.020408 | -0.071429 | -0.10816 | 0.068367 | 0.068367 | 0.064286 | 0.061224 | 0.057143 | 0.05102 | 0.043878 | 0.030612 | 0.02551 | 0.016327 | -0.0040816 | -0.010204 | -0.016327 | 0.16735 | 0.16735 | 0.16122 | 0.13878 | 0.11327 | 0.095918 | 0.069388 | 0.034694 | 0.019388 | -0.0040816 | -0.05102 | -0.069388 | -0.087755
|  | LYNESS | FB |  |  |  |  | 0.2051 | 0.20204 | 0.20408 | 0.20204 | 0.20306 | 0.2 | 0.19592 | 0.19286 | 0.18163 | 0.17245 | 0.11531 | 0.047959 | 0.02449 | 0.076531 | 0.07449 | 0.07449 | 0.072449 | 0.071429 | 0.069388 | 0.064286 | 0.065306 | 0.060204 | 0.053061 | 0.027551 | -0.012245 | -0.031633 | 0.17959 | 0.17653 | 0.17755 | 0.16939 | 0.16429 | 0.15714 | 0.14694 | 0.14286 | 0.12959 | 0.11939 | 0.068367 | -0.005102 | -0.016327
| STORNOWAY | MAARUIG | MINIMUM HEADROOM | NB 19162 06332 | YES | YES | 0.012 | 0.038041 | 0.03702 | 0.030898 | 0.025796 | 0.021714 | 0.015592 | 0.0074286 | 0.0013061 | -0.0048163 | -0.0078776 | -0.024204 | -0.033388 | -0.043592 | 0.084327 | 0.083306 | 0.081265 | 0.079224 | 0.079224 | 0.075143 | 0.074122 | 0.071061 | 0.06902 | 0.068 | 0.059837 | 0.058816 | 0.057796 | 0.062714 | 0.059653 | 0.054551 | 0.050469 | 0.047408 | 0.041286 | 0.036184 | 0.032102 | 0.02802 | 0.021898 | 0.010673 | 0.0035306 | -0.0046327
|  | MAARUIG | EE |  |  |  |  | 0.038041 | 0.03702 | 0.030898 | 0.025796 | 0.021714 | 0.015592 | 0.0074286 | 0.0033469 | -0.0037959 | -0.0078776 | -0.024204 | -0.033388 | -0.041551 | 0.084327 | 0.083306 | 0.081265 | 0.079224 | 0.079224 | 0.075143 | 0.074122 | 0.071061 | 0.06902 | 0.068 | 0.060857 | 0.059837 | 0.059837 | 0.062714 | 0.059653 | 0.054551 | 0.050469 | 0.047408 | 0.041286 | 0.036184 | 0.032102 | 0.02802 | 0.021898 | 0.010673 | 0.0035306 | 0.00046939
|  | MAARUIG | HT |  |  |  |  | 0.038041 | 0.03702 | 0.031918 | 0.025796 | 0.021714 | 0.016612 | 0.0074286 | 0.0023265 | -0.0027755 | -0.0058367 | -0.020122 | -0.032367 | -0.042571 | 0.084327 | 0.083306 | 0.081265 | 0.079224 | 0.079224 | 0.076163 | 0.074122 | 0.071061 | 0.06902 | 0.068 | 0.059837 | 0.058816 | 0.059837 | 0.062714 | 0.059653 | 0.054551 | 0.050469 | 0.048429 | 0.042306 | 0.037204 | 0.032102 | 0.029041 | 0.022918 | 0.012714 | 0.0035306 | -0.0036122
|  | MAARUIG | HE |  |  |  |  | 0.038041 | 0.03702 | 0.031918 | 0.025796 | 0.021714 | 0.015592 | 0.0074286 | 0.0013061 | -0.0048163 | -0.0068571 | -0.019102 | -0.032367 | -0.043592 | 0.084327 | 0.083306 | 0.081265 | 0.079224 | 0.079224 | 0.076163 | 0.074122 | 0.071061 | 0.06902 | 0.068 | 0.061878 | 0.059837 | 0.057796 | 0.062714 | 0.059653 | 0.054551 | 0.050469 | 0.047408 | 0.041286 | 0.036184 | 0.032102 | 0.02802 | 0.021898 | 0.013735 | 0.0035306 | -0.0046327
|  | MAARUIG | FB |  |  |  |  | 0.050286 | 0.039061 | 0.043143 | 0.042122 | 0.041102 | 0.031918 | 0.031918 | 0.027837 | 0.024776 | 0.024776 | 0.012531 | 0.00028571 | -0.0027755 | 0.09249 | 0.084327 | 0.086367 | 0.086367 | 0.086367 | 0.081265 | 0.081265 | 0.078204 | 0.076163 | 0.077184 | 0.071061 | 0.062898 | 0.058816 | 0.071898 | 0.061694 | 0.066796 | 0.064755 | 0.064755 | 0.055571 | 0.055571 | 0.05149 | 0.049449 | 0.048429 | 0.038224 | 0.02802 | 0.02598
| LYNDHURST | MACALPINE ROAD | MINIMUM HEADROOM | NO 38034 33691 | NO | YES | 1.201 | 13.45 | 13.499 | 13.5439 | 13.4235 | 13.2551 | 13.1531 | 12.9755 | 12.6847 | 12.3112 | 12.0745 | 10.5173 | 9.5602 | 9.1459 | 14.4622 | 14.4857 | 14.499 | 14.4224 | 14.2092 | 14.0571 | 13.8296 | 13.551 | 13.251 | 13.0531 | 11.9867 | 11.3622 | 10.2255 | 14.1551 | 14.1571 | 14.148 | 14.0398 | 13.8357 | 13.702 | 13.5235 | 13.2214 | 12.8684 | 12.6347 | 11.1255 | 10.2061 | 9.8214
|  | MACALPINE ROAD | EE |  |  |  |  | 13.45 | 13.499 | 13.5439 | 13.4235 | 13.2571 | 13.1531 | 12.9939 | 12.702 | 12.3357 | 12.102 | 10.5173 | 9.5602 | 9.1459 | 14.4673 | 14.4857 | 14.499 | 14.4224 | 14.2112 | 14.0571 | 13.8429 | 13.5673 | 13.2684 | 13.0776 | 11.9867 | 11.3622 | 10.9143 | 14.1551 | 14.1571 | 14.148 | 14.0398 | 13.8357 | 13.702 | 13.5265 | 13.2367 | 12.8857 | 12.6531 | 11.1255 | 10.2061 | 9.8214
|  | MACALPINE ROAD | HT |  |  |  |  | 13.451 | 13.5071 | 13.5571 | 13.4347 | 13.2592 | 13.1888 | 12.9755 | 12.6847 | 12.3112 | 12.0745 | 10.5347 | 9.8255 | 9.7602 | 14.4643 | 14.4878 | 14.499 | 14.4224 | 14.2112 | 14.1041 | 13.8327 | 13.551 | 13.251 | 13.0531 | 12.0214 | 11.7888 | 11.8051 | 14.1622 | 14.1755 | 14.1755 | 14.0541 | 13.8367 | 13.7235 | 13.5235 | 13.2214 | 12.8684 | 12.6347 | 11.1449 | 10.4469 | 10.3949
|  | MACALPINE ROAD | HE |  |  |  |  | 13.4531 | 13.5112 | 13.5612 | 13.4357 | 13.2551 | 13.1857 | 12.9939 | 12.7276 | 12.399 | 12.2204 | 11.1622 | 10.5224 | 10.3694 | 14.4622 | 14.4867 | 14.499 | 14.4224 | 14.2092 | 14.0939 | 13.8296 | 13.5663 | 13.2918 | 13.1296 | 12.3327 | 11.7867 | 11.4367 | 14.1633 | 14.1776 | 14.1796 | 14.0602 | 13.848 | 13.7367 | 13.551 | 13.2602 | 12.9398 | 12.7622 | 11.7673 | 11.1327 | 11.002
|  | MACALPINE ROAD | FB |  |  |  |  | 13.5541 | 13.6235 | 13.6969 | 13.6184 | 13.5969 | 13.5347 | 13.4939 | 13.4082 | 13.4071 | 13.3378 | 12.7735 | 11.6 | 10.6388 | 14.5367 | 14.5663 | 14.5939 | 14.55 | 14.4949 | 14.3531 | 14.2408 | 14.051 | 13.9827 | 13.8235 | 13.0367 | 11.6561 | 10.2255 | 14.2418 | 14.2704 | 14.2969 | 14.2112 | 14.1633 | 14.0857 | 14.0224 | 13.9286 | 13.8745 | 13.7867 | 13.2531 | 11.8959 | 11.1633
| MACDUFF | MACDUFF | MINIMUM HEADROOM | NJ 70363 63908 | NO | NO | 1.226 | 12.1566 | 11.7933 | 11.4903 | 11.0168 | 10.4413 | 9.5872 | 8.624 | 8.0342 | 7.1505 | 6.3699 | 2.5229 | 0.32498 | -0.91073 | 13.8046 | 13.4393 | 13.1087 | 12.7393 | 12.2648 | 11.7087 | 11.0954 | 10.8933 | 10.6168 | 10.424 | 8.3842 | 7.774 | 6.8638 | 13.0382 | 12.6923 | 12.3811 | 11.9984 | 11.5015 | 10.824 | 10.0678 | 9.5505 | 8.8423 | 8.2576 | 5.1025 | 3.5229 | 2.7168
|  | MACDUFF | EE |  |  |  |  | 12.274 | 11.7933 | 11.4974 | 11.0372 | 10.4699 | 9.6209 | 8.6607 | 8.0342 | 7.1505 | 6.6587 | 2.5229 | 0.32498 | -0.76788 | 13.9393 | 13.4393 | 13.1117 | 12.7464 | 12.2709 | 11.7107 | 11.0995 | 10.8933 | 10.6168 | 10.4454 | 8.4444 | 7.774 | 7.5525 | 13.1597 | 12.6923 | 12.3872 | 12.0087 | 11.5178 | 10.8413 | 10.0872 | 9.5505 | 8.8423 | 8.4454 | 5.1025 | 3.5229 | 2.8076
|  | MACDUFF | HT |  |  |  |  | 12.2036 | 11.8056 | 11.4903 | 11.0291 | 10.4658 | 10.0168 | 9.2811 | 8.4393 | 7.227 | 6.3699 | 2.7178 | 0.58212 | -0.91073 | 13.8576 | 13.4536 | 13.1087 | 12.7393 | 12.2648 | 12.1331 | 11.8933 | 11.626 | 11.0668 | 10.424 | 8.3842 | 7.8597 | 7.7025 | 13.0862 | 12.7066 | 12.3811 | 12.0015 | 11.5087 | 11.2291 | 10.674 | 10.0168 | 9.0342 | 8.2576 | 5.2168 | 3.7117 | 2.7168
|  | MACDUFF | HE |  |  |  |  | 12.1566 | 11.7954 | 11.4954 | 11.0168 | 10.4413 | 9.5872 | 8.624 | 8.0342 | 7.1974 | 6.7158 | 3.6872 | 1.1576 | 0.13314 | 13.8046 | 13.4403 | 13.1107 | 12.7423 | 12.2709 | 11.7087 | 11.0954 | 10.8984 | 10.6331 | 10.4729 | 8.878 | 8.1178 | 7.8076 | 13.0382 | 12.6933 | 12.3852 | 11.9984 | 11.5015 | 10.824 | 10.0678 | 9.5505 | 8.8801 | 8.4933 | 5.9546 | 4.1515 | 3.4536
|  | MACDUFF | FB |  |  |  |  | 12.6607 | 12.3525 | 11.9566 | 11.7576 | 11.3301 | 10.8423 | 10.328 | 9.6923 | 9.5076 | 9.326 | 7.9709 | 5.0974 | 3.7627 | 14.3372 | 13.975 | 13.5597 | 13.3382 | 12.9015 | 12.4117 | 11.9046 | 11.275 | 11.1607 | 11.0342 | 10.174 | 8.224 | 6.8638 | 13.5372 | 13.226 | 12.8393 | 12.6301 | 12.2413 | 11.7811 | 11.3036 | 10.7046 | 10.5678 | 10.4311 | 9.2566 | 6.4627 | 5.7484
| CARRADALE 1 | MACHRIE | MINIMUM HEADROOM | NR 90092 33864 | YES | YES | 0.035 | 1.2582 | 1.5367 | 1.5051 | 1.4724 | 1.4357 | 1.3684 | 1.3163 | 1.2439 | 1.1796 | 1.1551 | 1.0398 | 0.97959 | 0.93367 | 1.6413 | 2.1633 | 2.1561 | 2.1592 | 2.1531 | 2.1214 | 2.0969 | 2.0561 | 2.0276 | 2.0194 | 1.9541 | 1.9571 | 1.9173 | 1.4936 | 1.8908 | 1.8724 | 1.8622 | 1.8459 | 1.7959 | 1.7806 | 1.7276 | 1.6837 | 1.6724 | 1.601 | 1.5612 | 1.5337
|  | MACHRIE | EE |  |  |  |  | 1.2582 | 1.5367 | 1.5122 | 1.4724 | 1.4418 | 1.3735 | 1.3163 | 1.2439 | 1.1796 | 1.1551 | 1.0398 | 0.98776 | 0.93367 | 1.6413 | 2.1633 | 2.1582 | 2.1612 | 2.1531 | 2.1235 | 2.0969 | 2.0561 | 2.0276 | 2.0204 | 1.9684 | 1.9816 | 1.9827 | 1.4936 | 1.8908 | 1.8806 | 1.8684 | 1.85 | 1.801 | 1.7816 | 1.7276 | 1.6837 | 1.6735 | 1.601 | 1.5735 | 1.5469
|  | MACHRIE | HT |  |  |  |  | 1.2582 | 1.5367 | 1.5163 | 1.4796 | 1.4469 | 1.3827 | 1.3306 | 1.2592 | 1.1939 | 1.1714 | 1.05 | 0.98673 | 0.94184 | 1.6413 | 2.1633 | 2.1592 | 2.1602 | 2.1551 | 2.1224 | 2.1 | 2.0582 | 2.0276 | 2.0214 | 1.9541 | 1.9694 | 2.0061 | 1.4936 | 1.8918 | 1.8827 | 1.8735 | 1.8571 | 1.8102 | 1.7949 | 1.7388 | 1.6908 | 1.6837 | 1.6102 | 1.5786 | 1.5541
|  | MACHRIE | HE |  |  |  |  | 1.2602 | 1.5439 | 1.5051 | 1.4816 | 1.4357 | 1.3684 | 1.3163 | 1.2449 | 1.2122 | 1.1582 | 1.0582 | 0.97959 | 0.93469 | 1.6444 | 2.1673 | 2.1561 | 2.1592 | 2.1531 | 2.1214 | 2.0969 | 2.0571 | 2.05 | 2.0194 | 1.9704 | 1.9704 | 1.9694 | 1.4997 | 1.902 | 1.8724 | 1.8622 | 1.8459 | 1.7959 | 1.7806 | 1.7286 | 1.7071 | 1.6724 | 1.6153 | 1.5612 | 1.5337
|  | MACHRIE | FB |  |  |  |  | 1.2827 | 1.5837 | 1.5714 | 1.5612 | 1.548 | 1.5378 | 1.5184 | 1.5041 | 1.4796 | 1.4694 | 1.3684 | 1.251 | 1.2439 | 1.6719 | 2.201 | 2.198 | 2.2031 | 2.2041 | 2.2031 | 2.1878 | 2.1755 | 2.1561 | 2.1469 | 2.0776 | 1.9571 | 1.9173 | 1.5304 | 1.9469 | 1.9408 | 1.9469 | 1.95 | 1.949 | 1.9367 | 1.9276 | 1.9102 | 1.9061 | 1.8398 | 1.7388 | 1.7367
| FORT WILLIAM | MALLAIG | MINIMUM HEADROOM | NM 67637 94811 | YES | NO | 0.131 | 0.72561 | 0.73378 | 0.73888 | 0.72561 | 0.71439 | 0.56847 | 0.30214 | -0.061122 | -0.255 | -0.30806 | -0.47235 | -0.55908 | -0.62031 | 0.87051 | 0.87153 | 0.87459 | 0.86847 | 0.86133 | 0.69398 | 0.42357 | 0.04602 | -0.13561 | -0.15806 | -0.22541 | -0.21622 | -0.22439 | 0.66847 | 0.67357 | 0.68071 | 0.67255 | 0.66745 | 0.50929 | 0.25418 | -0.085612 | -0.26214 | -0.29888 | -0.39888 | -0.43561 | -0.4601
|  | MALLAIG | EE |  |  |  |  | 0.72561 | 0.73378 | 0.73888 | 0.72765 | 0.71541 | 0.67867 | 0.6348 | 0.48786 | 0.2348 | -0.14786 | -0.47235 | -0.55908 | -0.61112 | 0.87051 | 0.87153 | 0.87459 | 0.86847 | 0.86235 | 0.84908 | 0.82867 | 0.66235 | 0.38786 | 0.0072449 | -0.21418 | -0.21622 | -0.20398 | 0.66847 | 0.67357 | 0.68071 | 0.67459 | 0.66847 | 0.63684 | 0.6052 | 0.47357 | 0.21949 | -0.1448 | -0.39888 | -0.43561 | -0.45908
|  | MALLAIG | HT |  |  |  |  | 0.72663 | 0.73378 | 0.73888 | 0.72663 | 0.71541 | 0.56847 | 0.30214 | -0.061122 | -0.255 | -0.30806 | -0.455 | -0.53153 | -0.62031 | 0.87051 | 0.87153 | 0.87459 | 0.86847 | 0.86133 | 0.69398 | 0.42357 | 0.04602 | -0.13561 | -0.15806 | -0.22541 | -0.20398 | -0.19684 | 0.66847 | 0.67357 | 0.68071 | 0.67255 | 0.66847 | 0.50929 | 0.25418 | -0.085612 | -0.26214 | -0.29888 | -0.39684 | -0.42847 | -0.4601
|  | MALLAIG | HE |  |  |  |  | 0.72663 | 0.73378 | 0.73888 | 0.72561 | 0.71439 | 0.68071 | 0.6348 | 0.47153 | 0.17867 | -0.26929 | -0.45194 | -0.54786 | -0.60704 | 0.87051 | 0.87153 | 0.87459 | 0.86847 | 0.86133 | 0.8501 | 0.82969 | 0.645 | 0.33888 | -0.11112 | -0.21214 | -0.21214 | -0.2101 | 0.66847 | 0.67357 | 0.68071 | 0.67255 | 0.66745 | 0.63786 | 0.60316 | 0.45418 | 0.17051 | -0.25602 | -0.38969 | -0.42847 | -0.45704
|  | MALLAIG | FB |  |  |  |  | 0.74092 | 0.75827 | 0.77357 | 0.78276 | 0.78684 | 0.78276 | 0.7848 | 0.7848 | 0.66745 | 0.47969 | -0.18153 | -0.24276 | -0.26724 | 0.88071 | 0.89092 | 0.895 | 0.89908 | 0.9001 | 0.89602 | 0.89092 | 0.88888 | 0.75418 | 0.55214 | -0.12031 | -0.18459 | -0.22439 | 0.68378 | 0.69908 | 0.71337 | 0.72459 | 0.72969 | 0.72663 | 0.72867 | 0.72765 | 0.61031 | 0.42357 | -0.23051 | -0.28459 | -0.29378
| KEITH 1 | MARNOCH | MINIMUM HEADROOM | NJ 61955 53001 | NO | YES | 0.787 | 3.1265 | 3.0837 | 3.0143 | 2.8827 | 2.7755 | 2.6469 | 2.4867 | 2.2816 | 2.0929 | 2.1133 | 1.3347 | 1.0663 | 0.89388 | 1.9286 | 1.8816 | 1.8235 | 1.7459 | 1.6633 | 1.5857 | 1.4796 | 1.3449 | 1.2347 | 1.2878 | 0.74286 | 0.73469 | 0.76837 | 3.4786 | 3.4388 | 3.3837 | 3.2898 | 3.2378 | 3.1908 | 3.0673 | 2.9112 | 2.7582 | 2.6908 | 2.1888 | 1.9082 | 1.7235
|  | MARNOCH | EE |  |  |  |  | 3.1327 | 3.0837 | 3.0143 | 2.8878 | 2.7867 | 2.6633 | 2.502 | 2.3214 | 2.1357 | 2.1531 | 1.3347 | 1.0663 | 0.89388 | 1.9398 | 1.8816 | 1.8235 | 1.7459 | 1.6633 | 1.5857 | 1.4837 | 1.3694 | 1.25 | 1.3031 | 0.74286 | 0.73469 | 0.76837 | 3.4878 | 3.4388 | 3.3837 | 3.2929 | 3.251 | 3.2071 | 3.0857 | 2.9469 | 2.8163 | 2.7439 | 2.1888 | 1.9082 | 1.7235
|  | MARNOCH | HT |  |  |  |  | 3.1306 | 3.0847 | 3.0194 | 2.8929 | 2.7898 | 2.6704 | 2.4949 | 2.2827 | 2.0929 | 2.1133 | 1.6765 | 1.3724 | 1.1276 | 1.9337 | 1.8837 | 1.8245 | 1.7459 | 1.6643 | 1.5857 | 1.4796 | 1.3449 | 1.2347 | 1.2878 | 0.98061 | 0.97755 | 1.0245 | 3.4827 | 3.4398 | 3.3867 | 3.2959 | 3.2551 | 3.2133 | 3.0735 | 2.9112 | 2.7582 | 2.6908 | 2.3531 | 2.0408 | 1.7684
|  | MARNOCH | HE |  |  |  |  | 3.1265 | 3.0837 | 3.0173 | 2.8827 | 2.7755 | 2.6469 | 2.4867 | 2.2816 | 2.101 | 2.1194 | 1.6806 | 1.3959 | 1.2163 | 1.9286 | 1.8816 | 1.8245 | 1.7469 | 1.6633 | 1.5878 | 1.4837 | 1.3541 | 1.248 | 1.301 | 1.0316 | 1.0122 | 1.0102 | 3.4786 | 3.4398 | 3.3847 | 3.2898 | 3.2378 | 3.1908 | 3.0673 | 2.9173 | 2.7776 | 2.7061 | 2.3378 | 2.0531 | 1.8571
|  | MARNOCH | FB |  |  |  |  | 3.1969 | 3.1633 | 3.1296 | 3.0786 | 2.999 | 2.9633 | 2.8878 | 2.8306 | 2.7378 | 2.6694 | 2.3684 | 1.9582 | 1.8429 | 1.998 | 1.9582 | 1.9214 | 1.8878 | 1.8204 | 1.7796 | 1.7102 | 1.6571 | 1.5816 | 1.5204 | 1.351 | 1.0571 | 0.86939 | 3.549 | 3.5194 | 3.4867 | 3.4541 | 3.4082 | 3.3796 | 3.3357 | 3.3163 | 3.2827 | 3.2459 | 2.9337 | 2.5684 | 2.5184
| BEAULY | MARYBANK | MINIMUM HEADROOM | NH 46749 53948 | YES | NO | 1.01 | 2.9169 | 2.918 | 2.9129 | 2.8822 | 2.8373 | 2.7853 | 2.719 | 2.6588 | 2.5894 | 2.5486 | 2.3782 | 2.2118 | 2.0608 | 3.1488 | 3.1488 | 3.1416 | 3.1273 | 3.1039 | 3.0773 | 3.0406 | 3.0141 | 2.9702 | 2.9294 | 2.8253 | 2.8253 | 2.762 | 3.0829 | 3.0829 | 3.0757 | 3.0522 | 3.0165 | 2.9594 | 2.8982 | 2.8757 | 2.8135 | 2.7573 | 2.6227 | 2.5298 | 2.4604
|  | MARYBANK | EE |  |  |  |  | 2.918 | 2.92 | 2.9129 | 2.8863 | 2.8455 | 2.7853 | 2.7302 | 2.67 | 2.6027 | 2.568 | 2.3782 | 2.2118 | 2.0924 | 3.1488 | 3.1488 | 3.1427 | 3.1284 | 3.1039 | 3.0773 | 3.0406 | 3.0151 | 2.9743 | 2.9335 | 2.8416 | 2.8376 | 2.8386 | 3.0829 | 3.0849 | 3.0778 | 3.0563 | 3.0186 | 2.9594 | 2.8982 | 2.8839 | 2.8237 | 2.7716 | 2.6227 | 2.5298 | 2.4849
|  | MARYBANK | HT |  |  |  |  | 2.9169 | 2.918 | 2.9129 | 2.8863 | 2.8465 | 2.8078 | 2.7394 | 2.6802 | 2.6129 | 2.5802 | 2.4282 | 2.2353 | 2.0608 | 3.1488 | 3.1488 | 3.1416 | 3.1284 | 3.1039 | 3.0794 | 3.0427 | 3.0151 | 2.9702 | 2.9324 | 2.8253 | 2.8253 | 2.8427 | 3.0839 | 3.0839 | 3.0757 | 3.0553 | 3.0206 | 2.9727 | 2.9073 | 2.889 | 2.8288 | 2.7767 | 2.641 | 2.538 | 2.4604
|  | MARYBANK | HE |  |  |  |  | 2.9169 | 2.918 | 2.9129 | 2.8822 | 2.8373 | 2.7863 | 2.719 | 2.6588 | 2.5894 | 2.5486 | 2.421 | 2.2333 | 2.1169 | 3.1488 | 3.1488 | 3.1416 | 3.1273 | 3.1039 | 3.0773 | 3.0406 | 3.0141 | 2.9712 | 2.9294 | 2.8457 | 2.8304 | 2.809 | 3.0839 | 3.0829 | 3.0757 | 3.0522 | 3.0165 | 2.9604 | 2.9176 | 2.8757 | 2.8135 | 2.7573 | 2.6441 | 2.5298 | 2.4686
|  | MARYBANK | FB |  |  |  |  | 2.9363 | 2.9455 | 2.9547 | 2.9506 | 2.9445 | 2.9333 | 2.918 | 2.9088 | 2.8873 | 2.8639 | 2.7914 | 2.6598 | 2.618 | 3.1631 | 3.1671 | 3.1702 | 3.1682 | 3.1631 | 3.1559 | 3.1376 | 3.1304 | 3.1069 | 3.0784 | 2.9784 | 2.8437 | 2.762 | 3.1114 | 3.1196 | 3.1278 | 3.1257 | 3.1176 | 3.1063 | 3.0849 | 3.0767 | 3.0502 | 3.0216 | 2.9135 | 2.791 | 2.7767
| LUNANHEAD | MARYTON | MINIMUM HEADROOM | NO 39206 53075 | NO | YES | 1.117 | 7.8378 | 7.7357 | 7.4714 | 7.1112 | 6.8663 | 6.3327 | 5.3714 | 4.0112 | 1.4194 | 0.48673 | -3.1255 | -7.9939 | -12.3439 | 9.2949 | 9.1235 | 8.8276 | 8.4704 | 8.2918 | 7.9806 | 6.9561 | 5.7633 | 2.8735 | 1.9592 | -1.7633 | -6.7184 | -11.5602 | 8.5821 | 8.4464 | 8.1056 | 7.6607 | 7.3628 | 6.926 | 5.8617 | 4.473 | 1.4454 | 0.45663 | -3.5352 | -8.9872 | -14.0423
|  | MARYTON | EE |  |  |  |  | 7.8378 | 7.7357 | 7.4714 | 7.1357 | 6.9153 | 6.4153 | 5.5429 | 4.4806 | 3.0194 | 2.3 | -0.53673 | -5.7735 | -7.849 | 9.2949 | 9.1255 | 8.8306 | 8.4755 | 8.2969 | 8.0071 | 7.2357 | 6.2235 | 4.7092 | 4.0796 | 1.6439 | -3.5653 | -5.3418 | 8.5842 | 8.4474 | 8.1066 | 7.6607 | 7.3923 | 6.9811 | 6.1107 | 4.9842 | 3.3485 | 2.6413 | -0.20051 | -5.9689 | -8.0974
|  | MARYTON | HT |  |  |  |  | 7.8378 | 7.7357 | 7.4755 | 7.1429 | 6.9224 | 6.4163 | 5.3714 | 4.2449 | 2.5194 | 1.8082 | -1.1612 | -6.8449 | -10.8071 | 9.2959 | 9.1235 | 8.8276 | 8.4704 | 8.2929 | 7.9806 | 6.9561 | 5.8408 | 3.9643 | 3.3469 | 0.6551 | -5.0286 | -8.9949 | 8.5821 | 8.4464 | 8.1087 | 7.6689 | 7.3974 | 6.973 | 5.8617 | 4.6434 | 2.6699 | 1.9658 | -1.0668 | -7.373 | -11.826
|  | MARYTON | HE |  |  |  |  | 7.8388 | 7.7367 | 7.4714 | 7.1112 | 6.8663 | 6.3327 | 5.3847 | 4.0112 | 1.4194 | 0.48673 | -3.1255 | -7.9939 | -12.3439 | 9.2959 | 9.1245 | 8.8286 | 8.4724 | 8.2918 | 7.9888 | 7.1459 | 5.7633 | 2.8735 | 1.9592 | -1.7633 | -6.7184 | -11.5602 | 8.5832 | 8.4485 | 8.1056 | 7.6699 | 7.3628 | 6.926 | 5.977 | 4.473 | 1.4454 | 0.45663 | -3.5352 | -8.9872 | -14.0423
|  | MARYTON | FB |  |  |  |  | 7.9337 | 7.8684 | 7.7408 | 7.5969 | 7.5153 | 7.3255 | 6.901 | 6.5296 | 5.6367 | 5.2918 | 3.8561 | 1.8531 | 0.32755 | 9.3786 | 9.2265 | 9.051 | 8.8704 | 8.7439 | 8.5112 | 8.0408 | 7.6061 | 6.5316 | 6.1316 | 4.6571 | 2.5245 | 0.65 | 8.6556 | 8.5974 | 8.4077 | 8.1842 | 8.0505 | 7.7546 | 7.2842 | 6.8383 | 5.7719 | 5.3862 | 3.877 | 1.3311 | 0.093367
| STRICHEN | MAUD | MINIMUM HEADROOM | NJ 92528 47491 | NO | YES | 0.319 | 4.5039 | 4.4631 | 4.4029 | 4.2967 | 4.2018 | 3.9702 | 3.7171 | 3.4978 | 3.1386 | 2.9886 | 2.0631 | 1.4896 | 1.0284 | 5.508 | 5.4876 | 5.4518 | 5.409 | 5.3549 | 5.2671 | 5.1457 | 5.059 | 4.9243 | 4.8569 | 4.4927 | 4.4447 | 4.2947 | 5.3335 | 5.3059 | 5.2467 | 5.1835 | 5.1029 | 4.9212 | 4.7049 | 4.5559 | 4.2753 | 4.1365 | 3.311 | 2.9529 | 2.6335
|  | MAUD | EE |  |  |  |  | 4.5039 | 4.4794 | 4.4192 | 4.3222 | 4.2273 | 4.0233 | 3.7916 | 3.609 | 3.3212 | 3.1763 | 2.0631 | 1.4896 | 1.0284 | 5.508 | 5.4937 | 5.458 | 5.4171 | 5.3661 | 5.2753 | 5.1682 | 5.0927 | 4.9753 | 4.8967 | 4.4927 | 4.4447 | 4.2947 | 5.3345 | 5.3171 | 5.258 | 5.1998 | 5.1202 | 4.9559 | 4.7559 | 4.6355 | 4.4029 | 4.2651 | 3.311 | 2.9529 | 2.6335
|  | MAUD | HT |  |  |  |  | 4.5059 | 4.4631 | 4.4029 | 4.2967 | 4.2018 | 4.0171 | 3.7233 | 3.4978 | 3.1386 | 2.9886 | 2.358 | 1.7478 | 1.1876 | 5.508 | 5.4876 | 5.4518 | 5.409 | 5.3549 | 5.2671 | 5.1457 | 5.059 | 4.9243 | 4.8569 | 4.5488 | 4.5273 | 4.5457 | 5.3335 | 5.3059 | 5.2467 | 5.1835 | 5.1029 | 4.9518 | 4.7059 | 4.5559 | 4.2753 | 4.1365 | 3.5916 | 3.21 | 2.8814
|  | MAUD | HE |  |  |  |  | 4.5059 | 4.4814 | 4.4212 | 4.308 | 4.2029 | 3.9702 | 3.7171 | 3.5039 | 3.1733 | 3.011 | 2.2631 | 1.6498 | 1.2182 | 5.508 | 5.4927 | 5.4559 | 5.4151 | 5.362 | 5.2682 | 5.161 | 5.0824 | 4.958 | 4.8906 | 4.5937 | 4.561 | 4.5437 | 5.3345 | 5.3171 | 5.26 | 5.1927 | 5.109 | 4.9212 | 4.7049 | 4.5651 | 4.3008 | 4.1549 | 3.5539 | 3.159 | 2.8824
|  | MAUD | FB |  |  |  |  | 4.5845 | 4.6008 | 4.61 | 4.5804 | 4.5569 | 4.4804 | 4.4018 | 4.3396 | 4.2365 | 4.1794 | 3.6967 | 3.2182 | 3.111 | 5.5498 | 5.5529 | 5.5529 | 5.5406 | 5.5008 | 5.4518 | 5.4059 | 5.3549 | 5.2886 | 5.2498 | 5.0773 | 4.8355 | 4.661 | 5.3865 | 5.3988 | 5.3967 | 5.3712 | 5.3263 | 5.261 | 5.2182 | 5.159 | 5.0773 | 5.0324 | 4.6947 | 4.2508 | 4.1988
| DOUNREAY | MELVICH | MINIMUM HEADROOM | NC 88547 64274 | YES | NO | 0.87 | -0.19599 | -0.19803 | -0.20823 | -0.22354 | -0.25619 | -0.29089 | -0.31436 | -0.3664 | -0.39599 | -0.43987 | -0.5664 | -0.70517 | -0.82354 | 0.054012 | 0.050951 | 0.039727 | 0.041767 | 0.02238 | 0.011155 | -0.0092531 | -0.038845 | -0.049049 | -0.07558 | -0.14905 | -0.14803 | -0.18068 | -0.067416 | -0.066396 | -0.07762 | -0.084763 | -0.11129 | -0.1368 | -0.17048 | -0.21436 | -0.24293 | -0.25415 | -0.35517 | -0.43068 | -0.48476
|  | MELVICH | EE |  |  |  |  | -0.19599 | -0.19497 | -0.20109 | -0.2215 | -0.25007 | -0.28782 | -0.31231 | -0.36436 | -0.39293 | -0.43272 | -0.5664 | -0.70517 | -0.81333 | 0.054012 | 0.054012 | 0.04789 | 0.041767 | 0.02442 | 0.011155 | -0.0082327 | -0.038845 | -0.049049 | -0.07558 | -0.13476 | -0.13987 | -0.13374 | -0.067416 | -0.064355 | -0.071498 | -0.082722 | -0.10721 | -0.1368 | -0.16844 | -0.21231 | -0.23987 | -0.24905 | -0.35517 | -0.43068 | -0.47456
|  | MELVICH | HT |  |  |  |  | -0.19599 | -0.19497 | -0.20109 | -0.22252 | -0.25313 | -0.28782 | -0.31129 | -0.36231 | -0.39089 | -0.42966 | -0.5368 | -0.66844 | -0.82354 | 0.054012 | 0.054012 | 0.04789 | 0.041767 | 0.02238 | 0.012176 | -0.0092531 | -0.038845 | -0.049049 | -0.074559 | -0.14905 | -0.14803 | -0.1317 | -0.067416 | -0.064355 | -0.071498 | -0.083743 | -0.10925 | -0.13578 | -0.1664 | -0.21129 | -0.23884 | -0.24599 | -0.33782 | -0.4164 | -0.48476
|  | MELVICH | HE |  |  |  |  | -0.19599 | -0.19803 | -0.20823 | -0.22354 | -0.25619 | -0.29089 | -0.31436 | -0.3664 | -0.39599 | -0.43987 | -0.53578 | -0.67456 | -0.78884 | 0.055033 | 0.050951 | 0.039727 | 0.041767 | 0.02442 | 0.014216 | -0.0072122 | -0.038845 | -0.049049 | -0.07558 | -0.1317 | -0.14395 | -0.16333 | -0.065376 | -0.066396 | -0.07762 | -0.084763 | -0.11129 | -0.13476 | -0.17048 | -0.21436 | -0.24293 | -0.25415 | -0.33374 | -0.4215 | -0.48374
|  | MELVICH | FB |  |  |  |  | -0.17354 | -0.17048 | -0.16946 | -0.1664 | -0.16742 | -0.18374 | -0.19089 | -0.19803 | -0.21436 | -0.2266 | -0.29191 | -0.38578 | -0.41333 | 0.070339 | 0.070339 | 0.066257 | 0.071359 | 0.068298 | 0.055033 | 0.04789 | 0.041767 | 0.02442 | 0.016257 | -0.044967 | -0.13476 | -0.18068 | -0.044967 | -0.040886 | -0.039865 | -0.038845 | -0.036804 | -0.05109 | -0.056192 | -0.064355 | -0.078641 | -0.088845 | -0.16027 | -0.25313 | -0.26538
| CHARLESTON | MENZIESHILL | MINIMUM HEADROOM | NO 35918 31022 | NO | YES | 2.08 | 10.514 | 10.061 | 9.8681 | 9.7783 | 9.6018 | 9.2528 | 8.8569 | 8.4405 | 8.0293 | 7.6089 | 5.5803 | 4.1232 | 3.2508 | 9.4293 | 8.9752 | 8.7916 | 8.7824 | 8.713 | 8.6528 | 8.5252 | 8.3834 | 8.0599 | 7.6875 | 6.5161 | 5.8487 | 4.9375 | 9.8992 | 9.437 | 9.2339 | 9.1655 | 9.0074 | 8.788 | 8.4951 | 8.1768 | 7.8635 | 7.3737 | 5.5268 | 4.289 | 3.5543
|  | MENZIESHILL | EE |  |  |  |  | 10.5344 | 10.061 | 9.8681 | 9.7783 | 9.611 | 9.2528 | 8.8569 | 8.4405 | 8.0293 | 7.6089 | 5.5803 | 4.1232 | 3.2508 | 9.4671 | 8.9763 | 8.7956 | 8.7865 | 8.7181 | 8.6569 | 8.5314 | 8.3834 | 8.0661 | 7.6875 | 6.5161 | 5.8487 | 5.2803 | 9.9237 | 9.437 | 9.2339 | 9.1686 | 9.0247 | 8.788 | 8.4951 | 8.1768 | 7.8635 | 7.3737 | 5.5268 | 4.289 | 3.5543
|  | MENZIESHILL | HT |  |  |  |  | 10.5232 | 10.0926 | 9.9038 | 9.811 | 9.6303 | 9.314 | 8.9263 | 8.5222 | 8.1028 | 7.6793 | 5.6099 | 4.2844 | 3.5997 | 9.4416 | 8.9885 | 8.7916 | 8.7824 | 8.713 | 8.6701 | 8.5334 | 8.3844 | 8.0599 | 7.6997 | 6.5712 | 6.3201 | 6.1681 | 9.9125 | 9.4727 | 9.2686 | 9.1982 | 9.039 | 8.8227 | 8.5227 | 8.2043 | 7.8737 | 7.4349 | 5.5962 | 4.6196 | 4.1982
|  | MENZIESHILL | HE |  |  |  |  | 10.514 | 10.0722 | 9.8905 | 9.7814 | 9.6018 | 9.2916 | 8.9487 | 8.6028 | 8.2314 | 7.9201 | 6.4395 | 5.3681 | 4.6548 | 9.4293 | 8.9752 | 8.7936 | 8.7834 | 8.714 | 8.6528 | 8.5252 | 8.3885 | 8.0854 | 7.7905 | 6.9252 | 6.3712 | 5.8477 | 9.8992 | 9.4451 | 9.2441 | 9.1655 | 9.0074 | 8.7911 | 8.5237 | 8.2431 | 7.9523 | 7.6227 | 6.3268 | 5.4686 | 4.9135
|  | MENZIESHILL | FB |  |  |  |  | 10.6793 | 10.4171 | 10.2416 | 10.1763 | 10.0926 | 9.9793 | 9.9008 | 9.813 | 9.7252 | 9.615 | 9.0252 | 7.8354 | 6.7742 | 9.5946 | 9.3334 | 9.1171 | 9.064 | 9.0048 | 8.9222 | 8.862 | 8.7967 | 8.7589 | 8.6814 | 7.9354 | 6.411 | 4.9375 | 10.0829 | 9.8309 | 9.638 | 9.5533 | 9.4829 | 9.3758 | 9.2931 | 9.2013 | 9.1166 | 9.0043 | 8.4329 | 7.0033 | 6.2431
| KINTORE | METHLICK | MINIMUM HEADROOM | NJ 85339 36835 | NO | YES | 0.241 | 4.5153 | 6.188 | 6.14 | 6.0369 | 5.9512 | 5.8145 | 5.6818 | 5.5431 | 5.4114 | 5.2706 | 5.0951 | 4.7512 | 4.4145 | 4.7898 | 6.4798 | 6.4696 | 6.4114 | 6.339 | 6.2359 | 6.1441 | 6.0369 | 5.9237 | 5.8288 | 5.7359 | 5.7471 | 5.8022 | 4.649 | 6.3278 | 6.2839 | 6.1839 | 6.0971 | 5.988 | 5.8747 | 5.7502 | 5.6288 | 5.5063 | 5.3808 | 5.2563 | 5.0727
|  | METHLICK | EE |  |  |  |  | 4.5153 | 6.188 | 6.14 | 6.0369 | 5.9614 | 5.8267 | 5.6971 | 5.5573 | 5.4257 | 5.2869 | 5.0951 | 4.7512 | 4.4308 | 4.7898 | 6.4798 | 6.4696 | 6.4114 | 6.339 | 6.2359 | 6.1441 | 6.04 | 5.9441 | 5.8318 | 5.7839 | 5.7971 | 5.8359 | 4.65 | 6.3278 | 6.2839 | 6.189 | 6.1033 | 5.9971 | 5.8839 | 5.7584 | 5.642 | 5.5176 | 5.3808 | 5.2716 | 5.0869
|  | METHLICK | HT |  |  |  |  | 4.5163 | 6.19 | 6.1451 | 6.0461 | 5.9716 | 5.839 | 5.7073 | 5.5584 | 5.4124 | 5.2941 | 5.1257 | 4.8461 | 4.4145 | 4.7908 | 6.4798 | 6.4696 | 6.4114 | 6.341 | 6.238 | 6.1441 | 6.0369 | 5.9237 | 5.8288 | 5.7359 | 5.7471 | 5.8022 | 4.649 | 6.3288 | 6.2869 | 6.1931 | 6.1114 | 5.988 | 5.889 | 5.7594 | 5.6288 | 5.5206 | 5.3818 | 5.2563 | 5.0727
|  | METHLICK | HE |  |  |  |  | 4.5153 | 6.188 | 6.142 | 6.0451 | 5.9512 | 5.8145 | 5.6818 | 5.5431 | 5.4114 | 5.2706 | 5.1451 | 4.8124 | 4.5073 | 4.7898 | 6.4798 | 6.4706 | 6.4114 | 6.339 | 6.2369 | 6.1451 | 6.04 | 5.9451 | 5.8349 | 5.7849 | 5.7941 | 5.8165 | 4.649 | 6.3278 | 6.2849 | 6.1839 | 6.0971 | 5.988 | 5.8747 | 5.7502 | 5.6349 | 5.5063 | 5.4104 | 5.2951 | 5.1206
|  | METHLICK | FB |  |  |  |  | 4.5694 | 6.2492 | 6.239 | 6.2063 | 6.1676 | 6.1012 | 6.0696 | 6.0196 | 5.9461 | 5.8992 | 5.6073 | 5.5033 | 5.4318 | 4.8245 | 6.5155 | 6.5145 | 6.5135 | 6.5043 | 6.442 | 6.4114 | 6.3522 | 6.2829 | 6.24 | 6.0084 | 5.9502 | 5.8971 | 4.701 | 6.3829 | 6.3716 | 6.339 | 6.2992 | 6.2329 | 6.2033 | 6.141 | 6.0716 | 6.0257 | 5.7747 | 5.6624 | 5.6318
| SHETLAND | MID YELL | MINIMUM HEADROOM | HU4817291442 | YES | YES | 0.007 | -0.061224 | -0.070408 | -0.081633 | -0.13469 | -0.15816 | -0.21735 | -0.28673 | -0.35408 | -0.42653 | -0.46939 | -0.60204 | -0.74694 | -0.85306 | 0.19082 | 0.18673 | 0.18469 | 0.17143 | 0.16122 | 0.13469 | 0.1102 | 0.088776 | 0.061224 | 0.031633 | -0.030612 | -0.035714 | -0.041837 | 0.10102 | 0.091837 | 0.085714 | 0.05102 | 0.026531 | -0.021429 | -0.063265 | -0.094898 | -0.14694 | -0.18571 | -0.27551 | -0.34898 | -0.4102
|  | MID YELL | EE |  |  |  |  | -0.059184 | -0.067347 | -0.078571 | -0.13061 | -0.14592 | -0.21429 | -0.28571 | -0.35306 | -0.42653 | -0.46837 | -0.60204 | -0.74694 | -0.85306 | 0.19286 | 0.18673 | 0.18469 | 0.17143 | 0.16122 | 0.13469 | 0.11122 | 0.090816 | 0.063265 | 0.032653 | -0.021429 | -0.019388 | -0.014286 | 0.10408 | 0.093878 | 0.085714 | 0.053061 | 0.031633 | -0.021429 | -0.05 | -0.092857 | -0.14694 | -0.18469 | -0.27551 | -0.34898 | -0.40918
|  | MID YELL | HT |  |  |  |  | -0.059184 | -0.067347 | -0.076531 | -0.11837 | -0.15816 | -0.19694 | -0.26327 | -0.32755 | -0.39388 | -0.4398 | -0.53061 | -0.69796 | -0.85102 | 0.19286 | 0.18673 | 0.18469 | 0.17143 | 0.16327 | 0.13776 | 0.11327 | 0.090816 | 0.063265 | 0.033673 | -0.030612 | -0.035714 | -0.021429 | 0.10306 | 0.093878 | 0.087755 | 0.059184 | 0.040816 | -0.014286 | -0.063265 | -0.081633 | -0.13163 | -0.17041 | -0.24592 | -0.32653 | -0.4102
|  | MID YELL | HE |  |  |  |  | -0.061224 | -0.070408 | -0.081633 | -0.13469 | -0.15714 | -0.21735 | -0.28673 | -0.35408 | -0.42347 | -0.46939 | -0.54184 | -0.71429 | -0.82551 | 0.19082 | 0.18673 | 0.18469 | 0.17143 | 0.16122 | 0.14184 | 0.1102 | 0.088776 | 0.061224 | 0.031633 | -0.018367 | -0.034694 | -0.041837 | 0.10102 | 0.091837 | 0.085714 | 0.05102 | 0.026531 | -0.018367 | -0.05102 | -0.094898 | -0.14694 | -0.18571 | -0.24898 | -0.3398 | -0.4
|  | MID YELL | FB |  |  |  |  | -0.034694 | -0.030612 | -0.027551 | -0.028571 | -0.035714 | -0.042857 | -0.058163 | -0.064286 | -0.07449 | -0.089796 | -0.18367 | -0.24082 | -0.27857 | 0.21224 | 0.21224 | 0.21122 | 0.20816 | 0.2051 | 0.19694 | 0.18061 | 0.17551 | 0.16224 | 0.14388 | 0.07449 | -0.0020408 | -0.038776 | 0.13265 | 0.13061 | 0.13265 | 0.12959 | 0.12755 | 0.11735 | 0.1 | 0.092857 | 0.082653 | 0.061224 | -0.02551 | -0.12143 | -0.14082
| KINTORE | MIDMAR | MINIMUM HEADROOM | NJ 68253 06875 | YES | YES | 0.445 | 3.2837 | 3.2337 | 3.1561 | 4.9335 | 4.8702 | 4.6916 | 4.4988 | 4.3927 | 4.2202 | 4.0733 | 3.4202 | 2.9049 | 2.56 | 3.8755 | 3.8398 | 3.7765 | 5.6488 | 5.609 | 5.5253 | 5.411 | 5.4018 | 5.2998 | 5.1753 | 4.6447 | 4.5763 | 4.6192 | 3.574 | 3.525 | 3.4352 | 5.2702 | 5.1814 | 5.0345 | 4.8569 | 4.8192 | 4.6661 | 4.5212 | 3.8957 | 3.5967 | 3.3927
|  | MIDMAR | EE |  |  |  |  | 3.2847 | 3.2551 | 3.1796 | 4.9335 | 4.8702 | 4.7304 | 4.5518 | 4.4559 | 4.2906 | 4.1549 | 3.4202 | 2.9049 | 2.56 | 3.8786 | 3.85 | 3.7898 | 5.6539 | 5.6151 | 5.5335 | 5.4222 | 5.4151 | 5.3039 | 5.1794 | 4.6447 | 4.5763 | 4.6192 | 3.575 | 3.5403 | 3.4536 | 5.2702 | 5.1835 | 5.0488 | 4.8753 | 4.8447 | 4.6906 | 4.5498 | 3.8957 | 3.5967 | 3.3927
|  | MIDMAR | HT |  |  |  |  | 3.2837 | 3.2337 | 3.1561 | 4.9365 | 4.8743 | 4.7233 | 4.5539 | 4.4702 | 4.3182 | 4.1814 | 3.7682 | 3.2478 | 2.7182 | 3.8755 | 3.8398 | 3.7765 | 5.6488 | 5.609 | 5.5253 | 5.412 | 5.4069 | 5.3018 | 5.1753 | 4.8008 | 4.8131 | 4.8733 | 3.574 | 3.525 | 3.4352 | 5.2702 | 5.1876 | 5.0488 | 4.8794 | 4.8518 | 4.7059 | 4.5631 | 4.1447 | 3.8957 | 3.6151
|  | MIDMAR | HE |  |  |  |  | 3.2837 | 3.2571 | 3.1949 | 4.9447 | 4.8702 | 4.6916 | 4.4988 | 4.3927 | 4.2202 | 4.0733 | 3.711 | 3.1927 | 2.8447 | 3.8755 | 3.85 | 3.7908 | 5.658 | 5.6182 | 5.5263 | 5.411 | 5.4018 | 5.2998 | 5.1753 | 4.8651 | 4.8773 | 4.8835 | 3.575 | 3.5423 | 3.4617 | 5.2773 | 5.1814 | 5.0345 | 4.8569 | 4.8192 | 4.6661 | 4.5212 | 4.1692 | 3.8702 | 3.6569
|  | MIDMAR | FB |  |  |  |  | 3.3704 | 3.3735 | 3.3684 | 5.1855 | 5.1743 | 5.1202 | 5.0569 | 5.0039 | 4.9427 | 4.8794 | 4.6376 | 4.3324 | 4.2294 | 3.9418 | 3.9306 | 3.9112 | 5.8049 | 5.7773 | 5.7396 | 5.6773 | 5.6284 | 5.5702 | 5.4998 | 5.3559 | 5.0712 | 4.9049 | 3.6372 | 3.6291 | 3.6179 | 5.4712 | 5.4294 | 5.3733 | 5.2896 | 5.2437 | 5.1702 | 5.0804 | 4.8886 | 4.5467 | 4.5039
| BRIDGE OF DUN | MILL RD | MINIMUM HEADROOM | NO 71317 57683 | NO | NO | 0 | 5.6959 | 5.7367 | 5.5918 | 5.3806 | 4.9602 | 4.3357 | 2.5765 | 0.63367 | -2.8827 | -3.848 | -8.6245 | -19.9112 | -28.951 | 7.1276 | 7.1224 | 6.8051 | 6.5418 | 6.1214 | 5.5612 | 3.5051 | 1.2633 | -2.9071 | -3.8745 | -8.8582 | -21.8735 | -32.6898 | 6.4217 | 6.4145 | 6.0554 | 5.7747 | 5.3676 | 4.7656 | 2.6952 | 0.40944 | -3.7895 | -4.7885 | -10.1028 | -23.6293 | -34.6599
|  | MILL RD | EE |  |  |  |  | 5.6959 | 5.7398 | 5.5918 | 5.3806 | 4.9602 | 4.3357 | 3.0949 | 1.4888 | -1.5398 | -2.4173 | -6.8133 | -17.0745 | -21.5561 | 7.1276 | 7.1367 | 6.8061 | 6.5418 | 6.1245 | 5.5612 | 4.2041 | 2.3796 | -1.1653 | -2.0316 | -6.4459 | -18.2296 | -23.2755 | 6.4217 | 6.4196 | 6.0554 | 5.7747 | 5.3676 | 4.7656 | 3.3645 | 1.4992 | -2.0773 | -2.9804 | -7.7946 | -19.9875 | -25.2089
|  | MILL RD | HT |  |  |  |  | 5.702 | 5.7367 | 5.6102 | 5.401 | 4.9745 | 4.3786 | 2.5765 | 0.76735 | -2.8827 | -3.848 | -8.6245 | -19.9112 | -28.951 | 7.1286 | 7.1224 | 6.8051 | 6.5418 | 6.1214 | 5.5827 | 3.5051 | 1.4214 | -2.9071 | -3.8745 | -8.7888 | -21.8735 | -32.6898 | 6.4278 | 6.4145 | 6.0727 | 5.7911 | 5.3768 | 4.8033 | 2.6952 | 0.56964 | -3.7895 | -4.7885 | -10.1028 | -23.6293 | -34.6599
|  | MILL RD | HE |  |  |  |  | 5.702 | 5.7551 | 5.6112 | 5.3929 | 4.9684 | 4.3541 | 3.0347 | 0.63367 | -0.10204 | -1.5806 | -8.352 | -18.4459 | -28.0745 | 7.1296 | 7.1418 | 6.8112 | 6.5469 | 6.1286 | 5.5663 | 4.0908 | 1.2633 | 0.57755 | -1.0888 | -8.8582 | -20.8122 | -32.448 | 6.4247 | 6.4278 | 6.0696 | 5.786 | 5.3737 | 4.7798 | 3.2727 | 0.40944 | -0.30281 | -1.9916 | -9.9916 | -22.2008 | -33.9508
|  | MILL RD | FB |  |  |  |  | 5.898 | 5.8204 | 5.8367 | 5.8357 | 5.8429 | 5.7551 | 4.9031 | 3.8561 | 1.799 | 1.0347 | -0.88878 | -4.1408 | -7.3745 | 7.3061 | 7.1918 | 7.1255 | 7.051 | 6.9724 | 6.7939 | 5.7735 | 4.5184 | 1.9878 | 1.0867 | -1.0592 | -4.6143 | -8.2592 | 6.686 | 6.5105 | 6.4462 | 6.3676 | 6.2921 | 6.1166 | 5.1207 | 3.8788 | 1.3605 | 0.48087 | -1.6375 | -5.963 | -8.6814
| ABERNETHY | MILNATHORT | MINIMUM HEADROOM | NO 11900 05074 | NO | YES | 6.312 | -1.0487 | -1.1864 | -1.414 | 21.9442 | 21.6462 | 20.736 | 19.435 | 17.5605 | 14.7003 | 13.4993 | 8.8758 | 3.0003 | -1.9109 | 2.6003 | 2.4472 | 2.1472 | 24.9901 | 24.7085 | 24.1503 | 22.8891 | 21.2197 | 18.1574 | 17.087 | 12.7248 | 7.5513 | 2.5666 | 1.1937 | 1.1243 | 0.8998 | 24.3105 | 23.9779 | 23.185 | 21.8381 | 19.934 | 16.6768 | 15.4779 | 10.7034 | 4.5523 | -0.89663
|  | MILNATHORT | EE |  |  |  |  | -1.0262 | -1.1864 | -1.3895 | 21.983 | 21.7105 | 20.8523 | 19.5952 | 18.0758 | 16.3626 | 15.5636 | 11.5656 | 5.5095 | 2.5299 | 2.6177 | 2.4493 | 2.1626 | 25.0054 | 24.7248 | 24.1952 | 23.1391 | 21.7472 | 20.1095 | 19.5064 | 16.4809 | 11.1646 | 8.9615 | 1.212 | 1.1243 | 0.9202 | 24.3381 | 24.0228 | 23.2758 | 22.0503 | 20.5095 | 18.683 | 17.9503 | 14.2799 | 8.0503 | 5.2268
|  | MILNATHORT | HT |  |  |  |  | -1.0426 | -1.1854 | -1.414 | 21.9666 | 21.6962 | 20.9217 | 19.4728 | 17.8983 | 15.9442 | 15.1177 | 11.0493 | 4.3646 | -0.73031 | 2.6074 | 2.4472 | 2.1472 | 24.9901 | 24.7085 | 24.235 | 22.8891 | 21.3901 | 19.4156 | 18.7799 | 15.3758 | 9.4799 | 5.0054 | 1.1998 | 1.1273 | 0.8998 | 24.3207 | 24.0064 | 23.3319 | 21.8381 | 20.2105 | 18.0677 | 17.3013 | 13.4177 | 6.4809 | 1.0942
|  | MILNATHORT | HE |  |  |  |  | -1.0487 | -1.1823 | -1.3977 | 21.9442 | 21.6462 | 20.736 | 19.435 | 17.5605 | 14.7003 | 13.4993 | 8.8758 | 3.0003 | -1.9109 | 2.6003 | 2.4483 | 2.1544 | 24.9942 | 24.7115 | 24.1503 | 23.0401 | 21.2197 | 18.1574 | 17.087 | 12.7248 | 7.5513 | 2.5666 | 1.1937 | 1.1273 | 0.91102 | 24.3105 | 23.9779 | 23.185 | 21.9074 | 19.934 | 16.6768 | 15.4779 | 10.7034 | 4.5523 | -0.89663
|  | MILNATHORT | FB |  |  |  |  | -0.8099 | -0.7548 | -0.78337 | 22.7891 | 22.7554 | 22.6738 | 22.2381 | 21.6544 | 20.6401 | 20.0779 | 18.1585 | 15.6034 | 13.736 | 2.7483 | 2.7472 | 2.6411 | 25.6309 | 25.5554 | 25.4268 | 24.8626 | 24.1289 | 22.8728 | 22.2115 | 20.3013 | 17.8258 | 15.6166 | 1.4161 | 1.4641 | 1.4529 | 25.133 | 25.1187 | 25.0279 | 24.4891 | 23.7564 | 22.5023 | 21.8677 | 19.9391 | 16.9493 | 15.6299
| MILTON OF CRAIGIE | MILTON OF CRAIGIE | MINIMUM HEADROOM | NO 43137 31857 | NO | NO | 6.755 | 8.9062 | 8.6419 | 8.6664 | 8.4572 | 8.0225 | 7.7133 | 7.4705 | 7.2378 | 7.0368 | 6.6888 | 4.8786 | 3.6705 | 2.9623 | 10.1878 | 9.7766 | 9.7735 | 9.6399 | 9.1715 | 8.8256 | 8.6052 | 8.4021 | 8.2307 | 7.8378 | 6.5939 | 5.9593 | 5.2695 | 10.4256 | 10.2195 | 10.2205 | 10.0419 | 9.6286 | 9.2521 | 8.9878 | 8.7174 | 8.4705 | 8.0358 | 6.3756 | 5.3797 | 4.7205
|  | MILTON OF CRAIGIE | EE |  |  |  |  | 8.9317 | 8.6419 | 8.6664 | 8.5246 | 8.097 | 7.7133 | 7.4705 | 7.2378 | 7.0368 | 6.7776 | 4.8786 | 3.6705 | 2.9623 | 10.2123 | 9.7776 | 9.7868 | 9.6756 | 9.2103 | 8.848 | 8.6327 | 8.4256 | 8.2307 | 7.9378 | 6.5939 | 5.9593 | 5.4093 | 10.4582 | 10.2195 | 10.2205 | 10.0695 | 9.6776 | 9.2593 | 8.9888 | 8.7174 | 8.4705 | 8.1225 | 6.3756 | 5.3797 | 4.7205
|  | MILTON OF CRAIGIE | HT |  |  |  |  | 8.9215 | 8.6542 | 8.6674 | 8.4572 | 8.0225 | 7.8021 | 7.5766 | 7.3552 | 7.1664 | 6.6888 | 4.9613 | 3.9409 | 3.4817 | 10.197 | 9.7797 | 9.7735 | 9.6399 | 9.1715 | 8.9419 | 8.7154 | 8.5072 | 8.3317 | 7.8378 | 6.7052 | 6.3195 | 6.1337 | 10.445 | 10.245 | 10.2327 | 10.0419 | 9.6286 | 9.3439 | 9.0674 | 8.8082 | 8.5868 | 8.0358 | 6.4297 | 5.5868 | 5.2276
|  | MILTON OF CRAIGIE | HE |  |  |  |  | 8.9062 | 8.649 | 8.6817 | 8.5113 | 8.0909 | 7.7225 | 7.5021 | 7.2858 | 7.1613 | 6.9613 | 5.6093 | 4.746 | 4.1919 | 10.1878 | 9.7766 | 9.7858 | 9.6644 | 9.198 | 8.8256 | 8.6052 | 8.4021 | 8.2725 | 8.0266 | 7.0858 | 6.5082 | 6.0521 | 10.4256 | 10.2317 | 10.2307 | 10.0654 | 9.6695 | 9.2521 | 8.9878 | 8.7368 | 8.5644 | 8.2878 | 7.0888 | 6.346 | 5.8919
|  | MILTON OF CRAIGIE | FB |  |  |  |  | 9.0674 | 9.0297 | 8.8756 | 8.8307 | 8.6807 | 8.5031 | 8.3225 | 8.1827 | 8.1031 | 8.0215 | 7.4582 | 6.1695 | 5.2103 | 10.3031 | 10.2327 | 9.8919 | 9.8337 | 9.6766 | 9.5062 | 9.2756 | 9.0705 | 8.9593 | 8.8062 | 8.0725 | 6.6746 | 5.2695 | 10.5858 | 10.5133 | 10.4052 | 10.3399 | 10.1348 | 9.9419 | 9.7786 | 9.6786 | 9.6154 | 9.4766 | 8.797 | 7.2746 | 6.4276
| STRICHEN | MINTLAW | MINIMUM HEADROOM | NK 00897 48662 | NO | YES | 2.232 | 6.9641 | 6.6049 | 6.1937 | 5.7243 | 5.4855 | 4.8804 | 4.2253 | 3.5733 | 2.9375 | 1.4926 | 0.12938 | -0.95838 | -1.7012 | 8.061 | 7.7273 | 7.3937 | 7.0508 | 6.9569 | 6.8294 | 6.611 | 6.3069 | 6.0233 | 5.5039 | 4.7467 | 4.5784 | 4.4733 | 7.6411 | 7.3442 | 6.988 | 6.6125 | 6.4238 | 5.8993 | 5.3829 | 4.8717 | 4.335 | 3.2901 | 2.134 | 1.3942 | 0.99009
|  | MINTLAW | EE |  |  |  |  | 7.0243 | 6.6049 | 6.2018 | 5.7243 | 5.4977 | 4.9069 | 4.2886 | 3.6641 | 3.0804 | 1.5722 | 0.12938 | -0.95838 | -1.6247 | 8.1365 | 7.7273 | 7.4059 | 7.0539 | 6.9671 | 6.8335 | 6.6661 | 6.3467 | 6.0977 | 5.5182 | 4.8161 | 4.5784 | 4.4733 | 7.6952 | 7.3452 | 7.0023 | 6.6125 | 6.4319 | 5.9248 | 5.4421 | 4.9289 | 4.4717 | 3.3309 | 2.134 | 1.3942 | 1.0044
|  | MINTLAW | HT |  |  |  |  | 6.9886 | 6.6202 | 6.1937 | 5.7294 | 5.4855 | 4.912 | 4.2304 | 3.6263 | 3.0284 | 1.5875 | 0.30489 | -0.88287 | -1.7012 | 8.0906 | 7.7416 | 7.3937 | 7.0508 | 6.9569 | 6.8335 | 6.611 | 6.3069 | 6.0233 | 5.5039 | 4.7467 | 4.5957 | 4.6508 | 7.6656 | 7.3554 | 6.988 | 6.6156 | 6.4238 | 5.935 | 5.3829 | 4.8962 | 4.4003 | 3.3401 | 2.2156 | 1.4432 | 0.99009
|  | MINTLAW | HE |  |  |  |  | 6.9641 | 6.6069 | 6.2049 | 5.7314 | 5.512 | 4.8804 | 4.2253 | 3.5733 | 2.9375 | 1.4926 | 0.47529 | -0.51858 | -1.1339 | 8.061 | 7.7273 | 7.4049 | 7.0539 | 6.9651 | 6.8294 | 6.6559 | 6.3396 | 6.0233 | 5.5233 | 4.9773 | 4.8559 | 4.6569 | 7.6411 | 7.3442 | 7.0054 | 6.6176 | 6.4411 | 5.8993 | 5.3993 | 4.8717 | 4.335 | 3.2901 | 2.4278 | 1.8105 | 1.4013
|  | MINTLAW | FB |  |  |  |  | 7.2733 | 7.0335 | 6.7192 | 6.4712 | 6.2375 | 5.962 | 5.712 | 5.5192 | 5.409 | 4.4498 | 3.8998 | 3.2886 | 2.8141 | 8.3508 | 8.0784 | 7.7651 | 7.5549 | 7.3569 | 7.2008 | 7.0712 | 6.9753 | 6.9467 | 6.6926 | 6.3467 | 5.7722 | 5.0365 | 7.9411 | 7.7095 | 7.4595 | 7.2574 | 7.0554 | 6.834 | 6.6268 | 6.4656 | 6.3972 | 5.7248 | 5.2238 | 4.6023 | 4.0738
| BRIDGE OF DUN | MONTROSE NORTH | MINIMUM HEADROOM | NO 71226 59070 | NO | NO | 0.764 | 4.1946 | 3.8375 | 3.8079 | 27.3058 | 27.1548 | 26.8477 | 26.5477 | 26.1069 | 25.6813 | 25.2834 | 23.5732 | 22.4334 | 21.7171 | 5.0722 | 4.7446 | 4.7181 | 27.6946 | 27.5915 | 27.4385 | 27.2824 | 27.0548 | 26.8589 | 26.6711 | 26.0497 | 25.6048 | 25.3211 | 4.687 | 4.3716 | 4.3104 | 27.8711 | 27.7497 | 27.5405 | 27.2966 | 26.9773 | 26.6671 | 26.4089 | 24.8732 | 23.9007 | 23.3548
|  | MONTROSE NORTH | EE |  |  |  |  | 4.6518 | 3.913 | 3.8079 | 27.3079 | 27.1732 | 26.8477 | 26.5558 | 26.1477 | 25.7701 | 25.4262 | 23.5732 | 22.4334 | 21.7171 | 5.6171 | 4.8456 | 4.7181 | 27.6956 | 27.5946 | 27.4415 | 27.3028 | 27.0956 | 26.9283 | 26.7599 | 26.0885 | 25.6569 | 25.3211 | 5.1737 | 4.4451 | 4.3104 | 27.8711 | 27.7681 | 27.5405 | 27.3099 | 27.016 | 26.7456 | 26.5028 | 24.8732 | 23.9446 | 23.3548
|  | MONTROSE NORTH | HT |  |  |  |  | 4.3824 | 3.8375 | 3.8262 | 27.3242 | 27.1803 | 26.862 | 26.5477 | 26.1069 | 25.6813 | 25.2834 | 23.6303 | 22.513 | 22.1885 | 5.3007 | 4.7446 | 4.7201 | 27.6977 | 27.5915 | 27.4385 | 27.2824 | 27.0548 | 26.8589 | 26.6711 | 26.0497 | 25.6048 | 25.7569 | 4.8921 | 4.3716 | 4.3349 | 27.8926 | 27.7752 | 27.5446 | 27.2966 | 26.9773 | 26.6671 | 26.4089 | 24.9069 | 23.9007 | 23.7436
|  | MONTROSE NORTH | HE |  |  |  |  | 4.1946 | 3.9262 | 3.8283 | 27.3058 | 27.1548 | 26.8609 | 26.6089 | 26.2538 | 25.9313 | 25.6589 | 24.3466 | 23.4048 | 22.9018 | 5.0722 | 4.8487 | 4.7201 | 27.6946 | 27.5926 | 27.4385 | 27.3007 | 27.1007 | 26.9375 | 26.7997 | 26.2977 | 26.1222 | 25.9936 | 4.687 | 4.4574 | 4.3288 | 27.8711 | 27.7497 | 27.5426 | 27.3354 | 27.0711 | 26.8334 | 26.6283 | 25.5732 | 24.8497 | 24.464
|  | MONTROSE NORTH | FB |  |  |  |  | 5.662 | 4.815 | 4.4252 | 27.7344 | 27.6232 | 27.4813 | 27.3895 | 27.313 | 27.2089 | 27.1915 | 26.6079 | 25.4293 | 24.5242 | 6.7028 | 5.7783 | 5.3211 | 28.0518 | 27.9089 | 27.7946 | 27.7099 | 27.6395 | 27.5762 | 27.5334 | 27.1364 | 26.3558 | 25.4201 | 6.2257 | 5.3676 | 4.9298 | 28.2803 | 28.1242 | 28.0007 | 27.9201 | 27.8405 | 27.7538 | 27.6987 | 27.1977 | 26.116 | 25.466
| TARLAND | MOSSAT | MINIMUM HEADROOM | NJ 47470 19897 | NO | NO | 2.09 | 0.22712 | 0.14957 | 4.5851 | 4.4779 | 4.4126 | 4.3014 | 4.1361 | 3.982 | 3.831 | 3.8218 | 3.4616 | 3.1065 | 2.7494 | 0.76794 | 0.69957 | 4.7463 | 4.6626 | 4.6402 | 4.58 | 4.4871 | 4.3983 | 4.3269 | 4.3575 | 4.1371 | 4.132 | 4.0412 | 0.55569 | 0.48018 | 4.7218 | 4.6096 | 4.5534 | 4.4922 | 4.3616 | 4.2392 | 4.1177 | 4.1208 | 3.8412 | 3.6208 | 3.4269
|  | MOSSAT | EE |  |  |  |  | 0.22916 | 0.14957 | 4.5851 | 4.4953 | 4.4453 | 4.3483 | 4.1953 | 4.0534 | 3.9147 | 3.9034 | 3.4616 | 3.1065 | 2.7626 | 0.76794 | 0.69957 | 4.7463 | 4.6637 | 4.6402 | 4.5871 | 4.4932 | 4.4075 | 4.33 | 4.3708 | 4.1637 | 4.1494 | 4.1075 | 0.55569 | 0.48018 | 4.7218 | 4.6218 | 4.579 | 4.5218 | 4.3983 | 4.2851 | 4.1728 | 4.1779 | 3.8412 | 3.6208 | 3.4483
|  | MOSSAT | HT |  |  |  |  | 0.23324 | 0.15671 | 4.5953 | 4.4851 | 4.4616 | 4.3606 | 4.2177 | 4.082 | 3.9534 | 3.9432 | 3.582 | 3.1841 | 2.7494 | 0.77406 | 0.69957 | 4.7473 | 4.6647 | 4.6432 | 4.5881 | 4.4973 | 4.4106 | 4.3341 | 4.3657 | 4.1371 | 4.1698 | 4.1841 | 0.5608 | 0.48529 | 4.729 | 4.629 | 4.5892 | 4.53 | 4.4147 | 4.3034 | 4.1983 | 4.2014 | 3.9065 | 3.6647 | 3.4534
|  | MOSSAT | HE |  |  |  |  | 0.22712 | 0.15365 | 4.5881 | 4.4779 | 4.4126 | 4.3014 | 4.1361 | 3.982 | 3.831 | 3.8218 | 3.532 | 3.133 | 2.8432 | 0.76998 | 0.69957 | 4.7463 | 4.6626 | 4.6402 | 4.58 | 4.4871 | 4.3983 | 4.3269 | 4.3575 | 4.1698 | 4.132 | 4.0565 | 0.55569 | 0.48324 | 4.7249 | 4.6096 | 4.5534 | 4.4922 | 4.3616 | 4.2392 | 4.1177 | 4.1208 | 3.883 | 3.6239 | 3.4269
|  | MOSSAT | FB |  |  |  |  | 0.32916 | 0.28222 | 4.7494 | 4.6963 | 4.6565 | 4.5902 | 4.5739 | 4.5198 | 4.4922 | 4.4402 | 4.1718 | 3.9994 | 3.8994 | 0.85161 | 0.79855 | 4.8677 | 4.8239 | 4.7912 | 4.731 | 4.6943 | 4.6371 | 4.6065 | 4.5524 | 4.3637 | 4.2024 | 4.0412 | 0.65263 | 0.60365 | 4.8759 | 4.8249 | 4.7892 | 4.7269 | 4.6943 | 4.6381 | 4.6126 | 4.5606 | 4.3657 | 4.1932 | 4.1483
| THURSO | MOUNT PLEASANT | MINIMUM HEADROOM | ND 12706 67832 | YES | NO | 1.436 | 9.3867 | 9.3888 | 9.4 | 9.298 | 9.1816 | 8.3735 | 7.6643 | 7.0469 | 6.55 | 6.1184 | 4.9806 | 4.1112 | 3.4918 | 10.2092 | 10.2245 | 10.2357 | 10.2327 | 10.2173 | 9.6827 | 9.202 | 8.7776 | 8.5541 | 8.45 | 8.0969 | 7.9643 | 7.7622 | 9.6903 | 9.6566 | 9.6015 | 9.4964 | 9.3413 | 8.7536 | 8.2199 | 7.8464 | 7.5066 | 7.2515 | 6.5015 | 5.9046 | 5.4495
|  | MOUNT PLEASANT | EE |  |  |  |  | 9.3867 | 9.3898 | 9.4 | 9.298 | 9.1816 | 8.8806 | 8.4847 | 7.6653 | 6.85 | 6.199 | 4.9806 | 4.1112 | 3.4918 | 10.2092 | 10.2255 | 10.2367 | 10.2337 | 10.2235 | 10.15 | 10.0643 | 9.6031 | 9.1265 | 8.6306 | 8.1214 | 7.9643 | 7.7622 | 9.6903 | 9.6577 | 9.6026 | 9.4964 | 9.3413 | 9.1342 | 8.8638 | 8.377 | 7.826 | 7.3352 | 6.523 | 5.9046 | 5.4495
|  | MOUNT PLEASANT | HT |  |  |  |  | 9.3867 | 9.3888 | 9.402 | 9.3031 | 9.1969 | 8.3735 | 7.6643 | 7.0469 | 6.55 | 6.2122 | 5.149 | 4.2867 | 3.6153 | 10.2092 | 10.2255 | 10.2357 | 10.2327 | 10.2235 | 9.6827 | 9.202 | 8.7776 | 8.5541 | 8.45 | 8.0969 | 8.0031 | 7.9337 | 9.6903 | 9.6566 | 9.6015 | 9.4974 | 9.3434 | 8.7536 | 8.2199 | 7.8464 | 7.5066 | 7.2699 | 6.5015 | 6.0352 | 5.5168
|  | MOUNT PLEASANT | HE |  |  |  |  | 9.3878 | 9.3888 | 9.4 | 9.3082 | 9.202 | 8.9133 | 8.5306 | 7.6622 | 6.8133 | 6.1184 | 5.3143 | 4.4888 | 4.0265 | 10.2092 | 10.2245 | 10.2357 | 10.2337 | 10.2173 | 10.1531 | 10.0673 | 9.5551 | 9.0255 | 8.4959 | 8.1592 | 8.0245 | 7.8908 | 9.6903 | 9.6566 | 9.6026 | 9.4985 | 9.3454 | 9.1423 | 8.877 | 8.3515 | 7.773 | 7.2515 | 6.6199 | 6.174 | 5.8423
|  | MOUNT PLEASANT | FB |  |  |  |  | 9.449 | 9.502 | 9.5418 | 9.5551 | 9.5694 | 9.549 | 9.5316 | 9.4888 | 9.0408 | 8.6765 | 7.4347 | 6.8408 | 6.5316 | 10.2602 | 10.299 | 10.3265 | 10.3459 | 10.3459 | 10.3265 | 10.3082 | 10.2643 | 9.8582 | 9.5092 | 8.5214 | 8.1061 | 7.7816 | 9.7423 | 9.7526 | 9.7413 | 9.7066 | 9.6291 | 9.5862 | 9.5311 | 9.4423 | 9.0638 | 8.7321 | 7.8189 | 7.1862 | 7.0648
| BEAULY | MUIR OF ORD | MINIMUM HEADROOM | NH 53420 48534 | NO | NO | 5.8 | 2.3602 | 2.2224 | 2.0949 | 1.7051 | 1.5969 | 0.06018 | -1.2786 | -2.3888 | -3.2806 | -3.8368 | -5.4296 | -6.698 | -7.7408 | 5.4888 | 5.4306 | 5.3796 | 5.2694 | 5.3092 | 4.4439 | 3.4418 | 2.7234 | 2.1847 | 1.8418 | 1.0581 | 1.0102 | 0.72038 | 4.5847 | 4.4673 | 4.3541 | 4.0724 | 4.0388 | 2.8581 | 1.6285 | 0.71222 | 0.021404 | -0.44696 | -1.6837 | -2.3898 | -3.0286
|  | MUIR OF ORD | EE |  |  |  |  | 2.3622 | 2.2224 | 2.0949 | 1.7061 | 1.5969 | 0.94385 | 0.33467 | -1.05 | -2.2786 | -3.2031 | -5.4296 | -6.698 | -7.6041 | 5.4898 | 5.4316 | 5.3806 | 5.2704 | 5.3102 | 5.1581 | 4.8908 | 3.8949 | 3.0194 | 2.3826 | 1.1551 | 1.0724 | 0.97753 | 4.5857 | 4.4683 | 4.3551 | 4.0745 | 4.0398 | 3.6183 | 3.1357 | 1.9428 | 0.87344 | 0.1163 | -1.6837 | -2.3898 | -2.9174
|  | MUIR OF ORD | HT |  |  |  |  | 2.3602 | 2.2224 | 2.0969 | 1.7051 | 1.5969 | 0.06018 | -1.2786 | -2.3888 | -3.2806 | -3.8368 | -5.1388 | -6.5368 | -7.7408 | 5.4898 | 5.4316 | 5.3796 | 5.2694 | 5.3092 | 4.4439 | 3.4418 | 2.7234 | 2.1847 | 1.8418 | 1.0581 | 1.0102 | 1.053 | 4.5847 | 4.4673 | 4.3541 | 4.0724 | 4.0388 | 2.8581 | 1.6285 | 0.71222 | 0.021404 | -0.44696 | -1.5868 | -2.3174 | -3.0286
|  | MUIR OF ORD | HE |  |  |  |  | 2.3602 | 2.2224 | 2.0969 | 1.7081 | 1.599 | 0.91018 | 0.33161 | -1.1102 | -2.3276 | -3.3143 | -4.8684 | -6.3266 | -7.1347 | 5.4888 | 5.4306 | 5.3796 | 5.2704 | 5.3092 | 5.1306 | 4.8898 | 3.9653 | 3.1714 | 2.3949 | 1.4918 | 1.399 | 1.2857 | 4.5847 | 4.4673 | 4.3541 | 4.0755 | 4.0398 | 3.5775 | 3.1336 | 1.9898 | 0.98569 | 0.097935 | -1.1857 | -2.099 | -2.597
|  | MUIR OF ORD | FB |  |  |  |  | 2.5153 | 2.4939 | 2.4836 | 2.2928 | 2.2653 | 2.2041 | 2.0326 | 1.7959 | 0.99793 | 0.37038 | -1.951 | -2.7286 | -3.1255 | 5.6 | 5.5775 | 5.5775 | 5.5183 | 5.4877 | 5.4173 | 5.3755 | 5.2336 | 4.6041 | 4.0714 | 2.252 | 1.4632 | 0.72038 | 4.7275 | 4.6785 | 4.652 | 4.5326 | 4.4918 | 4.4204 | 4.3245 | 4.1234 | 3.4785 | 2.95 | 0.8714 | 0.13263 | -0.23574
| BEAULY | MUIREND | MINIMUM HEADROOM | NH 64508 54337 | YES | NO | 0.11 | 0.19363 | 0.17118 | 0.14057 | -0.03902 | -0.088 | -0.51963 | -0.93698 | -1.2207 | -1.4023 | -1.5104 | -1.7798 | -2.1309 | -2.438 | 1.3834 | 1.3773 | 1.3549 | 1.2875 | 1.2732 | 1.0069 | 0.71608 | 0.49465 | 0.37527 | 0.33139 | 0.23955 | 0.24261 | 0.14363 | 0.87731 | 0.85588 | 0.812 | 0.69669 | 0.6569 | 0.30486 | -0.026776 | -0.25943 | -0.41759 | -0.51555 | -0.72065 | -0.9482 | -1.138
|  | MUIREND | EE |  |  |  |  | 0.19363 | 0.17118 | 0.14057 | -0.03902 | -0.084939 | -0.26861 | -0.58188 | -0.85739 | -1.1921 | -1.4268 | -1.7798 | -2.1309 | -2.4084 | 1.3844 | 1.3783 | 1.3569 | 1.2875 | 1.2742 | 1.1987 | 1.0793 | 0.85486 | 0.59873 | 0.40282 | 0.27833 | 0.26608 | 0.28139 | 0.87833 | 0.85588 | 0.812 | 0.69669 | 0.65894 | 0.52118 | 0.28751 | 0.035469 | -0.25229 | -0.45433 | -0.72065 | -0.9482 | -1.1084
|  | MUIREND | HT |  |  |  |  | 0.19465 | 0.1722 | 0.14261 | -0.038 | -0.088 | -0.51963 | -0.93698 | -1.2207 | -1.4023 | -1.4839 | -1.69 | -2.0666 | -2.438 | 1.3844 | 1.3783 | 1.3549 | 1.2875 | 1.2732 | 1.0069 | 0.71608 | 0.49465 | 0.37527 | 0.33139 | 0.23955 | 0.24261 | 0.25078 | 0.87833 | 0.85588 | 0.81302 | 0.69669 | 0.65792 | 0.30486 | -0.026776 | -0.25943 | -0.41759 | -0.50024 | -0.66351 | -0.91657 | -1.138
|  | MUIREND | HE |  |  |  |  | 0.19363 | 0.1722 | 0.14261 | -0.038 | -0.08698 | -0.31759 | -0.54514 | -0.88902 | -1.2604 | -1.5104 | -1.6849 | -2.1013 | -2.3543 | 1.3834 | 1.3773 | 1.3549 | 1.2885 | 1.2732 | 1.1824 | 1.0906 | 0.83547 | 0.5569 | 0.34363 | 0.26914 | 0.26404 | 0.25078 | 0.87731 | 0.85588 | 0.81302 | 0.69669 | 0.6569 | 0.48547 | 0.312 | 0.0099592 | -0.30229 | -0.51555 | -0.65841 | -0.93392 | -1.089
|  | MUIREND | FB |  |  |  |  | 0.25282 | 0.25588 | 0.24261 | 0.16302 | 0.15384 | 0.11506 | 0.0017959 | -0.12678 | -0.29208 | -0.48902 | -0.99412 | -1.1482 | -1.2298 | 1.4283 | 1.4253 | 1.4222 | 1.3844 | 1.3783 | 1.3447 | 1.2885 | 1.2171 | 1.0487 | 0.87935 | 0.42118 | 0.3069 | 0.14363 | 0.93241 | 0.92935 | 0.91506 | 0.83955 | 0.82833 | 0.78853 | 0.72424 | 0.62016 | 0.45792 | 0.28853 | -0.15535 | -0.31147 | -0.34922
| NAIRN | NAIRN CENTRAL | MINIMUM HEADROOM | NH 88496 56295 | NO | YES | 3.163 | 2.8261 | 2.7017 | 2.47 | 2.121 | 2.0006 | 0.80778 | -0.30957 | -1.5228 | -2.6422 | -3.3953 | -6.1514 | -8.6851 | -10.2922 | 4.4557 | 4.4119 | 4.3394 | 4.2374 | 4.2598 | 3.5843 | 2.8996 | 2.1057 | 1.3782 | 1.0261 | 0.065939 | -0.36365 | -0.72998 | 3.9471 | 3.8909 | 3.745 | 3.5124 | 3.4613 | 2.5358 | 1.6481 | 0.65012 | -0.25498 | -0.81722 | -2.7193 | -4.2223 | -5.0856
|  | NAIRN CENTRAL | EE |  |  |  |  | 2.8272 | 2.719 | 2.47 | 2.1323 | 2.0384 | 1.0945 | 0.35982 | -0.64324 | -1.7637 | -2.8963 | -6.1514 | -8.6851 | -10.2922 | 4.4557 | 4.4312 | 4.3394 | 4.2374 | 4.2639 | 3.9527 | 3.6302 | 3.0333 | 2.3425 | 1.5945 | 0.13431 | -0.36365 | -0.72182 | 3.9471 | 3.9093 | 3.745 | 3.5205 | 3.4807 | 2.8767 | 2.3562 | 1.5583 | 0.66339 | -0.27743 | -2.7193 | -4.2223 | -5.0856
|  | NAIRN CENTRAL | HT |  |  |  |  | 2.8261 | 2.718 | 2.47 | 2.1394 | 2.0374 | 0.80778 | -0.30957 | -1.5228 | -2.6422 | -3.3953 | -5.9524 | -8.4514 | -10.179 | 4.4557 | 4.4312 | 4.3404 | 4.2394 | 4.2608 | 3.5843 | 2.8996 | 2.1057 | 1.3782 | 1.0261 | 0.065939 | -0.2208 | -0.26263 | 3.9491 | 3.9103 | 3.745 | 3.5236 | 3.4797 | 2.5358 | 1.6481 | 0.65012 | -0.25498 | -0.81722 | -2.6315 | -4.0274 | -4.9336
|  | NAIRN CENTRAL | HE |  |  |  |  | 2.8272 | 2.7017 | 2.471 | 2.121 | 2.0006 | 1.0761 | 0.34757 | -0.73814 | -1.9422 | -3.1269 | -5.683 | -7.9637 | -9.1463 | 4.4568 | 4.4119 | 4.3414 | 4.2374 | 4.2598 | 3.9384 | 3.6374 | 2.9925 | 2.2414 | 1.467 | 0.269 | -0.11978 | -0.47794 | 3.9481 | 3.8909 | 3.7471 | 3.5124 | 3.4613 | 2.8613 | 2.3583 | 1.5011 | 0.5338 | -0.44886 | -2.3938 | -3.7029 | -4.3621
|  | NAIRN CENTRAL | FB |  |  |  |  | 2.9863 | 2.9649 | 2.8343 | 2.5547 | 2.5384 | 2.4557 | 2.3221 | 2.1619 | 1.7476 | 1.2823 | -0.96059 | -2.0718 | -2.6973 | 4.5812 | 4.5751 | 4.5414 | 4.3098 | 4.3057 | 4.2231 | 4.1955 | 4.0833 | 3.6966 | 3.2588 | 1.3588 | 0.24859 | -0.72998 | 4.1164 | 4.1103 | 4.0603 | 3.8236 | 3.8256 | 3.7634 | 3.7246 | 3.6011 | 3.2246 | 2.7899 | 0.76951 | -0.38865 | -0.76212
| STRICHEN | NEW PITSLIGO | MINIMUM HEADROOM | NJ 88529 54853 | NO | YES | 0.091 | 6.1084 | 6.1186 | 6.0931 | 6.0267 | 5.9369 | 5.8563 | 5.7318 | 5.6124 | 5.4635 | 5.3778 | 4.9839 | 4.6951 | 4.4053 | 6.3257 | 6.3216 | 6.3022 | 6.288 | 6.2522 | 6.2186 | 6.141 | 6.0757 | 5.9767 | 5.9084 | 5.6267 | 5.6227 | 5.5196 | 6.1665 | 6.1645 | 6.1533 | 6.1247 | 6.0553 | 5.9961 | 5.8849 | 5.7808 | 5.6502 | 5.5716 | 5.2308 | 5.1155 | 4.9308
|  | NEW PITSLIGO | EE |  |  |  |  | 6.1084 | 6.1186 | 6.0941 | 6.0318 | 5.9451 | 5.8686 | 5.7471 | 5.638 | 5.5043 | 5.4196 | 4.9839 | 4.6951 | 4.4114 | 6.3257 | 6.3227 | 6.3033 | 6.29 | 6.2553 | 6.2216 | 6.1533 | 6.0859 | 5.99 | 5.9216 | 5.6767 | 5.6737 | 5.5196 | 6.1665 | 6.1655 | 6.1533 | 6.1278 | 6.0604 | 5.9961 | 5.8961 | 5.7982 | 5.6808 | 5.6002 | 5.2502 | 5.1522 | 4.9308
|  | NEW PITSLIGO | HT |  |  |  |  | 6.1094 | 6.1186 | 6.0931 | 6.0298 | 5.9441 | 5.8706 | 5.7339 | 5.6135 | 5.4635 | 5.3778 | 5.0002 | 4.7278 | 4.4053 | 6.3257 | 6.3216 | 6.3022 | 6.288 | 6.2533 | 6.2216 | 6.141 | 6.0757 | 5.9767 | 5.9084 | 5.6267 | 5.6227 | 5.6655 | 6.1665 | 6.1645 | 6.1533 | 6.1257 | 6.0594 | 5.9971 | 5.8849 | 5.7808 | 5.6502 | 5.5716 | 5.2308 | 5.1155 | 5.0594
|  | NEW PITSLIGO | HE |  |  |  |  | 6.1084 | 6.1186 | 6.0941 | 6.0267 | 5.9369 | 5.8563 | 5.7318 | 5.6124 | 5.4676 | 5.3798 | 5.0155 | 4.7369 | 4.5196 | 6.3257 | 6.3227 | 6.3022 | 6.289 | 6.2522 | 6.2186 | 6.1522 | 6.0839 | 5.9859 | 5.9206 | 5.6737 | 5.6573 | 5.6482 | 6.1665 | 6.1655 | 6.1543 | 6.1247 | 6.0553 | 6.0022 | 5.888 | 5.7849 | 5.6604 | 5.5798 | 5.2655 | 5.1522 | 5.0849
|  | NEW PITSLIGO | FB |  |  |  |  | 6.1482 | 6.1706 | 6.1676 | 6.1502 | 6.1206 | 6.0696 | 6.0431 | 6.0022 | 5.9594 | 5.94 | 5.6645 | 5.4165 | 5.3614 | 6.3645 | 6.3676 | 6.3635 | 6.3676 | 6.3584 | 6.3206 | 6.3022 | 6.2645 | 6.2267 | 6.2135 | 6.0247 | 5.7941 | 5.6747 | 6.1941 | 6.2053 | 6.2073 | 6.2073 | 6.2002 | 6.1788 | 6.1665 | 6.1216 | 6.0655 | 6.0471 | 5.8104 | 5.5624 | 5.5257
| DUNOON | NEWTON | MINIMUM HEADROOM | NS 04939 98621 | YES | YES | 0.084 | 0.15054 | 0.1434 | 0.13829 | 0.13421 | 0.12809 | 0.11584 | 0.098498 | 0.090335 | 0.074008 | 0.066865 | 0.02809 | 0.010743 | -0.0035429 | 0.17252 | 0.1664 | 0.16129 | 0.15721 | 0.15517 | 0.14497 | 0.13374 | 0.12864 | 0.1164 | 0.10925 | 0.070478 | 0.069457 | 0.061294 | 0.16663 | 0.16051 | 0.15439 | 0.15132 | 0.14724 | 0.135 | 0.12071 | 0.11357 | 0.098263 | 0.095202 | 0.057447 | 0.045202 | 0.034998
|  | NEWTON | EE |  |  |  |  | 0.15054 | 0.1434 | 0.13829 | 0.13421 | 0.12809 | 0.11687 | 0.098498 | 0.090335 | 0.074008 | 0.067886 | 0.02809 | 0.011763 | 0.0025796 | 0.17252 | 0.1664 | 0.16129 | 0.15721 | 0.15517 | 0.14599 | 0.13374 | 0.12864 | 0.1164 | 0.10925 | 0.070478 | 0.074559 | 0.079661 | 0.16663 | 0.16051 | 0.15439 | 0.15132 | 0.14724 | 0.135 | 0.12071 | 0.11357 | 0.099284 | 0.096222 | 0.057447 | 0.047243 | 0.043161
|  | NEWTON | HT |  |  |  |  | 0.15156 | 0.14442 | 0.14033 | 0.13523 | 0.12911 | 0.11789 | 0.098498 | 0.093396 | 0.07809 | 0.070947 | 0.046457 | 0.015845 | 0.00053878 | 0.17252 | 0.1664 | 0.16231 | 0.15823 | 0.15517 | 0.14701 | 0.13374 | 0.12966 | 0.1164 | 0.10925 | 0.079661 | 0.069457 | 0.07762 | 0.16663 | 0.16051 | 0.15541 | 0.15234 | 0.14826 | 0.13704 | 0.12173 | 0.11459 | 0.10132 | 0.097243 | 0.071733 | 0.049284 | 0.042141
|  | NEWTON | HE |  |  |  |  | 0.15156 | 0.1434 | 0.13931 | 0.13421 | 0.12911 | 0.11584 | 0.098498 | 0.091355 | 0.075029 | 0.066865 | 0.034212 | 0.010743 | -0.0035429 | 0.17252 | 0.1664 | 0.16129 | 0.15721 | 0.15517 | 0.14497 | 0.13374 | 0.12864 | 0.1164 | 0.10925 | 0.070478 | 0.070478 | 0.070478 | 0.16765 | 0.16051 | 0.15439 | 0.15132 | 0.14724 | 0.135 | 0.12071 | 0.11357 | 0.098263 | 0.095202 | 0.061529 | 0.045202 | 0.034998
|  | NEWTON | FB |  |  |  |  | 0.1638 | 0.15768 | 0.15564 | 0.15156 | 0.1485 | 0.14544 | 0.13829 | 0.13217 | 0.12605 | 0.11993 | 0.095437 | 0.060743 | 0.051559 | 0.18068 | 0.17558 | 0.1715 | 0.16844 | 0.16436 | 0.16231 | 0.15721 | 0.14803 | 0.14191 | 0.13578 | 0.11436 | 0.078641 | 0.061294 | 0.17888 | 0.17377 | 0.17071 | 0.16765 | 0.16357 | 0.16051 | 0.15643 | 0.14928 | 0.14214 | 0.13602 | 0.11561 | 0.073773 | 0.070712
| REDMOSS | NEWTONHILL | MINIMUM HEADROOM | NO 90190 93653 | NO | NO | 6.813 | -2.357 | -3.4804 | 9.8002 | 8.5032 | 7.4063 | 6.0267 | 4.4512 | 3.4175 | 2.3379 | -5.3661 | -8.1814 | -9.8427 | -10.9427 | -0.53247 | -1.659 | 10.9951 | 9.8522 | 9.0522 | 8.239 | 7.3441 | 7.041 | 6.7063 | 4.8053 | 2.791 | 2.5981 | 2.4288 | -1.1973 | -2.2687 | 10.7196 | 9.5032 | 8.5839 | 7.4441 | 6.1716 | 5.4298 | 4.6665 | -0.18859 | -2.5998 | -3.7427 | -4.4508
|  | NEWTONHILL | EE |  |  |  |  | -2.1968 | -3.4804 | 9.839 | 8.6002 | 7.5084 | 6.1726 | 4.6992 | 3.7196 | 2.7298 | -4.8641 | -8.1814 | -9.807 | -10.9233 | -0.33859 | -1.659 | 11.0063 | 9.8798 | 9.0869 | 8.2522 | 7.3675 | 7.0665 | 6.7594 | 4.8788 | 2.9135 | 2.7135 | 2.4288 | -1.0432 | -2.2687 | 10.74 | 9.5594 | 8.6481 | 7.539 | 6.3288 | 5.6226 | 4.9135 | 0.13386 | -2.5998 | -3.708 | -4.4508
|  | NEWTONHILL | HT |  |  |  |  | -2.2886 | -3.4274 | 9.8196 | 8.5094 | 7.4104 | 6.4992 | 5.4859 | 4.4655 | 3.1971 | -4.8161 | -8.0968 | -9.8427 | -10.9427 | -0.45185 | -1.6223 | 10.9951 | 9.8522 | 9.0522 | 8.8043 | 8.5053 | 8.1237 | 7.4553 | 4.942 | 2.791 | 2.5981 | 2.6359 | -1.133 | -2.2248 | 10.7247 | 9.5032 | 8.5992 | 7.9543 | 7.2379 | 6.5094 | 5.5165 | 0.19304 | -2.5845 | -3.7427 | -4.3998
|  | NEWTONHILL | HE |  |  |  |  | -2.357 | -3.4763 | 9.8002 | 8.5032 | 7.4063 | 6.0267 | 4.4512 | 3.4175 | 2.3379 | -5.3661 | -8.0457 | -9.3784 | -10.161 | -0.53247 | -1.658 | 11.0012 | 9.8675 | 9.0767 | 8.239 | 7.3441 | 7.041 | 6.7063 | 4.8053 | 2.9624 | 2.8471 | 2.6277 | -1.1973 | -2.2656 | 10.7196 | 9.5114 | 8.5839 | 7.4441 | 6.1716 | 5.4298 | 4.6665 | -0.18859 | -2.4927 | -3.3825 | -3.911
|  | NEWTONHILL | FB |  |  |  |  | -1.7151 | -2.5988 | 10.8594 | 9.9277 | 9.1532 | 8.2757 | 7.243 | 6.1992 | 5.7584 | -0.79981 | -2.3947 | -4.1916 | -4.7865 | 0.12672 | -0.84981 | 11.8522 | 10.9839 | 10.193 | 9.4135 | 8.5339 | 7.6094 | 7.442 | 5.9308 | 4.8992 | 3.4206 | 2.693 | -0.59318 | -1.4646 | 11.6328 | 10.739 | 9.9635 | 9.1481 | 8.2216 | 7.2726 | 6.9869 | 3.1145 | 1.7461 | 0.021616 | -0.34675
| ALNESS | NIGG | MINIMUM HEADROOM | NH 79490 69773 | YES | NO | 8.5 | -7.5163 | -7.5163 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | -7.0082 | -7.0082 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | -7.4357 | -7.4357 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143
|  | NIGG | EE |  |  |  |  | -7.5163 | -7.5163 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | -7.0082 | -7.0082 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | -7.4357 | -7.4357 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143
|  | NIGG | HT |  |  |  |  | -7.5163 | -7.5163 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | -7.0082 | -7.0082 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | -7.4357 | -7.4357 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143
|  | NIGG | HE |  |  |  |  | -7.5163 | -7.5163 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | -7.0082 | -7.0082 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | -7.4357 | -7.4357 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143
|  | NIGG | FB |  |  |  |  | -7.5163 | -7.5163 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | 20.5837 | -7.0082 | -7.0082 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | 19.5918 | -7.4357 | -7.4357 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143 | 19.9143
| CHARLESTON | NINEWELLS | MINIMUM HEADROOM | NO 35148 30641 | NO | YES | 3.266 | 7.7435 | 7.5792 | 7.4364 | 7.4333 | 7.4139 | 7.1344 | 6.9109 | 6.6292 | 6.6119 | 6.4721 | 5.7782 | 5.5007 | 5.3048 | 8.1344 | 7.965 | 7.9252 | 7.917 | 7.8915 | 7.7252 | 7.5558 | 7.2864 | 7.316 | 7.1333 | 6.4956 | 6.5048 | 5.6068 | 8.0787 | 7.9206 | 7.8094 | 7.794 | 7.7512 | 7.4287 | 7.2216 | 6.9379 | 6.9318 | 6.7951 | 6.0991 | 5.8849 | 5.7063
|  | NINEWELLS | EE |  |  |  |  | 7.7435 | 7.5792 | 7.4364 | 7.4333 | 7.4139 | 7.1741 | 6.9109 | 6.6292 | 6.6119 | 6.4721 | 5.8048 | 5.5007 | 5.3048 | 8.1344 | 7.965 | 7.9252 | 7.918 | 7.8925 | 7.7782 | 7.567 | 7.2864 | 7.316 | 7.1619 | 6.6139 | 6.5292 | 6.2466 | 8.0787 | 7.9206 | 7.8094 | 7.794 | 7.7512 | 7.4828 | 7.2379 | 6.9379 | 6.9318 | 6.7971 | 6.1349 | 5.8849 | 5.7063
|  | NINEWELLS | HT |  |  |  |  | 7.7466 | 7.5895 | 7.4619 | 7.4517 | 7.419 | 7.1344 | 6.9344 | 6.7905 | 6.7456 | 6.4966 | 5.7782 | 5.5241 | 5.4537 | 8.1344 | 7.9711 | 7.9272 | 7.918 | 7.8915 | 7.7252 | 7.5558 | 7.3997 | 7.3966 | 7.1333 | 6.4956 | 6.5048 | 6.5701 | 8.0818 | 7.9308 | 7.8308 | 7.8073 | 7.7522 | 7.4287 | 7.2216 | 7.0869 | 7.0502 | 6.7951 | 6.0991 | 5.8991 | 5.8563
|  | NINEWELLS | HE |  |  |  |  | 7.7466 | 7.5823 | 7.4497 | 7.4507 | 7.4282 | 7.3384 | 7.0884 | 6.8119 | 6.8078 | 6.717 | 6.3292 | 6.0976 | 5.8935 | 8.1344 | 7.965 | 7.9262 | 7.917 | 7.8915 | 7.8476 | 7.6313 | 7.4497 | 7.4874 | 7.368 | 7.0231 | 6.9201 | 6.5966 | 8.0818 | 7.9247 | 7.8196 | 7.8042 | 7.7594 | 7.6716 | 7.4389 | 7.1379 | 7.1471 | 7.0594 | 6.7022 | 6.5175 | 6.3267
|  | NINEWELLS | FB |  |  |  |  | 7.7905 | 7.7058 | 7.6037 | 7.6068 | 7.5946 | 7.5772 | 7.4599 | 7.4088 | 7.3792 | 7.3435 | 7.1864 | 6.8344 | 6.2568 | 8.1558 | 8.0752 | 8.0088 | 7.9956 | 7.967 | 7.9374 | 7.7915 | 7.6986 | 7.6231 | 7.5558 | 7.2956 | 6.5946 | 5.6068 | 8.1369 | 8.0675 | 7.9583 | 7.9563 | 7.9328 | 7.9206 | 7.7991 | 7.7349 | 7.6808 | 7.64 | 7.5042 | 7.043 | 6.4757
| THURSO | NORTH HOY | MINIMUM HEADROOM | HY 25681 02549 | YES | NO | 0 | 0.15437 | 0.15539 | 0.15743 | 0.14824 | 0.14212 | 0.136 | 0.1309 | 0.12478 | 0.12069 | 0.11559 | 0.10947 | 0.097224 | 0.090082 | 0.1629 | 0.16392 | 0.16392 | 0.1578 | 0.15473 | 0.15167 | 0.15065 | 0.14861 | 0.14657 | 0.14351 | 0.13433 | 0.13229 | 0.12718 | 0.16067 | 0.16271 | 0.16373 | 0.15353 | 0.14945 | 0.14333 | 0.14027 | 0.13618 | 0.1321 | 0.12802 | 0.11986 | 0.11373 | 0.10863
|  | NORTH HOY | EE |  |  |  |  | 0.15437 | 0.15539 | 0.15947 | 0.14927 | 0.14212 | 0.13702 | 0.13192 | 0.1258 | 0.12171 | 0.11559 | 0.10947 | 0.098245 | 0.094163 | 0.1629 | 0.16392 | 0.16596 | 0.15882 | 0.15473 | 0.15167 | 0.15065 | 0.14861 | 0.14657 | 0.14351 | 0.13739 | 0.13433 | 0.13433 | 0.16067 | 0.16271 | 0.16476 | 0.15455 | 0.14945 | 0.14435 | 0.14129 | 0.13618 | 0.1321 | 0.12802 | 0.12292 | 0.11373 | 0.11169
|  | NORTH HOY | HT |  |  |  |  | 0.15437 | 0.15539 | 0.15947 | 0.14824 | 0.14416 | 0.13702 | 0.13294 | 0.12988 | 0.12376 | 0.11967 | 0.10947 | 0.098245 | 0.090082 | 0.1629 | 0.16392 | 0.16698 | 0.1578 | 0.15576 | 0.15167 | 0.15065 | 0.14861 | 0.14759 | 0.14453 | 0.13433 | 0.13229 | 0.13229 | 0.16067 | 0.16271 | 0.16476 | 0.15455 | 0.15047 | 0.14435 | 0.14231 | 0.1372 | 0.13516 | 0.1321 | 0.11986 | 0.11373 | 0.10863
|  | NORTH HOY | HE |  |  |  |  | 0.15437 | 0.15539 | 0.15947 | 0.14824 | 0.14314 | 0.136 | 0.1309 | 0.12478 | 0.12069 | 0.11661 | 0.10947 | 0.097224 | 0.092122 | 0.1629 | 0.16392 | 0.16596 | 0.1578 | 0.15473 | 0.15167 | 0.15065 | 0.14861 | 0.14657 | 0.14453 | 0.13637 | 0.13229 | 0.13024 | 0.16067 | 0.16271 | 0.16476 | 0.15353 | 0.15047 | 0.14333 | 0.14027 | 0.13618 | 0.1321 | 0.12904 | 0.12088 | 0.11373 | 0.10965
|  | NORTH HOY | FB |  |  |  |  | 0.16457 | 0.16865 | 0.15743 | 0.16151 | 0.16049 | 0.16151 | 0.15845 | 0.15131 | 0.15233 | 0.15029 | 0.14008 | 0.12784 | 0.1258 | 0.1731 | 0.17412 | 0.16392 | 0.17004 | 0.16596 | 0.16698 | 0.15984 | 0.15371 | 0.15576 | 0.15371 | 0.14657 | 0.13331 | 0.12718 | 0.17088 | 0.17292 | 0.16373 | 0.16884 | 0.16578 | 0.16578 | 0.16476 | 0.15557 | 0.15659 | 0.15455 | 0.14537 | 0.13108 | 0.13312
| BEAULY | NORTH KESSOCK | MINIMUM HEADROOM | NH 65004 48461 | YES | NO | 1.5 | 2.0149 | 2.0067 | 1.9884 | 1.9047 | 1.8373 | 1.4139 | 1.0578 | 0.84245 | 0.69551 | 0.59347 | 0.29449 | -0.027959 | -0.27694 | 2.2865 | 2.2784 | 2.2641 | 2.2324 | 2.1876 | 1.8559 | 1.5988 | 1.4447 | 1.3529 | 1.3202 | 1.2284 | 1.2233 | 1.1376 | 2.2053 | 2.192 | 2.1706 | 2.0931 | 2.04 | 1.7267 | 1.4206 | 1.2451 | 1.1196 | 1.0451 | 0.81245 | 0.62367 | 0.47776
|  | NORTH KESSOCK | EE |  |  |  |  | 2.0149 | 2.0067 | 1.9884 | 1.9088 | 1.8424 | 1.721 | 1.4639 | 1.1241 | 0.85571 | 0.6598 | 0.29449 | -0.027959 | -0.27286 | 2.2876 | 2.2784 | 2.2651 | 2.2345 | 2.1876 | 2.1437 | 2.0355 | 1.7804 | 1.5406 | 1.3722 | 1.2294 | 1.2284 | 1.2324 | 2.2053 | 2.192 | 2.1706 | 2.0961 | 2.04 | 1.9747 | 1.7788 | 1.489 | 1.2584 | 1.0982 | 0.81245 | 0.62776 | 0.48592
|  | NORTH KESSOCK | HT |  |  |  |  | 2.0169 | 2.0088 | 1.9924 | 1.9098 | 1.8465 | 1.4139 | 1.0578 | 0.84245 | 0.69551 | 0.62102 | 0.41082 | 0.051633 | -0.27694 | 2.2865 | 2.2784 | 2.2641 | 2.2345 | 2.1886 | 1.8559 | 1.5988 | 1.4447 | 1.3529 | 1.3202 | 1.2284 | 1.2233 | 1.2467 | 2.2053 | 2.1941 | 2.1727 | 2.0951 | 2.0431 | 1.7267 | 1.4206 | 1.2451 | 1.1196 | 1.0604 | 0.87061 | 0.67367 | 0.47776
|  | NORTH KESSOCK | HE |  |  |  |  | 2.0169 | 2.0098 | 1.9924 | 1.9047 | 1.8373 | 1.6924 | 1.4976 | 1.0782 | 0.79449 | 0.59347 | 0.3802 | -0.011633 | -0.20959 | 2.2876 | 2.2794 | 2.2641 | 2.2324 | 2.1876 | 2.1396 | 2.0406 | 1.7437 | 1.4896 | 1.3273 | 1.2304 | 1.2263 | 1.2386 | 2.2073 | 2.1961 | 2.1727 | 2.0931 | 2.0614 | 1.9553 | 1.8022 | 1.4533 | 1.2084 | 1.0451 | 0.85122 | 0.62367 | 0.51449
|  | NORTH KESSOCK | FB |  |  |  |  | 2.0547 | 2.0639 | 2.068 | 2.0016 | 1.9822 | 1.9812 | 1.8782 | 1.7792 | 1.569 | 1.3955 | 0.99755 | 0.80061 | 0.73122 | 2.309 | 2.31 | 2.312 | 2.2845 | 2.2773 | 2.26 | 2.2059 | 2.1457 | 1.9335 | 1.7427 | 1.3855 | 1.258 | 1.1376 | 2.2441 | 2.2441 | 2.242 | 2.188 | 2.1757 | 2.1563 | 2.0696 | 2.0104 | 1.8288 | 1.6849 | 1.3329 | 1.1176 | 1.0829
| BROADFORD | NOSTIE BRIDGE | MINIMUM HEADROOM | NG 85209 27252 | YES | YES | 0.521 | -1.201 | -1.2061 | -1.2214 | -1.2551 | -1.3204 | -1.4204 | -1.5276 | -1.648 | -1.7684 | -1.8714 | -2.248 | -2.4837 | -2.7184 | -0.72551 | -0.72755 | -0.7398 | -0.74796 | -0.77347 | -0.8 | -0.83878 | -0.87551 | -0.91327 | -0.95918 | -1.048 | -1.0449 | -1.1 | -0.77551 | -0.77959 | -0.79796 | -0.83265 | -0.88673 | -0.94388 | -1.0469 | -1.1408 | -1.2296 | -1.3184 | -1.5908 | -1.6235 | -1.8061
|  | NOSTIE BRIDGE | EE |  |  |  |  | -1.201 | -1.2061 | -1.2214 | -1.2541 | -1.3163 | -1.4204 | -1.5265 | -1.6429 | -1.7643 | -1.8592 | -2.248 | -2.4837 | -2.7184 | -0.72449 | -0.72755 | -0.7398 | -0.74694 | -0.77245 | -0.8 | -0.83878 | -0.87551 | -0.91122 | -0.95714 | -1.048 | -0.98571 | -1.0265 | -0.77449 | -0.77959 | -0.79796 | -0.83061 | -0.88571 | -0.94388 | -1.0459 | -1.1367 | -1.2245 | -1.3092 | -1.5908 | -1.6235 | -1.8061
|  | NOSTIE BRIDGE | HT |  |  |  |  | -1.201 | -1.2061 | -1.2204 | -1.2531 | -1.3194 | -1.4112 | -1.5143 | -1.6296 | -1.7408 | -1.8684 | -2.1347 | -2.4367 | -2.7143 | -0.72551 | -0.72755 | -0.73878 | -0.74796 | -0.77347 | -0.79898 | -0.83776 | -0.87551 | -0.91327 | -0.95918 | -1.0194 | -0.99898 | -0.97245 | -0.77551 | -0.77959 | -0.79694 | -0.83061 | -0.88673 | -0.93469 | -1.0388 | -1.1276 | -1.2122 | -1.3173 | -1.4531 | -1.601 | -1.7449
|  | NOSTIE BRIDGE | HE |  |  |  |  | -1.201 | -1.2051 | -1.2194 | -1.2551 | -1.3204 | -1.4173 | -1.5276 | -1.648 | -1.7684 | -1.8714 | -2.1684 | -2.4408 | -2.6347 | -0.72449 | -0.72755 | -0.73776 | -0.74694 | -0.77143 | -0.79898 | -0.83776 | -0.87551 | -0.9102 | -0.95714 | -1.0459 | -0.9898 | -1.002 | -0.77347 | -0.77755 | -0.79592 | -0.83265 | -0.88673 | -0.94082 | -1.0469 | -1.1408 | -1.2296 | -1.3184 | -1.5459 | -1.6153 | -1.7224
|  | NOSTIE BRIDGE | FB |  |  |  |  | -1.1694 | -1.1531 | -1.1398 | -1.1378 | -1.1459 | -1.1612 | -1.1837 | -1.2051 | -1.198 | -1.2418 | -1.4776 | -1.6939 | -1.7612 | -0.70204 | -0.6949 | -0.69184 | -0.69184 | -0.69898 | -0.70918 | -0.73061 | -0.75408 | -0.76429 | -0.79286 | -0.89592 | -1.0449 | -1.1 | -0.72551 | -0.71327 | -0.70612 | -0.7 | -0.70408 | -0.72041 | -0.75102 | -0.78265 | -0.7949 | -0.83265 | -1.0194 | -1.2255 | -1.2531
| TAYNUILT | OBAN | MINIMUM HEADROOM | NM 85643 29338 | NO | YES | 5.535 | 6.8706 | 6.5482 | 6.539 | 6.391 | 6.1359 | 5.2165 | 3.2941 | 1.0951 | -2.7069 | -3.6008 | -9.1773 | -19.4631 | -27.6335 | 9.7767 | 9.39 | 9.14 | 8.8441 | 8.5869 | 7.8655 | 5.842 | 3.5359 | -0.64265 | -1.56 | -7.5396 | -19.3998 | -28.9733 | 8.8237 | 8.3727 | 8.1135 | 7.7727 | 7.5022 | 6.7033 | 4.5931 | 2.2022 | -2.0876 | -3.0631 | -9.0416 | -21.1906 | -31.0508
|  | OBAN | EE |  |  |  |  | 6.8706 | 6.9686 | 6.5665 | 6.4635 | 6.2206 | 5.3176 | 3.8727 | 1.9859 | -1.1263 | -1.6722 | -7.6498 | -16.8916 | -20.8233 | 9.7767 | 9.7635 | 9.1604 | 8.891 | 8.639 | 7.9247 | 6.4951 | 4.5859 | 1.2043 | 0.63898 | -5.3906 | -15.9702 | -20.5161 | 8.8237 | 8.8267 | 8.1216 | 7.84 | 7.5676 | 6.7788 | 5.2686 | 3.2624 | -0.20796 | -0.7651 | -7.0243 | -17.8937 | -22.46
|  | OBAN | HT |  |  |  |  | 6.8716 | 6.5482 | 6.539 | 6.391 | 6.1359 | 5.2165 | 3.2941 | 1.1706 | -2.7069 | -3.6008 | -9.1773 | -19.4631 | -27.6335 | 9.7767 | 9.39 | 9.14 | 8.8441 | 8.5869 | 7.8655 | 5.842 | 3.6431 | -0.64265 | -1.56 | -7.5396 | -19.3998 | -28.9733 | 8.8267 | 8.3727 | 8.1135 | 7.7727 | 7.5022 | 6.7033 | 4.5931 | 2.3063 | -2.0876 | -3.0631 | -9.0416 | -21.1906 | -31.0508
|  | OBAN | HE |  |  |  |  | 6.8716 | 6.9686 | 6.5573 | 6.4278 | 6.1686 | 5.2767 | 3.6849 | 1.0951 | 0.28898 | -1.1018 | -8.6947 | -18.2753 | -26.2345 | 9.7767 | 9.7635 | 9.1512 | 8.8686 | 8.6145 | 7.9176 | 6.3339 | 3.5359 | 2.9849 | 1.4329 | -7.1518 | -18.2171 | -28.0539 | 8.8247 | 8.8278 | 8.1298 | 7.8053 | 7.5278 | 6.7543 | 5.0941 | 2.2022 | 1.5278 | -0.012041 | -8.7692 | -20.0182 | -29.8753
|  | OBAN | FB |  |  |  |  | 6.9573 | 7.1165 | 7.2492 | 6.9308 | 6.989 | 6.9757 | 6.4584 | 5.6114 | 3.6982 | 2.8849 | 0.04 | -3.8376 | -6.7202 | 9.8798 | 9.8992 | 9.8971 | 9.5227 | 9.4696 | 9.2533 | 8.4624 | 7.1971 | 4.8941 | 3.9124 | 0.83694 | -3.4886 | -7.1141 | 8.9798 | 9.0216 | 9.0676 | 8.6247 | 8.6308 | 8.4614 | 7.7186 | 6.4839 | 4.1931 | 3.2839 | 0.2951 | -4.5539 | -6.7661
| MILTON OF CRAIGIE | OLD CRAIGIE ROAD | MINIMUM HEADROOM | NO 42156 32130 | NO | NO | 1.31 | 6.9337 | 6.9031 | 6.8725 | 6.847 | 6.7939 | 6.3868 | 6.0194 | 5.899 | 5.5919 | 5.3654 | 4.0307 | 3.1909 | 2.7378 | 8.0041 | 7.997 | 7.9756 | 7.9817 | 7.9256 | 7.5848 | 7.3256 | 7.3092 | 7.1092 | 6.9072 | 6.3184 | 6.3205 | 5.345 | 7.6776 | 7.6368 | 7.6092 | 7.5858 | 7.5399 | 7.1643 | 6.8429 | 6.7572 | 6.4817 | 6.2715 | 5.1256 | 4.4562 | 4.1092
|  | OLD CRAIGIE ROAD | EE |  |  |  |  | 6.9337 | 6.9031 | 6.8725 | 6.847 | 6.7939 | 6.4235 | 6.0194 | 5.899 | 5.5919 | 5.3654 | 4.0307 | 3.1909 | 2.7378 | 8.0072 | 7.998 | 7.9797 | 7.9848 | 7.9276 | 7.6501 | 7.3358 | 7.3266 | 7.1092 | 6.9613 | 6.3797 | 6.3307 | 6.0246 | 7.6776 | 7.6368 | 7.6092 | 7.5858 | 7.5409 | 7.2062 | 6.8429 | 6.7572 | 6.4817 | 6.2817 | 5.1256 | 4.4562 | 4.1092
|  | OLD CRAIGIE ROAD | HT |  |  |  |  | 6.9358 | 6.9123 | 6.8929 | 6.8664 | 6.8062 | 6.3868 | 6.098 | 5.948 | 5.6786 | 5.3674 | 4.0786 | 3.3592 | 3.0735 | 8.0041 | 7.997 | 7.9776 | 7.9848 | 7.9256 | 7.5848 | 7.3684 | 7.3194 | 7.1337 | 6.9072 | 6.3184 | 6.3205 | 6.3756 | 7.6786 | 7.647 | 7.6266 | 7.6001 | 7.548 | 7.1643 | 6.9072 | 6.7919 | 6.549 | 6.2715 | 5.1654 | 4.6062 | 4.4062
|  | OLD CRAIGIE ROAD | HE |  |  |  |  | 6.9358 | 6.9072 | 6.8797 | 6.8521 | 6.796 | 6.4378 | 6.0592 | 5.9521 | 5.7297 | 5.4909 | 4.5766 | 3.9572 | 3.5439 | 8.0041 | 7.997 | 7.9756 | 7.9817 | 7.9266 | 7.645 | 7.3256 | 7.3092 | 7.1562 | 6.9715 | 6.5592 | 6.4827 | 6.2082 | 7.6786 | 7.6419 | 7.6174 | 7.5899 | 7.5399 | 7.2164 | 6.8705 | 6.7919 | 6.595 | 6.3735 | 5.5919 | 5.1123 | 4.7919
|  | OLD CRAIGIE ROAD | FB |  |  |  |  | 7.0184 | 7.049 | 7.0654 | 7.0817 | 7.0786 | 7.0368 | 6.997 | 6.9541 | 6.8878 | 6.8378 | 6.6072 | 5.8746 | 4.949 | 8.048 | 8.0592 | 8.0552 | 8.0654 | 8.0521 | 7.9939 | 7.9327 | 7.8684 | 7.7827 | 7.7133 | 7.3888 | 6.5133 | 5.345 | 7.7633 | 7.7746 | 7.7756 | 7.7827 | 7.7888 | 7.745 | 7.7031 | 7.6592 | 7.5868 | 7.5368 | 7.3052 | 6.5031 | 5.7562
| KINTORE | OLDMELDRUM | MINIMUM HEADROOM | NJ 81659 27360 | NO | YES | 1.1 | 1.0228 | 0.76358 | 21.8046 | 21.4577 | 21.1036 | 20.7464 | 20.0485 | 19.3332 | 18.1332 | 17.6097 | 15.3842 | 13.1107 | 11.2454 | 1.8034 | 1.5585 | 21.5781 | 21.3189 | 21.0026 | 20.7689 | 20.276 | 19.7475 | 18.6056 | 18.274 | 16.5066 | 14.6852 | 12.8822 | 1.6646 | 1.4054 | 21.9515 | 21.6536 | 21.2964 | 20.9464 | 20.2362 | 19.4781 | 18.0658 | 17.5117 | 15.2832 | 12.9903 | 10.973
|  | OLDMELDRUM | EE |  |  |  |  | 1.0717 | 0.7646 | 21.8454 | 21.5546 | 21.2015 | 20.8291 | 20.1944 | 19.5944 | 18.8556 | 18.474 | 16.3301 | 13.9811 | 12.7505 | 1.8615 | 1.5585 | 21.5903 | 21.3515 | 21.0352 | 20.7862 | 20.322 | 19.9332 | 19.3291 | 19.1383 | 17.7934 | 15.8975 | 15.025 | 1.7156 | 1.4054 | 21.9822 | 21.7189 | 21.374 | 21.0199 | 20.3546 | 19.7097 | 18.8934 | 18.4832 | 16.5158 | 14.1393 | 12.9791
|  | OLDMELDRUM | HT |  |  |  |  | 1.0391 | 0.76664 | 21.8046 | 21.4577 | 21.1036 | 20.8107 | 20.1689 | 19.574 | 18.674 | 18.0995 | 16.1015 | 13.5005 | 11.4209 | 1.8238 | 1.5626 | 21.5781 | 21.3189 | 21.0026 | 20.9046 | 20.4617 | 20.0424 | 19.2342 | 18.8464 | 17.3546 | 15.2577 | 13.576 | 1.684 | 1.4085 | 21.9515 | 21.6536 | 21.2964 | 21.024 | 20.2832 | 19.6322 | 18.6505 | 18.0975 | 16.1617 | 13.5077 | 11.3771
|  | OLDMELDRUM | HE |  |  |  |  | 1.0228 | 0.76358 | 21.8311 | 21.5087 | 21.1464 | 20.7464 | 20.0485 | 19.3332 | 18.1332 | 17.6097 | 15.3842 | 13.1107 | 11.2454 | 1.8034 | 1.5585 | 21.5852 | 21.3393 | 21.023 | 20.7689 | 20.276 | 19.7475 | 18.6056 | 18.274 | 16.5066 | 14.6852 | 12.8822 | 1.6646 | 1.4054 | 21.9699 | 21.6913 | 21.3332 | 20.9464 | 20.2362 | 19.4781 | 18.0658 | 17.5117 | 15.2832 | 12.9903 | 10.973
|  | OLDMELDRUM | FB |  |  |  |  | 1.3024 | 1.0779 | 22.0893 | 21.9271 | 21.7709 | 21.5791 | 21.2526 | 20.8495 | 20.4954 | 20.3128 | 19.3556 | 18.3117 | 17.7373 | 2.0677 | 1.8207 | 21.7301 | 21.5617 | 21.4046 | 21.2066 | 20.8566 | 20.4434 | 20.0536 | 19.8781 | 19.2475 | 18.4352 | 17.6179 | 1.9279 | 1.6891 | 22.1556 | 22.0005 | 21.8587 | 21.6699 | 21.323 | 20.9046 | 20.4995 | 20.3281 | 19.2913 | 17.9577 | 17.4913
| THURSO | ORMLIE | MINIMUM HEADROOM | ND 10757 67408 | NO | NO | 0.813 | 10.1306 | 10.0786 | 10.0939 | 10.0327 | 9.8765 | 8.9663 | 7.8643 | 6.5429 | 5.1755 | 4.3918 | 2.4112 | 1.7582 | 1.3806 | 13.1888 | 12.9673 | 12.9755 | 12.8735 | 12.6531 | 12.0245 | 11.2153 | 10.0184 | 8.7031 | 7.9816 | 6.4143 | 6.3184 | 6.3224 | 13.5811 | 13.3852 | 13.3679 | 13.2944 | 12.9893 | 12.2791 | 11.3526 | 10.0617 | 8.6974 | 7.926 | 6.177 | 5.7107 | 5.4964
|  | ORMLIE | EE |  |  |  |  | 10.1306 | 10.0806 | 10.0939 | 10.0327 | 9.8765 | 9.6612 | 9.251 | 8.2653 | 7.2051 | 6.052 | 2.4867 | 1.7582 | 1.449 | 13.1888 | 12.9857 | 12.9755 | 12.9296 | 12.6531 | 12.5204 | 12.3184 | 11.6082 | 10.8112 | 9.8449 | 6.6398 | 6.3286 | 6.3224 | 13.5811 | 13.4005 | 13.3679 | 13.2944 | 12.9893 | 12.7862 | 12.4781 | 11.6668 | 10.7199 | 9.6046 | 6.2913 | 5.7107 | 5.5046
|  | ORMLIE | HT |  |  |  |  | 10.1327 | 10.0816 | 10.0959 | 10.0388 | 9.8878 | 8.9663 | 7.8643 | 6.5429 | 5.1755 | 4.3918 | 2.4112 | 1.8051 | 1.3806 | 13.1898 | 12.9867 | 12.9776 | 12.9306 | 12.6551 | 12.0245 | 11.2153 | 10.0184 | 8.7031 | 7.9816 | 6.4143 | 6.3184 | 6.3337 | 13.5832 | 13.4015 | 13.3709 | 13.2974 | 12.9934 | 12.2791 | 11.3526 | 10.0617 | 8.6974 | 7.926 | 6.177 | 5.7607 | 5.4964
|  | ORMLIE | HE |  |  |  |  | 10.1327 | 10.0786 | 10.0949 | 10.0439 | 9.898 | 9.6857 | 9.2673 | 8.2867 | 7.0745 | 5.7051 | 2.7184 | 2.0112 | 1.748 | 13.1898 | 12.9673 | 12.9776 | 12.9306 | 12.6561 | 12.5214 | 12.3071 | 11.6316 | 10.6908 | 9.4735 | 6.7163 | 6.4704 | 6.4622 | 13.5832 | 13.3852 | 13.3719 | 13.2995 | 12.9995 | 12.7954 | 12.476 | 11.6964 | 10.5913 | 9.2546 | 6.4668 | 5.9291 | 5.7526
|  | ORMLIE | FB |  |  |  |  | 10.1786 | 10.2255 | 10.2551 | 10.1806 | 10.1867 | 10.1806 | 10.1398 | 10.1173 | 9.5316 | 8.8724 | 4.8316 | 3.8673 | 3.6245 | 13.2204 | 13.2327 | 13.2092 | 12.8735 | 12.8276 | 12.8031 | 12.7429 | 12.7061 | 12.2418 | 11.7235 | 7.5561 | 6.5796 | 6.348 | 13.625 | 13.6413 | 13.625 | 13.2985 | 13.2485 | 13.2209 | 13.175 | 13.1342 | 12.6607 | 12.1403 | 8.0587 | 7.1117 | 6.9944
| DUNOON | OTTER FERRY | MINIMUM HEADROOM | NR 93352 84713 | YES | YES | 0.282 | -0.27041 | -0.29694 | -0.29796 | -0.31122 | -0.31429 | -0.33367 | -0.34796 | -0.37449 | -0.39184 | -0.40714 | -0.45612 | -0.47857 | -0.49898 | 0.14082 | 0.091837 | 0.089796 | 0.083673 | 0.082653 | 0.07449 | 0.068367 | 0.055102 | 0.046939 | 0.027551 | -0.0061224 | 0 | -0.018367 | -0.10306 | -0.14286 | -0.14388 | -0.15408 | -0.15816 | -0.17653 | -0.19082 | -0.21633 | -0.23265 | -0.25306 | -0.29286 | -0.29388 | -0.31327
|  | OTTER FERRY | EE |  |  |  |  | -0.26735 | -0.26939 | -0.29796 | -0.31122 | -0.31327 | -0.33163 | -0.34592 | -0.37347 | -0.3898 | -0.40204 | -0.45612 | -0.47857 | -0.4898 | 0.14286 | 0.14286 | 0.089796 | 0.083673 | 0.083673 | 0.07449 | 0.069388 | 0.056122 | 0.046939 | 0.027551 | 0.0010204 | 0.0061224 | 0.019388 | -0.1 | -0.10204 | -0.14388 | -0.15408 | -0.15612 | -0.17449 | -0.1898 | -0.21633 | -0.23163 | -0.24898 | -0.29286 | -0.29388 | -0.29796
|  | OTTER FERRY | HT |  |  |  |  | -0.26735 | -0.29694 | -0.29592 | -0.30918 | -0.31122 | -0.32755 | -0.34286 | -0.36837 | -0.38265 | -0.40714 | -0.45204 | -0.47755 | -0.49286 | 0.14286 | 0.091837 | 0.089796 | 0.083673 | 0.082653 | 0.076531 | 0.068367 | 0.055102 | 0.047959 | 0.029592 | -0.0061224 | 0.0030612 | 0.018367 | -0.1 | -0.14286 | -0.14184 | -0.15102 | -0.1551 | -0.17143 | -0.18571 | -0.21122 | -0.22449 | -0.24388 | -0.28367 | -0.28673 | -0.30102
|  | OTTER FERRY | HE |  |  |  |  | -0.27041 | -0.26939 | -0.29592 | -0.30918 | -0.31429 | -0.33367 | -0.34796 | -0.37449 | -0.39184 | -0.40306 | -0.44694 | -0.47653 | -0.49898 | 0.14082 | 0.14286 | 0.090816 | 0.083673 | 0.082653 | 0.07551 | 0.068367 | 0.055102 | 0.046939 | 0.027551 | 0.0040816 | 0 | -0.0030612 | -0.10306 | -0.10204 | -0.14388 | -0.15408 | -0.15816 | -0.17653 | -0.19082 | -0.21633 | -0.23265 | -0.25306 | -0.28367 | -0.29286 | -0.31327
|  | OTTER FERRY | FB |  |  |  |  | -0.25816 | -0.24898 | -0.24796 | -0.27755 | -0.27551 | -0.27449 | -0.28163 | -0.28776 | -0.29592 | -0.29388 | -0.35204 | -0.4 | -0.41429 | 0.15 | 0.15306 | 0.15306 | 0.1 | 0.10102 | 0.09898 | 0.093878 | 0.090816 | 0.083673 | 0.082653 | 0.044898 | 0 | -0.018367 | -0.086735 | -0.080612 | -0.079592 | -0.12143 | -0.12143 | -0.11939 | -0.13061 | -0.13367 | -0.14592 | -0.14286 | -0.18776 | -0.23571 | -0.23673
| DUDHOPE | OVERGATE | MINIMUM HEADROOM | NO 40033 30155 | NO | NO | 3.986 | 13.1037 | 13.0292 | 12.7966 | 12.6231 | 12.4731 | 12.2986 | 11.5446 | 11.2241 | 10.7588 | 10.2813 | 8.8976 | 7.2099 | 6.669 | 15.4333 | 15.3752 | 14.9752 | 14.6997 | 14.2629 | 13.9139 | 13.2578 | 12.9109 | 12.5068 | 12.0456 | 10.8711 | 9.365 | 8.8272 | 14.0639 | 13.9935 | 13.6731 | 13.4466 | 13.1425 | 12.8813 | 12.3272 | 12.0956 | 11.7609 | 11.4262 | 10.1986 | 8.7823 | 8.3752
|  | OVERGATE | EE |  |  |  |  | 13.1415 | 13.0292 | 12.867 | 12.7588 | 12.6109 | 12.4099 | 12.0456 | 11.3894 | 10.9343 | 10.419 | 8.8976 | 7.2099 | 6.669 | 15.4558 | 15.3752 | 15.0139 | 14.766 | 14.3323 | 13.9241 | 13.5986 | 13.0211 | 12.6292 | 12.1292 | 10.8711 | 9.365 | 8.8272 | 14.0894 | 13.9935 | 13.718 | 13.5415 | 13.2446 | 12.9394 | 12.6701 | 12.2048 | 11.868 | 11.5078 | 10.1986 | 8.7823 | 8.3752
|  | OVERGATE | HT |  |  |  |  | 13.1252 | 13.0374 | 12.7966 | 12.6231 | 12.4731 | 12.2986 | 11.5446 | 11.2486 | 10.8619 | 10.315 | 9.0017 | 7.4262 | 7.219 | 15.4425 | 15.3813 | 14.9752 | 14.6997 | 14.2629 | 13.9343 | 13.2578 | 13.0088 | 12.6476 | 12.1109 | 11.0333 | 9.7119 | 9.5762 | 14.0752 | 14.0037 | 13.6731 | 13.4466 | 13.1425 | 12.8813 | 12.3272 | 12.1129 | 11.8303 | 11.4425 | 10.3099 | 8.9762 | 8.8486
|  | OVERGATE | HE |  |  |  |  | 13.1037 | 13.0292 | 12.8446 | 12.7048 | 12.5599 | 12.3752 | 11.915 | 11.2241 | 10.7588 | 10.2813 | 9.1772 | 8.4058 | 8.1905 | 15.4333 | 15.3874 | 15.0007 | 14.7435 | 14.3088 | 13.9139 | 13.5323 | 12.9109 | 12.5068 | 12.0456 | 11.069 | 10.3027 | 10.0394 | 14.0639 | 14.0088 | 13.7068 | 13.5068 | 13.2088 | 12.9221 | 12.5813 | 12.0956 | 11.7609 | 11.4262 | 10.5007 | 9.8313 | 9.6976
|  | OVERGATE | FB |  |  |  |  | 13.2405 | 13.1517 | 13.0456 | 13.0211 | 12.9721 | 12.9048 | 12.8486 | 12.7068 | 12.5323 | 12.4272 | 11.3558 | 9.7803 | 8.3435 | 15.5854 | 15.4435 | 15.2905 | 15.2558 | 15.1405 | 14.9435 | 14.7925 | 14.4843 | 14.169 | 13.866 | 12.6629 | 10.9456 | 9.2058 | 14.216 | 14.1099 | 13.9823 | 13.9752 | 13.9109 | 13.8007 | 13.715 | 13.4905 | 13.2415 | 13.0435 | 12.1711 | 10.6609 | 9.7578
| CASSLEY | OVERSCAIG | MINIMUM HEADROOM | NC 39711 25382 | YES | NO | 0 | 0.15965 | 0.15965 | 0.14843 | 0.14843 | 0.14741 | 0.13924 | 0.13516 | 0.13414 | 0.13006 | 0.12904 | 0.12292 | 0.11884 | 0.1168 | 0.15023 | 0.15023 | 0.13901 | 0.14003 | 0.13799 | 0.13289 | 0.12983 | 0.12983 | 0.12779 | 0.12574 | 0.12064 | 0.12064 | 0.12166 | 0.15494 | 0.15494 | 0.14474 | 0.14576 | 0.14372 | 0.13556 | 0.13147 | 0.13045 | 0.12943 | 0.12637 | 0.12331 | 0.11923 | 0.11821
|  | OVERSCAIG | EE |  |  |  |  | 0.15965 | 0.15965 | 0.14843 | 0.14843 | 0.14843 | 0.13924 | 0.13618 | 0.13414 | 0.13006 | 0.12904 | 0.12394 | 0.11986 | 0.11884 | 0.15023 | 0.15023 | 0.13901 | 0.14003 | 0.13799 | 0.13289 | 0.12983 | 0.12983 | 0.12779 | 0.12574 | 0.12472 | 0.12166 | 0.12472 | 0.15494 | 0.15494 | 0.14474 | 0.14576 | 0.14372 | 0.13556 | 0.13249 | 0.13045 | 0.12943 | 0.12637 | 0.12331 | 0.11923 | 0.11923
|  | OVERSCAIG | HT |  |  |  |  | 0.15965 | 0.15965 | 0.14843 | 0.14843 | 0.14843 | 0.14129 | 0.13618 | 0.13414 | 0.13108 | 0.13006 | 0.12292 | 0.11884 | 0.1168 | 0.15023 | 0.15023 | 0.13901 | 0.14003 | 0.13799 | 0.13391 | 0.12983 | 0.12983 | 0.12779 | 0.12574 | 0.12064 | 0.12064 | 0.12268 | 0.15494 | 0.15494 | 0.14474 | 0.14576 | 0.14372 | 0.13658 | 0.13249 | 0.13147 | 0.12943 | 0.12739 | 0.12331 | 0.12025 | 0.11821
|  | OVERSCAIG | HE |  |  |  |  | 0.15965 | 0.15965 | 0.14843 | 0.14843 | 0.14741 | 0.13924 | 0.13516 | 0.13618 | 0.13006 | 0.12904 | 0.12598 | 0.1219 | 0.11884 | 0.15023 | 0.15023 | 0.13901 | 0.14003 | 0.13799 | 0.13289 | 0.12983 | 0.13187 | 0.12779 | 0.12574 | 0.12472 | 0.1237 | 0.1237 | 0.15494 | 0.15494 | 0.14474 | 0.14576 | 0.14372 | 0.13556 | 0.13147 | 0.13352 | 0.12943 | 0.12637 | 0.12535 | 0.12127 | 0.11923
|  | OVERSCAIG | FB |  |  |  |  | 0.15965 | 0.15965 | 0.15149 | 0.15251 | 0.15353 | 0.14945 | 0.14945 | 0.14741 | 0.14537 | 0.14639 | 0.13516 | 0.13312 | 0.12904 | 0.15023 | 0.15023 | 0.14207 | 0.14309 | 0.14207 | 0.13901 | 0.13901 | 0.13697 | 0.13697 | 0.13595 | 0.12881 | 0.12677 | 0.12166 | 0.15494 | 0.15494 | 0.14678 | 0.1478 | 0.1478 | 0.14474 | 0.14576 | 0.1427 | 0.1427 | 0.1427 | 0.13249 | 0.12535 | 0.12535
| KINTORE | PARK | MINIMUM HEADROOM | NO 79107 99434 | YES | YES | 0.197 | -1.0786 | -1.0684 | -1.0776 | -1.1102 | -1.1204 | -1.1602 | -1.2439 | -1.3173 | -1.3776 | -1.4306 | -1.6908 | -1.7898 | -1.7878 | -0.19694 | -0.2051 | -0.23061 | -0.27347 | -0.2949 | -0.3449 | -0.44082 | -0.52245 | -0.59388 | -0.65918 | -0.90714 | -0.99184 | -1.0071 | -0.57959 | -0.57959 | -0.59796 | -0.63265 | -0.65714 | -0.7 | -0.7949 | -0.87857 | -0.95 | -1.0173 | -1.3031 | -1.3939 | -1.3878
|  | PARK | EE |  |  |  |  | -1.0786 | -1.0673 | -1.0765 | -1.1031 | -1.1122 | -1.149 | -1.2255 | -1.298 | -1.3612 | -1.4133 | -1.6908 | -1.7898 | -1.7878 | -0.19694 | -0.2051 | -0.22857 | -0.27041 | -0.2898 | -0.33776 | -0.42959 | -0.51122 | -0.58571 | -0.65 | -0.90714 | -0.99184 | -1.0071 | -0.57755 | -0.57857 | -0.59796 | -0.62959 | -0.65306 | -0.69082 | -0.77857 | -0.86327 | -0.93673 | -1.0041 | -1.3031 | -1.3939 | -1.3878
|  | PARK | HT |  |  |  |  | -1.0786 | -1.0673 | -1.0776 | -1.1102 | -1.1204 | -1.1602 | -1.2439 | -1.3173 | -1.3755 | -1.4265 | -1.501 | -1.5061 | -1.4908 | -0.19694 | -0.2051 | -0.22959 | -0.27347 | -0.2949 | -0.3449 | -0.44082 | -0.52245 | -0.59388 | -0.65918 | -0.75306 | -0.74592 | -0.71224 | -0.57959 | -0.57857 | -0.59694 | -0.63265 | -0.65714 | -0.7 | -0.7949 | -0.87857 | -0.94796 | -1.0163 | -1.1051 | -1.1082 | -1.0827
|  | PARK | HE |  |  |  |  | -1.0786 | -1.0684 | -1.0776 | -1.1051 | -1.1143 | -1.1541 | -1.2388 | -1.3133 | -1.3776 | -1.4306 | -1.4959 | -1.5163 | -1.5378 | -0.19694 | -0.2051 | -0.23061 | -0.27143 | -0.29082 | -0.34082 | -0.43571 | -0.51837 | -0.59388 | -0.65816 | -0.72347 | -0.73776 | -0.76429 | -0.57857 | -0.57959 | -0.59694 | -0.63061 | -0.65306 | -0.6949 | -0.7898 | -0.87449 | -0.95 | -1.0173 | -1.0878 | -1.101 | -1.1122
|  | PARK | FB |  |  |  |  | -1.0245 | -1.0173 | -1.0041 | -1.001 | -1 | -1.0214 | -1.0357 | -1.0633 | -1.0796 | -1.1194 | -1.25 | -1.301 | -1.3418 | -0.14388 | -0.15714 | -0.15918 | -0.17551 | -0.17755 | -0.21633 | -0.23776 | -0.2949 | -0.32857 | -0.38367 | -0.57143 | -0.68878 | -0.82245 | -0.52653 | -0.52653 | -0.52755 | -0.5398 | -0.5449 | -0.57041 | -0.58776 | -0.62347 | -0.63367 | -0.68061 | -0.84592 | -0.91633 | -0.9398
| ALNESS | PEDDIESTON | MINIMUM HEADROOM | NH 74198 63656 | NO | NO | 0.027 | 1.6806 | 1.6939 | 1.5878 | 1.598 | 1.5673 | 1.4551 | 1.351 | 1.2847 | 1.2153 | 1.1449 | 0.97347 | 0.79898 | 0.66939 | 2.2612 | 2.2633 | 2.2255 | 2.2163 | 2.1837 | 2.1163 | 2.0418 | 2.001 | 1.948 | 1.9071 | 1.7918 | 1.799 | 1.7306 | 1.8929 | 1.9 | 1.8153 | 1.8082 | 1.7755 | 1.7041 | 1.6082 | 1.552 | 1.4878 | 1.4265 | 1.2796 | 1.1663 | 1.0816
|  | PEDDIESTON | EE |  |  |  |  | 1.6816 | 1.6939 | 1.5898 | 1.599 | 1.5724 | 1.4939 | 1.449 | 1.3449 | 1.2459 | 1.1673 | 0.97347 | 0.79898 | 0.66939 | 2.2633 | 2.2633 | 2.2255 | 2.2173 | 2.1847 | 2.1602 | 2.1133 | 2.0449 | 1.9735 | 1.9122 | 1.8153 | 1.8031 | 1.7898 | 1.8929 | 1.9 | 1.8153 | 1.8102 | 1.7786 | 1.7398 | 1.6898 | 1.601 | 1.5143 | 1.4418 | 1.2796 | 1.1663 | 1.0898
|  | PEDDIESTON | HT |  |  |  |  | 1.6806 | 1.6939 | 1.5878 | 1.598 | 1.5704 | 1.4551 | 1.351 | 1.2847 | 1.2153 | 1.1684 | 1.0143 | 0.84388 | 0.67653 | 2.2612 | 2.2633 | 2.2255 | 2.2163 | 2.1837 | 2.1163 | 2.0418 | 2.001 | 1.948 | 1.9071 | 1.7918 | 1.799 | 1.8092 | 1.8929 | 1.9 | 1.8153 | 1.8092 | 1.7776 | 1.7041 | 1.6082 | 1.552 | 1.4878 | 1.4408 | 1.2959 | 1.1949 | 1.0969
|  | PEDDIESTON | HE |  |  |  |  | 1.6806 | 1.6939 | 1.5878 | 1.598 | 1.5673 | 1.5031 | 1.4398 | 1.3296 | 1.2255 | 1.1449 | 1.0102 | 0.81531 | 0.67551 | 2.2612 | 2.2633 | 2.2255 | 2.2163 | 2.1837 | 2.1602 | 2.1122 | 2.0408 | 1.9673 | 1.9082 | 1.8143 | 1.8 | 1.7704 | 1.8929 | 1.9 | 1.8153 | 1.8082 | 1.7755 | 1.7439 | 1.6837 | 1.5908 | 1.5 | 1.4265 | 1.3031 | 1.1704 | 1.0816
|  | PEDDIESTON | FB |  |  |  |  | 1.7102 | 1.7265 | 1.6663 | 1.6735 | 1.6796 | 1.6612 | 1.6694 | 1.649 | 1.5939 | 1.5408 | 1.3755 | 1.2286 | 1.1735 | 2.2816 | 2.2827 | 2.2663 | 2.2582 | 2.2551 | 2.2367 | 2.2214 | 2.198 | 2.152 | 2.099 | 1.9622 | 1.8173 | 1.7306 | 1.9214 | 1.9316 | 1.8857 | 1.8888 | 1.8918 | 1.8724 | 1.8592 | 1.8378 | 1.7837 | 1.7286 | 1.5918 | 1.4367 | 1.4092
| PETERHEAD GRANGE | PETERHEAD GRANGE | MINIMUM HEADROOM | NK 11738 46516 | NO | YES | 6.003 | 6.9437 | 6.7967 | 6.6927 | 6.3518 | 5.3886 | 4.2988 | 2.5876 | 1.2753 | -1.142 | -2.0859 | -8.5247 | -13.7482 | -17.8349 | 9.3002 | 9.1553 | 9.141 | 8.942 | 8.2135 | 7.3716 | 6.0859 | 4.8522 | 2.4063 | 1.6318 | -3.3569 | -7.5753 | -11.8427 | 8.7053 | 8.541 | 8.5033 | 8.191 | 7.3288 | 6.2859 | 4.7522 | 3.3186 | 0.61449 | -0.38755 | -6.6641 | -11.6824 | -16.2233
|  | PETERHEAD GRANGE | EE |  |  |  |  | 6.9804 | 6.7967 | 6.7151 | 6.4233 | 5.4814 | 4.2988 | 2.5876 | 1.3161 | -0.32673 | -1.1124 | -7.1033 | -12.4278 | -15.0288 | 9.3359 | 9.1584 | 9.1655 | 8.989 | 8.2533 | 7.3982 | 6.1329 | 5.2196 | 3.8818 | 3.4216 | -0.51102 | -4.8876 | -6.958 | 8.7339 | 8.541 | 8.5114 | 8.2431 | 7.3971 | 6.2859 | 4.7522 | 3.5369 | 1.891 | 1.1655 | -4.3947 | -9.9671 | -12.5365
|  | PETERHEAD GRANGE | HT |  |  |  |  | 6.96 | 6.8059 | 6.6927 | 6.3518 | 5.3886 | 4.7916 | 3.5222 | 2.1814 | -0.0063265 | -1.5471 | -8.0186 | -13.7482 | -17.8349 | 9.3135 | 9.1553 | 9.141 | 8.942 | 8.2135 | 7.8543 | 6.9073 | 5.8829 | 3.9696 | 2.8553 | -1.4559 | -6.0069 | -9.561 | 8.7186 | 8.5533 | 8.5033 | 8.191 | 7.3288 | 6.7349 | 5.5318 | 4.1788 | 1.9441 | 0.58286 | -5.2437 | -11.1722 | -15.509
|  | PETERHEAD GRANGE | HE |  |  |  |  | 6.9437 | 6.808 | 6.7171 | 6.4069 | 5.4631 | 4.3396 | 2.708 | 1.2753 | -1.142 | -2.0859 | -8.5247 | -13.2278 | -17.2716 | 9.3002 | 9.1553 | 9.1573 | 8.9696 | 8.2349 | 7.3716 | 6.0859 | 4.8522 | 2.4063 | 1.6318 | -3.3569 | -7.5753 | -11.8427 | 8.7053 | 8.5522 | 8.5206 | 8.2308 | 7.3829 | 6.3114 | 4.8022 | 3.3186 | 0.61449 | -0.38755 | -6.6641 | -11.6824 | -16.2233
|  | PETERHEAD GRANGE | FB |  |  |  |  | 7.2631 | 7.2151 | 7.1722 | 7.0355 | 6.6508 | 6.109 | 5.159 | 4.0182 | 3.2406 | 2.9202 | 0.61408 | -2.488 | -4.3196 | 9.6094 | 9.5522 | 9.5176 | 9.342 | 9.0461 | 8.5645 | 7.5798 | 6.4033 | 5.5257 | 5.1604 | 3.2288 | 0.28694 | -1.8743 | 9.0624 | 9.0257 | 9.0155 | 8.8298 | 8.5237 | 8.0778 | 7.1227 | 5.9829 | 5.0318 | 4.6237 | 2.5002 | -1.1049 | -2.6222
| PETERHEAD GRANGE | PETERHEAD NORTH STREET | MINIMUM HEADROOM | NK 13470 46450 | NO | YES | 4.148 | 4.6432 | 4.5932 | 4.5809 | 4.5544 | 4.4768 | 4.384 | 4.2728 | 4.1534 | 4.0534 | 3.9391 | 3.2503 | 2.632 | 2.2044 | 9.6813 | 9.6497 | 9.6456 | 9.6405 | 9.5364 | 9.3028 | 9.0568 | 8.7803 | 8.5854 | 8.3538 | 7.6375 | 7.3752 | 6.8579 | 7.1303 | 6.9079 | 6.8273 | 6.8222 | 6.616 | 6.3671 | 6.115 | 5.8283 | 5.615 | 5.3558 | 4.4242 | 3.9885 | 3.6487
|  | PETERHEAD NORTH STREET | EE |  |  |  |  | 4.6432 | 4.5932 | 4.5809 | 4.5544 | 4.483 | 4.386 | 4.2738 | 4.1534 | 4.0636 | 3.9483 | 3.2503 | 2.632 | 2.2044 | 9.6834 | 9.6497 | 9.6456 | 9.6415 | 9.5364 | 9.3273 | 9.0864 | 8.8436 | 8.6375 | 8.3813 | 7.6375 | 7.3752 | 7.065 | 7.1303 | 6.9079 | 6.8568 | 6.8334 | 6.616 | 6.3875 | 6.1395 | 5.8752 | 5.6528 | 5.3793 | 4.4242 | 3.9885 | 3.6487
|  | PETERHEAD NORTH STREET | HT |  |  |  |  | 4.6483 | 4.6064 | 4.5952 | 4.5697 | 4.4922 | 4.3911 | 4.2728 | 4.1646 | 4.0534 | 3.9391 | 3.3105 | 2.7626 | 2.4524 | 9.6824 | 9.6507 | 9.6497 | 9.6436 | 9.5385 | 9.3171 | 9.0568 | 8.8671 | 8.6007 | 8.3538 | 7.6691 | 7.4599 | 7.3028 | 7.1344 | 6.916 | 6.8681 | 6.8456 | 6.6242 | 6.3824 | 6.115 | 5.9048 | 5.6211 | 5.3558 | 4.4579 | 4.0364 | 3.7875
|  | PETERHEAD NORTH STREET | HE |  |  |  |  | 4.6452 | 4.5993 | 4.585 | 4.5564 | 4.4768 | 4.384 | 4.2789 | 4.1595 | 4.0707 | 3.9871 | 3.584 | 3.4003 | 3.2462 | 9.6813 | 9.6507 | 9.6477 | 9.6405 | 9.5385 | 9.3028 | 9.0691 | 8.7803 | 8.5854 | 8.3956 | 7.9507 | 7.9232 | 7.765 | 7.1334 | 6.913 | 6.862 | 6.8375 | 6.6191 | 6.3671 | 6.1171 | 5.8283 | 5.615 | 5.4191 | 4.8415 | 4.713 | 4.6201
|  | PETERHEAD NORTH STREET | FB |  |  |  |  | 4.6717 | 4.6809 | 4.6156 | 4.6075 | 4.5983 | 4.5738 | 4.5656 | 4.5503 | 4.5034 | 4.4534 | 4.2952 | 4.0442 | 3.8289 | 9.6936 | 9.7017 | 9.6456 | 9.6466 | 9.6456 | 9.6038 | 9.562 | 9.5232 | 9.3956 | 9.2579 | 8.7803 | 7.9364 | 6.8579 | 7.165 | 7.162 | 6.8273 | 6.8222 | 6.8171 | 6.7701 | 6.7548 | 6.7426 | 6.6201 | 6.4936 | 6.1171 | 5.4885 | 5.0773
| FORT WILLIAM | PINEGROVE | MINIMUM HEADROOM | NN 10496 73556 | NO | NO | 0.539 | 5.6327 | 5.6837 | 5.7378 | 5.6745 | 5.6592 | 5.3653 | 5.0765 | 4.9357 | 4.801 | 4.8327 | 4.3143 | 4.0786 | 3.8786 | 6.7908 | 6.8184 | 6.8429 | 6.8235 | 6.8276 | 6.7173 | 6.5143 | 6.4592 | 6.3878 | 6.4378 | 6.1704 | 6.1071 | 5.8133 | 6.4694 | 6.5041 | 6.5286 | 6.4939 | 6.4837 | 6.2653 | 6.0224 | 5.9092 | 5.7969 | 5.8327 | 5.4102 | 5.249 | 5.1204
|  | PINEGROVE | EE |  |  |  |  | 5.6327 | 5.6837 | 5.7378 | 5.6776 | 5.6653 | 5.5153 | 5.0765 | 4.9357 | 4.801 | 4.8327 | 4.3143 | 4.0786 | 3.8786 | 6.7908 | 6.8184 | 6.8429 | 6.8235 | 6.8296 | 6.7959 | 6.5143 | 6.4592 | 6.3878 | 6.4378 | 6.1704 | 6.1327 | 6.0245 | 6.4694 | 6.5041 | 6.5286 | 6.4959 | 6.4878 | 6.3806 | 6.0224 | 5.9092 | 5.7969 | 5.8327 | 5.4102 | 5.249 | 5.1204
|  | PINEGROVE | HT |  |  |  |  | 5.6337 | 5.6847 | 5.7388 | 5.6765 | 5.6633 | 5.3653 | 5.1959 | 5.0306 | 4.9255 | 4.9061 | 4.5408 | 4.1531 | 3.9602 | 6.7918 | 6.8204 | 6.8429 | 6.8245 | 6.8276 | 6.7173 | 6.6378 | 6.5602 | 6.5071 | 6.5327 | 6.2816 | 6.1469 | 6.1755 | 6.4714 | 6.5071 | 6.5296 | 6.4969 | 6.4847 | 6.2653 | 6.1265 | 5.9949 | 5.9061 | 5.9031 | 5.5816 | 5.3041 | 5.1929
|  | PINEGROVE | HE |  |  |  |  | 5.6337 | 5.6847 | 5.7398 | 5.6745 | 5.6592 | 5.4531 | 5.0816 | 4.9439 | 4.8143 | 4.8439 | 4.4112 | 4.1286 | 4.1439 | 6.7929 | 6.8204 | 6.8439 | 6.8235 | 6.8296 | 6.7663 | 6.5214 | 6.4643 | 6.3969 | 6.4459 | 6.2 | 6.1582 | 6.2122 | 6.4724 | 6.5071 | 6.5306 | 6.4939 | 6.4837 | 6.3347 | 6.0306 | 5.9173 | 5.8112 | 5.8429 | 5.4888 | 5.299 | 5.3439
|  | PINEGROVE | FB |  |  |  |  | 5.6939 | 5.7633 | 5.8214 | 5.8398 | 5.8704 | 5.8816 | 5.8418 | 5.8 | 5.7857 | 5.7684 | 5.401 | 5.0949 | 4.9888 | 6.8388 | 6.8816 | 6.9041 | 6.9163 | 6.9337 | 6.9173 | 6.8796 | 6.8184 | 6.7857 | 6.7418 | 6.4939 | 6.1071 | 5.8133 | 6.5378 | 6.598 | 6.6388 | 6.651 | 6.6776 | 6.6898 | 6.648 | 6.5878 | 6.5643 | 6.5388 | 6.2378 | 5.8959 | 5.8408
| TUMMEL BRIDGE | PITLOCHRY | MINIMUM HEADROOM | NN 95756 58991 | NO | YES | 2.06 | 0.79723 | 0.73295 | 0.69928 | 0.62989 | 0.49417 | 0.2656 | 0.01152 | -0.25277 | -0.4997 | -0.61399 | -1.6354 | -2.363 | -2.8109 | 1.7847 | 1.7266 | 1.7062 | 1.6847 | 1.5858 | 1.449 | 1.2204 | 0.9582 | 0.75208 | 0.698 | -0.002 | -0.31424 | -0.48873 | 1.543 | 1.4665 | 1.3798 | 1.3563 | 1.1461 | 0.83282 | 0.52568 | 0.18894 | -0.09677 | -0.17942 | -1.0886 | -1.6437 | -1.9611
|  | PITLOCHRY | EE |  |  |  |  | 0.79723 | 0.73295 | 0.7105 | 0.62989 | 0.5003 | 0.27581 | 0.017643 | -0.24562 | -0.46297 | -0.60174 | -1.6354 | -2.363 | -2.8109 | 1.7847 | 1.7266 | 1.7062 | 1.6847 | 1.5858 | 1.4572 | 1.2286 | 0.9582 | 0.77045 | 0.698 | 0.0020816 | -0.31424 | -0.48873 | 1.543 | 1.4665 | 1.4287 | 1.393 | 1.1471 | 0.84507 | 0.53384 | 0.18894 | -0.068199 | -0.17942 | -1.0886 | -1.6437 | -1.9611
|  | PITLOCHRY | HT |  |  |  |  | 0.79928 | 0.73601 | 0.69928 | 0.64723 | 0.5207 | 0.31764 | 0.072745 | -0.17726 | -0.39664 | -0.53542 | -1.4997 | -2.2364 | -2.7089 | 1.7847 | 1.7266 | 1.7072 | 1.6858 | 1.5888 | 1.4633 | 1.2225 | 0.96127 | 0.77657 | 0.70208 | -0.002 | -0.27037 | -0.33567 | 1.544 | 1.4675 | 1.4349 | 1.3849 | 1.1594 | 0.87058 | 0.55323 | 0.22364 | -0.025342 | -0.13861 | -1.006 | -1.5488 | -1.8549
|  | PITLOCHRY | HE |  |  |  |  | 0.79826 | 0.73397 | 0.71458 | 0.62989 | 0.49417 | 0.2656 | 0.01152 | -0.25277 | -0.4997 | -0.61399 | -1.4293 | -1.8722 | -2.1232 | 1.7847 | 1.7266 | 1.7072 | 1.6858 | 1.5858 | 1.449 | 1.2204 | 0.97147 | 0.75208 | 0.72555 | 0.11127 | 0.094939 | 0.053102 | 1.544 | 1.4675 | 1.4318 | 1.3736 | 1.1461 | 0.83282 | 0.52568 | 0.20119 | -0.09677 | -0.15902 | -0.92126 | -1.1835 | -1.3274
|  | PITLOCHRY | FB |  |  |  |  | 0.84621 | 0.8503 | 0.7605 | 0.73091 | 0.74417 | 0.68397 | 0.63295 | 0.58703 | 0.51764 | 0.45744 | 0.19213 | -0.28644 | -0.74562 | 1.8194 | 1.8174 | 1.7307 | 1.7194 | 1.7133 | 1.6766 | 1.6511 | 1.6337 | 1.5307 | 1.397 | 1.0756 | 0.46637 | -0.072408 | 1.5838 | 1.5828 | 1.3798 | 1.3563 | 1.3542 | 1.2696 | 1.2461 | 1.1808 | 1.0491 | 0.91343 | 0.57466 | -0.059015 | -0.45799
| ARDMORE | POLLACHAR | MINIMUM HEADROOM | NF 75073 14513 | NO | YES | 1.19 | 1.5574 | 1.5104 | 1.5064 | 1.487 | 1.2472 | 1.0298 | 0.61453 | 0.35229 | 0.15535 | -0.0038367 | -0.58853 | -1.1732 | -1.3732 | 2.54 | 2.4645 | 2.4737 | 2.4809 | 2.1584 | 2.036 | 1.7135 | 1.536 | 1.4247 | 1.3064 | 0.87984 | 0.60841 | 0.62167 | 1.9645 | 1.9013 | 1.889 | 1.8543 | 1.486 | 1.3002 | 0.91555 | 0.67371 | 0.51147 | 0.36351 | -0.18649 | -0.64363 | -0.73853
|  | POLLACHAR | EE |  |  |  |  | 1.5625 | 1.5809 | 1.5064 | 1.488 | 1.2492 | 1.0411 | 0.63392 | 0.38392 | 0.19208 | 0.029837 | -0.58853 | -1.1732 | -1.3732 | 2.5411 | 2.5696 | 2.4737 | 2.4809 | 2.1584 | 2.0543 | 1.7319 | 1.5676 | 1.4625 | 1.3298 | 0.888 | 0.60841 | 0.62167 | 1.9666 | 1.9809 | 1.889 | 1.8553 | 1.486 | 1.3207 | 0.93596 | 0.70943 | 0.55535 | 0.39514 | -0.18649 | -0.64363 | -0.73853
|  | POLLACHAR | HT |  |  |  |  | 1.5574 | 1.5104 | 1.5094 | 1.49 | 1.2543 | 1.0472 | 0.78698 | 0.58086 | 0.338 | 0.088 | -0.44159 | -1.0702 | -1.3089 | 2.54 | 2.4645 | 2.4747 | 2.4819 | 2.1615 | 2.0421 | 1.8492 | 1.7278 | 1.5696 | 1.3502 | 0.87984 | 0.61657 | 0.72065 | 1.9645 | 1.9013 | 1.8931 | 1.8574 | 1.49 | 1.3125 | 1.0696 | 0.89106 | 0.68086 | 0.43494 | -0.10384 | -0.57935 | -0.67731
|  | POLLACHAR | HE |  |  |  |  | 1.5584 | 1.5829 | 1.5104 | 1.487 | 1.2472 | 1.0298 | 0.61453 | 0.35229 | 0.15535 | -0.0038367 | -0.36608 | -0.74261 | -0.9569 | 2.5421 | 2.5696 | 2.4758 | 2.4829 | 2.1604 | 2.036 | 1.7135 | 1.536 | 1.4247 | 1.3064 | 1.0258 | 1.0482 | 1.0329 | 1.9666 | 1.9829 | 1.8931 | 1.8543 | 1.488 | 1.3002 | 0.91555 | 0.67371 | 0.51147 | 0.36351 | 0.018612 | -0.19363 | -0.30996
|  | POLLACHAR | FB |  |  |  |  | 1.6104 | 1.6625 | 1.689 | 1.638 | 1.6492 | 1.6523 | 1.5656 | 1.39 | 1.39 | 1.2156 | 0.77984 | 0.44616 | 0.11147 | 2.5717 | 2.6043 | 2.6207 | 2.5339 | 2.5431 | 2.5431 | 2.4329 | 2.2472 | 2.2441 | 1.939 | 1.4982 | 1.1329 | 0.69616 | 2.0207 | 2.0574 | 2.0635 | 2.0023 | 2.0033 | 2.0013 | 1.8982 | 1.7247 | 1.7156 | 1.3431 | 0.89412 | 0.50739 | 0.20433
| FORT WILLIAM | POOR HOUSE | MINIMUM HEADROOM | NM 71766 70148 | YES | NO | 0 | 0.1078 | 0.10882 | 0.10882 | 0.1078 | 0.096571 | 0.096571 | 0.09351 | 0.09249 | 0.088408 | 0.088408 | 0.084327 | 0.083306 | 0.081265 | 0.10288 | 0.1039 | 0.1039 | 0.1039 | 0.089612 | 0.089612 | 0.089612 | 0.090633 | 0.086551 | 0.086551 | 0.082469 | 0.08349 | 0.081449 | 0.10636 | 0.10738 | 0.10738 | 0.10738 | 0.094112 | 0.092071 | 0.091051 | 0.090031 | 0.086969 | 0.085949 | 0.082888 | 0.081867 | 0.080847
|  | POOR HOUSE | EE |  |  |  |  | 0.1078 | 0.10882 | 0.10882 | 0.1078 | 0.097592 | 0.096571 | 0.09351 | 0.09249 | 0.088408 | 0.088408 | 0.084327 | 0.085347 | 0.084327 | 0.10288 | 0.1039 | 0.1039 | 0.1039 | 0.089612 | 0.089612 | 0.091653 | 0.090633 | 0.087571 | 0.086551 | 0.08349 | 0.08451 | 0.08451 | 0.10636 | 0.10738 | 0.10738 | 0.10738 | 0.094112 | 0.092071 | 0.091051 | 0.090031 | 0.086969 | 0.085949 | 0.083908 | 0.083908 | 0.083908
|  | POOR HOUSE | HT |  |  |  |  | 0.1078 | 0.10882 | 0.10882 | 0.1078 | 0.097592 | 0.096571 | 0.094531 | 0.09351 | 0.088408 | 0.089429 | 0.084327 | 0.083306 | 0.081265 | 0.10288 | 0.1039 | 0.1039 | 0.1039 | 0.089612 | 0.089612 | 0.091653 | 0.090633 | 0.086551 | 0.086551 | 0.082469 | 0.08349 | 0.081449 | 0.10636 | 0.10738 | 0.10738 | 0.10738 | 0.094112 | 0.093092 | 0.091051 | 0.090031 | 0.086969 | 0.086969 | 0.082888 | 0.081867 | 0.080847
|  | POOR HOUSE | HE |  |  |  |  | 0.1078 | 0.10882 | 0.10882 | 0.1078 | 0.096571 | 0.096571 | 0.09351 | 0.09249 | 0.088408 | 0.088408 | 0.085347 | 0.083306 | 0.084327 | 0.10288 | 0.1039 | 0.1039 | 0.1039 | 0.089612 | 0.089612 | 0.091653 | 0.090633 | 0.086551 | 0.086551 | 0.08349 | 0.08451 | 0.085531 | 0.10636 | 0.10738 | 0.10738 | 0.10738 | 0.094112 | 0.092071 | 0.091051 | 0.090031 | 0.086969 | 0.085949 | 0.083908 | 0.081867 | 0.083908
|  | POOR HOUSE | FB |  |  |  |  | 0.1078 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.096571 | 0.10065 | 0.10065 | 0.10065 | 0.09351 | 0.09249 | 0.089429 | 0.10288 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.089612 | 0.093694 | 0.093694 | 0.093694 | 0.087571 | 0.085531 | 0.082469 | 0.10636 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.093092 | 0.097173 | 0.097173 | 0.097173 | 0.091051 | 0.08901 | 0.085949
| PORT ANN | PORT ASKAIG | MINIMUM HEADROOM | NR 42082 68818 | NO | YES | 1.161 | -0.83808 | -1.1044 | -1.3401 | -1.5248 | -1.8116 | -1.9687 | -2.1075 | -2.2473 | -2.3422 | -2.4513 | -2.8401 | -3.1411 | -3.2973 | -0.61053 | -0.90441 | -1.1646 | -1.3442 | -1.5922 | -1.7585 | -1.9095 | -2.0309 | -2.1238 | -2.2156 | -2.5779 | -2.8218 | -2.935 | -0.58706 | -0.88298 | -1.1248 | -1.3024 | -1.6095 | -1.7932 | -1.9534 | -2.0881 | -2.182 | -2.2626 | -2.6473 | -2.9248 | -3.0605
|  | PORT ASKAIG | EE |  |  |  |  | -0.83808 | -0.83298 | -1.1085 | -1.3605 | -1.6636 | -1.9646 | -2.0952 | -2.2146 | -2.332 | -2.4483 | -2.8401 | -3.1411 | -3.2973 | -0.61053 | -0.61155 | -0.90339 | -1.1718 | -1.4605 | -1.7564 | -1.8962 | -1.9993 | -2.1003 | -2.2156 | -2.5779 | -2.8218 | -2.935 | -0.58706 | -0.58502 | -0.88298 | -1.1401 | -1.482 | -1.7901 | -1.9411 | -2.0564 | -2.1687 | -2.2626 | -2.6473 | -2.9248 | -3.0605
|  | PORT ASKAIG | HT |  |  |  |  | -0.83808 | -1.1044 | -1.3401 | -1.5248 | -1.8116 | -1.9544 | -2.0769 | -2.2248 | -2.3422 | -2.4177 | -2.7942 | -3.1116 | -3.2595 | -0.61053 | -0.90441 | -1.1646 | -1.3442 | -1.5922 | -1.7564 | -1.8901 | -2.0218 | -2.1238 | -2.1983 | -2.5636 | -2.8156 | -2.8962 | -0.58706 | -0.88298 | -1.1248 | -1.3024 | -1.6095 | -1.7871 | -1.9269 | -2.0728 | -2.182 | -2.2616 | -2.6126 | -2.9024 | -3.0228
|  | PORT ASKAIG | HE |  |  |  |  | -0.83706 | -0.83502 | -1.1075 | -1.3605 | -1.6626 | -1.9687 | -2.1075 | -2.2473 | -2.3238 | -2.4513 | -2.6575 | -2.6932 | -2.7248 | -0.60849 | -0.61257 | -0.90339 | -1.1718 | -1.4605 | -1.7585 | -1.9095 | -2.0309 | -2.0901 | -2.2126 | -2.4075 | -2.3718 | -2.3595 | -0.58502 | -0.58706 | -0.88298 | -1.1391 | -1.483 | -1.7932 | -1.9534 | -2.0881 | -2.1585 | -2.2616 | -2.4697 | -2.4799 | -2.4891
|  | PORT ASKAIG | FB |  |  |  |  | -0.81665 | -0.80951 | -0.80237 | -1.084 | -1.3177 | -1.4891 | -1.6616 | -1.6656 | -1.6667 | -1.8105 | -2.1064 | -2.4207 | -2.636 | -0.59114 | -0.59216 | -0.59012 | -0.89829 | -1.1575 | -1.334 | -1.5167 | -1.5228 | -1.5269 | -1.6799 | -1.984 | -2.3024 | -2.5503 | -0.56665 | -0.56359 | -0.56053 | -0.86971 | -1.1095 | -1.2799 | -1.4513 | -1.4575 | -1.4585 | -1.6677 | -1.9707 | -2.3248 | -2.5177
| PORT ANN | PORT ELLEN | MINIMUM HEADROOM | NR 36459 45513 | YES | YES | 3.186 | -0.72519 | -0.96907 | -1.0517 | -1.1538 | -1.2905 | -1.5425 | -1.7038 | -1.817 | -1.9905 | -2.2017 | -2.7129 | -3.0405 | -3.2027 | -0.50662 | -0.75254 | -0.77091 | -0.90968 | -0.91784 | -1.1689 | -1.3678 | -1.4597 | -1.5944 | -1.7995 | -2.3056 | -2.5883 | -2.7087 | -0.62254 | -0.85315 | -0.92254 | -0.95519 | -1.0725 | -1.2807 | -1.4613 | -1.5593 | -1.7266 | -1.9378 | -2.4593 | -2.8011 | -2.9409
|  | PORT ELLEN | EE |  |  |  |  | -0.72417 | -0.73336 | -1.0283 | -1.0609 | -1.1905 | -1.3874 | -1.6436 | -1.7997 | -1.9568 | -2.0425 | -2.7129 | -3.0405 | -3.2027 | -0.5056 | -0.5056 | -0.76172 | -0.77193 | -0.89029 | -1.0964 | -1.3393 | -1.4597 | -1.5883 | -1.6811 | -2.3056 | -2.5883 | -2.7087 | -0.62152 | -0.62152 | -0.89295 | -0.91131 | -1.0327 | -1.1572 | -1.4134 | -1.5593 | -1.7062 | -1.7991 | -2.4593 | -2.8011 | -2.9409
|  | PORT ELLEN | HT |  |  |  |  | -0.72417 | -0.96907 | -1.0517 | -1.1538 | -1.2905 | -1.5425 | -1.6885 | -1.817 | -1.9905 | -2.2017 | -2.6762 | -2.9721 | -3.1589 | -0.5056 | -0.75254 | -0.77091 | -0.79029 | -0.91376 | -1.1689 | -1.2944 | -1.4148 | -1.577 | -1.7995 | -2.3046 | -2.5505 | -2.6525 | -0.6205 | -0.85315 | -0.92254 | -0.95519 | -1.0725 | -1.2807 | -1.4215 | -1.5511 | -1.7195 | -1.9378 | -2.4378 | -2.7389 | -2.8991
|  | PORT ELLEN | HE |  |  |  |  | -0.72519 | -0.73744 | -1.0283 | -1.0936 | -1.2232 | -1.4262 | -1.7038 | -1.815 | -1.9864 | -2.0915 | -2.5997 | -2.6364 | -2.6864 | -0.50662 | -0.50662 | -0.7658 | -0.77805 | -0.89948 | -1.1076 | -1.3678 | -1.4413 | -1.5944 | -1.7076 | -2.1985 | -2.1301 | -2.128 | -0.62254 | -0.6256 | -0.90519 | -0.9358 | -1.0307 | -1.1868 | -1.4613 | -1.5593 | -1.7266 | -1.8389 | -2.347 | -2.3491 | -2.3695
|  | PORT ELLEN | FB |  |  |  |  | -0.70274 | -0.68642 | -0.71499 | -1.1191 | -1.1201 | -1.118 | -1.1201 | -1.1538 | -1.1629 | -1.2813 | -1.6885 | -2.1772 | -2.4507 | -0.49131 | -0.48315 | -0.49131 | -0.90968 | -0.91784 | -0.92499 | -0.93621 | -0.9607 | -0.97805 | -1.125 | -1.5352 | -2.0383 | -2.3995 | -0.59397 | -0.57968 | -0.59907 | -0.95315 | -0.95417 | -0.95315 | -0.95417 | -0.97866 | -0.99499 | -1.1215 | -1.5174 | -2.0634 | -2.3042
| DUNVEGAN | PORTREE | MINIMUM HEADROOM | NG 48102 44602 | NO | NO | 1.345 | 3.2786 | 3.2418 | 3.15 | 2.9949 | 2.902 | 1.5265 | 0.40102 | -0.76939 | -1.5173 | -2.0276 | -3.1541 | -3.5673 | -3.9561 | 3.9345 | 3.9212 | 3.8988 | 3.8784 | 3.7345 | 2.7559 | 1.7273 | 0.65286 | 0.063061 | -0.21551 | -0.72776 | -0.70224 | -0.69714 | 3.609 | 3.5753 | 3.5151 | 3.4131 | 3.3437 | 2.0253 | 0.91102 | -0.2002 | -0.76245 | -1.2227 | -2.2104 | -2.4318 | -2.5706
|  | PORTREE | EE |  |  |  |  | 3.2786 | 3.2418 | 3.152 | 2.9949 | 2.902 | 2.4235 | 1.8918 | 0.76531 | -0.18163 | -1.1918 | -3.1541 | -3.5673 | -3.8898 | 3.9345 | 3.9212 | 3.8998 | 3.8784 | 3.8447 | 3.5059 | 3.3273 | 2.3855 | 1.6192 | 0.5549 | -0.70531 | -0.69918 | -0.69 | 3.609 | 3.5753 | 3.5171 | 3.4131 | 3.3437 | 2.9171 | 2.5233 | 1.4141 | 0.46408 | -0.51347 | -2.2104 | -2.4318 | -2.5706
|  | PORTREE | HT |  |  |  |  | 3.2796 | 3.2429 | 3.151 | 2.999 | 2.9031 | 1.5265 | 0.40102 | -0.76939 | -1.5173 | -2.0276 | -3.0571 | -3.5041 | -3.9561 | 3.9355 | 3.9212 | 3.8988 | 3.8804 | 3.8447 | 2.7559 | 1.7273 | 0.65286 | 0.063061 | -0.21551 | -0.72776 | -0.70224 | -0.66449 | 3.611 | 3.5763 | 3.5161 | 3.4161 | 3.3437 | 2.0253 | 0.91102 | -0.2002 | -0.76245 | -1.2227 | -2.1553 | -2.3604 | -2.5706
|  | PORTREE | HE |  |  |  |  | 3.2796 | 3.2418 | 3.15 | 3.0163 | 2.9296 | 2.4378 | 1.9286 | 0.75408 | -0.3551 | -1.4918 | -3.0122 | -3.4765 | -3.751 | 3.9355 | 3.9212 | 3.8988 | 3.8824 | 3.8478 | 3.562 | 3.308 | 2.3641 | 1.41 | 0.22531 | -0.67163 | -0.66449 | -0.66449 | 3.611 | 3.5763 | 3.5151 | 3.4273 | 3.361 | 2.9508 | 2.5447 | 1.3937 | 0.2702 | -0.79 | -2.0737 | -2.3073 | -2.4053
|  | PORTREE | FB |  |  |  |  | 3.35 | 3.3806 | 3.3541 | 3.3357 | 3.0276 | 2.9918 | 2.8765 | 2.7643 | 2.1071 | 1.4918 | -1.1857 | -1.5612 | -1.7327 | 3.9876 | 4.0029 | 4.0059 | 4.0039 | 3.7345 | 3.7029 | 3.6243 | 3.5661 | 2.9427 | 2.2631 | -0.24306 | -0.5298 | -0.69714 | 3.6763 | 3.6978 | 3.6784 | 3.6539 | 3.4069 | 3.3835 | 3.262 | 3.1712 | 2.4835 | 1.81 | -0.46755 | -0.86041 | -1.0676
| MACDUFF | PORTSOY | MINIMUM HEADROOM | NJ 58491 65037 | YES | NO | 0.082 | -0.40588 | -0.40384 | -0.41098 | -0.44873 | -0.47731 | -0.56404 | -0.65792 | -0.77527 | -0.86812 | -0.9569 | -1.2651 | -1.5824 | -1.8253 | 0.22473 | 0.22882 | 0.22371 | 0.21351 | 0.19922 | 0.16963 | 0.14718 | 0.10637 | 0.084939 | 0.06351 | -0.090571 | -0.16506 | -0.32322 | -0.028327 | -0.027306 | -0.033429 | -0.06302 | -0.094653 | -0.16302 | -0.21506 | -0.30588 | -0.39261 | -0.45486 | -0.7171 | -0.95078 | -1.0855
|  | PORTSOY | EE |  |  |  |  | -0.4018 | -0.40384 | -0.41098 | -0.44465 | -0.47731 | -0.5518 | -0.64261 | -0.75486 | -0.84261 | -0.92731 | -1.2651 | -1.5824 | -1.7783 | 0.22984 | 0.22882 | 0.22371 | 0.21351 | 0.19922 | 0.17065 | 0.14922 | 0.10637 | 0.085959 | 0.067592 | -0.070163 | -0.10792 | -0.14363 | -0.023224 | -0.027306 | -0.032408 | -0.06098 | -0.089551 | -0.16302 | -0.2069 | -0.29159 | -0.37424 | -0.43547 | -0.7171 | -0.95078 | -1.0855
|  | PORTSOY | HT |  |  |  |  | -0.4018 | -0.40384 | -0.40996 | -0.43853 | -0.4722 | -0.54261 | -0.61812 | -0.7171 | -0.79159 | -0.87118 | -1.2202 | -1.5671 | -1.8253 | 0.22984 | 0.22882 | 0.22473 | 0.21453 | 0.19922 | 0.17065 | 0.1482 | 0.11045 | 0.090041 | 0.064531 | -0.090571 | -0.10486 | -0.095673 | -0.023224 | -0.027306 | -0.033429 | -0.055878 | -0.08649 | -0.1569 | -0.19261 | -0.26812 | -0.34261 | -0.39873 | -0.67731 | -0.91404 | -1.0804
|  | PORTSOY | HE |  |  |  |  | -0.40588 | -0.40384 | -0.40894 | -0.44873 | -0.46812 | -0.56404 | -0.65792 | -0.77527 | -0.86812 | -0.9569 | -1.2151 | -1.5161 | -1.6814 | 0.22473 | 0.22882 | 0.22473 | 0.21351 | 0.19922 | 0.16963 | 0.14718 | 0.10739 | 0.084939 | 0.06351 | -0.069143 | -0.10588 | -0.15894 | -0.028327 | -0.027306 | -0.032408 | -0.06302 | -0.094653 | -0.14976 | -0.21506 | -0.30588 | -0.39261 | -0.45486 | -0.68649 | -0.92016 | -1.0467
|  | PORTSOY | FB |  |  |  |  | -0.38547 | -0.37322 | -0.37118 | -0.37527 | -0.38343 | -0.41098 | -0.42424 | -0.45486 | -0.46098 | -0.47833 | -0.59873 | -0.77016 | -0.83751 | 0.24106 | 0.25127 | 0.25127 | 0.25127 | 0.24922 | 0.23188 | 0.22371 | 0.20433 | 0.18596 | 0.17678 | 0.057388 | -0.16506 | -0.32322 | -0.0079184 | 0.0012653 | 0.0033061 | -0.00077551 | -0.0099592 | -0.030367 | -0.047714 | -0.073224 | -0.096694 | -0.11302 | -0.2069 | -0.43649 | -0.48343
| WOODHILL | QUEENS LANE NORTH | MINIMUM HEADROOM | NJ 92224 05823 | NO | NO | 0.894 | 2.9044 | 2.9269 | 19.9151 | 19.8417 | 19.658 | 19.457 | 19.1978 | 18.9019 | 18.5753 | 18.1896 | 15.9049 | 14.4366 | 13.4019 | 5.3713 | 5.3927 | 21.4998 | 21.409 | 21.2509 | 20.9968 | 20.708 | 20.36 | 20.0815 | 19.7151 | 18.2641 | 17.3794 | 15.2458 | 4.4429 | 4.4429 | 20.9743 | 20.8907 | 20.7294 | 20.5223 | 20.2529 | 19.956 | 19.6621 | 19.1917 | 17.0376 | 15.5845 | 14.6713
|  | QUEENS LANE NORTH | EE |  |  |  |  | 2.9065 | 2.9289 | 19.9202 | 19.8682 | 19.708 | 19.4804 | 19.2192 | 18.9049 | 18.5835 | 18.2162 | 16.16 | 14.4876 | 13.4019 | 5.3753 | 5.3968 | 21.507 | 21.4825 | 21.2631 | 20.9968 | 20.7284 | 20.3907 | 20.0927 | 19.7151 | 18.2641 | 17.4315 | 16.6407 | 4.444 | 4.444 | 20.9764 | 20.9111 | 20.7662 | 20.5427 | 20.2784 | 19.9672 | 19.6621 | 19.1917 | 17.0376 | 15.5845 | 14.6713
|  | QUEENS LANE NORTH | HT |  |  |  |  | 2.9167 | 2.9524 | 19.959 | 19.907 | 19.7509 | 19.509 | 19.2376 | 18.9019 | 18.5753 | 18.1896 | 15.9049 | 14.4366 | 13.7539 | 5.3713 | 5.3927 | 21.4998 | 21.4753 | 21.2509 | 21.0111 | 20.7427 | 20.3733 | 20.0815 | 19.7335 | 18.4223 | 18.0366 | 17.8468 | 4.4552 | 4.4685 | 21.0151 | 20.9447 | 20.7958 | 20.5723 | 20.2927 | 19.9611 | 19.6621 | 19.2498 | 17.1243 | 15.9651 | 15.5049
|  | QUEENS LANE NORTH | HE |  |  |  |  | 2.9044 | 2.9269 | 19.9151 | 19.8417 | 19.658 | 19.457 | 19.1978 | 18.9039 | 18.6151 | 18.2917 | 16.7264 | 15.7304 | 14.7702 | 5.3733 | 5.3958 | 21.5039 | 21.4702 | 21.2529 | 21.006 | 20.708 | 20.36 | 20.0866 | 19.7182 | 18.5417 | 17.7968 | 16.9182 | 4.4429 | 4.4429 | 20.9743 | 20.8907 | 20.7294 | 20.5223 | 20.2529 | 19.956 | 19.6866 | 19.2958 | 17.7539 | 16.7417 | 15.8733
|  | QUEENS LANE NORTH | FB |  |  |  |  | 2.9983 | 3.0708 | 20.1131 | 20.0529 | 20.0233 | 19.9498 | 19.9274 | 19.8427 | 19.7529 | 19.6172 | 18.9682 | 17.7356 | 16.3172 | 5.4029 | 5.4202 | 21.5366 | 21.409 | 21.3366 | 21.1468 | 21.1192 | 20.9794 | 20.8243 | 20.5621 | 19.4304 | 17.3794 | 15.2458 | 4.5348 | 4.5817 | 21.1641 | 21.0917 | 21.0468 | 20.9825 | 20.9651 | 20.8835 | 20.7815 | 20.6253 | 19.9223 | 17.9733 | 16.909
| THURSO | RACKWICK | MINIMUM HEADROOM | ND 20206 99857 | YES | NO | 0 | 0.071061 | 0.072082 | 0.061878 | 0.061878 | 0.054735 | 0.052694 | 0.047592 | 0.044531 | 0.039429 | 0.040449 | 0.035347 | 0.029224 | 0.025143 | 0.077367 | 0.077367 | 0.069204 | 0.068184 | 0.064102 | 0.064102 | 0.061041 | 0.06002 | 0.055939 | 0.056959 | 0.046755 | 0.046755 | 0.046755 | 0.076765 | 0.076765 | 0.067582 | 0.066561 | 0.059418 | 0.058398 | 0.053296 | 0.050235 | 0.046153 | 0.048194 | 0.042071 | 0.036969 | 0.035949
|  | RACKWICK | EE |  |  |  |  | 0.071061 | 0.072082 | 0.062898 | 0.061878 | 0.055755 | 0.053714 | 0.048612 | 0.044531 | 0.041469 | 0.040449 | 0.035347 | 0.029224 | 0.027184 | 0.077367 | 0.077367 | 0.069204 | 0.068184 | 0.065122 | 0.064102 | 0.062061 | 0.06002 | 0.056959 | 0.056959 | 0.050837 | 0.049816 | 0.050837 | 0.076765 | 0.076765 | 0.067582 | 0.066561 | 0.060439 | 0.059418 | 0.054316 | 0.051255 | 0.048194 | 0.048194 | 0.042071 | 0.03901 | 0.03901
|  | RACKWICK | HT |  |  |  |  | 0.071061 | 0.072082 | 0.061878 | 0.061878 | 0.054735 | 0.053714 | 0.047592 | 0.045551 | 0.041469 | 0.04249 | 0.035347 | 0.030245 | 0.026163 | 0.077367 | 0.077367 | 0.070224 | 0.068184 | 0.064102 | 0.064102 | 0.061041 | 0.06002 | 0.055939 | 0.056959 | 0.046755 | 0.046755 | 0.046755 | 0.076765 | 0.076765 | 0.067582 | 0.066561 | 0.060439 | 0.059418 | 0.053296 | 0.051255 | 0.047173 | 0.049214 | 0.042071 | 0.036969 | 0.036969
|  | RACKWICK | HE |  |  |  |  | 0.071061 | 0.072082 | 0.061878 | 0.061878 | 0.054735 | 0.052694 | 0.047592 | 0.044531 | 0.039429 | 0.040449 | 0.036367 | 0.030245 | 0.025143 | 0.077367 | 0.077367 | 0.069204 | 0.068184 | 0.064102 | 0.064102 | 0.061041 | 0.06002 | 0.055939 | 0.056959 | 0.050837 | 0.049816 | 0.048796 | 0.076765 | 0.076765 | 0.067582 | 0.066561 | 0.059418 | 0.058398 | 0.054316 | 0.050235 | 0.046153 | 0.048194 | 0.042071 | 0.040031 | 0.035949
|  | RACKWICK | FB |  |  |  |  | 0.071061 | 0.072082 | 0.072082 | 0.068 | 0.06698 | 0.065959 | 0.064939 | 0.063918 | 0.064939 | 0.063918 | 0.052694 | 0.045551 | 0.045551 | 0.077367 | 0.077367 | 0.078388 | 0.072265 | 0.072265 | 0.073286 | 0.070224 | 0.068184 | 0.070224 | 0.067163 | 0.055939 | 0.049816 | 0.049816 | 0.076765 | 0.076765 | 0.077786 | 0.070643 | 0.070643 | 0.071663 | 0.069622 | 0.067582 | 0.068602 | 0.066561 | 0.055337 | 0.046153 | 0.048194
| FORT WILLIAM | RAHOY | MINIMUM HEADROOM | NM 69621 49222 | YES | NO | 0 | 0.98878 | 0.98878 | 0.98878 | 0.98776 | 0.98776 | 0.98776 | 0.97143 | 0.97041 | 0.96939 | 0.96633 | 0.96429 | 0.96327 | 0.95816 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.97959 | 0.97959 | 0.97857 | 0.97653 | 0.97449 | 0.97551 | 0.97143 | 0.99184 | 0.99184 | 0.99184 | 0.99184 | 0.99082 | 0.99082 | 0.97551 | 0.97347 | 0.97245 | 0.97041 | 0.96837 | 0.96735 | 0.96327
|  | RAHOY | EE |  |  |  |  | 0.98878 | 0.98878 | 0.98878 | 0.98776 | 0.98776 | 0.98776 | 0.97551 | 0.97041 | 0.96939 | 0.96633 | 0.96531 | 0.96327 | 0.9602 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.98163 | 0.97959 | 0.97857 | 0.97653 | 0.97653 | 0.97551 | 0.97347 | 0.99184 | 0.99184 | 0.99184 | 0.99184 | 0.99082 | 0.99082 | 0.97959 | 0.97449 | 0.97245 | 0.97041 | 0.97041 | 0.96735 | 0.96429
|  | RAHOY | HT |  |  |  |  | 0.98878 | 0.98878 | 0.98878 | 0.98776 | 0.98776 | 0.98776 | 0.97551 | 0.97041 | 0.96939 | 0.96633 | 0.96429 | 0.96429 | 0.95816 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.98163 | 0.97959 | 0.97959 | 0.97653 | 0.97449 | 0.97653 | 0.97143 | 0.99184 | 0.99184 | 0.99184 | 0.99184 | 0.99082 | 0.99082 | 0.97959 | 0.97449 | 0.97347 | 0.97041 | 0.96837 | 0.96837 | 0.96327
|  | RAHOY | HE |  |  |  |  | 0.98878 | 0.98878 | 0.98878 | 0.98776 | 0.98776 | 0.98776 | 0.97143 | 0.97041 | 0.96939 | 0.96633 | 0.96531 | 0.96429 | 0.96122 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.97959 | 0.97959 | 0.97857 | 0.97653 | 0.97551 | 0.97653 | 0.97347 | 0.99184 | 0.99184 | 0.99184 | 0.99184 | 0.99082 | 0.99082 | 0.97551 | 0.97347 | 0.97245 | 0.97041 | 0.96837 | 0.96837 | 0.96633
|  | RAHOY | FB |  |  |  |  | 0.98878 | 0.98878 | 0.98878 | 0.98878 | 0.98878 | 0.98878 | 0.98878 | 0.98163 | 0.98061 | 0.97653 | 0.97347 | 0.97347 | 0.96735 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.99388 | 0.98469 | 0.98469 | 0.97959 | 0.97755 | 0.97755 | 0.97143 | 0.99184 | 0.99184 | 0.99184 | 0.99184 | 0.99184 | 0.99184 | 0.99184 | 0.98367 | 0.98367 | 0.97857 | 0.97653 | 0.97347 | 0.97041
| INVERNESS | RAIGMORE | MINIMUM HEADROOM | NH 68427 44693 | NO | NO | 4.986 | 11.7456 | 11.7088 | 11.7123 | 11.6352 | 11.5428 | 9.8269 | 7.5302 | 5.1224 | 3.1814 | 2.6284 | 0.48462 | -1.3389 | -2.9097 | 11.8985 | 11.8755 | 11.8742 | 11.8443 | 11.7887 | 10.1423 | 7.8686 | 5.4455 | 3.4614 | 3.0154 | 0.98831 | -0.68869 | -2.3289 | 8.9915 | 8.9533 | 8.9387 | 8.8838 | 8.797 | 7.1846 | 4.9665 | 2.6219 | 0.63992 | 0.13835 | -2.1152 | -4.0472 | -5.8068
|  | RAIGMORE | EE |  |  |  |  | 11.7456 | 11.7088 | 11.7123 | 11.6352 | 11.5483 | 11.2899 | 10.8682 | 9.0092 | 6.625 | 4.4416 | 1.278 | -0.6769 | -1.5599 | 11.8985 | 11.8762 | 11.8742 | 11.8443 | 11.7894 | 11.7165 | 11.4907 | 9.6831 | 7.2135 | 4.9904 | 2.2374 | 0.5701 | -0.10862 | 8.9915 | 8.9533 | 8.9387 | 8.8838 | 8.7984 | 8.6365 | 8.2989 | 6.5212 | 4.1565 | 2.021 | -0.96552 | -2.9503 | -3.7867
|  | RAIGMORE | HT |  |  |  |  | 11.7477 | 11.7095 | 11.7144 | 11.6365 | 11.5428 | 9.8269 | 7.5302 | 5.1224 | 3.1814 | 2.6284 | 0.88268 | -1.2528 | -2.8548 | 11.8985 | 11.8762 | 11.8742 | 11.845 | 11.7887 | 10.1423 | 7.8686 | 5.4455 | 3.4614 | 3.0154 | 1.8226 | 0.0080922 | -1.507 | 8.9929 | 8.9582 | 8.9464 | 8.8887 | 8.7998 | 7.1846 | 4.9665 | 2.6219 | 0.63992 | 0.13835 | -1.4261 | -3.6311 | -5.3699
|  | RAIGMORE | HE |  |  |  |  | 11.7484 | 11.713 | 11.7213 | 11.6407 | 11.5511 | 11.3066 | 10.88 | 8.7904 | 5.8199 | 3.3023 | 0.48462 | -1.3389 | -2.9097 | 11.8985 | 11.8755 | 11.8742 | 11.845 | 11.7894 | 11.7151 | 11.4698 | 9.3594 | 6.1721 | 3.5531 | 0.98831 | -0.68869 | -2.3289 | 8.9922 | 8.9554 | 8.9443 | 8.8859 | 8.797 | 8.6386 | 8.2878 | 6.2405 | 3.1804 | 0.67743 | -2.1152 | -4.0472 | -5.8068
|  | RAIGMORE | FB |  |  |  |  | 11.7762 | 11.8047 | 11.8165 | 11.7963 | 11.7401 | 11.7199 | 11.4962 | 11.2253 | 9.8331 | 8.3201 | 3.4836 | 2.6333 | 2.1623 | 11.9138 | 11.9304 | 11.9367 | 11.9221 | 11.8804 | 11.8651 | 11.6852 | 11.4664 | 9.9019 | 8.2805 | 3.2155 | 2.4666 | 2.0095 | 9.0165 | 9.0325 | 9.0388 | 9.0089 | 8.9526 | 8.936 | 8.7206 | 8.4545 | 6.9964 | 5.4972 | 0.7337 | -0.19094 | -0.52161
| ARBROATH | REDFORD | MINIMUM HEADROOM | NO 55879 44046 | YES | YES | 0.231 | -1.6561 | -1.6622 | -1.6786 | -1.7439 | -1.7765 | -1.8969 | -2.0551 | -2.2296 | -2.3816 | -2.501 | -2.749 | -3.1969 | -3.5173 | -0.77755 | -0.78061 | -0.7898 | -0.8102 | -0.83265 | -0.87041 | -0.91735 | -0.99184 | -1.0378 | -1.0888 | -1.1796 | -1.1735 | -1.2643 | -1.5602 | -1.5684 | -1.5867 | -1.6367 | -1.6939 | -1.7653 | -1.8908 | -2.0408 | -2.1643 | -2.2643 | -2.4388 | -2.6714 | -2.8224
|  | REDFORD | EE |  |  |  |  | -1.6551 | -1.6622 | -1.6786 | -1.7214 | -1.749 | -1.8561 | -1.9867 | -2.1469 | -2.2837 | -2.401 | -2.749 | -3.1969 | -3.5143 | -0.77755 | -0.77959 | -0.7898 | -0.80306 | -0.82653 | -0.85918 | -0.90102 | -0.97449 | -1.0296 | -1.0786 | -1.1357 | -1.1571 | -1.1867 | -1.5602 | -1.5684 | -1.5867 | -1.6245 | -1.6694 | -1.7378 | -1.848 | -1.9888 | -2.102 | -2.199 | -2.4388 | -2.6714 | -2.8224
|  | REDFORD | HT |  |  |  |  | -1.6541 | -1.6612 | -1.6724 | -1.7357 | -1.7622 | -1.8786 | -2.0102 | -2.148 | -2.2643 | -2.3776 | -2.6592 | -3.1163 | -3.5173 | -0.77755 | -0.78061 | -0.78878 | -0.8102 | -0.83265 | -0.87041 | -0.91531 | -0.98367 | -1.0327 | -1.0847 | -1.1796 | -1.1408 | -1.1112 | -1.5592 | -1.5684 | -1.5837 | -1.6347 | -1.6796 | -1.7571 | -1.8622 | -1.9898 | -2.0898 | -2.1857 | -2.3959 | -2.6357 | -2.8173
|  | REDFORD | HE |  |  |  |  | -1.6561 | -1.6612 | -1.6745 | -1.7439 | -1.7765 | -1.8969 | -2.0551 | -2.2296 | -2.3816 | -2.501 | -2.7163 | -3.1398 | -3.4051 | -0.77755 | -0.77959 | -0.78776 | -0.80714 | -0.83265 | -0.86735 | -0.91735 | -0.99184 | -1.0378 | -1.0888 | -1.1357 | -1.1735 | -1.2296 | -1.5592 | -1.5684 | -1.5867 | -1.6367 | -1.6939 | -1.7653 | -1.8908 | -2.0408 | -2.1643 | -2.2643 | -2.4194 | -2.6684 | -2.8204
|  | REDFORD | FB |  |  |  |  | -1.6184 | -1.6 | -1.5867 | -1.5918 | -1.602 | -1.6245 | -1.6571 | -1.6673 | -1.7204 | -1.7408 | -1.9745 | -2.1224 | -2.1969 | -0.75714 | -0.74286 | -0.73776 | -0.73673 | -0.74388 | -0.76122 | -0.78878 | -0.80714 | -0.84592 | -0.8602 | -1.0092 | -1.1337 | -1.2643 | -1.5163 | -1.5051 | -1.4969 | -1.4969 | -1.5102 | -1.5347 | -1.5714 | -1.598 | -1.6531 | -1.6786 | -1.8816 | -2.0255 | -2.0541
| BURGHMUIR | REDGORTON | MINIMUM HEADROOM | NO 07650 28860 | NO | YES | 4.254 | 5.1513 | 4.6411 | 3.8819 | 2.9493 | 2.4401 | 1.2554 | 0.1268 | -0.91605 | -1.9763 | -2.8181 | -6.7905 | -8.5365 | -9.0405 | 7.6707 | 7.439 | 7.187 | 6.8156 | 6.4625 | 5.9993 | 5.4574 | 4.9533 | 4.3921 | 3.9605 | 1.7125 | 1.1942 | 1.1656 | 6.612 | 6.2324 | 5.7069 | 5.0253 | 4.5967 | 3.6702 | 2.7487 | 1.8885 | 1.0008 | 0.31405 | -2.9655 | -4.2298 | -4.5492
|  | REDGORTON | EE |  |  |  |  | 5.1523 | 4.6411 | 3.8819 | 2.9493 | 2.4401 | 1.2554 | 0.1268 | -0.91605 | -1.9763 | -2.8181 | -6.7763 | -8.5365 | -9.0405 | 7.6727 | 7.439 | 7.2064 | 6.8156 | 6.4707 | 5.9993 | 5.4574 | 4.9533 | 4.3921 | 3.9727 | 2.0625 | 1.2237 | 1.1656 | 6.614 | 6.2324 | 5.7069 | 5.0253 | 4.5967 | 3.6702 | 2.7487 | 1.8885 | 1.0008 | 0.31405 | -2.8268 | -4.2298 | -4.5492
|  | REDGORTON | HT |  |  |  |  | 5.1574 | 4.6574 | 3.9686 | 3.0737 | 2.4901 | 1.4911 | 0.47068 | -0.61911 | -1.7365 | -2.6722 | -6.7905 | -8.414 | -8.9691 | 7.6727 | 7.4401 | 7.1931 | 6.8237 | 6.4625 | 6.0625 | 5.587 | 5.0442 | 4.4482 | 3.9605 | 1.7125 | 1.1942 | 1.2993 | 6.6171 | 6.2436 | 5.762 | 5.1038 | 4.6232 | 3.8314 | 2.9977 | 2.0885 | 1.16 | 0.3967 | -2.9655 | -4.1645 | -4.4737
|  | REDGORTON | HE |  |  |  |  | 5.1513 | 4.6442 | 3.9074 | 3.0513 | 2.5666 | 1.4615 | 0.38599 | -0.71299 | -1.7967 | -2.6334 | -6.463 | -8.1426 | -8.4722 | 7.6707 | 7.439 | 7.187 | 6.8227 | 6.4809 | 6.0278 | 5.5227 | 4.9748 | 4.3982 | 4.0207 | 2.1299 | 1.4686 | 1.5339 | 6.612 | 6.2355 | 5.7222 | 5.0906 | 4.6743 | 3.8018 | 2.9345 | 2.0161 | 1.1089 | 0.45078 | -2.5982 | -3.8768 | -4.0411
|  | REDGORTON | FB |  |  |  |  | 5.4115 | 4.9288 | 4.4054 | 3.8554 | 3.5278 | 2.8533 | 2.1146 | 1.3942 | 0.85844 | 0.31966 | -2.6997 | -4.6058 | -5.3191 | 7.8472 | 7.5258 | 7.3258 | 7.1248 | 6.9013 | 6.6064 | 6.2197 | 5.8431 | 5.6707 | 5.3778 | 3.9299 | 2.4921 | 1.5268 | 6.8753 | 6.4467 | 6.0845 | 5.7069 | 5.4345 | 4.9355 | 4.3345 | 3.7487 | 3.3702 | 2.9192 | 0.52629 | -1.386 | -1.9829
| REDMOSS | REDMOSS | MINIMUM HEADROOM | NJ 94562 01919 | NO | NO | 14.699 | 7.4787 | 6.5675 | 5.3624 | 4.1838 | 3.391 | 1.3155 | -0.60801 | -2.9315 | -6.2896 | -7.11 | -11.6805 | -22.4203 | -31.56 | 11.4104 | 10.6624 | 9.8083 | 8.9797 | 8.3104 | 7.4757 | 5.294 | 2.9685 | -1.0927 | -1.7733 | -6.559 | -18.5111 | -29.2723 | 10.1308 | 9.3165 | 8.3471 | 7.3951 | 6.7318 | 5.3961 | 3.2134 | 0.79403 | -3.2703 | -4.059 | -9.2009 | -21.906 | -32.9315
|  | REDMOSS | EE |  |  |  |  | 7.6257 | 6.5675 | 5.3879 | 4.2451 | 3.4614 | 1.7114 | -0.024335 | -1.9264 | -4.9682 | -5.6254 | -9.6162 | -19.1223 | -23.2672 | 11.5746 | 10.6685 | 9.8318 | 9.0226 | 8.3644 | 7.6053 | 6.1073 | 4.14 | 0.73791 | 0.20424 | -3.6549 | -14.4672 | -18.8907 | 10.2869 | 9.3195 | 8.3736 | 7.444 | 6.7869 | 5.6389 | 4.0134 | 1.991 | -1.5274 | -2.158 | -6.4652 | -17.8162 | -22.6264
|  | REDMOSS | HT |  |  |  |  | 7.541 | 6.6267 | 5.4369 | 4.2644 | 3.4655 | 1.4379 | -0.60801 | -2.659 | -6.2896 | -7.11 | -11.5713 | -22.4203 | -31.56 | 11.4787 | 10.694 | 9.8083 | 8.9797 | 8.3104 | 7.4757 | 5.294 | 3.091 | -1.0927 | -1.7733 | -6.1968 | -18.5111 | -29.0896 | 10.1951 | 9.3553 | 8.3685 | 7.4063 | 6.7348 | 5.4144 | 3.2134 | 0.99403 | -3.2703 | -4.059 | -8.9407 | -21.906 | -32.9315
|  | REDMOSS | HE |  |  |  |  | 7.4787 | 6.5695 | 5.3624 | 4.1838 | 3.391 | 1.3155 | -0.24984 | -2.9315 | -3.6264 | -4.9152 | -11.6805 | -21.5182 | -30.956 | 11.4104 | 10.6624 | 9.8124 | 8.994 | 8.3318 | 7.493 | 5.9297 | 2.9685 | 2.4685 | 1.044 | -6.559 | -17.9978 | -29.2723 | 10.1308 | 9.3165 | 8.3471 | 7.3951 | 6.7318 | 5.3961 | 3.7971 | 0.79403 | 0.19301 | -1.2856 | -9.2009 | -21.0703 | -32.6019
|  | REDMOSS | FB |  |  |  |  | 8.0695 | 7.391 | 6.3695 | 5.642 | 4.8522 | 3.6104 | 2.0297 | 0.8022 | -1.4284 | -2.0927 | -3.907 | -6.4927 | -8.4325 | 11.9797 | 11.3583 | 10.5502 | 10.0379 | 9.2767 | 8.542 | 7.1848 | 5.7951 | 3.1348 | 2.392 | 0.57158 | -2.1049 | -4.1917 | 10.7063 | 10.0665 | 9.1889 | 8.5746 | 7.8267 | 6.8624 | 5.3532 | 3.9797 | 1.3338 | 0.6124 | -1.1437 | -4.3998 | -6.0692
| CASSLEY | RHICONICH | MINIMUM HEADROOM | NC 25554 52924 | YES | NO | 0.213 | -0.65306 | -0.66122 | -0.66224 | -0.93571 | -0.93673 | -1.1837 | -1.3531 | -1.4796 | -1.6429 | -1.7684 | -2.1582 | -2.4408 | -2.6082 | -0.36122 | -0.37449 | -0.37755 | -0.64694 | -0.64592 | -0.79286 | -0.93163 | -1.0255 | -1.148 | -1.2633 | -1.5449 | -1.6786 | -1.7337 | -0.56531 | -0.57755 | -0.58163 | -0.8551 | -0.85408 | -1.0786 | -1.2112 | -1.3194 | -1.4663 | -1.5786 | -1.9235 | -2.149 | -2.2653
|  | RHICONICH | EE |  |  |  |  | -0.65306 | -0.65816 | -0.66224 | -0.69286 | -0.72245 | -1.1816 | -1.3398 | -1.4673 | -1.599 | -1.748 | -2.1582 | -2.4408 | -2.6082 | -0.36122 | -0.37245 | -0.37755 | -0.38878 | -0.41327 | -0.79286 | -0.92959 | -1.0255 | -1.1255 | -1.2531 | -1.5449 | -1.6786 | -1.7337 | -0.56429 | -0.57755 | -0.58163 | -0.60714 | -0.64286 | -1.0776 | -1.201 | -1.3122 | -1.4296 | -1.5704 | -1.9235 | -2.149 | -2.2653
|  | RHICONICH | HT |  |  |  |  | -0.65306 | -0.66122 | -0.66122 | -0.69388 | -0.72245 | -1.1378 | -1.3112 | -1.452 | -1.5867 | -1.7469 | -2.0827 | -2.4041 | -2.5847 | -0.36122 | -0.37449 | -0.37755 | -0.38878 | -0.41224 | -0.77041 | -0.90816 | -1.0173 | -1.1224 | -1.2633 | -1.5327 | -1.6745 | -1.6816 | -0.56531 | -0.57755 | -0.58061 | -0.60714 | -0.64082 | -1.0378 | -1.1745 | -1.3 | -1.4224 | -1.5735 | -1.8745 | -2.1214 | -2.2357
|  | RHICONICH | HE |  |  |  |  | -0.65306 | -0.65918 | -0.65918 | -0.69898 | -0.72959 | -1.1837 | -1.3531 | -1.4796 | -1.6429 | -1.7684 | -1.9612 | -2.1071 | -2.2163 | -0.3602 | -0.37245 | -0.37755 | -0.3898 | -0.41122 | -0.79286 | -0.93163 | -1.0184 | -1.148 | -1.2439 | -1.3796 | -1.3582 | -1.3663 | -0.56327 | -0.57755 | -0.58061 | -0.61122 | -0.6449 | -1.0786 | -1.2112 | -1.3194 | -1.4663 | -1.5786 | -1.7429 | -1.8235 | -1.8878
|  | RHICONICH | FB |  |  |  |  | -0.62143 | -0.61122 | -0.60918 | -0.93571 | -0.93673 | -0.95204 | -0.97755 | -0.9898 | -1.0163 | -1.0459 | -1.1531 | -1.2765 | -1.6184 | -0.32755 | -0.32551 | -0.33673 | -0.64694 | -0.64592 | -0.65612 | -0.67755 | -0.6898 | -0.71531 | -0.74184 | -0.83163 | -0.95204 | -1.3092 | -0.53061 | -0.52041 | -0.53061 | -0.8551 | -0.85408 | -0.86633 | -0.88571 | -0.89694 | -0.92347 | -0.95 | -1.0551 | -1.1561 | -1.4704
| DUDHOPE | ROSEBANK STREET | MINIMUM HEADROOM | NO 39943 31150 | NO | NO | 1.879 | 10.3326 | 10.3582 | 10.2316 | 10.15 | 9.9571 | 9.6724 | 8.6153 | 7.3694 | 4.0816 | 3.2296 | -2.0041 | -9.1755 | -15.9592 | 11.9582 | 11.9408 | 11.7612 | 11.6398 | 11.3173 | 10.898 | 9.5531 | 7.8316 | 3.7592 | 2.5847 | -2.7123 | -9.9929 | -17.3316 | 11.9678 | 12.025 | 12.0311 | 12.075 | 11.9056 | 11.474 | 10.1393 | 8.4566 | 4.374 | 3.2117 | -2.7577 | -11.0403 | -18.976
|  | ROSEBANK STREET | EE |  |  |  |  | 10.3326 | 10.3582 | 10.2367 | 10.1582 | 9.9663 | 9.6724 | 8.8673 | 7.8082 | 6.1296 | 5.5898 | 1.0122 | -7.1969 | -11.0316 | 11.9582 | 11.9755 | 11.7673 | 11.649 | 11.3235 | 10.9224 | 9.8847 | 8.4928 | 6.4775 | 5.7398 | 2.5888 | -4.9623 | -8.3123 | 11.9678 | 12.0648 | 12.0311 | 12.075 | 11.9056 | 11.474 | 10.3954 | 8.9648 | 6.9025 | 6.1413 | 1.5025 | -7.6148 | -11.7444
|  | ROSEBANK STREET | HT |  |  |  |  | 10.3663 | 10.3612 | 10.3316 | 10.249 | 10.0531 | 9.7459 | 8.6153 | 7.3888 | 5.2928 | 4.7326 | 0.16632 | -8.2643 | -14.298 | 11.9592 | 11.9408 | 11.7612 | 11.6398 | 11.3173 | 10.9275 | 9.5531 | 7.9296 | 5.4071 | 4.6224 | 1.0939 | -7.1112 | -13.7765 | 11.9801 | 12.025 | 12.0638 | 12.0995 | 11.9301 | 11.5372 | 10.1393 | 8.5015 | 5.9495 | 5.1423 | 0.41887 | -9.1515 | -16.3128
|  | ROSEBANK STREET | HE |  |  |  |  | 10.3347 | 10.3622 | 10.2316 | 10.15 | 9.9571 | 9.6888 | 8.8735 | 7.3694 | 4.0816 | 3.2296 | -2.0041 | -9.1755 | -15.9592 | 11.9602 | 11.9796 | 11.7673 | 11.649 | 11.3265 | 10.898 | 9.8163 | 7.8316 | 3.7592 | 2.5847 | -2.7123 | -9.9929 | -17.3316 | 11.9801 | 12.0934 | 12.0678 | 12.1097 | 11.9281 | 11.5168 | 10.4393 | 8.4566 | 4.374 | 3.2117 | -2.7577 | -11.0403 | -18.976
|  | ROSEBANK STREET | FB |  |  |  |  | 10.5296 | 10.5306 | 10.6071 | 10.5194 | 10.4724 | 10.3806 | 9.8735 | 9.3051 | 8.0969 | 7.6551 | 6.4194 | 3.6806 | 0.60509 | 12.3418 | 12.05 | 12.1 | 11.9898 | 11.8724 | 11.7163 | 11.0122 | 10.2602 | 8.7745 | 8.1337 | 6.3449 | 3.5806 | -0.42552 | 12.0954 | 12.1668 | 12.2832 | 12.2913 | 12.3474 | 12.3536 | 11.8046 | 11.1025 | 9.6485 | 9.0464 | 7.3127 | 3.227 | 0.86377
| KEITH 2 | ROTHES | MINIMUM HEADROOM | NJ 27901 49693 | NO | YES | 1.653 | 0.47935 | 0.46098 | 0.41302 | 0.37424 | 0.2018 | 0.028327 | -0.15229 | -0.41759 | -0.58086 | -0.70841 | -1.2615 | -1.74 | -2.0492 | 1.7293 | 1.7222 | 1.7038 | 1.6589 | 1.5589 | 1.4875 | 1.3814 | 1.213 | 1.0987 | 1.013 | 0.66914 | 0.48037 | 0.35282 | 0.8518 | 0.83649 | 0.80078 | 0.68649 | 0.51302 | 0.31812 | 0.14057 | -0.11453 | -0.27371 | -0.41045 | -0.80637 | -1.086 | -1.2615
|  | ROTHES | EE |  |  |  |  | 0.48853 | 0.46404 | 0.44976 | 0.39873 | 0.24465 | 0.067102 | -0.076776 | -0.33698 | -0.538 | -0.70841 | -1.2615 | -1.74 | -2.0492 | 1.7406 | 1.7232 | 1.713 | 1.6936 | 1.5722 | 1.4957 | 1.4293 | 1.2498 | 1.1334 | 1.013 | 0.68241 | 0.48037 | 0.35282 | 0.86098 | 0.83751 | 0.82731 | 0.78547 | 0.52935 | 0.33139 | 0.19567 | -0.066571 | -0.24106 | -0.41045 | -0.80535 | -1.0788 | -1.2615
|  | ROTHES | HT |  |  |  |  | 0.48241 | 0.46098 | 0.41302 | 0.38037 | 0.2018 | 0.035469 | -0.15229 | -0.34004 | -0.57984 | -0.70024 | -1.1911 | -1.6758 | -2.0319 | 1.7334 | 1.7222 | 1.7038 | 1.6824 | 1.5589 | 1.4885 | 1.3814 | 1.2702 | 1.0987 | 1.0212 | 0.66914 | 0.48751 | 0.41506 | 0.85588 | 0.83649 | 0.80078 | 0.75996 | 0.51302 | 0.34363 | 0.14057 | -0.017592 | -0.27371 | -0.39208 | -0.80637 | -1.086 | -1.237
|  | ROTHES | HE |  |  |  |  | 0.47935 | 0.46404 | 0.43445 | 0.39057 | 0.20792 | 0.028327 | -0.14106 | -0.41759 | -0.58086 | -0.70229 | -1.0451 | -1.3125 | -1.5196 | 1.7293 | 1.7232 | 1.71 | 1.6865 | 1.563 | 1.4875 | 1.4059 | 1.213 | 1.1375 | 1.061 | 0.85996 | 0.87629 | 0.8171 | 0.8518 | 0.83751 | 0.81404 | 0.76506 | 0.51404 | 0.31812 | 0.16812 | -0.11453 | -0.24208 | -0.35739 | -0.61861 | -0.67882 | -0.79922
|  | ROTHES | FB |  |  |  |  | 0.55078 | 0.53955 | 0.53343 | 0.37424 | 0.35996 | 0.34363 | 0.30792 | 0.29159 | 0.212 | 0.17527 | -0.2931 | -0.61759 | -0.97882 | 1.7926 | 1.7824 | 1.7712 | 1.6589 | 1.6436 | 1.6283 | 1.6069 | 1.5885 | 1.5477 | 1.5171 | 1.1181 | 0.84261 | 0.44057 | 0.91914 | 0.90792 | 0.89873 | 0.68649 | 0.63853 | 0.60996 | 0.55588 | 0.52118 | 0.44363 | 0.38139 | -0.14718 | -0.53188 | -0.73494
| DUNOON | ROTHESAY | MINIMUM HEADROOM | NS 08636 64647 | NO | YES | 0.835 | 10.0571 | 9.9337 | 9.9592 | 9.8643 | 9.7633 | 9.4745 | 9.1367 | 8.6929 | 8.448 | 8.1092 | 6.1888 | 4.3918 | 3.2776 | 10.352 | 10.1612 | 10.1673 | 10.05 | 9.9327 | 9.6255 | 9.4214 | 9.0469 | 8.8918 | 8.6173 | 7.4224 | 6.5592 | 5.9592 | 10.5485 | 10.3158 | 10.2893 | 10.0638 | 9.8434 | 9.4474 | 9.1413 | 8.7077 | 8.5219 | 8.1832 | 6.6199 | 5.1362 | 4.2179
|  | ROTHESAY | EE |  |  |  |  | 10.0571 | 9.9357 | 9.9755 | 9.9102 | 9.8092 | 9.5082 | 9.1592 | 8.6949 | 8.448 | 8.1092 | 6.1888 | 4.3918 | 3.2776 | 10.352 | 10.1612 | 10.1745 | 10.0755 | 9.9439 | 9.6582 | 9.4296 | 9.0469 | 8.8918 | 8.6173 | 7.4224 | 6.5592 | 5.9592 | 10.5485 | 10.3158 | 10.2923 | 10.0995 | 9.8648 | 9.473 | 9.1515 | 8.7107 | 8.5219 | 8.1832 | 6.6199 | 5.1362 | 4.2179
|  | ROTHESAY | HT |  |  |  |  | 10.0602 | 9.9337 | 9.9592 | 9.8908 | 9.7929 | 9.4816 | 9.1704 | 8.7367 | 8.5469 | 8.1765 | 6.5939 | 4.8612 | 3.8878 | 10.3541 | 10.1622 | 10.1673 | 10.0684 | 9.9367 | 9.6255 | 9.4214 | 9.0571 | 8.9429 | 8.6265 | 7.5622 | 6.8122 | 6.5541 | 10.5495 | 10.3168 | 10.2893 | 10.0995 | 9.8668 | 9.4474 | 9.1556 | 8.7281 | 8.5801 | 8.2036 | 6.8872 | 5.5821 | 4.8709
|  | ROTHESAY | HE |  |  |  |  | 10.0602 | 9.9347 | 9.9684 | 9.8643 | 9.7633 | 9.4745 | 9.1367 | 8.6929 | 8.4969 | 8.1929 | 7.0684 | 5.5796 | 4.7694 | 10.3551 | 10.1622 | 10.1714 | 10.05 | 9.9327 | 9.649 | 9.4224 | 9.0561 | 8.9449 | 8.7071 | 7.9673 | 7.2367 | 6.7939 | 10.5495 | 10.3168 | 10.2913 | 10.0638 | 9.8434 | 9.4556 | 9.1413 | 8.7077 | 8.5587 | 8.2526 | 7.3311 | 6.1852 | 5.5332
|  | ROTHESAY | FB |  |  |  |  | 10.1061 | 10.0102 | 10.0684 | 10.0929 | 10.0622 | 10.0755 | 9.9786 | 9.9337 | 9.8418 | 9.7122 | 9.0735 | 7.5898 | 6.6255 | 10.3816 | 10.2122 | 10.2327 | 10.2276 | 10.1398 | 10.1184 | 9.9673 | 9.8969 | 9.7653 | 9.5786 | 8.9163 | 7.5163 | 6.4429 | 10.5872 | 10.377 | 10.3709 | 10.3148 | 10.1689 | 10.1321 | 9.9495 | 9.8607 | 9.7026 | 9.4811 | 8.7862 | 7.3444 | 6.7015
| THURSO | ROUSAY | MINIMUM HEADROOM | HY 43876 30573 | YES | NO | 0.023 | 0.2551 | 0.25102 | 0.2449 | 0.22857 | 0.20612 | 0.19184 | 0.16633 | 0.13571 | 0.13367 | 0.11633 | -0.093878 | -0.1102 | -0.18469 | 0.51939 | 0.51531 | 0.50714 | 0.49388 | 0.47755 | 0.46837 | 0.45306 | 0.43265 | 0.42857 | 0.40714 | 0.20816 | 0.2102 | 0.15204 | 0.47959 | 0.47755 | 0.47245 | 0.45918 | 0.44082 | 0.42857 | 0.40918 | 0.38061 | 0.37143 | 0.35102 | 0.14694 | 0.13673 | 0.082653
|  | ROUSAY | EE |  |  |  |  | 0.2551 | 0.25102 | 0.2449 | 0.22857 | 0.20918 | 0.19388 | 0.16837 | 0.13776 | 0.13776 | 0.11735 | -0.093878 | -0.1102 | -0.18469 | 0.51939 | 0.51531 | 0.50714 | 0.49388 | 0.47857 | 0.46837 | 0.45408 | 0.43367 | 0.42959 | 0.40714 | 0.20816 | 0.2102 | 0.15204 | 0.47959 | 0.47755 | 0.47245 | 0.45918 | 0.44286 | 0.42959 | 0.41122 | 0.38265 | 0.37449 | 0.35204 | 0.14694 | 0.13673 | 0.082653
|  | ROUSAY | HT |  |  |  |  | 0.2551 | 0.25102 | 0.2449 | 0.23265 | 0.20918 | 0.19388 | 0.17245 | 0.14286 | 0.13469 | 0.11633 | 0.076531 | 0.052041 | 0.035714 | 0.51939 | 0.51633 | 0.50714 | 0.49694 | 0.47857 | 0.46837 | 0.45306 | 0.43367 | 0.42959 | 0.40816 | 0.35918 | 0.35714 | 0.36531 | 0.48163 | 0.47755 | 0.47245 | 0.46327 | 0.44286 | 0.42959 | 0.41327 | 0.38571 | 0.37959 | 0.3602 | 0.30918 | 0.2898 | 0.29592
|  | ROUSAY | HE |  |  |  |  | 0.2551 | 0.25102 | 0.2449 | 0.23265 | 0.20612 | 0.19184 | 0.16633 | 0.13571 | 0.13367 | 0.11633 | 0.079592 | 0.058163 | 0.037755 | 0.51939 | 0.51633 | 0.50714 | 0.49694 | 0.47755 | 0.46837 | 0.45306 | 0.43265 | 0.42857 | 0.40714 | 0.36939 | 0.36633 | 0.36429 | 0.48163 | 0.47755 | 0.47245 | 0.46327 | 0.44082 | 0.42857 | 0.40918 | 0.38061 | 0.37143 | 0.35102 | 0.31327 | 0.29592 | 0.29796
|  | ROUSAY | FB |  |  |  |  | 0.26429 | 0.26429 | 0.26224 | 0.25816 | 0.25408 | 0.23776 | 0.22959 | 0.22857 | 0.21531 | 0.21122 | 0.17143 | 0.12551 | 0.10714 | 0.52653 | 0.52449 | 0.52041 | 0.51429 | 0.50612 | 0.48776 | 0.47755 | 0.47755 | 0.46429 | 0.45612 | 0.41837 | 0.37347 | 0.35714 | 0.49082 | 0.49082 | 0.48776 | 0.48469 | 0.48061 | 0.46429 | 0.45714 | 0.4551 | 0.44286 | 0.43878 | 0.40102 | 0.34694 | 0.33878
| CRAIGIEBUCKLER | RUTHRIESTON | MINIMUM HEADROOM | NJ 92574 04060 | NO | NO | 1.617 | 14.3313 | 14.3598 | 14.3741 | 14.2945 | 14.2762 | 14.0354 | 13.7374 | 13.266 | 12.966 | 12.616 | 10.5762 | 8.9639 | 8.0149 | 15.4874 | 15.5088 | 15.5098 | 15.4741 | 15.5149 | 15.3945 | 15.2333 | 14.8466 | 14.6772 | 14.4537 | 13.4802 | 12.8262 | 11.4251 | 14.419 | 14.4119 | 14.3935 | 14.317 | 14.2313 | 14.0486 | 13.8221 | 13.5139 | 13.2507 | 12.9527 | 11.1823 | 9.9354 | 9.3547
|  | RUTHRIESTON | EE |  |  |  |  | 14.3313 | 14.3598 | 14.3741 | 14.2945 | 14.2762 | 14.0354 | 13.7374 | 13.4068 | 13.0905 | 12.768 | 10.5762 | 8.9639 | 8.0149 | 15.4874 | 15.5098 | 15.5109 | 15.4762 | 15.516 | 15.4007 | 15.2394 | 15.0517 | 14.8649 | 14.6568 | 13.4802 | 12.8262 | 12.2098 | 14.419 | 14.4119 | 14.3935 | 14.317 | 14.2313 | 14.0486 | 13.8221 | 13.5721 | 13.3139 | 13.0425 | 11.319 | 10.0649 | 9.3905
|  | RUTHRIESTON | HT |  |  |  |  | 14.3405 | 14.3813 | 14.3915 | 14.3211 | 14.3088 | 14.0547 | 13.7721 | 13.266 | 12.966 | 12.616 | 10.6935 | 9.3619 | 8.72 | 15.4874 | 15.5088 | 15.5098 | 15.4741 | 15.5149 | 15.3945 | 15.2333 | 14.8466 | 14.6772 | 14.4537 | 13.6047 | 13.3588 | 13.2262 | 14.4313 | 14.4405 | 14.4374 | 14.3517 | 14.2629 | 14.0639 | 13.8354 | 13.5139 | 13.2507 | 12.9527 | 11.1823 | 9.9354 | 9.3547
|  | RUTHRIESTON | HE |  |  |  |  | 14.3384 | 14.3721 | 14.3945 | 14.3098 | 14.2945 | 14.0864 | 13.8129 | 13.5251 | 13.2476 | 12.9813 | 11.5578 | 10.4323 | 9.6088 | 15.4884 | 15.5129 | 15.516 | 15.4792 | 15.5211 | 15.4119 | 15.2445 | 15.0537 | 14.8833 | 14.6905 | 13.9149 | 13.3374 | 12.717 | 14.4241 | 14.4251 | 14.4109 | 14.3282 | 14.2364 | 14.069 | 13.8527 | 13.6262 | 13.4027 | 13.169 | 11.9598 | 11.066 | 10.4486
|  | RUTHRIESTON | FB |  |  |  |  | 14.4517 | 14.5445 | 14.6007 | 14.6476 | 14.6527 | 14.6058 | 14.5568 | 14.5517 | 14.4619 | 14.3527 | 13.7721 | 12.4037 | 11.3854 | 15.5394 | 15.5751 | 15.5802 | 15.5915 | 15.569 | 15.4864 | 15.4047 | 15.3629 | 15.2496 | 15.1149 | 14.4027 | 12.9058 | 11.4251 | 14.5068 | 14.5547 | 14.5741 | 14.5588 | 14.5374 | 14.4976 | 14.4425 | 14.3894 | 14.3027 | 14.1976 | 13.6792 | 12.47 | 11.9527
| TAYNUILT | SALEN | MINIMUM HEADROOM | NM 57252 42849 | NO | YES | 1.09 | 5.7746 | 5.7665 | 5.7583 | 5.6879 | 5.4103 | 5.094 | 4.7899 | 4.5961 | 4.4134 | 4.3216 | 3.9236 | 3.5807 | 3.3858 | 6.0226 | 6.0267 | 6.0287 | 6.0083 | 5.8205 | 5.6083 | 5.392 | 5.2756 | 5.1552 | 5.0695 | 4.6746 | 4.4767 | 4.3593 | 5.8226 | 5.8134 | 5.8063 | 5.7379 | 5.545 | 5.2512 | 4.9665 | 4.7991 | 4.6389 | 4.5481 | 4.1654 | 3.8542 | 3.691
|  | SALEN | EE |  |  |  |  | 5.7848 | 5.7705 | 5.7583 | 5.6879 | 5.4103 | 5.094 | 4.7899 | 4.5961 | 4.4134 | 4.3216 | 3.9236 | 3.5807 | 3.3858 | 6.0348 | 6.0287 | 6.0297 | 6.0103 | 5.8216 | 5.6083 | 5.392 | 5.2756 | 5.1573 | 5.0695 | 4.7185 | 4.4767 | 4.3593 | 5.8328 | 5.8175 | 5.8063 | 5.7379 | 5.545 | 5.2512 | 4.9665 | 4.7991 | 4.6389 | 4.5481 | 4.1654 | 3.8542 | 3.691
|  | SALEN | HT |  |  |  |  | 5.7746 | 5.7705 | 5.7644 | 5.6981 | 5.4175 | 5.1522 | 4.8828 | 4.6961 | 4.4838 | 4.3899 | 3.9348 | 3.6512 | 3.444 | 6.0226 | 6.0287 | 6.0307 | 6.0083 | 5.8205 | 5.6348 | 5.444 | 5.3277 | 5.194 | 5.1114 | 4.6746 | 4.5012 | 4.4369 | 5.8226 | 5.8175 | 5.8103 | 5.7461 | 5.5481 | 5.3042 | 5.0532 | 4.8797 | 4.6981 | 4.6063 | 4.1695 | 3.9134 | 3.7542
|  | SALEN | HE |  |  |  |  | 5.7838 | 5.7665 | 5.7593 | 5.691 | 5.4114 | 5.1246 | 4.893 | 4.6644 | 4.4491 | 4.4063 | 4.0277 | 3.9236 | 3.8542 | 6.0348 | 6.0267 | 6.0287 | 6.0103 | 5.8205 | 5.6165 | 5.4593 | 5.3073 | 5.1552 | 5.1226 | 4.791 | 4.8246 | 4.842 | 5.8318 | 5.8134 | 5.8063 | 5.741 | 5.5461 | 5.2828 | 5.0675 | 4.8522 | 4.6603 | 4.6205 | 4.2726 | 4.2134 | 4.1828
|  | SALEN | FB |  |  |  |  | 5.8144 | 5.8277 | 5.8256 | 5.793 | 5.7777 | 5.4542 | 5.4093 | 5.391 | 5.3501 | 5.2073 | 4.9614 | 4.594 | 4.2583 | 6.0583 | 6.0634 | 6.0654 | 6.0552 | 6.0644 | 5.793 | 5.7593 | 5.7461 | 5.7114 | 5.5869 | 5.3797 | 5.0093 | 4.6114 | 5.8614 | 5.8665 | 5.8736 | 5.8512 | 5.8573 | 5.5542 | 5.5103 | 5.492 | 5.4797 | 5.3481 | 5.1175 | 4.6461 | 4.391
| FORT WILLIAM | SALEN 2 | MINIMUM HEADROOM | NM 69002 65519 | YES | NO | 0.33 | 0.37653 | 0.37347 | 1.0653 | 1.0143 | 0.98163 | 0.86939 | 0.79286 | 0.72041 | 0.64694 | 0.61224 | 0.43367 | 0.22755 | 0.080612 | 0.50867 | 0.50867 | 1.4265 | 1.4112 | 1.398 | 1.351 | 1.2969 | 1.2694 | 1.2204 | 1.199 | 1.0918 | 1.1041 | 1.0612 | 0.48036 | 0.47832 | 0.89571 | 0.86714 | 0.83551 | 0.77429 | 0.70694 | 0.65796 | 0.59265 | 0.55898 | 0.41816 | 0.32735 | 0.2651
|  | SALEN 2 | EE |  |  |  |  | 0.37653 | 0.37347 | 1.0663 | 1.0204 | 0.99796 | 0.86939 | 0.79796 | 0.72245 | 0.64898 | 0.61735 | 0.43367 | 0.22755 | 0.080612 | 0.50969 | 0.50867 | 1.4265 | 1.4112 | 1.398 | 1.351 | 1.3 | 1.2704 | 1.2214 | 1.202 | 1.1082 | 1.1112 | 1.1112 | 0.48036 | 0.47832 | 0.89776 | 0.8702 | 0.84367 | 0.77633 | 0.71102 | 0.66 | 0.59367 | 0.56204 | 0.41816 | 0.32735 | 0.27327
|  | SALEN 2 | HT |  |  |  |  | 0.37755 | 0.37449 | 1.0653 | 1.0204 | 0.99694 | 0.91429 | 0.82755 | 0.75102 | 0.66837 | 0.64286 | 0.51531 | 0.29184 | 0.088776 | 0.50969 | 0.50867 | 1.4265 | 1.4112 | 1.4 | 1.3551 | 1.3031 | 1.2735 | 1.2224 | 1.2031 | 1.0918 | 1.1041 | 1.1296 | 0.48138 | 0.47934 | 0.89571 | 0.8702 | 0.84571 | 0.77429 | 0.72531 | 0.67429 | 0.60388 | 0.57531 | 0.44265 | 0.34673 | 0.27429
|  | SALEN 2 | HE |  |  |  |  | 0.37755 | 0.37449 | 1.0653 | 1.0143 | 0.98163 | 0.87449 | 0.79286 | 0.72041 | 0.64694 | 0.61224 | 0.50306 | 0.25408 | 0.09898 | 0.50867 | 0.50867 | 1.4265 | 1.4112 | 1.398 | 1.351 | 1.2969 | 1.2694 | 1.2204 | 1.199 | 1.1143 | 1.1102 | 1.0898 | 0.48138 | 0.47934 | 0.89571 | 0.86714 | 0.83551 | 0.77939 | 0.70694 | 0.65796 | 0.59265 | 0.55898 | 0.45388 | 0.33653 | 0.2651
|  | SALEN 2 | FB |  |  |  |  | 0.4051 | 0.41327 | 1.1194 | 1.1173 | 1.1133 | 1.0969 | 1.0816 | 1.0714 | 1.051 | 1.0347 | 0.94184 | 0.79694 | 0.75408 | 0.54235 | 0.54439 | 1.4684 | 1.4643 | 1.4643 | 1.4541 | 1.4276 | 1.4143 | 1.3847 | 1.3551 | 1.2561 | 1.1306 | 1.0612 | 0.52015 | 0.52934 | 0.96 | 0.96102 | 0.96306 | 0.9498 | 0.92633 | 0.9202 | 0.89265 | 0.8702 | 0.76612 | 0.66306 | 0.65082
| THURSO | SANDAY | MINIMUM HEADROOM | HY 61184 35797 | YES | NO | 0.064 | 0.22449 | 0.21939 | 0.21837 | 0.1949 | 0.16327 | -0.10204 | -0.26429 | -0.36429 | -0.47449 | -0.55816 | -0.82653 | -0.8949 | -0.94796 | 0.52245 | 0.52143 | 0.52551 | 0.51837 | 0.51122 | 0.28571 | 0.13061 | 0.071429 | -0.02449 | -0.086735 | -0.34592 | -0.33878 | -0.31633 | 0.40204 | 0.39694 | 0.39184 | 0.36837 | 0.34184 | 0.11633 | -0.060204 | -0.12245 | -0.21735 | -0.29694 | -0.55102 | -0.58367 | -0.60816
|  | SANDAY | EE |  |  |  |  | 0.22551 | 0.22143 | 0.22041 | 0.20204 | 0.17551 | -0.047959 | -0.26429 | -0.34184 | -0.42653 | -0.55102 | -0.82653 | -0.8949 | -0.93571 | 0.52245 | 0.52245 | 0.52551 | 0.51939 | 0.51327 | 0.3398 | 0.13061 | 0.086735 | 0.030612 | -0.085714 | -0.33673 | -0.32755 | -0.29796 | 0.40306 | 0.39796 | 0.39388 | 0.37449 | 0.35204 | 0.17347 | -0.060204 | -0.10204 | -0.17245 | -0.29286 | -0.55102 | -0.58367 | -0.59592
|  | SANDAY | HT |  |  |  |  | 0.22449 | 0.21939 | 0.21837 | 0.20102 | 0.17449 | -0.10204 | -0.22755 | -0.28673 | -0.44694 | -0.49898 | -0.78163 | -0.86939 | -0.94796 | 0.52245 | 0.52143 | 0.52551 | 0.51939 | 0.51327 | 0.28571 | 0.15408 | 0.11531 | -0.02449 | -0.068367 | -0.34592 | -0.33878 | -0.31633 | 0.40204 | 0.39694 | 0.39184 | 0.37245 | 0.35102 | 0.11633 | -0.030612 | -0.080612 | -0.20714 | -0.25408 | -0.53265 | -0.57041 | -0.60816
|  | SANDAY | HE |  |  |  |  | 0.22449 | 0.22245 | 0.21837 | 0.1949 | 0.16327 | -0.034694 | -0.17347 | -0.36429 | -0.47449 | -0.55816 | -0.57245 | -0.65612 | -0.72143 | 0.52245 | 0.52347 | 0.52551 | 0.51837 | 0.51122 | 0.33878 | 0.22755 | 0.071429 | -0.0071429 | -0.086735 | -0.13061 | -0.12143 | -0.11531 | 0.40204 | 0.39796 | 0.39184 | 0.36837 | 0.34184 | 0.16531 | 0.034694 | -0.12245 | -0.21735 | -0.29694 | -0.32551 | -0.35408 | -0.38878
|  | SANDAY | FB |  |  |  |  | 0.24388 | 0.24592 | 0.25204 | 0.25714 | 0.25 | 0.24592 | 0.23571 | 0.21939 | 0.21531 | 0.2 | 0.13469 | 0.041837 | -0.36429 | 0.53367 | 0.53367 | 0.53878 | 0.54082 | 0.53367 | 0.53265 | 0.53163 | 0.52245 | 0.52143 | 0.5 | 0.43673 | 0.33469 | -0.09898 | 0.41837 | 0.41429 | 0.41939 | 0.42245 | 0.41327 | 0.40816 | 0.40408 | 0.39286 | 0.38673 | 0.37551 | 0.30612 | 0.18776 | -0.23061
| DUNOON | SANDBANK | MINIMUM HEADROOM | NS 15274 81386 | NO | YES | 0.441 | 4.3988 | 4.4284 | 4.2631 | 4.258 | 4.0355 | 3.7671 | 3.5376 | 3.2508 | 3.0355 | 2.812 | 2.0784 | 1.3049 | 0.95898 | 5.1284 | 5.1355 | 4.8712 | 4.8396 | 4.6376 | 4.3906 | 4.1773 | 3.961 | 3.81 | 3.5927 | 3.1049 | 2.6682 | 2.5447 | 4.8835 | 4.8967 | 4.7059 | 4.6886 | 4.4559 | 4.2029 | 3.9671 | 3.7039 | 3.509 | 3.2947 | 2.6559 | 2.0059 | 1.7539
|  | SANDBANK | EE |  |  |  |  | 4.3998 | 4.4294 | 4.4324 | 4.4355 | 4.0355 | 3.7671 | 3.5814 | 3.2865 | 3.0631 | 2.812 | 2.0784 | 1.3049 | 0.95898 | 5.1294 | 5.1365 | 5.1335 | 5.1304 | 4.6396 | 4.3906 | 4.2529 | 3.9916 | 3.8222 | 3.6029 | 3.1151 | 2.6682 | 2.5447 | 4.8835 | 4.8978 | 4.8927 | 4.8763 | 4.4559 | 4.2029 | 4.0294 | 3.7365 | 3.5304 | 3.2947 | 2.6559 | 2.0059 | 1.7539
|  | SANDBANK | HT |  |  |  |  | 4.3998 | 4.4294 | 4.4376 | 4.4141 | 4.0365 | 3.808 | 3.5376 | 3.2773 | 3.0753 | 2.8233 | 2.1947 | 1.412 | 1.0722 | 5.1284 | 5.1365 | 5.1314 | 5.1273 | 4.6376 | 4.4376 | 4.1773 | 3.961 | 3.8212 | 3.5927 | 3.1049 | 2.6682 | 2.6386 | 4.8845 | 4.8978 | 4.8957 | 4.8753 | 4.4559 | 4.2508 | 3.9671 | 3.7192 | 3.5396 | 3.2988 | 2.7294 | 2.0835 | 1.8661
|  | SANDBANK | HE |  |  |  |  | 4.3988 | 4.4284 | 4.4314 | 4.4273 | 4.0671 | 3.8018 | 3.5569 | 3.2508 | 3.0355 | 2.8192 | 2.2324 | 1.8671 | 1.5927 | 5.1284 | 5.1355 | 5.1314 | 5.1263 | 4.6927 | 4.4508 | 4.2427 | 3.9702 | 3.81 | 3.6345 | 3.1937 | 3.1906 | 3.1222 | 4.8835 | 4.8967 | 4.8916 | 4.8692 | 4.4947 | 4.2518 | 4.01 | 3.7039 | 3.509 | 3.312 | 2.7824 | 2.5478 | 2.3539
|  | SANDBANK | FB |  |  |  |  | 4.4518 | 4.4865 | 4.2631 | 4.258 | 4.2784 | 4.1794 | 4.1722 | 4.1641 | 4.1294 | 4.1192 | 3.5222 | 2.8824 | 2.56 | 5.1651 | 5.1743 | 4.8712 | 4.8396 | 4.8386 | 4.71 | 4.6763 | 4.66 | 4.6202 | 4.6039 | 3.9753 | 3.3978 | 2.9967 | 4.9345 | 4.9508 | 4.7059 | 4.6886 | 4.6967 | 4.5845 | 4.5518 | 4.5386 | 4.5008 | 4.4835 | 3.8641 | 3.108 | 2.9467
| SHETLAND | SANDWICK | MINIMUM HEADROOM | HU4308625957 | YES | YES | 0.148 | 0.5102 | 0.51633 | 5.2743 | 5.2314 | 5.1529 | 5.0447 | 4.8978 | 4.7447 | 4.5927 | 4.5202 | 4.2804 | 4.0396 | 3.8365 | 1.5929 | 1.5939 | 5.9488 | 5.9376 | 5.9171 | 5.8253 | 5.7437 | 5.6508 | 5.5416 | 5.4549 | 5.3386 | 5.3427 | 5.2998 | 1.0449 | 1.049 | 5.6018 | 5.5294 | 5.4988 | 5.4273 | 5.3222 | 5.21 | 5.1018 | 5.0437 | 4.8671 | 4.7273 | 4.61
|  | SANDWICK | EE |  |  |  |  | 0.5102 | 0.52551 | 5.2743 | 5.2376 | 5.1651 | 5.0488 | 4.8978 | 4.7447 | 4.5927 | 4.5202 | 4.2804 | 4.0396 | 3.8641 | 1.5939 | 1.6031 | 5.9488 | 5.9376 | 5.9171 | 5.8273 | 5.7457 | 5.6518 | 5.5416 | 5.4549 | 5.3916 | 5.3967 | 5.4365 | 1.0459 | 1.0571 | 5.6018 | 5.5355 | 5.5049 | 5.4304 | 5.3222 | 5.21 | 5.1018 | 5.0437 | 4.8671 | 4.7273 | 4.6355
|  | SANDWICK | HT |  |  |  |  | 0.5102 | 0.52143 | 5.2794 | 5.2529 | 5.1855 | 5.0753 | 4.9396 | 4.7967 | 4.661 | 4.5824 | 4.3753 | 4.0886 | 3.8365 | 1.5929 | 1.5949 | 5.9508 | 5.9396 | 5.9171 | 5.8253 | 5.7437 | 5.6508 | 5.56 | 5.4549 | 5.3386 | 5.3427 | 5.3937 | 1.0449 | 1.052 | 5.6059 | 5.5498 | 5.5182 | 5.4447 | 5.3478 | 5.2416 | 5.1437 | 5.0804 | 4.9141 | 4.7478 | 4.61
|  | SANDWICK | HE |  |  |  |  | 0.5102 | 0.51633 | 5.2743 | 5.2314 | 5.1529 | 5.0447 | 4.908 | 4.76 | 4.6182 | 4.5355 | 4.3692 | 4.0651 | 3.8753 | 1.5949 | 1.5939 | 5.9498 | 5.9396 | 5.9182 | 5.8273 | 5.7457 | 5.6518 | 5.561 | 5.4549 | 5.3886 | 5.3702 | 5.3743 | 1.0469 | 1.049 | 5.6018 | 5.5294 | 5.4988 | 5.4273 | 5.3304 | 5.2202 | 5.1182 | 5.0529 | 4.9222 | 4.7365 | 4.6253
|  | SANDWICK | FB |  |  |  |  | 0.58061 | 0.61939 | 5.4141 | 5.4304 | 5.4467 | 5.4324 | 5.4284 | 5.3967 | 5.3753 | 5.3447 | 5.1365 | 5.009 | 4.9355 | 1.6439 | 1.6571 | 6.0294 | 6.0304 | 6.0324 | 6.0049 | 5.9886 | 5.9529 | 5.8947 | 5.858 | 5.6049 | 5.4722 | 5.2998 | 1.1092 | 1.1337 | 5.712 | 5.7141 | 5.7151 | 5.6947 | 5.6886 | 5.661 | 5.6631 | 5.6406 | 5.4508 | 5.3182 | 5.2845
| SHETLAND | SCALLOWAY | MINIMUM HEADROOM | HU4139939639 | YES | YES | 0.051 | -2.6265 | -2.6745 | 4.0131 | 3.8376 | 3.7427 | 3.5141 | 3.2988 | 3.1049 | 2.9559 | 2.8671 | 2.5702 | 2.2376 | 2.0222 | -1.3684 | -1.3684 | 4.9722 | 4.9518 | 4.9212 | 4.8651 | 4.7855 | 4.7008 | 4.7294 | 4.6661 | 4.4631 | 4.3682 | 4.16 | -1.9663 | -1.9929 | 4.5284 | 4.4222 | 4.362 | 4.2141 | 4.0631 | 3.9233 | 3.8294 | 3.7498 | 3.5131 | 3.309 | 3.1814
|  | SCALLOWAY | EE |  |  |  |  | -2.6265 | -2.6327 | 4.0508 | 3.8376 | 3.7427 | 3.5141 | 3.2988 | 3.1049 | 2.9559 | 2.8671 | 2.5702 | 2.2376 | 2.0365 | -1.3673 | -1.3531 | 4.9886 | 4.962 | 4.9324 | 4.8692 | 4.7855 | 4.7018 | 4.7518 | 4.6824 | 4.4988 | 4.4029 | 4.3937 | -1.9653 | -1.9663 | 4.5284 | 4.4263 | 4.3661 | 4.2141 | 4.0631 | 3.9233 | 3.8294 | 3.7498 | 3.5131 | 3.31 | 3.212
|  | SCALLOWAY | HT |  |  |  |  | -2.6265 | -2.6745 | 4.0131 | 3.8386 | 3.7437 | 3.5784 | 3.3988 | 3.2151 | 3.0743 | 2.9804 | 2.712 | 2.3151 | 2.0222 | -1.3684 | -1.3684 | 4.9722 | 4.9518 | 4.9212 | 4.8712 | 4.7927 | 4.7069 | 4.7355 | 4.6661 | 4.4631 | 4.3682 | 4.4253 | -1.9663 | -1.9929 | 4.5284 | 4.4222 | 4.362 | 4.2498 | 4.1202 | 3.9814 | 3.8967 | 3.8141 | 3.5702 | 3.3294 | 3.1814
|  | SCALLOWAY | HE |  |  |  |  | -2.6255 | -2.6337 | 4.0692 | 3.8967 | 3.8018 | 3.5222 | 3.3396 | 3.1416 | 2.9927 | 2.8906 | 2.6743 | 2.2549 | 2.1059 | -1.3673 | -1.3551 | 4.9896 | 4.9753 | 4.9437 | 4.8651 | 4.7865 | 4.7008 | 4.7294 | 4.6804 | 4.5029 | 4.3784 | 4.4416 | -1.9643 | -1.9663 | 4.5427 | 4.462 | 4.4008 | 4.2171 | 4.0855 | 3.9386 | 3.8498 | 3.7631 | 3.5692 | 3.309 | 3.2488
|  | SCALLOWAY | FB |  |  |  |  | -2.549 | -2.5163 | 4.2722 | 4.2416 | 4.2294 | 4.2182 | 4.1427 | 4.1447 | 4.1151 | 4.0886 | 3.91 | 3.6406 | 3.5569 | -1.3214 | -1.2786 | 5.1029 | 5.0916 | 5.0845 | 5.059 | 4.9988 | 4.9722 | 4.9151 | 4.8763 | 4.7447 | 4.3865 | 4.16 | -1.9041 | -1.8704 | 4.7161 | 4.6978 | 4.6865 | 4.6631 | 4.6018 | 4.6273 | 4.5988 | 4.562 | 4.4263 | 4.109 | 4.0692
| TAYNUILT | SCAMMADALE | MINIMUM HEADROOM | NM 84207 19638 | YES | YES | 0 | 0.054735 | 0.054735 | 0.044531 | 0.040449 | 0.039429 | 0.032286 | 0.027184 | 0.01902 | 0.0088163 | 0.0098367 | -0.0064898 | -0.012612 | -0.017714 | 0.061041 | 0.061041 | 0.051857 | 0.048796 | 0.050837 | 0.045735 | 0.040633 | 0.03349 | 0.026347 | 0.025327 | 0.0079796 | 0.009 | 0.013082 | 0.058398 | 0.058398 | 0.048194 | 0.043092 | 0.043092 | 0.036969 | 0.031867 | 0.022684 | 0.017582 | 0.016561 | 0.00023469 | -0.0038469 | -0.0058878
|  | SCAMMADALE | EE |  |  |  |  | 0.054735 | 0.054735 | 0.044531 | 0.041469 | 0.039429 | 0.033306 | 0.027184 | 0.01902 | 0.0088163 | 0.0098367 | -0.0064898 | -0.012612 | -0.015673 | 0.061041 | 0.061041 | 0.051857 | 0.050837 | 0.050837 | 0.045735 | 0.040633 | 0.03349 | 0.026347 | 0.025327 | 0.011041 | 0.013082 | 0.018184 | 0.058398 | 0.058398 | 0.048194 | 0.044112 | 0.044112 | 0.036969 | 0.031867 | 0.022684 | 0.017582 | 0.016561 | 0.00023469 | -0.0028265 | -0.0018061
|  | SCAMMADALE | HT |  |  |  |  | 0.054735 | 0.054735 | 0.049633 | 0.040449 | 0.041469 | 0.033306 | 0.029224 | 0.021061 | 0.011878 | 0.010857 | -0.0024082 | -0.011592 | -0.017714 | 0.061041 | 0.061041 | 0.054918 | 0.048796 | 0.050837 | 0.045735 | 0.041653 | 0.03349 | 0.026347 | 0.025327 | 0.0079796 | 0.009 | 0.013082 | 0.058398 | 0.058398 | 0.053296 | 0.043092 | 0.045133 | 0.036969 | 0.032888 | 0.025745 | 0.019622 | 0.016561 | 0.00023469 | -0.0038469 | -0.0058878
|  | SCAMMADALE | HE |  |  |  |  | 0.054735 | 0.054735 | 0.049633 | 0.041469 | 0.039429 | 0.032286 | 0.027184 | 0.020041 | 0.0098367 | 0.010857 | -0.0034286 | -0.012612 | -0.016694 | 0.061041 | 0.061041 | 0.054918 | 0.050837 | 0.050837 | 0.045735 | 0.040633 | 0.03349 | 0.026347 | 0.025327 | 0.011041 | 0.012061 | 0.013082 | 0.058398 | 0.058398 | 0.053296 | 0.045133 | 0.043092 | 0.036969 | 0.031867 | 0.023704 | 0.017582 | 0.016561 | 0.0022755 | -0.0018061 | -0.0058878
|  | SCAMMADALE | FB |  |  |  |  | 0.054735 | 0.060857 | 0.056776 | 0.054735 | 0.056776 | 0.050653 | 0.049633 | 0.045551 | 0.044531 | 0.04249 | 0.031265 | 0.021061 | 0.014939 | 0.061041 | 0.066143 | 0.062061 | 0.062061 | 0.059 | 0.053898 | 0.051857 | 0.047776 | 0.048796 | 0.044714 | 0.031449 | 0.021245 | 0.016143 | 0.058398 | 0.06452 | 0.061459 | 0.059418 | 0.060439 | 0.052276 | 0.049214 | 0.048194 | 0.044112 | 0.042071 | 0.029827 | 0.016561 | 0.0135
| ABERNETHY | SCONE | MINIMUM HEADROOM | NO 14401 25495 | NO | YES | 3.485 | 8.1896 | 7.9151 | 7.7732 | 7.4651 | 7.1539 | 6.5518 | 6.0508 | 5.3794 | 4.8508 | 4.2141 | 2.0988 | 0.62018 | -0.26451 | 8.9294 | 8.712 | 8.6569 | 8.5028 | 8.3263 | 7.9702 | 7.7743 | 7.3559 | 7.0916 | 6.6488 | 5.5457 | 5.0773 | 4.7528 | 8.6238 | 8.288 | 8.188 | 7.9084 | 7.6084 | 7.087 | 6.6982 | 6.1084 | 5.6799 | 5.1003 | 3.337 | 2.2227 | 1.5595
|  | SCONE | EE |  |  |  |  | 8.1896 | 7.9151 | 7.7732 | 7.4651 | 7.1539 | 6.5518 | 6.0508 | 5.3794 | 4.8508 | 4.2141 | 2.0988 | 0.62018 | -0.26451 | 8.9294 | 8.713 | 8.6569 | 8.5028 | 8.3283 | 7.9834 | 7.7845 | 7.3559 | 7.0916 | 6.6488 | 5.56 | 5.0773 | 4.7528 | 8.6238 | 8.288 | 8.188 | 7.9084 | 7.6084 | 7.0942 | 6.6982 | 6.1084 | 5.6799 | 5.1003 | 3.337 | 2.2227 | 1.5595
|  | SCONE | HT |  |  |  |  | 8.1916 | 7.9192 | 7.7916 | 7.4988 | 7.1692 | 6.5957 | 6.1161 | 5.5467 | 4.9569 | 4.3467 | 2.2028 | 0.72324 | -0.12573 | 8.9294 | 8.712 | 8.6569 | 8.5059 | 8.3263 | 7.9855 | 7.7753 | 7.4498 | 7.0988 | 6.6814 | 5.5457 | 5.1508 | 5.012 | 8.6258 | 8.2901 | 8.2033 | 7.9299 | 7.6156 | 7.1166 | 6.7299 | 6.2523 | 5.7462 | 5.1952 | 3.4115 | 2.3289 | 1.734
|  | SCONE | HE |  |  |  |  | 8.1906 | 7.9181 | 7.7814 | 7.4794 | 7.1641 | 6.5518 | 6.0732 | 5.4161 | 4.9008 | 4.3365 | 2.5641 | 1.2732 | 0.55896 | 8.9294 | 8.7141 | 8.6569 | 8.5049 | 8.3314 | 7.9702 | 7.7743 | 7.3569 | 7.1039 | 6.7508 | 5.8467 | 5.4834 | 5.1498 | 8.6238 | 8.2921 | 8.1942 | 7.9187 | 7.6166 | 7.087 | 6.7095 | 6.134 | 5.7166 | 5.2258 | 3.7533 | 2.8136 | 2.2615
|  | SCONE | FB |  |  |  |  | 8.309 | 8.2692 | 7.9539 | 7.8549 | 7.7681 | 7.6212 | 7.3814 | 7.1232 | 6.9957 | 6.7457 | 5.5641 | 4.4426 | 3.5508 | 9.0079 | 8.9743 | 8.7253 | 8.6824 | 8.6314 | 8.5406 | 8.3732 | 8.1926 | 8.1345 | 7.9437 | 7.0345 | 6.0304 | 4.9528 | 8.7329 | 8.6809 | 8.3013 | 8.2299 | 8.1523 | 8.0319 | 7.8013 | 7.5625 | 7.4584 | 7.2187 | 6.1299 | 4.8554 | 4.1574
| THURSO | SHAPINSAY | MINIMUM HEADROOM | HY 48313 17148 | YES | NO | 0 | 0.67245 | 0.66327 | 0.66122 | 0.64592 | 0.63163 | 0.43673 | 0.41633 | 0.21327 | 0.16735 | 0.12959 | -0.092857 | -0.11531 | -0.13061 | 0.79184 | 0.78673 | 0.78469 | 0.77857 | 0.77143 | 0.58673 | 0.57857 | 0.38571 | 0.35 | 0.31837 | 0.10408 | 0.11837 | 0.12551 | 0.74796 | 0.74082 | 0.73878 | 0.72755 | 0.70714 | 0.52551 | 0.51224 | 0.31327 | 0.26327 | 0.23878 | 0.0040816 | -0.005102 | 0.012245
|  | SHAPINSAY | EE |  |  |  |  | 0.67245 | 0.66531 | 0.66224 | 0.64796 | 0.63571 | 0.6102 | 0.58367 | 0.37143 | 0.17245 | 0.15204 | -0.092857 | -0.11531 | -0.1 | 0.79184 | 0.78776 | 0.78469 | 0.77857 | 0.77245 | 0.75714 | 0.74898 | 0.5551 | 0.35204 | 0.33571 | 0.10408 | 0.11837 | 0.15816 | 0.74796 | 0.74184 | 0.7398 | 0.72857 | 0.70918 | 0.68776 | 0.66939 | 0.47347 | 0.26327 | 0.24796 | 0.0040816 | -0.005102 | 0.043878
|  | SHAPINSAY | HT |  |  |  |  | 0.67245 | 0.66327 | 0.66122 | 0.64898 | 0.63571 | 0.43673 | 0.41633 | 0.21327 | 0.16735 | 0.12959 | -0.044898 | -0.07449 | -0.13061 | 0.79184 | 0.78673 | 0.78469 | 0.78163 | 0.77143 | 0.58673 | 0.57857 | 0.38571 | 0.35 | 0.31837 | 0.13265 | 0.14286 | 0.12551 | 0.74796 | 0.74184 | 0.73878 | 0.72857 | 0.70816 | 0.52551 | 0.51224 | 0.31327 | 0.27041 | 0.23878 | 0.04898 | 0.030612 | 0.012245
|  | SHAPINSAY | HE |  |  |  |  | 0.67245 | 0.66327 | 0.66122 | 0.64592 | 0.63163 | 0.60612 | 0.57857 | 0.55 | 0.54184 | 0.53469 | 0.50714 | 0.45816 | 0.41939 | 0.79184 | 0.78673 | 0.78469 | 0.77857 | 0.77143 | 0.75714 | 0.74898 | 0.73469 | 0.71939 | 0.71633 | 0.68265 | 0.67653 | 0.67551 | 0.74796 | 0.74082 | 0.73878 | 0.72755 | 0.70714 | 0.68571 | 0.66735 | 0.64388 | 0.61939 | 0.61531 | 0.58061 | 0.55408 | 0.55306
|  | SHAPINSAY | FB |  |  |  |  | 0.68265 | 0.68265 | 0.68061 | 0.67959 | 0.67755 | 0.65918 | 0.65408 | 0.64592 | 0.64082 | 0.63265 | 0.5949 | 0.55 | 0.53265 | 0.80204 | 0.8 | 0.79796 | 0.79694 | 0.79388 | 0.77449 | 0.77041 | 0.75816 | 0.7551 | 0.74694 | 0.72041 | 0.68367 | 0.66633 | 0.75816 | 0.75918 | 0.75612 | 0.75204 | 0.7449 | 0.72755 | 0.72143 | 0.70714 | 0.70204 | 0.69184 | 0.65918 | 0.61224 | 0.60306
| BROADFORD | SHIELDAIG | MINIMUM HEADROOM | NG 81637 52250 | YES | YES | 0.028 | 0.37551 | 0.36735 | 0.36429 | 0.35204 | 0.33776 | 0.31531 | 0.30306 | 0.28469 | 0.26531 | 0.24592 | 0.21531 | 0.20714 | 0.20204 | 0.63469 | 0.62857 | 0.62959 | 0.62449 | 0.61939 | 0.6102 | 0.60408 | 0.59898 | 0.58571 | 0.57857 | 0.5602 | 0.55816 | 0.56122 | 0.56939 | 0.55816 | 0.5602 | 0.55 | 0.54184 | 0.52551 | 0.51531 | 0.50102 | 0.47959 | 0.46429 | 0.43367 | 0.41735 | 0.41327
|  | SHIELDAIG | EE |  |  |  |  | 0.37551 | 0.36735 | 0.36429 | 0.35204 | 0.33776 | 0.31531 | 0.3051 | 0.28571 | 0.26633 | 0.24694 | 0.21531 | 0.21224 | 0.21122 | 0.63469 | 0.62857 | 0.62959 | 0.62449 | 0.61939 | 0.61122 | 0.60612 | 0.59898 | 0.58673 | 0.57857 | 0.56224 | 0.56327 | 0.56633 | 0.56939 | 0.55816 | 0.5602 | 0.55 | 0.54286 | 0.52755 | 0.51633 | 0.50204 | 0.48163 | 0.46531 | 0.43367 | 0.42245 | 0.41837
|  | SHIELDAIG | HT |  |  |  |  | 0.37551 | 0.36837 | 0.36429 | 0.35204 | 0.33878 | 0.31633 | 0.3051 | 0.28673 | 0.26735 | 0.24898 | 0.21531 | 0.20714 | 0.20204 | 0.63469 | 0.62857 | 0.62959 | 0.62449 | 0.61939 | 0.61122 | 0.6051 | 0.59898 | 0.58571 | 0.57857 | 0.5602 | 0.55816 | 0.56122 | 0.56939 | 0.55918 | 0.5602 | 0.55102 | 0.54286 | 0.52755 | 0.51633 | 0.50306 | 0.48163 | 0.46633 | 0.43469 | 0.41735 | 0.41327
|  | SHIELDAIG | HE |  |  |  |  | 0.37551 | 0.37041 | 0.36429 | 0.35204 | 0.33776 | 0.31531 | 0.30306 | 0.28469 | 0.26531 | 0.24592 | 0.22143 | 0.21327 | 0.20612 | 0.63469 | 0.63061 | 0.62959 | 0.62449 | 0.61939 | 0.6102 | 0.60408 | 0.59898 | 0.58571 | 0.57857 | 0.56327 | 0.56224 | 0.56224 | 0.56939 | 0.56122 | 0.5602 | 0.55 | 0.54184 | 0.52551 | 0.51531 | 0.50102 | 0.47959 | 0.46429 | 0.43878 | 0.42245 | 0.41531
|  | SHIELDAIG | FB |  |  |  |  | 0.38776 | 0.38469 | 0.38061 | 0.37551 | 0.37041 | 0.3602 | 0.35714 | 0.34898 | 0.33776 | 0.33673 | 0.29796 | 0.27245 | 0.26327 | 0.64286 | 0.6398 | 0.63776 | 0.63673 | 0.63571 | 0.63061 | 0.62857 | 0.62449 | 0.61939 | 0.61939 | 0.59898 | 0.58163 | 0.57551 | 0.57755 | 0.57449 | 0.57245 | 0.57041 | 0.56837 | 0.56122 | 0.5602 | 0.5551 | 0.54796 | 0.54592 | 0.50612 | 0.47653 | 0.47143
| SHIN | SHIN | MINIMUM HEADROOM | NH 57246 97463 | YES | NO | 0.019 | 2.4867 | 2.4847 | 2.4806 | 2.4622 | 2.4469 | 2.4143 | 2.3806 | 2.3531 | 2.3429 | 2.3245 | 2.2418 | 2.1714 | 2.1082 | 2.4628 | 2.4597 | 2.4526 | 2.4423 | 2.4383 | 2.424 | 2.4036 | 2.3923 | 2.374 | 2.3617 | 2.3179 | 2.3138 | 2.3077 | 2.4702 | 2.4671 | 2.462 | 2.4446 | 2.4365 | 2.411 | 2.3814 | 2.364 | 2.3365 | 2.3181 | 2.2538 | 2.2385 | 2.211
|  | SHIN | EE |  |  |  |  | 2.4888 | 2.4847 | 2.4816 | 2.4643 | 2.451 | 2.4143 | 2.3857 | 2.3612 | 2.352 | 2.3327 | 2.2418 | 2.1714 | 2.1133 | 2.4658 | 2.4607 | 2.4536 | 2.4423 | 2.4383 | 2.424 | 2.4036 | 2.3923 | 2.375 | 2.3638 | 2.3189 | 2.3189 | 2.325 | 2.4732 | 2.4681 | 2.462 | 2.4446 | 2.4395 | 2.411 | 2.3844 | 2.3661 | 2.3426 | 2.3263 | 2.2538 | 2.2426 | 2.2263
|  | SHIN | HT |  |  |  |  | 2.4867 | 2.4847 | 2.4806 | 2.4653 | 2.4541 | 2.4255 | 2.3898 | 2.3653 | 2.3541 | 2.3367 | 2.2816 | 2.201 | 2.1082 | 2.4628 | 2.4597 | 2.4526 | 2.4444 | 2.4393 | 2.425 | 2.4056 | 2.3934 | 2.374 | 2.3638 | 2.3301 | 2.3291 | 2.3219 | 2.4702 | 2.4671 | 2.462 | 2.4467 | 2.4406 | 2.4171 | 2.3865 | 2.3691 | 2.3416 | 2.3293 | 2.2844 | 2.263 | 2.2171
|  | SHIN | HE |  |  |  |  | 2.4867 | 2.4847 | 2.4806 | 2.4622 | 2.4469 | 2.4143 | 2.3806 | 2.3531 | 2.3429 | 2.3245 | 2.2612 | 2.1786 | 2.1224 | 2.4628 | 2.4607 | 2.4526 | 2.4434 | 2.4383 | 2.425 | 2.4056 | 2.3923 | 2.374 | 2.3617 | 2.3179 | 2.3138 | 2.3107 | 2.4702 | 2.4681 | 2.462 | 2.4457 | 2.4365 | 2.411 | 2.3814 | 2.364 | 2.3365 | 2.3181 | 2.2661 | 2.2385 | 2.211
|  | SHIN | FB |  |  |  |  | 2.5051 | 2.502 | 2.501 | 2.5 | 2.498 | 2.4888 | 2.4837 | 2.4724 | 2.4663 | 2.4561 | 2.4082 | 2.3469 | 2.3286 | 2.4801 | 2.4719 | 2.4699 | 2.4668 | 2.4638 | 2.4546 | 2.4526 | 2.4403 | 2.4311 | 2.4199 | 2.3872 | 2.3321 | 2.3077 | 2.4926 | 2.4844 | 2.4855 | 2.4804 | 2.4783 | 2.4712 | 2.4671 | 2.4538 | 2.4467 | 2.4355 | 2.3957 | 2.3334 | 2.3283
| FORT WILLIAM | SHONA BEG | MINIMUM HEADROOM | NM 67173 74363 | YES | NO | 0 | 0.10473 | 0.10473 | 0.10576 | 0.094531 | 0.090449 | 0.084327 | 0.081265 | 0.080245 | 0.076163 | 0.076163 | 0.06698 | 0.062898 | 0.061878 | 0.098796 | 0.098796 | 0.098796 | 0.087571 | 0.08451 | 0.082469 | 0.079408 | 0.080429 | 0.076347 | 0.077367 | 0.068184 | 0.069204 | 0.069204 | 0.10228 | 0.10228 | 0.1033 | 0.091051 | 0.086969 | 0.081867 | 0.079827 | 0.078806 | 0.075745 | 0.075745 | 0.067582 | 0.066561 | 0.06452
|  | SHONA BEG | EE |  |  |  |  | 0.10473 | 0.10473 | 0.10576 | 0.094531 | 0.094531 | 0.084327 | 0.083306 | 0.080245 | 0.077184 | 0.076163 | 0.06698 | 0.062898 | 0.062898 | 0.098796 | 0.098796 | 0.098796 | 0.087571 | 0.087571 | 0.082469 | 0.080429 | 0.080429 | 0.076347 | 0.077367 | 0.068184 | 0.070224 | 0.073286 | 0.10228 | 0.10228 | 0.1033 | 0.091051 | 0.091051 | 0.082888 | 0.081867 | 0.078806 | 0.076765 | 0.075745 | 0.067582 | 0.066561 | 0.066561
|  | SHONA BEG | HT |  |  |  |  | 0.10473 | 0.10473 | 0.10576 | 0.094531 | 0.09351 | 0.086367 | 0.081265 | 0.081265 | 0.076163 | 0.077184 | 0.071061 | 0.064939 | 0.061878 | 0.098796 | 0.098796 | 0.098796 | 0.087571 | 0.085531 | 0.08349 | 0.079408 | 0.080429 | 0.076347 | 0.077367 | 0.071245 | 0.069204 | 0.071245 | 0.10228 | 0.10228 | 0.1033 | 0.091051 | 0.090031 | 0.084929 | 0.079827 | 0.079827 | 0.075745 | 0.076765 | 0.071663 | 0.066561 | 0.065541
|  | SHONA BEG | HE |  |  |  |  | 0.10473 | 0.10473 | 0.10576 | 0.094531 | 0.090449 | 0.084327 | 0.082286 | 0.080245 | 0.077184 | 0.076163 | 0.06902 | 0.065959 | 0.062898 | 0.098796 | 0.098796 | 0.098796 | 0.087571 | 0.08451 | 0.082469 | 0.080429 | 0.080429 | 0.076347 | 0.077367 | 0.068184 | 0.071245 | 0.071245 | 0.10228 | 0.10228 | 0.1033 | 0.091051 | 0.086969 | 0.081867 | 0.081867 | 0.078806 | 0.076765 | 0.075745 | 0.068602 | 0.068602 | 0.06452
|  | SHONA BEG | FB |  |  |  |  | 0.10473 | 0.10473 | 0.10576 | 0.10576 | 0.098612 | 0.097592 | 0.098612 | 0.09249 | 0.09249 | 0.091469 | 0.085347 | 0.075143 | 0.075143 | 0.098796 | 0.098796 | 0.098796 | 0.098796 | 0.089612 | 0.088592 | 0.088592 | 0.082469 | 0.082469 | 0.08349 | 0.079408 | 0.070224 | 0.069204 | 0.10228 | 0.10228 | 0.1033 | 0.1033 | 0.095133 | 0.094112 | 0.094112 | 0.08799 | 0.08799 | 0.08901 | 0.082888 | 0.072684 | 0.072684
| KINTORE | SKENE | MINIMUM HEADROOM | NJ 82203 06495 | NO | YES | 2.223 | 14.2016 | 14.2016 | 14.1577 | 14.1271 | 14.0138 | 13.7546 | 13.5097 | 13.2342 | 12.9781 | 12.6985 | 11.8383 | 11.6822 | 11.7005 | 16.6924 | 16.672 | 16.6077 | 16.5597 | 16.4311 | 16.1648 | 15.9158 | 15.6383 | 15.375 | 15.1056 | 14.226 | 14.0577 | 13.8832 | 15.7669 | 15.7495 | 15.6822 | 15.6281 | 15.4883 | 15.2005 | 14.9301 | 14.6311 | 14.3516 | 14.0597 | 13.1954 | 13.0832 | 13.1311
|  | SKENE | EE |  |  |  |  | 14.2016 | 14.2016 | 14.1587 | 14.1271 | 14.0138 | 13.7567 | 13.5179 | 13.2424 | 12.9924 | 12.7148 | 12.0087 | 11.8822 | 11.8873 | 16.6924 | 16.672 | 16.6087 | 16.5618 | 16.4352 | 16.1709 | 15.926 | 15.6464 | 15.3873 | 15.1209 | 14.3822 | 14.1179 | 13.8832 | 15.7689 | 15.7495 | 15.6832 | 15.6281 | 15.4913 | 15.2036 | 14.9424 | 14.6383 | 14.3648 | 14.0771 | 13.3587 | 13.2893 | 13.3301
|  | SKENE | HT |  |  |  |  | 14.2016 | 14.2046 | 14.1577 | 14.1281 | 14.0138 | 13.7546 | 13.5097 | 13.2342 | 12.9781 | 12.6985 | 11.8383 | 11.6822 | 11.7005 | 16.6924 | 16.672 | 16.6077 | 16.5597 | 16.4311 | 16.1648 | 15.9158 | 15.6383 | 15.375 | 15.1056 | 14.226 | 14.0577 | 14.1077 | 15.7669 | 15.7526 | 15.6822 | 15.6281 | 15.4883 | 15.2016 | 14.9301 | 14.6311 | 14.3516 | 14.0597 | 13.1954 | 13.0832 | 13.1311
|  | SKENE | HE |  |  |  |  | 14.2046 | 14.2087 | 14.1679 | 14.1301 | 14.0158 | 13.7556 | 13.5158 | 13.2403 | 12.9903 | 12.7138 | 12.0801 | 12.0087 | 12.0301 | 16.6944 | 16.675 | 16.6138 | 16.5618 | 16.4352 | 16.1679 | 15.923 | 15.6464 | 15.3862 | 15.1199 | 14.5332 | 14.3689 | 14.2301 | 15.7709 | 15.7536 | 15.6893 | 15.6281 | 15.4903 | 15.2005 | 14.9352 | 14.6383 | 14.3628 | 14.072 | 13.424 | 13.4046 | 13.4475
|  | SKENE | FB |  |  |  |  | 14.3056 | 14.3475 | 14.3811 | 14.2842 | 14.275 | 14.2495 | 14.172 | 14.0822 | 13.9801 | 13.8669 | 13.4067 | 12.8393 | 12.6026 | 16.7913 | 16.8067 | 16.8158 | 16.7056 | 16.6781 | 16.6383 | 16.5454 | 16.4444 | 16.3271 | 16.2026 | 15.6913 | 14.9924 | 14.0832 | 15.874 | 15.8934 | 15.9107 | 15.7893 | 15.7638 | 15.7199 | 15.623 | 15.5179 | 15.3985 | 15.2679 | 14.7362 | 14.073 | 13.9311
| BROADFORD | SKULAMUS | MINIMUM HEADROOM | NG 65881 22438 | YES | YES | 5.142 | -5.2947 | 1.8841 | 1.8545 | 1.781 | 1.7117 | 0.93207 | 0.013698 | -1.1036 | -1.9965 | -2.3792 | -3.1241 | -3.4536 | -3.673 | -4.7661 | 2.428 | 2.4137 | 2.3994 | 2.3678 | 1.8351 | 1.079 | 0.04431 | -0.79753 | -1.1832 | -1.8924 | -1.8781 | -1.8955 | -5.0049 | 2.181 | 2.1494 | 2.0933 | 2.0708 | 1.3555 | 0.51982 | -0.49957 | -1.3118 | -1.6588 | -2.3251 | -2.5394 | -2.6741
|  | SKULAMUS | EE |  |  |  |  | -5.2936 | 1.8861 | 1.8586 | 1.781 | 1.7137 | 1.5892 | 1.4157 | 0.64635 | -0.31691 | -1.3455 | -3.0679 | -3.4536 | -3.6475 | -4.7641 | 2.43 | 2.4137 | 2.3994 | 2.3688 | 2.3372 | 2.2739 | 1.7208 | 0.99635 | -0.025078 | -1.7067 | -1.8496 | -1.8312 | -5.0028 | 2.1841 | 2.1515 | 2.1178 | 2.0729 | 1.9861 | 1.8637 | 1.1596 | 0.28717 | -0.67712 | -2.2536 | -2.5394 | -2.6526
|  | SKULAMUS | HT |  |  |  |  | -5.2936 | 1.8861 | 1.8576 | 1.781 | 1.7117 | 0.93207 | 0.013698 | -1.1036 | -1.9965 | -2.3792 | -3.1241 | -3.4036 | -3.673 | -4.7641 | 2.43 | 2.4137 | 2.4004 | 2.3678 | 1.8351 | 1.079 | 0.04431 | -0.79753 | -1.1832 | -1.8924 | -1.8628 | -1.8271 | -5.0028 | 2.1831 | 2.1504 | 2.1188 | 2.0708 | 1.3555 | 0.51982 | -0.49957 | -1.3118 | -1.6588 | -2.3251 | -2.5057 | -2.6741
|  | SKULAMUS | HE |  |  |  |  | -5.2947 | 1.8841 | 1.8545 | 1.7831 | 1.7157 | 1.5831 | 1.4137 | 0.58104 | -0.46283 | -1.6404 | -2.9771 | -3.4036 | -3.5883 | -4.7661 | 2.428 | 2.4137 | 2.3994 | 2.3698 | 2.3341 | 2.2708 | 1.6647 | 0.82696 | -0.36487 | -1.7026 | -1.8557 | -1.8588 | -5.0049 | 2.181 | 2.1494 | 2.0933 | 2.0749 | 1.9821 | 1.8596 | 1.0953 | 0.13921 | -0.96385 | -2.1924 | -2.5139 | -2.6404
|  | SKULAMUS | FB |  |  |  |  | -5.2406 | 1.9739 | 1.98 | 1.9688 | 1.9678 | 1.9749 | 1.9137 | 1.8739 | 1.3443 | 0.73104 | -2.022 | -2.4751 | -2.5057 | -4.7212 | 2.4831 | 2.4912 | 2.4912 | 2.4851 | 2.4739 | 2.429 | 2.4096 | 1.9729 | 1.4861 | -1.4139 | -1.8781 | -1.8955 | -4.9539 | 2.2606 | 2.2719 | 2.2657 | 2.2647 | 2.2555 | 2.2035 | 2.1719 | 1.6912 | 1.1168 | -1.469 | -1.8873 | -1.8832
| WOODHILL | SPRINGHILL | MINIMUM HEADROOM | NJ 89850 06421 | NO | NO | 5.874 | 2.2812 | 19.9602 | 19.9908 | 19.7265 | 19.3398 | 18.5071 | 17.551 | 16.4592 | 15.3143 | 14.4173 | 9.5 | 5.5959 | 3.4684 | 4.8792 | 22.3133 | 22.3867 | 22.2735 | 22.1092 | 21.5827 | 21.0714 | 20.4643 | 19.8408 | 19.3286 | 17.1643 | 15.8684 | 15.101 | 3.9246 | 21.8112 | 21.8378 | 21.6224 | 21.3092 | 20.5337 | 19.7367 | 18.8184 | 17.7949 | 16.9684 | 12.699 | 9.8051 | 8.3143
|  | SPRINGHILL | EE |  |  |  |  | 2.2822 | 19.9602 | 19.9908 | 19.7337 | 19.3837 | 18.5071 | 17.6276 | 16.601 | 15.5816 | 14.7265 | 10.1857 | 5.5959 | 3.4684 | 4.8792 | 22.3133 | 22.3867 | 22.2745 | 22.1092 | 21.5827 | 21.1102 | 20.5347 | 19.9735 | 19.4704 | 17.351 | 15.8684 | 15.1051 | 3.9246 | 21.8112 | 21.8378 | 21.6224 | 21.3316 | 20.5337 | 19.7806 | 18.9051 | 17.9878 | 17.1918 | 13.2633 | 9.8051 | 8.3143
|  | SPRINGHILL | HT |  |  |  |  | 2.2812 | 19.9969 | 20.05 | 19.7857 | 19.4378 | 18.5582 | 17.551 | 16.4592 | 15.3143 | 14.4173 | 9.5 | 6.0337 | 4.4765 | 4.8802 | 22.3143 | 22.3888 | 22.2776 | 22.1112 | 21.599 | 21.0714 | 20.4643 | 19.8408 | 19.3286 | 17.1643 | 16.4816 | 16.3245 | 3.9409 | 21.8265 | 21.8918 | 21.6653 | 21.3694 | 20.5765 | 19.7367 | 18.8184 | 17.7949 | 16.9684 | 12.699 | 10.1051 | 9.048
|  | SPRINGHILL | HE |  |  |  |  | 2.2822 | 19.9878 | 20.0255 | 19.7265 | 19.3398 | 18.5133 | 17.6653 | 16.6561 | 15.6898 | 14.9367 | 10.9031 | 7.5316 | 6.0388 | 4.8802 | 22.3163 | 22.3878 | 22.2735 | 22.1245 | 21.5898 | 21.1133 | 20.5051 | 19.9827 | 19.499 | 17.4786 | 16.3469 | 15.6398 | 3.9399 | 21.8388 | 21.8745 | 21.6265 | 21.3092 | 20.5459 | 19.8153 | 18.9347 | 18.0786 | 17.3541 | 13.8724 | 11.4031 | 10.3235
|  | SPRINGHILL | FB |  |  |  |  | 2.4843 | 20.3224 | 20.3929 | 20.2092 | 20.2184 | 20.0316 | 19.8378 | 19.5857 | 19.2796 | 18.9867 | 17.1959 | 13.1133 | 11.4112 | 5.0231 | 22.5388 | 22.5694 | 22.3469 | 22.3745 | 22.2061 | 22.0194 | 21.799 | 21.5541 | 21.2816 | 19.8531 | 17.0173 | 15.101 | 4.146 | 22.1582 | 22.2173 | 21.9776 | 22.001 | 21.8235 | 21.6398 | 21.4071 | 21.1276 | 20.848 | 19.2041 | 15.3245 | 14.1714
| BRIDGE OF DUN | ST CYRUS | MINIMUM HEADROOM | NO 74889 65577 | NO | NO | 0.676 | 4.9501 | 4.8858 | 4.7868 | 4.7082 | 4.6286 | 4.5031 | 4.4123 | 4.2909 | 4.1827 | 4.0939 | 3.8868 | 3.6174 | 3.3562 | 5.7317 | 5.6776 | 5.6082 | 5.5439 | 5.5113 | 5.4684 | 5.4235 | 5.3245 | 5.2572 | 5.1847 | 5.1001 | 5.1215 | 5.0082 | 5.4205 | 5.347 | 5.2603 | 5.1603 | 5.1245 | 5.0347 | 4.9735 | 4.8674 | 4.7837 | 4.7072 | 4.5684 | 4.399 | 4.2164
|  | ST CYRUS | EE |  |  |  |  | 4.9633 | 4.8858 | 4.7868 | 4.7113 | 4.6439 | 4.5327 | 4.4511 | 4.3419 | 4.247 | 4.1613 | 3.8868 | 3.6174 | 3.3562 | 5.745 | 5.6776 | 5.6092 | 5.547 | 5.5154 | 5.4766 | 5.4256 | 5.3286 | 5.2613 | 5.1909 | 5.1409 | 5.149 | 5.0205 | 5.4327 | 5.348 | 5.2603 | 5.1664 | 5.1317 | 5.0541 | 4.999 | 4.9001 | 4.8276 | 4.7511 | 4.5684 | 4.399 | 4.2164
|  | ST CYRUS | HT |  |  |  |  | 4.9582 | 4.8898 | 4.796 | 4.7174 | 4.6409 | 4.5409 | 4.4705 | 4.3694 | 4.2776 | 4.1919 | 3.9694 | 3.6511 | 3.3633 | 5.7398 | 5.6796 | 5.6082 | 5.545 | 5.5113 | 5.4735 | 5.4235 | 5.3266 | 5.2572 | 5.1847 | 5.1001 | 5.1215 | 5.1756 | 5.4266 | 5.3521 | 5.2654 | 5.1674 | 5.1286 | 5.0592 | 5.0072 | 4.9082 | 4.8337 | 4.7592 | 4.6164 | 4.4205 | 4.2501
|  | ST CYRUS | HE |  |  |  |  | 4.9501 | 4.8858 | 4.7919 | 4.7082 | 4.6286 | 4.5031 | 4.4123 | 4.2909 | 4.1827 | 4.0939 | 3.9368 | 3.6439 | 3.447 | 5.7317 | 5.6776 | 5.6092 | 5.5439 | 5.5123 | 5.4684 | 5.4235 | 5.3245 | 5.2572 | 5.1868 | 5.1388 | 5.1337 | 5.1113 | 5.4205 | 5.347 | 5.2633 | 5.1603 | 5.1245 | 5.0347 | 4.9735 | 4.8674 | 4.7837 | 4.7072 | 4.6001 | 4.4082 | 4.2756
|  | ST CYRUS | FB |  |  |  |  | 5.0388 | 5.0021 | 4.947 | 4.897 | 4.8603 | 4.796 | 4.7623 | 4.7398 | 4.7092 | 4.6919 | 4.498 | 4.3664 | 4.299 | 5.8001 | 5.7592 | 5.7082 | 5.6735 | 5.6286 | 5.5827 | 5.5378 | 5.5194 | 5.4817 | 5.4582 | 5.2909 | 5.1623 | 5.0082 | 5.4898 | 5.4419 | 5.3786 | 5.3276 | 5.2756 | 5.2215 | 5.1939 | 5.1735 | 5.1378 | 5.1235 | 4.9378 | 4.8541 | 4.8225
| ST FERGUS GAS | ST FERGUS GAS TERM | MINIMUM HEADROOM | NK 0916 5377 | NO | NO | 0 | 34.8276 | 34.7786 | 34.7378 | 34.652 | 34.5786 | 34.4429 | 34.3235 | 34.1918 | 34.0357 | 33.9337 | 33.5327 | 33.3235 | 33.1561 | 33.8051 | 33.7724 | 33.749 | 33.6837 | 33.6255 | 33.5439 | 33.4867 | 33.4133 | 33.3235 | 33.2602 | 33.0082 | 33.0051 | 33.0296 | 33.05 | 33.0204 | 32.9837 | 32.9194 | 32.8765 | 32.7949 | 32.6867 | 32.5939 | 32.4704 | 32.3878 | 32.0714 | 31.8071 | 31.6235
|  | ST FERGUS GAS TERM | EE |  |  |  |  | 34.8276 | 34.7796 | 34.7378 | 34.6531 | 34.5786 | 34.4429 | 34.3265 | 34.1969 | 34.049 | 33.9469 | 33.5622 | 33.3694 | 33.2163 | 33.8051 | 33.7735 | 33.75 | 33.6847 | 33.6265 | 33.5459 | 33.4888 | 33.4163 | 33.3296 | 33.2663 | 33.0531 | 33.051 | 33.0796 | 33.05 | 33.0204 | 32.9837 | 32.9204 | 32.8786 | 32.7959 | 32.6888 | 32.601 | 32.4857 | 32.4031 | 32.0714 | 31.8265 | 31.6745
|  | ST FERGUS GAS TERM | HT |  |  |  |  | 34.8276 | 34.7786 | 34.7378 | 34.652 | 34.5786 | 34.4439 | 34.3235 | 34.1918 | 34.0357 | 33.9337 | 33.5327 | 33.3235 | 33.1561 | 33.8051 | 33.7724 | 33.749 | 33.6837 | 33.6255 | 33.5439 | 33.4867 | 33.4133 | 33.3235 | 33.2602 | 33.0082 | 33.0051 | 33.0449 | 33.05 | 33.0204 | 32.9847 | 32.9194 | 32.8765 | 32.7969 | 32.6867 | 32.5939 | 32.4704 | 32.3878 | 32.0816 | 31.8071 | 31.6235
|  | ST FERGUS GAS TERM | HE |  |  |  |  | 34.8276 | 34.7806 | 34.7388 | 34.6541 | 34.5786 | 34.4429 | 34.3265 | 34.1929 | 34.0388 | 33.9378 | 33.6 | 33.4061 | 33.3133 | 33.8051 | 33.7724 | 33.749 | 33.6847 | 33.6265 | 33.5449 | 33.4888 | 33.4163 | 33.3286 | 33.2643 | 33.0541 | 33.0367 | 33.0296 | 33.05 | 33.0214 | 32.9847 | 32.9214 | 32.8786 | 32.7949 | 32.6898 | 32.5949 | 32.4704 | 32.3898 | 32.1173 | 31.8755 | 31.752
|  | ST FERGUS GAS TERM | FB |  |  |  |  | 34.8612 | 34.85 | 34.8224 | 34.7908 | 34.7582 | 34.7112 | 34.6908 | 34.6337 | 34.5714 | 34.548 | 34.3245 | 34.099 | 34.0316 | 33.8347 | 33.8276 | 33.8102 | 33.7908 | 33.7653 | 33.7306 | 33.7071 | 33.6612 | 33.6112 | 33.5949 | 33.4184 | 33.2378 | 33.1786 | 33.0755 | 33.0704 | 33.052 | 33.0306 | 33.0184 | 32.9888 | 32.9633 | 32.9235 | 32.8888 | 32.8684 | 32.7694 | 32.5898 | 32.5602
| PERSLEY | ST MACHAR | MINIMUM HEADROOM | NJ 93584 08102 | NO | NO | 0.184 | 15.4224 | 15.4694 | 15.4765 | 15.4378 | 15.3449 | 14.9704 | 14.7102 | 14.3163 | 13.7735 | 13.2184 | 10.7347 | 8.5398 | 7.3469 | 16.2004 | 16.1463 | 16.0137 | 15.7535 | 15.53 | 15.2004 | 14.9902 | 14.6167 | 14.1167 | 13.6678 | 12.3963 | 11.381 | 10.3178 | 15.9106 | 15.9178 | 15.8871 | 15.7688 | 15.5759 | 15.2351 | 15.0096 | 14.6473 | 14.1535 | 13.6412 | 11.4422 | 9.5463 | 8.5106
|  | ST MACHAR | EE |  |  |  |  | 15.4224 | 15.4694 | 15.4765 | 15.4378 | 15.3449 | 14.9704 | 14.7102 | 14.3163 | 13.7735 | 13.2184 | 10.7347 | 8.5398 | 7.3469 | 16.2004 | 16.1463 | 16.0137 | 15.7535 | 15.53 | 15.2004 | 14.9902 | 14.6616 | 14.1769 | 13.6678 | 12.3963 | 11.381 | 10.7657 | 15.9106 | 15.9178 | 15.8871 | 15.7688 | 15.5759 | 15.2351 | 15.0096 | 14.6473 | 14.1535 | 13.6412 | 11.4422 | 9.5463 | 8.5106
|  | ST MACHAR | HT |  |  |  |  | 15.4306 | 15.4867 | 15.5031 | 15.4602 | 15.3867 | 15.0398 | 14.8 | 14.3776 | 13.8357 | 13.2673 | 11.0306 | 9.1194 | 8.4398 | 16.2014 | 16.1473 | 16.0147 | 15.7596 | 15.5341 | 15.2341 | 15.0504 | 14.6912 | 14.2076 | 13.6892 | 12.5412 | 11.8616 | 11.731 | 15.9249 | 15.9494 | 15.9382 | 15.8106 | 15.6014 | 15.2984 | 15.0922 | 14.7055 | 14.2106 | 13.6871 | 11.68 | 10.031 | 9.4667
|  | ST MACHAR | HE |  |  |  |  | 15.4235 | 15.4724 | 15.4806 | 15.4408 | 15.3459 | 15.002 | 14.7806 | 14.3622 | 13.8337 | 13.6684 | 11.6867 | 9.8827 | 9.0102 | 16.2035 | 16.1484 | 16.0188 | 15.7606 | 15.5361 | 15.2004 | 15.0045 | 14.6167 | 14.1167 | 13.98 | 12.7616 | 11.8065 | 11.4157 | 15.9127 | 15.9188 | 15.8933 | 15.7769 | 15.5851 | 15.2596 | 15.0647 | 14.6749 | 14.1882 | 14.0218 | 12.2473 | 10.678 | 9.9402
|  | ST MACHAR | FB |  |  |  |  | 15.4796 | 15.5755 | 15.6388 | 15.6643 | 15.6714 | 15.6684 | 15.6163 | 15.5255 | 15.4235 | 15.3296 | 14.049 | 12.0429 | 9.95 | 16.2453 | 16.279 | 16.2351 | 16.2259 | 16.1229 | 16.0749 | 15.9024 | 15.6933 | 15.482 | 15.3943 | 14.1586 | 12.3576 | 10.3178 | 15.9718 | 16.0422 | 16.0769 | 16.0749 | 16.0484 | 16.0443 | 15.9841 | 15.8422 | 15.6576 | 15.5708 | 14.3718 | 12.1137 | 10.6178
| THURSO | ST MARYS | MINIMUM HEADROOM | HY 46965 01396 | YES | NO | 0 | -3.0551 | -3.2469 | -3.3051 | -3.3071 | -3.5439 | -3.9367 | -4.2612 | -4.6908 | -5.1827 | -5.4071 | -5.9959 | -6.6429 | -6.9143 | -3.3888 | -3.4724 | -3.5408 | -3.5418 | -3.6878 | -4.0173 | -4.2459 | -4.5327 | -4.8163 | -5.0194 | -5.6082 | -6.0031 | -6.0694 | -3.2408 | -3.4255 | -3.4929 | -3.5092 | -3.7653 | -4.1347 | -4.4255 | -4.7959 | -5.2031 | -5.4286 | -6.0031 | -6.4939 | -6.6694
|  | ST MARYS | EE |  |  |  |  | -3.0531 | -3.2276 | -3.2367 | -3.2745 | -3.5337 | -3.9204 | -4.1776 | -4.5765 | -4.9827 | -5.2204 | -5.9959 | -6.6429 | -6.6531 | -3.3878 | -3.4551 | -3.4602 | -3.4745 | -3.6847 | -4.0092 | -4.2051 | -4.4929 | -4.749 | -4.95 | -5.5541 | -5.9796 | -5.8694 | -3.2388 | -3.4071 | -3.4337 | -3.502 | -3.7582 | -4.1214 | -4.3694 | -4.7265 | -5.0724 | -5.3061 | -5.9857 | -6.4939 | -6.4163
|  | ST MARYS | HT |  |  |  |  | -3.0551 | -3.2286 | -3.2378 | -3.2806 | -3.5439 | -3.9306 | -4.2612 | -4.6908 | -5.1827 | -5.4071 | -5.9755 | -6.6031 | -6.9143 | -3.3888 | -3.4561 | -3.4643 | -3.4755 | -3.6878 | -4.0153 | -4.2398 | -4.5327 | -4.8163 | -5.0194 | -5.6082 | -6.0031 | -6.0694 | -3.2408 | -3.4082 | -3.4347 | -3.5071 | -3.7622 | -4.1286 | -4.4255 | -4.7959 | -5.2031 | -5.4286 | -6.0031 | -6.4929 | -6.6694
|  | ST MARYS | HE |  |  |  |  | -3.0551 | -3.2469 | -3.2367 | -3.2796 | -3.5439 | -3.9367 | -4.2286 | -4.5704 | -4.9918 | -5.1827 | -5.8643 | -6.0724 | -6.2153 | -3.3878 | -3.4724 | -3.4622 | -3.4755 | -3.6857 | -4.0173 | -4.2459 | -4.4816 | -4.7663 | -4.9112 | -5.4469 | -5.4378 | -5.4571 | -3.2408 | -3.4255 | -3.4347 | -3.5082 | -3.7653 | -4.1347 | -4.4143 | -4.7173 | -5.0837 | -5.2684 | -5.8694 | -5.9643 | -6.0102
|  | ST MARYS | FB |  |  |  |  | -2.9939 | -2.9857 | -3.3051 | -3.3071 | -3.3398 | -3.3714 | -3.4827 | -3.5184 | -3.5786 | -3.7143 | -4.3204 | -4.7908 | -5.1673 | -3.3551 | -3.3388 | -3.5408 | -3.5418 | -3.5714 | -3.6082 | -3.7204 | -3.7571 | -3.8255 | -3.9653 | -4.4816 | -4.9633 | -5.4316 | -3.201 | -3.1857 | -3.4929 | -3.5092 | -3.5633 | -3.6041 | -3.7184 | -3.7704 | -3.848 | -3.9857 | -4.551 | -5.0796 | -5.3276
| WILLOWDALE | ST NICHOLAS | MINIMUM HEADROOM | NJ 93737 06782 | NO | NO | 0.579 | 10.2597 | 10.125 | 10.0057 | 9.8567 | 9.6842 | 9.323 | 9.1006 | 8.8577 | 8.6271 | 8.5383 | 7.0118 | 5.9526 | 5.5312 | 12.4026 | 12.3046 | 12.2404 | 12.1567 | 11.9567 | 11.6628 | 11.4801 | 11.2148 | 10.9699 | 10.8781 | 9.5822 | 8.7138 | 6.6393 | 11.3822 | 11.2434 | 11.1271 | 10.9801 | 10.8934 | 10.5628 | 10.3393 | 10.0679 | 9.821 | 9.7261 | 8.2118 | 7.2567 | 6.9026
|  | ST NICHOLAS | EE |  |  |  |  | 10.2597 | 10.2536 | 10.1261 | 9.9638 | 9.8261 | 9.3455 | 9.1006 | 8.8577 | 8.6271 | 8.5383 | 7.0118 | 5.9526 | 5.5312 | 12.4026 | 12.374 | 12.3087 | 12.2199 | 12.0363 | 11.6985 | 11.4801 | 11.2148 | 10.9699 | 10.8781 | 9.5822 | 8.7301 | 8.1322 | 11.3822 | 11.3587 | 11.2312 | 11.072 | 10.9863 | 10.5842 | 10.3393 | 10.0679 | 9.821 | 9.7261 | 8.2118 | 7.2567 | 6.9026
|  | ST NICHOLAS | HT |  |  |  |  | 10.2628 | 10.125 | 10.0057 | 9.8567 | 9.6842 | 9.323 | 9.1679 | 8.9455 | 8.7006 | 8.6097 | 7.1822 | 6.3312 | 6.0342 | 12.4046 | 12.3046 | 12.2404 | 12.1567 | 11.9567 | 11.6628 | 11.4924 | 11.2465 | 10.9863 | 10.8965 | 9.8628 | 9.4322 | 9.1955 | 11.3893 | 11.2434 | 11.1271 | 10.9801 | 10.8934 | 10.5628 | 10.3893 | 10.1414 | 9.8832 | 9.7893 | 8.4108 | 7.6699 | 7.422
|  | ST NICHOLAS | HE |  |  |  |  | 10.2638 | 10.2618 | 10.2495 | 10.1944 | 10.1301 | 9.8801 | 9.672 | 9.4199 | 9.1373 | 9.1067 | 7.9822 | 7.1699 | 6.6842 | 12.4036 | 12.371 | 12.3557 | 12.3118 | 12.1648 | 11.9118 | 11.6985 | 11.4424 | 11.1597 | 11.1393 | 10.1495 | 9.3985 | 8.7465 | 11.3842 | 11.3516 | 11.3148 | 11.2485 | 11.1608 | 10.9771 | 10.7557 | 10.4944 | 10.2046 | 10.1791 | 9.1036 | 8.3781 | 7.9689
|  | ST NICHOLAS | FB |  |  |  |  | 10.2914 | 10.2934 | 10.3424 | 10.325 | 10.3332 | 10.2771 | 10.2363 | 10.1863 | 10.0975 | 9.9546 | 9.3444 | 8.0557 | 6.9659 | 12.4108 | 12.3699 | 12.3822 | 12.3475 | 12.271 | 12.1587 | 12.0404 | 11.8669 | 11.6842 | 11.471 | 10.5424 | 8.7138 | 6.6393 | 11.4199 | 11.4026 | 11.4373 | 11.3975 | 11.3801 | 11.321 | 11.2699 | 11.2108 | 11.1495 | 11.0557 | 10.3985 | 8.822 | 8.0689
| ARDMORE / HARRIS GRID | STOCKINISH | MINIMUM HEADROOM | NG 13447 94222 | YES | YES | 0.227 | 0.1141 | 0.11308 | 0.10389 | 0.085527 | 0.055935 | 0.034506 | -0.014473 | -0.073657 | -0.11345 | -0.15223 | -0.27774 | -0.37774 | -0.49202 | 0.22838 | 0.22736 | 0.22226 | 0.22022 | 0.21206 | 0.19879 | 0.17736 | 0.15185 | 0.13553 | 0.11104 | 0.050833 | 0.058996 | 0.040629 | 0.19981 | 0.18859 | 0.16716 | 0.13961 | 0.10083 | 0.07022 | 0.028384 | -0.025698 | -0.036922 | -0.077739 | -0.20019 | -0.22264 | -0.28182
|  | STOCKINISH | EE |  |  |  |  | 0.11818 | 0.11512 | 0.10593 | 0.091649 | 0.063078 | 0.035527 | -0.011412 | -0.068555 | -0.11039 | -0.14917 | -0.27774 | -0.37774 | -0.49202 | 0.23144 | 0.2294 | 0.22328 | 0.2243 | 0.21308 | 0.19879 | 0.17736 | 0.15185 | 0.13655 | 0.11104 | 0.050833 | 0.061037 | 0.040629 | 0.19981 | 0.18961 | 0.16716 | 0.14471 | 0.10287 | 0.07022 | 0.028384 | -0.025698 | -0.036922 | -0.077739 | -0.20019 | -0.22264 | -0.28182
|  | STOCKINISH | HT |  |  |  |  | 0.1141 | 0.11512 | 0.10389 | 0.091649 | 0.064098 | 0.041649 | -0.0052898 | -0.062433 | -0.10121 | -0.13692 | -0.21039 | -0.3359 | -0.47774 | 0.22838 | 0.2294 | 0.22226 | 0.2243 | 0.21308 | 0.19981 | 0.1794 | 0.15185 | 0.13757 | 0.11308 | 0.071241 | 0.060016 | 0.066139 | 0.19981 | 0.18961 | 0.16716 | 0.14471 | 0.10287 | 0.073282 | 0.032465 | -0.021616 | -0.03182 | -0.070596 | -0.15835 | -0.21856 | -0.26345
|  | STOCKINISH | HE |  |  |  |  | 0.11614 | 0.11308 | 0.10593 | 0.085527 | 0.055935 | 0.034506 | -0.014473 | -0.073657 | -0.11345 | -0.15223 | -0.241 | -0.35427 | -0.45427 | 0.23144 | 0.22736 | 0.22226 | 0.22022 | 0.21206 | 0.20083 | 0.17736 | 0.15185 | 0.13553 | 0.11104 | 0.054914 | 0.058996 | 0.042669 | 0.19981 | 0.18859 | 0.16818 | 0.13961 | 0.10083 | 0.072261 | 0.030424 | -0.025698 | -0.035902 | -0.075698 | -0.1808 | -0.21447 | -0.24917
|  | STOCKINISH | FB |  |  |  |  | 0.13757 | 0.14675 | 0.15287 | 0.15798 | 0.15185 | 0.14675 | 0.14165 | 0.13144 | 0.12736 | 0.12022 | 0.041649 | -0.035902 | -0.038963 | 0.24879 | 0.25491 | 0.25491 | 0.25696 | 0.25287 | 0.24879 | 0.24165 | 0.23042 | 0.22532 | 0.21818 | 0.16104 | 0.07022 | 0.051853 | 0.2141 | 0.21206 | 0.20696 | 0.19675 | 0.17328 | 0.16512 | 0.15287 | 0.13247 | 0.12532 | 0.11206 | 0.02022 | -0.10631 | -0.092024
| PORT ANN | STONEFIELD | MINIMUM HEADROOM | NR 86244 73400 | YES | YES | 0 | 0.35027 | 0.34007 | 0.34007 | 0.33803 | 0.33803 | 0.33292 | 0.32578 | 0.32374 | 0.26456 | 0.13088 | -0.1283 | -0.1334 | -0.1334 | 0.32906 | 0.31886 | 0.31886 | 0.31682 | 0.31478 | 0.31376 | 0.30866 | 0.30559 | 0.24743 | 0.10049 | -0.18318 | -0.18624 | -0.18624 | 0.3412 | 0.32895 | 0.32895 | 0.32691 | 0.32691 | 0.32079 | 0.31467 | 0.31263 | 0.26059 | 0.12691 | -0.13329 | -0.13839 | -0.13737
|  | STONEFIELD | EE |  |  |  |  | 0.35027 | 0.34007 | 0.34007 | 0.33803 | 0.33803 | 0.33292 | 0.3268 | 0.32578 | 0.3217 | 0.3217 | -0.1283 | -0.13238 | -0.13238 | 0.32906 | 0.31886 | 0.31886 | 0.31682 | 0.31478 | 0.31376 | 0.30866 | 0.30662 | 0.30253 | 0.30253 | -0.18318 | -0.18624 | -0.18318 | 0.3412 | 0.32895 | 0.32895 | 0.32691 | 0.32691 | 0.32079 | 0.31467 | 0.31467 | 0.31161 | 0.31059 | -0.13329 | -0.13839 | -0.13431
|  | STONEFIELD | HT |  |  |  |  | 0.35027 | 0.34007 | 0.34007 | 0.33803 | 0.33803 | 0.33394 | 0.3268 | 0.32476 | 0.26456 | 0.13088 | -0.12728 | -0.1334 | -0.1334 | 0.32906 | 0.31886 | 0.31886 | 0.31682 | 0.31478 | 0.31478 | 0.30866 | 0.30559 | 0.24743 | 0.10049 | -0.18318 | -0.18624 | -0.18522 | 0.3412 | 0.32895 | 0.32895 | 0.32691 | 0.32691 | 0.32181 | 0.31467 | 0.31365 | 0.26059 | 0.12691 | -0.13227 | -0.13737 | -0.13737
|  | STONEFIELD | HE |  |  |  |  | 0.35027 | 0.34007 | 0.34007 | 0.33803 | 0.33803 | 0.33292 | 0.32578 | 0.32374 | 0.32272 | 0.3217 | -0.12626 | -0.13034 | -0.13136 | 0.32906 | 0.31886 | 0.31886 | 0.31682 | 0.31478 | 0.31376 | 0.30866 | 0.30559 | 0.30355 | 0.30253 | -0.18216 | -0.18522 | -0.1842 | 0.3412 | 0.32895 | 0.32895 | 0.32691 | 0.32691 | 0.32079 | 0.31467 | 0.31263 | 0.31161 | 0.31161 | -0.13227 | -0.13737 | -0.13533
|  | STONEFIELD | FB |  |  |  |  | 0.35027 | 0.34211 | 0.34313 | 0.34211 | 0.34211 | 0.33905 | 0.33905 | 0.34007 | 0.33905 | 0.33497 | 0.15129 | -0.11606 | -0.12218 | 0.32906 | 0.3209 | 0.32192 | 0.3209 | 0.31784 | 0.3158 | 0.3158 | 0.3158 | 0.31478 | 0.3107 | 0.11274 | -0.18216 | -0.18624 | 0.3412 | 0.33099 | 0.33201 | 0.33304 | 0.32997 | 0.32691 | 0.32691 | 0.32793 | 0.32691 | 0.32181 | 0.14324 | -0.12717 | -0.13023
| FIDDES | STONEHAVEN | MINIMUM HEADROOM | NO 85903 85641 | NO | NO | 6.046 | 2.9775 | 2.154 | 1.204 | 0.22848 | -0.011314 | -0.73989 | -1.5368 | -2.4358 | -3.7195 | -4.3797 | -6.9552 | -9.9674 | -12.4368 | 5.3877 | 4.6111 | 3.7591 | 2.8724 | 2.6683 | 2.403 | 1.9479 | 1.3713 | 0.29175 | -0.12764 | -2.0011 | -3.8725 | -5.6685 | 4.4009 | 3.6632 | 2.8417 | 2.0132 | 1.802 | 1.2509 | 0.5744 | -0.31131 | -1.6909 | -2.3358 | -4.8613 | -7.5695 | -9.7236
|  | STONEHAVEN | EE |  |  |  |  | 3.1428 | 2.154 | 1.204 | 0.22848 | -0.0082531 | -0.67764 | -1.4501 | -2.2266 | -3.1144 | -3.7327 | -6.4338 | -9.6919 | -11.6195 | 5.553 | 4.6111 | 3.7622 | 2.8764 | 2.6815 | 2.4152 | 1.9979 | 1.5203 | 0.88154 | 0.55399 | -0.95111 | -2.896 | -3.9032 | 4.5622 | 3.6632 | 2.8417 | 2.0132 | 1.806 | 1.2938 | 0.64787 | -0.11131 | -1.0164 | -1.6185 | -4.0042 | -6.8827 | -8.446
|  | STONEHAVEN | HT |  |  |  |  | 3.0417 | 2.1724 | 1.2244 | 0.26113 | -0.0041714 | -0.59499 | -1.3623 | -2.1368 | -3.0929 | -3.7001 | -6.4736 | -9.8838 | -12.4368 | 5.453 | 4.6397 | 3.7591 | 2.8724 | 2.6683 | 2.4417 | 1.9479 | 1.4397 | 0.68664 | 0.34481 | -1.2889 | -3.1899 | -4.6634 | 4.4632 | 3.6856 | 2.854 | 2.0326 | 1.805 | 1.355 | 0.65807 | -0.11131 | -1.1083 | -1.6807 | -4.1766 | -7.2113 | -9.5021
|  | STONEHAVEN | HE |  |  |  |  | 2.9775 | 2.1785 | 1.2601 | 0.29889 | -0.011314 | -0.73989 | -1.5368 | -2.4358 | -3.7195 | -4.3797 | -6.9552 | -9.9674 | -12.2154 | 5.3877 | 4.6183 | 3.7754 | 2.8907 | 2.6805 | 2.403 | 1.9683 | 1.3713 | 0.29175 | -0.12764 | -2.0011 | -3.8725 | -5.6685 | 4.4009 | 3.6775 | 2.8775 | 2.056 | 1.802 | 1.2509 | 0.5744 | -0.31131 | -1.6909 | -2.3358 | -4.8613 | -7.5695 | -9.7236
|  | STONEHAVEN | FB |  |  |  |  | 3.6652 | 3.055 | 2.256 | 1.5326 | 1.0581 | 0.75909 | 0.35705 | 0.056033 | -0.30315 | -0.51131 | -1.5021 | -3.1215 | -4.0542 | 5.9917 | 5.4122 | 4.652 | 4.004 | 3.4979 | 3.1928 | 2.8162 | 2.4938 | 2.0958 | 1.8968 | 1.1387 | -0.46846 | -1.7378 | 5.0489 | 4.4775 | 3.7785 | 3.1407 | 2.7132 | 2.4642 | 2.0785 | 1.7744 | 1.3734 | 1.156 | 0.16624 | -1.7021 | -2.3195
| STRICHEN | STONEYHILL | MINIMUM HEADROOM | NK 6773 4109 | YES | YES | 0 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612
|  | STONEYHILL | EE |  |  |  |  | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612
|  | STONEYHILL | HT |  |  |  |  | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612
|  | STONEYHILL | HE |  |  |  |  | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612
|  | STONEYHILL | FB |  |  |  |  | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -1.1459 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.43673 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612 | -0.95612
| PERSLEY | STONEYWOOD T1&T2 | MINIMUM HEADROOM | NJ 89285 11082 | NO | NO | 0.458 | 13.551 | 13.2143 | 12.7133 | 12.399 | 11.3551 | 10.9867 | 10.6265 | 10.1337 | 9.648 | 9.3602 | 6.9163 | 5.7173 | 5.148 | 16.5239 | 16.3035 | 16.0137 | 15.8831 | 15.4861 | 15.3178 | 15.1137 | 14.8545 | 14.6402 | 14.3586 | 12.9596 | 12.5198 | 12.2698 | 16.2953 | 16.0004 | 15.5922 | 15.3524 | 14.6882 | 14.4371 | 14.1055 | 13.6494 | 13.2382 | 12.9239 | 10.8545 | 9.8933 | 9.4086
|  | STONEYWOOD T1&T2 | EE |  |  |  |  | 13.5673 | 13.2143 | 12.7133 | 12.4 | 11.4469 | 11.002 | 10.7755 | 10.4061 | 10.0918 | 9.8245 | 7.6214 | 5.7173 | 5.148 | 16.5453 | 16.3035 | 16.0137 | 15.8861 | 15.5402 | 15.3249 | 15.1912 | 14.982 | 14.8392 | 14.5718 | 13.2871 | 12.5198 | 12.2698 | 16.3076 | 16.0004 | 15.5922 | 15.3524 | 14.7351 | 14.4484 | 14.2208 | 13.8494 | 13.5606 | 13.2616 | 11.3871 | 9.8933 | 9.4086
|  | STONEYWOOD T1&T2 | HT |  |  |  |  | 13.5592 | 13.2378 | 12.7541 | 12.4378 | 11.3551 | 11.0306 | 10.6265 | 10.1337 | 9.648 | 9.3602 | 6.9163 | 5.8347 | 5.4265 | 16.5341 | 16.3065 | 16.0188 | 15.8892 | 15.4861 | 15.3178 | 15.1137 | 14.8545 | 14.6402 | 14.3586 | 12.9596 | 12.5729 | 12.4698 | 16.3035 | 16.028 | 15.6412 | 15.3912 | 14.6882 | 14.4586 | 14.1055 | 13.6494 | 13.2382 | 12.9239 | 10.8545 | 10.0045 | 9.6912
|  | STONEYWOOD T1&T2 | HE |  |  |  |  | 13.551 | 13.2214 | 12.7153 | 12.399 | 11.45 | 10.9867 | 10.7622 | 10.4235 | 10.1214 | 9.9276 | 8.2776 | 6.6429 | 6.1816 | 16.5239 | 16.3035 | 16.0137 | 15.8831 | 15.5371 | 15.3178 | 15.1769 | 14.9851 | 14.8453 | 14.6382 | 13.678 | 13.0453 | 12.8494 | 16.2953 | 16.0137 | 15.6076 | 15.3586 | 14.7382 | 14.4371 | 14.2024 | 13.8657 | 13.5892 | 13.3576 | 11.9545 | 10.7178 | 10.331
|  | STONEYWOOD T1&T2 | FB |  |  |  |  | 13.6571 | 13.3582 | 12.9857 | 12.7082 | 12.0765 | 11.7735 | 11.7194 | 11.6663 | 11.4357 | 11.3643 | 10.6878 | 8.151 | 7.2959 | 16.6218 | 16.3831 | 16.1739 | 16.0412 | 15.73 | 15.6055 | 15.5718 | 15.5576 | 15.4494 | 15.4045 | 15.0371 | 13.7249 | 13.1035 | 16.3973 | 16.1382 | 15.8606 | 15.6484 | 15.1637 | 14.9596 | 14.9086 | 14.879 | 14.7484 | 14.6871 | 14.032 | 11.6933 | 11.1147
| DYCE | STONEYWOOD T3 | MINIMUM HEADROOM | NJ 89285 11082 | NO | YES | 0 | 19.4398 | 19.4224 | 19.4 | 19.3765 | 19.35 | 19.2194 | 19.152 | 19.1092 | 19.0357 | 18.9724 | 18.7316 | 18.5541 | 18.5133 | 19.0606 | 19.0473 | 19.0371 | 19.0208 | 19.0065 | 18.9137 | 18.8667 | 18.8371 | 18.7922 | 18.7504 | 18.6382 | 18.5861 | 18.579 | 19.3524 | 19.3392 | 19.3198 | 19.3035 | 19.2851 | 19.1973 | 19.1473 | 19.1167 | 19.0514 | 18.9963 | 18.7892 | 18.6361 | 18.6106
|  | STONEYWOOD T3 | EE |  |  |  |  | 19.4408 | 19.4235 | 19.401 | 19.3786 | 19.3561 | 19.2235 | 19.1724 | 19.1102 | 19.0398 | 18.9724 | 18.7765 | 18.6163 | 18.5571 | 19.0606 | 19.0484 | 19.0371 | 19.0218 | 19.0076 | 18.9147 | 18.8841 | 18.8443 | 18.7943 | 18.7504 | 18.6494 | 18.5922 | 18.579 | 19.3524 | 19.3402 | 19.3218 | 19.3045 | 19.2882 | 19.1994 | 19.1627 | 19.1178 | 19.0535 | 18.9963 | 18.8106 | 18.682 | 18.6382
|  | STONEYWOOD T3 | HT |  |  |  |  | 19.4418 | 19.4276 | 19.4071 | 19.3847 | 19.3633 | 19.2327 | 19.152 | 19.1092 | 19.0357 | 19 | 18.7316 | 18.5541 | 18.5133 | 19.0606 | 19.0484 | 19.0371 | 19.0218 | 19.0076 | 18.9198 | 18.8667 | 18.8422 | 18.7922 | 18.7596 | 18.6382 | 18.5861 | 18.5984 | 19.3535 | 19.3422 | 19.3249 | 19.3086 | 19.2933 | 19.2045 | 19.1473 | 19.1178 | 19.0514 | 19.0086 | 18.7892 | 18.6361 | 18.6106
|  | STONEYWOOD T3 | HE |  |  |  |  | 19.4398 | 19.4224 | 19.4 | 19.3765 | 19.35 | 19.2194 | 19.1704 | 19.1102 | 19.0551 | 19.002 | 18.8327 | 18.7612 | 18.7184 | 19.0606 | 19.0473 | 19.0371 | 19.0208 | 19.0065 | 18.9137 | 18.88 | 18.8371 | 18.7963 | 18.7606 | 18.6739 | 18.6667 | 18.6678 | 19.3524 | 19.3392 | 19.3198 | 19.3035 | 19.2851 | 19.1973 | 19.1596 | 19.1167 | 19.0637 | 19.0178 | 18.8637 | 18.828 | 18.7953
|  | STONEYWOOD T3 | FB |  |  |  |  | 19.452 | 19.4429 | 19.4347 | 19.4071 | 19.3949 | 19.3806 | 19.3684 | 19.349 | 19.3306 | 19.3102 | 19.2235 | 19.1316 | 18.9122 | 19.0708 | 19.0627 | 19.0565 | 19.0382 | 19.0351 | 19.0249 | 19.0178 | 19.0024 | 18.9912 | 18.9739 | 18.9127 | 18.8524 | 18.7188 | 19.3637 | 19.3545 | 19.3473 | 19.3269 | 19.3178 | 19.3076 | 19.2994 | 19.2831 | 19.2718 | 19.2535 | 19.1902 | 19.1137 | 18.9392
| CLACHAN | STRACHUR | MINIMUM HEADROOM | NN 08672 01180 | YES | YES | 0.126 | 0.22755 | 0.21531 | 0.20714 | 0.18571 | 0.017347 | -0.16837 | -0.19898 | -0.24286 | -0.27755 | -0.37551 | -0.53571 | -0.56429 | -0.57857 | 0.59082 | 0.57959 | 0.57959 | 0.57653 | 0.44694 | 0.25612 | 0.24184 | 0.1949 | 0.17245 | 0.069388 | -0.082653 | -0.068367 | -0.037755 | 0.42551 | 0.4102 | 0.40816 | 0.39796 | 0.2398 | 0.047959 | 0.017347 | -0.040816 | -0.073469 | -0.17245 | -0.32857 | -0.31939 | -0.31939
|  | STRACHUR | EE |  |  |  |  | 0.22857 | 0.21735 | 0.20714 | 0.1898 | 0.16633 | -0.022449 | -0.044898 | -0.077551 | -0.097959 | -0.17857 | -0.40102 | -0.47755 | -0.5051 | 0.59286 | 0.58061 | 0.58061 | 0.57755 | 0.57551 | 0.41735 | 0.40918 | 0.39082 | 0.37041 | 0.28878 | 0.083673 | 0.028571 | 0.026531 | 0.42755 | 0.41224 | 0.40816 | 0.40204 | 0.39592 | 0.20204 | 0.18469 | 0.15714 | 0.12551 | 0.041837 | -0.16122 | -0.23163 | -0.25
|  | STRACHUR | HT |  |  |  |  | 0.22755 | 0.21735 | 0.20714 | 0.18571 | 0.16327 | -0.16837 | -0.19898 | -0.24286 | -0.27755 | -0.37551 | -0.53571 | -0.56429 | -0.57857 | 0.59082 | 0.58061 | 0.57959 | 0.57653 | 0.57449 | 0.25612 | 0.24184 | 0.1949 | 0.17245 | 0.069388 | -0.082653 | -0.068367 | -0.037755 | 0.42551 | 0.41122 | 0.40816 | 0.39796 | 0.39184 | 0.047959 | 0.017347 | -0.040816 | -0.073469 | -0.17245 | -0.32857 | -0.31939 | -0.31939
|  | STRACHUR | HE |  |  |  |  | 0.22959 | 0.21531 | 0.20714 | 0.18878 | 0.017347 | -0.012245 | -0.052041 | -0.077551 | -0.11633 | -0.12449 | -0.19082 | -0.22959 | -0.10204 | 0.59286 | 0.57959 | 0.58061 | 0.57755 | 0.44694 | 0.42755 | 0.40408 | 0.38163 | 0.35714 | 0.35408 | 0.3102 | 0.30408 | 0.43061 | 0.42755 | 0.4102 | 0.4102 | 0.40102 | 0.2398 | 0.21327 | 0.17653 | 0.14082 | 0.10102 | 0.096939 | 0.064286 | 0.034694 | 0.17755
|  | STRACHUR | FB |  |  |  |  | 0.24184 | 0.24184 | 0.23163 | 0.22449 | 0.21633 | 0.2051 | 0.19796 | 0.17857 | 0.17143 | 0.15612 | 0.090816 | 0.015306 | -0.005102 | 0.60612 | 0.60408 | 0.59898 | 0.60102 | 0.60306 | 0.59286 | 0.58878 | 0.57041 | 0.56531 | 0.55 | 0.49898 | 0.40714 | 0.35612 | 0.44286 | 0.44388 | 0.43265 | 0.43571 | 0.43673 | 0.42857 | 0.42245 | 0.40408 | 0.39694 | 0.38469 | 0.32347 | 0.22959 | 0.22041
| TARLAND | STRATHDON | MINIMUM HEADROOM | NJ 37343 11904 | YES | NO | 0.169 | -0.049359 | -0.056502 | -0.062624 | -0.095278 | -0.11977 | -0.16262 | -0.19834 | -0.24222 | -0.29426 | -0.33813 | -0.43813 | -0.55344 | -0.66875 | 0.37003 | 0.36187 | 0.35574 | 0.34044 | 0.33227 | 0.31289 | 0.28125 | 0.25778 | 0.22921 | 0.1986 | 0.14554 | 0.13738 | 0.11595 | 0.29044 | 0.28329 | 0.27819 | 0.25472 | 0.24044 | 0.20574 | 0.16391 | 0.12513 | 0.085335 | 0.045539 | -0.006502 | -0.073849 | -0.14222
|  | STRATHDON | EE |  |  |  |  | -0.049359 | -0.056502 | -0.061604 | -0.085073 | -0.10446 | -0.14324 | -0.19834 | -0.21773 | -0.26569 | -0.31058 | -0.43813 | -0.55344 | -0.6514 | 0.37003 | 0.36187 | 0.35574 | 0.34248 | 0.33329 | 0.31493 | 0.28125 | 0.25982 | 0.23023 | 0.20064 | 0.14758 | 0.14452 | 0.14248 | 0.29044 | 0.28329 | 0.27819 | 0.26084 | 0.25064 | 0.21901 | 0.17615 | 0.14656 | 0.10472 | 0.066967 | -0.006502 | -0.073849 | -0.12487
|  | STRATHDON | HT |  |  |  |  | -0.049359 | -0.054461 | -0.060584 | -0.083033 | -0.098339 | -0.13813 | -0.18813 | -0.20548 | -0.25038 | -0.2963 | -0.39426 | -0.52997 | -0.66875 | 0.37105 | 0.36187 | 0.35574 | 0.34146 | 0.33431 | 0.31493 | 0.28227 | 0.26187 | 0.23227 | 0.20064 | 0.14554 | 0.14554 | 0.15166 | 0.29044 | 0.28431 | 0.28023 | 0.26289 | 0.25574 | 0.22411 | 0.18329 | 0.1537 | 0.11697 | 0.079212 | 0.016967 | -0.062624 | -0.13609
|  | STRATHDON | HE |  |  |  |  | -0.049359 | -0.056502 | -0.062624 | -0.095278 | -0.11977 | -0.16262 | -0.19834 | -0.24222 | -0.29426 | -0.33813 | -0.41262 | -0.53916 | -0.64528 | 0.37105 | 0.36187 | 0.35574 | 0.34044 | 0.33227 | 0.31289 | 0.28125 | 0.25778 | 0.22921 | 0.1986 | 0.15166 | 0.13738 | 0.11595 | 0.29044 | 0.28329 | 0.27819 | 0.25472 | 0.24044 | 0.20574 | 0.16391 | 0.12513 | 0.085335 | 0.045539 | 0.0098245 | -0.071808 | -0.14222
|  | STRATHDON | FB |  |  |  |  | -0.020788 | -0.022829 | -0.024869 | -0.027931 | -0.032012 | -0.043237 | -0.060584 | -0.071808 | -0.083033 | -0.10344 | -0.20446 | -0.28813 | -0.28507 | 0.39452 | 0.38942 | 0.38431 | 0.37717 | 0.37717 | 0.36901 | 0.35064 | 0.3435 | 0.33125 | 0.31391 | 0.24962 | 0.16595 | 0.14962 | 0.31697 | 0.31187 | 0.3088 | 0.30982 | 0.31084 | 0.30166 | 0.28533 | 0.27717 | 0.26901 | 0.25064 | 0.17309 | 0.094518 | 0.083294
| STRICHEN | STRICHEN | MINIMUM HEADROOM | NJ 95900 55137 | NO | YES | 0.494 | 8.0971 | 7.7471 | 7.3829 | 6.9982 | 6.9308 | 6.6737 | 6.3931 | 6.1492 | 5.9522 | 5.7492 | 5.0951 | 4.5614 | 4.1094 | 9.5165 | 9.1012 | 8.6829 | 8.2573 | 8.2298 | 8.1084 | 7.9971 | 7.9216 | 7.8543 | 7.7329 | 7.2471 | 7.2614 | 7.3451 | 8.7686 | 8.3971 | 8.0124 | 7.5961 | 7.5624 | 7.3971 | 7.2145 | 7.0563 | 6.9135 | 6.7737 | 6.3482 | 6.0502 | 5.6869
|  | STRICHEN | EE |  |  |  |  | 8.0971 | 7.7471 | 7.3829 | 7.0063 | 6.9512 | 6.691 | 6.5084 | 6.2196 | 6.0931 | 5.9135 | 5.0951 | 4.5614 | 4.1808 | 9.5176 | 9.1012 | 8.6849 | 8.2584 | 8.2318 | 8.1237 | 8.0502 | 7.9441 | 7.9135 | 7.8033 | 7.3788 | 7.3961 | 7.442 | 8.7686 | 8.3971 | 8.0124 | 7.6022 | 7.5778 | 7.4084 | 7.2818 | 7.1002 | 6.9971 | 6.8665 | 6.3482 | 6.0502 | 5.7492
|  | STRICHEN | HT |  |  |  |  | 8.0971 | 7.7492 | 7.391 | 7.0155 | 6.9614 | 6.6737 | 6.3931 | 6.1492 | 5.9522 | 5.7492 | 5.2237 | 4.6339 | 4.1094 | 9.5165 | 9.1022 | 8.6829 | 8.2584 | 8.2308 | 8.1084 | 7.9971 | 7.9216 | 7.8543 | 7.7329 | 7.2471 | 7.2614 | 7.3451 | 8.7696 | 8.3982 | 8.0176 | 7.6063 | 7.5778 | 7.3971 | 7.2145 | 7.0563 | 6.9135 | 6.7737 | 6.3941 | 6.0829 | 5.6869
|  | STRICHEN | HE |  |  |  |  | 8.0971 | 7.7482 | 7.388 | 6.9982 | 6.9308 | 6.7543 | 6.5573 | 6.242 | 6.0767 | 5.9298 | 5.3747 | 4.788 | 4.342 | 9.5176 | 9.1012 | 8.6829 | 8.2573 | 8.2298 | 8.1645 | 8.09 | 7.9798 | 7.9431 | 7.8747 | 7.6635 | 7.6145 | 7.5573 | 8.7696 | 8.3982 | 8.0155 | 7.5961 | 7.5624 | 7.4441 | 7.3124 | 7.1155 | 6.9951 | 6.8859 | 6.5145 | 6.2288 | 5.9114
|  | STRICHEN | FB |  |  |  |  | 8.1706 | 7.8635 | 7.5431 | 7.2043 | 7.189 | 7.1869 | 7.1441 | 7.1155 | 7.0492 | 7.0104 | 6.6716 | 6.2798 | 6.0135 | 9.5563 | 9.1676 | 8.7696 | 8.3665 | 8.3482 | 8.339 | 8.3063 | 8.29 | 8.2482 | 8.2176 | 8.0798 | 7.8594 | 7.6992 | 8.8186 | 8.4757 | 8.1237 | 7.7563 | 7.7339 | 7.7196 | 7.6788 | 7.6635 | 7.6339 | 7.5961 | 7.3512 | 7.0512 | 6.9267
| THURSO | STROMNESS | MINIMUM HEADROOM | HY 25978 10409 | NO | NO | 0.285 | 2.0408 | 1.5337 | 1.2469 | 1.0408 | 0.70816 | 0.069388 | -0.62449 | -1.4694 | -3.298 | -3.8959 | -6.0235 | -8.9286 | -11.4908 | 4.1286 | 3.5765 | 3.3071 | 3.1449 | 2.8673 | 2.3357 | 1.7439 | 0.94184 | -1.0071 | -1.6398 | -4.0378 | -7.1673 | -10.1184 | 3.2582 | 2.7469 | 2.4592 | 2.2816 | 1.9745 | 1.3786 | 0.69694 | -0.20204 | -2.2694 | -2.9153 | -5.352 | -8.6837 | -11.7153
|  | STROMNESS | EE |  |  |  |  | 2.1163 | 1.5745 | 1.249 | 1.0449 | 0.71429 | 0.087755 | -0.5449 | -1.2245 | -2.3112 | -2.7745 | -4.4633 | -7.4745 | -8.6959 | 4.2061 | 3.6153 | 3.3082 | 3.1459 | 2.8673 | 2.3439 | 1.8204 | 1.2439 | 0.22449 | -0.22755 | -1.9245 | -5.1847 | -6.4337 | 3.3316 | 2.7857 | 2.4633 | 2.2847 | 1.9765 | 1.3918 | 0.77959 | 0.10204 | -1.049 | -1.5092 | -3.2837 | -6.7112 | -8.0439
|  | STROMNESS | HT |  |  |  |  | 2.0735 | 1.5816 | 1.2469 | 1.0408 | 0.71633 | 0.19184 | -0.53265 | -1.301 | -2.5245 | -3.0276 | -4.8194 | -8.1857 | -10.7592 | 4.1612 | 3.6245 | 3.3071 | 3.1449 | 2.8684 | 2.4653 | 1.8092 | 1.1602 | -0.11531 | -0.61837 | -2.5714 | -6.2041 | -8.9571 | 3.2888 | 2.7949 | 2.4592 | 2.2816 | 1.9786 | 1.5061 | 0.76429 | -0.0091837 | -1.3643 | -1.8745 | -3.8316 | -7.6643 | -10.6224
|  | STROMNESS | HE |  |  |  |  | 2.0408 | 1.5337 | 1.248 | 1.0418 | 0.70816 | 0.069388 | -0.62449 | -1.4694 | -3.298 | -3.8959 | -6.0235 | -8.9286 | -11.4908 | 4.1286 | 3.5765 | 3.3071 | 3.1459 | 2.8684 | 2.3357 | 1.7439 | 0.94184 | -1.0071 | -1.6398 | -4.0378 | -7.1673 | -10.1184 | 3.2582 | 2.7469 | 2.4612 | 2.2827 | 1.9745 | 1.3786 | 0.69694 | -0.20204 | -2.2694 | -2.9153 | -5.352 | -8.6837 | -11.7153
|  | STROMNESS | FB |  |  |  |  | 2.3214 | 1.9347 | 1.65 | 1.5857 | 1.5031 | 1.3184 | 1.0408 | 0.6602 | 0.012245 | -0.29898 | -1.2816 | -2.9306 | -3.751 | 4.4041 | 3.9367 | 3.6806 | 3.601 | 3.4459 | 3.2602 | 2.8765 | 2.4327 | 1.6582 | 1.3031 | 0.33163 | -1.4041 | -2.4143 | 3.5327 | 3.1378 | 2.8816 | 2.8133 | 2.6816 | 2.5071 | 2.1367 | 1.698 | 0.94898 | 0.60714 | -0.38571 | -2.1041 | -2.9633
| DUNOON | STRONDAVON | MINIMUM HEADROOM | NS 04281 90471 | YES | YES | 0 | 0.29109 | 0.29007 | 0.28752 | 0.28446 | 0.2819 | 0.27527 | 0.27323 | 0.2666 | 0.25894 | 0.25741 | 0.24415 | 0.23292 | 0.22527 | 0.28672 | 0.28519 | 0.28264 | 0.28162 | 0.28059 | 0.27498 | 0.27396 | 0.26886 | 0.26325 | 0.26325 | 0.24794 | 0.24641 | 0.24386 | 0.29018 | 0.28865 | 0.28559 | 0.28355 | 0.2815 | 0.27487 | 0.27283 | 0.2662 | 0.26008 | 0.25906 | 0.2463 | 0.23814 | 0.23304
|  | STRONDAVON | EE |  |  |  |  | 0.29109 | 0.29007 | 0.28752 | 0.28497 | 0.28241 | 0.27578 | 0.27425 | 0.2666 | 0.25946 | 0.25843 | 0.24415 | 0.23292 | 0.22629 | 0.28672 | 0.28519 | 0.28264 | 0.28162 | 0.28059 | 0.27549 | 0.27396 | 0.26886 | 0.26325 | 0.26325 | 0.24998 | 0.24947 | 0.25202 | 0.29018 | 0.28865 | 0.28559 | 0.28406 | 0.28201 | 0.27538 | 0.27334 | 0.2662 | 0.26008 | 0.25906 | 0.2463 | 0.23814 | 0.23559
|  | STRONDAVON | HT |  |  |  |  | 0.29109 | 0.29007 | 0.28803 | 0.28446 | 0.28292 | 0.27629 | 0.27425 | 0.26813 | 0.26099 | 0.26048 | 0.24772 | 0.2365 | 0.22578 | 0.28672 | 0.28519 | 0.28264 | 0.28162 | 0.28059 | 0.27498 | 0.27396 | 0.26886 | 0.26376 | 0.26376 | 0.24794 | 0.24641 | 0.25151 | 0.29018 | 0.28865 | 0.2861 | 0.28355 | 0.28252 | 0.27589 | 0.27385 | 0.26773 | 0.26161 | 0.26059 | 0.24783 | 0.24069 | 0.23559
|  | STRONDAVON | HE |  |  |  |  | 0.29109 | 0.29007 | 0.28752 | 0.28446 | 0.2819 | 0.27527 | 0.27323 | 0.2666 | 0.25894 | 0.25741 | 0.2467 | 0.23394 | 0.22527 | 0.28672 | 0.28519 | 0.28264 | 0.28162 | 0.28059 | 0.27498 | 0.27396 | 0.26886 | 0.26325 | 0.26325 | 0.24998 | 0.24845 | 0.24845 | 0.29018 | 0.28865 | 0.28559 | 0.28406 | 0.2815 | 0.27487 | 0.27283 | 0.26671 | 0.26059 | 0.25906 | 0.24783 | 0.23865 | 0.23304
|  | STRONDAVON | FB |  |  |  |  | 0.29415 | 0.29466 | 0.29313 | 0.2916 | 0.28905 | 0.28803 | 0.2865 | 0.28394 | 0.28241 | 0.28139 | 0.26864 | 0.25894 | 0.25282 | 0.28978 | 0.2908 | 0.28774 | 0.2857 | 0.28468 | 0.28417 | 0.28213 | 0.27906 | 0.27753 | 0.27549 | 0.26376 | 0.25202 | 0.24386 | 0.29375 | 0.29426 | 0.2912 | 0.28967 | 0.28814 | 0.28763 | 0.28508 | 0.28355 | 0.2815 | 0.27997 | 0.26722 | 0.25446 | 0.2514
| THURSO | STRONSAY | MINIMUM HEADROOM | HY 64548 27016 | YES | NO | 0.036 | 0.62653 | 0.62245 | 0.61939 | 0.60306 | 0.58367 | 0.55204 | 0.51837 | 0.50204 | 0.47347 | 0.45714 | 0.42449 | 0.36633 | 0.32143 | 0.77347 | 0.77041 | 0.76633 | 0.76327 | 0.75612 | 0.74286 | 0.73469 | 0.72449 | 0.70612 | 0.69082 | 0.67449 | 0.66939 | 0.65102 | 0.72653 | 0.72245 | 0.71837 | 0.7051 | 0.69082 | 0.66429 | 0.64082 | 0.61633 | 0.58163 | 0.56735 | 0.53673 | 0.52755 | 0.49898
|  | STRONSAY | EE |  |  |  |  | 0.62755 | 0.62347 | 0.62041 | 0.60816 | 0.5898 | 0.55714 | 0.52755 | 0.51429 | 0.47857 | 0.46327 | 0.42449 | 0.36633 | 0.32653 | 0.77347 | 0.77143 | 0.76735 | 0.76429 | 0.75714 | 0.74286 | 0.73673 | 0.72449 | 0.70714 | 0.69184 | 0.67959 | 0.67041 | 0.67245 | 0.72653 | 0.72347 | 0.71939 | 0.70714 | 0.6949 | 0.66735 | 0.64592 | 0.61735 | 0.58571 | 0.57143 | 0.53673 | 0.52755 | 0.50714
|  | STRONSAY | HT |  |  |  |  | 0.62653 | 0.62347 | 0.61939 | 0.60612 | 0.5898 | 0.5551 | 0.53265 | 0.50204 | 0.49898 | 0.47959 | 0.44898 | 0.38061 | 0.32143 | 0.77347 | 0.77041 | 0.76735 | 0.76429 | 0.75612 | 0.74286 | 0.73673 | 0.72551 | 0.70918 | 0.69388 | 0.67449 | 0.66939 | 0.67245 | 0.72653 | 0.72245 | 0.71837 | 0.70714 | 0.6949 | 0.66633 | 0.65 | 0.62755 | 0.60102 | 0.58061 | 0.55204 | 0.53571 | 0.5
|  | STRONSAY | HE |  |  |  |  | 0.62653 | 0.62245 | 0.61939 | 0.60306 | 0.58367 | 0.55204 | 0.51837 | 0.50816 | 0.47347 | 0.45714 | 0.44184 | 0.37653 | 0.32755 | 0.77347 | 0.77041 | 0.76633 | 0.76327 | 0.75612 | 0.74286 | 0.73469 | 0.72551 | 0.70612 | 0.69082 | 0.67959 | 0.67143 | 0.6602 | 0.72653 | 0.72245 | 0.71837 | 0.7051 | 0.69082 | 0.66429 | 0.64082 | 0.61633 | 0.58163 | 0.56735 | 0.55204 | 0.53367 | 0.49898
|  | STRONSAY | FB |  |  |  |  | 0.64082 | 0.64184 | 0.63878 | 0.64082 | 0.6398 | 0.63878 | 0.63265 | 0.62449 | 0.62143 | 0.61429 | 0.57857 | 0.53367 | 0.51837 | 0.78265 | 0.78367 | 0.77653 | 0.77857 | 0.77755 | 0.77449 | 0.76735 | 0.75714 | 0.75714 | 0.74694 | 0.72143 | 0.67551 | 0.65102 | 0.74082 | 0.74082 | 0.73469 | 0.73776 | 0.73776 | 0.73367 | 0.72755 | 0.71735 | 0.71633 | 0.70714 | 0.66939 | 0.61429 | 0.60408
| FORT WILLIAM | STRONTIAN | MINIMUM HEADROOM | NM 81521 61955 | YES | NO | 0.058 | 0.10102 | 0.097959 | 0.088776 | 0.069388 | 0.046939 | -0.13265 | -0.22959 | -0.3102 | -0.36327 | -0.38878 | -0.45204 | -0.51122 | -0.56429 | 0.45306 | 0.45102 | 0.44694 | 0.44388 | 0.43469 | 0.29184 | 0.19592 | 0.13163 | 0.096939 | 0.082653 | 0.056122 | 0.062245 | 0.061224 | 0.36429 | 0.36327 | 0.35918 | 0.34694 | 0.33061 | 0.17245 | 0.068367 | 0.0020408 | -0.047959 | -0.069388 | -0.090816 | -0.12653 | -0.1551
|  | STRONTIAN | EE |  |  |  |  | 0.10102 | 0.097959 | 0.088776 | 0.071429 | 0.05102 | -0.0020408 | -0.043878 | -0.19082 | -0.2949 | -0.37041 | -0.45204 | -0.51122 | -0.54898 | 0.45306 | 0.45102 | 0.44694 | 0.44388 | 0.43571 | 0.41531 | 0.39184 | 0.27551 | 0.17653 | 0.10306 | 0.062245 | 0.066327 | 0.07551 | 0.36429 | 0.36327 | 0.35918 | 0.34796 | 0.33265 | 0.2949 | 0.24592 | 0.11429 | 0.016327 | -0.052041 | -0.090816 | -0.12653 | -0.14286
|  | STRONTIAN | HT |  |  |  |  | 0.10102 | 0.09898 | 0.090816 | 0.071429 | 0.047959 | -0.13265 | -0.22959 | -0.3102 | -0.36327 | -0.38571 | -0.43878 | -0.5051 | -0.56429 | 0.45408 | 0.45204 | 0.44898 | 0.44388 | 0.43469 | 0.29184 | 0.19592 | 0.13163 | 0.096939 | 0.082653 | 0.056122 | 0.062245 | 0.072449 | 0.36531 | 0.36327 | 0.3602 | 0.34796 | 0.33061 | 0.17245 | 0.068367 | 0.0020408 | -0.047959 | -0.068367 | -0.086735 | -0.12347 | -0.1551
|  | STRONTIAN | HE |  |  |  |  | 0.10102 | 0.09898 | 0.090816 | 0.069388 | 0.046939 | -0.010204 | -0.045918 | -0.20408 | -0.31531 | -0.38878 | -0.42959 | -0.49796 | -0.53878 | 0.45408 | 0.45204 | 0.44898 | 0.44388 | 0.43571 | 0.4102 | 0.39184 | 0.26122 | 0.15714 | 0.084694 | 0.068367 | 0.07551 | 0.077551 | 0.36531 | 0.36327 | 0.3602 | 0.34694 | 0.33061 | 0.28776 | 0.24388 | 0.10306 | 0 | -0.069388 | -0.076531 | -0.11633 | -0.14082
|  | STRONTIAN | FB |  |  |  |  | 0.12143 | 0.11429 | 0.11633 | 0.11429 | 0.1102 | 0.10612 | 0.088776 | 0.068367 | -0.035714 | -0.10204 | -0.25306 | -0.29898 | -0.31224 | 0.46735 | 0.46429 | 0.46531 | 0.46327 | 0.46224 | 0.46122 | 0.44592 | 0.42857 | 0.33163 | 0.25918 | 0.11122 | 0.078571 | 0.061224 | 0.38163 | 0.37551 | 0.37959 | 0.37755 | 0.37245 | 0.37143 | 0.35918 | 0.34286 | 0.2398 | 0.17959 | 0.041837 | 0.0020408 | -0.0030612
| SHETLAND | SUMBURGH | MINIMUM HEADROOM | HU3900512755 | YES | YES | 0.109 | -0.57755 | -0.58776 | -0.60306 | -0.66429 | -0.69388 | -0.76327 | -0.83673 | -0.91939 | -0.98673 | -1.0327 | -1.1378 | -1.2643 | -1.3643 | -0.033673 | -0.032653 | -0.036735 | -0.040816 | -0.047959 | -0.076531 | -0.10204 | -0.13673 | -0.15 | -0.18163 | -0.25204 | -0.25816 | -0.33469 | -0.26633 | -0.2602 | -0.26224 | -0.29898 | -0.33571 | -0.39082 | -0.41224 | -0.47041 | -0.51633 | -0.55102 | -0.61837 | -0.69388 | -0.75
|  | SUMBURGH | EE |  |  |  |  | -0.57755 | -0.58673 | -0.60306 | -0.6602 | -0.68673 | -0.76224 | -0.83673 | -0.91939 | -0.98673 | -1.0327 | -1.1378 | -1.2643 | -1.3541 | -0.033673 | -0.031633 | -0.036735 | -0.038776 | -0.046939 | -0.07551 | -0.10204 | -0.13673 | -0.15 | -0.18163 | -0.24184 | -0.23673 | -0.23673 | -0.26633 | -0.25918 | -0.26224 | -0.2949 | -0.33061 | -0.38878 | -0.41224 | -0.47041 | -0.51633 | -0.55102 | -0.61837 | -0.69388 | -0.73878
|  | SUMBURGH | HT |  |  |  |  | -0.57755 | -0.58571 | -0.59898 | -0.64796 | -0.67551 | -0.74694 | -0.81327 | -0.89082 | -0.95306 | -0.99898 | -1.0847 | -1.2347 | -1.3643 | -0.033673 | -0.031633 | -0.034694 | -0.037755 | -0.045918 | -0.07449 | -0.09898 | -0.13469 | -0.14796 | -0.17959 | -0.25204 | -0.24388 | -0.22857 | -0.26633 | -0.2602 | -0.2602 | -0.28673 | -0.32143 | -0.37857 | -0.39592 | -0.45204 | -0.4949 | -0.53061 | -0.59082 | -0.67959 | -0.75
|  | SUMBURGH | HE |  |  |  |  | -0.57755 | -0.58776 | -0.60102 | -0.66429 | -0.69388 | -0.76327 | -0.83265 | -0.91327 | -0.97653 | -1.0245 | -1.0888 | -1.248 | -1.3439 | -0.033673 | -0.032653 | -0.035714 | -0.040816 | -0.047959 | -0.076531 | -0.10204 | -0.13673 | -0.15 | -0.18163 | -0.23571 | -0.24286 | -0.26224 | -0.26633 | -0.2602 | -0.26122 | -0.29898 | -0.33571 | -0.39082 | -0.40816 | -0.46633 | -0.5102 | -0.54694 | -0.58878 | -0.68571 | -0.74184
|  | SUMBURGH | FB |  |  |  |  | -0.54796 | -0.5449 | -0.53878 | -0.54286 | -0.54898 | -0.5551 | -0.56429 | -0.57857 | -0.59082 | -0.60816 | -0.70204 | -0.7551 | -0.78878 | -0.0081633 | -0.0040816 | -0.0010204 | 0.0040816 | 0.0010204 | -0.005102 | -0.015306 | -0.032653 | -0.042857 | -0.061224 | -0.14082 | -0.25816 | -0.33469 | -0.24388 | -0.22551 | -0.21531 | -0.21429 | -0.21633 | -0.21735 | -0.22041 | -0.23367 | -0.24286 | -0.25918 | -0.33367 | -0.41224 | -0.42551
| ALNESS | TAIN | MINIMUM HEADROOM | NH 77578 81489 | NO | NO | 4.146 | 6.4303 | 6.4467 | 6.4222 | 14.9991 | 14.942 | 13.7654 | 12.7716 | 11.7236 | 10.9858 | 10.5522 | 9.6736 | 9.194 | 8.7807 | 7.8722 | 7.9038 | 7.9354 | 16.2226 | 16.1848 | 15.4103 | 14.5665 | 13.6644 | 13.1246 | 12.8797 | 12.6001 | 12.6236 | 12.5522 | 7.4859 | 7.4982 | 7.5166 | 15.9563 | 15.9552 | 14.9001 | 14.0909 | 13.243 | 12.595 | 12.2491 | 11.6134 | 11.2981 | 11.0807
|  | TAIN | EE |  |  |  |  | 6.4314 | 6.4467 | 6.4222 | 15.0001 | 14.946 | 14.4583 | 14.045 | 13.3042 | 12.3379 | 11.3522 | 9.6736 | 9.194 | 8.8328 | 7.8722 | 7.9048 | 7.9354 | 16.2226 | 16.2481 | 16.0103 | 15.8563 | 15.2603 | 14.5216 | 13.596 | 12.6236 | 12.6236 | 12.6348 | 7.4859 | 7.4982 | 7.5166 | 15.9563 | 15.9552 | 15.5583 | 15.2563 | 14.5552 | 13.8471 | 12.9879 | 11.6134 | 11.2981 | 11.0807
|  | TAIN | HT |  |  |  |  | 6.4303 | 6.4487 | 6.4232 | 14.9991 | 14.942 | 13.7654 | 12.7716 | 11.7236 | 10.9858 | 10.5522 | 9.7838 | 9.2634 | 8.7807 | 7.8722 | 7.9038 | 7.9365 | 16.2246 | 16.2481 | 15.4103 | 14.5665 | 13.6644 | 13.1246 | 12.8797 | 12.6001 | 12.6246 | 12.6685 | 7.4859 | 7.4982 | 7.5176 | 15.9573 | 15.9583 | 14.9001 | 14.0909 | 13.243 | 12.595 | 12.2491 | 11.6909 | 11.3756 | 11.0858
|  | TAIN | HE |  |  |  |  | 6.4303 | 6.4477 | 6.4252 | 15.0022 | 14.9481 | 14.3532 | 14.0032 | 13.2134 | 12.1165 | 11.0369 | 9.8195 | 9.3103 | 9.0134 | 7.8722 | 7.9058 | 7.9375 | 16.2246 | 16.2491 | 15.9705 | 15.8695 | 15.2083 | 14.3369 | 13.3175 | 12.6705 | 12.6899 | 12.7093 | 7.487 | 7.4982 | 7.5186 | 15.9593 | 15.9624 | 15.4777 | 15.2267 | 14.4838 | 13.6318 | 12.7001 | 11.7338 | 11.4032 | 11.2226
|  | TAIN | FB |  |  |  |  | 6.4895 | 6.5375 | 6.5518 | 15.2501 | 15.0542 | 15.0624 | 14.8695 | 14.7205 | 14.2716 | 13.6797 | 11.2705 | 10.9379 | 10.7552 | 7.9099 | 7.9722 | 8.013 | 16.3154 | 16.1848 | 16.2001 | 16.1185 | 16.0685 | 15.6042 | 15.0409 | 12.9991 | 12.7552 | 12.5522 | 7.5625 | 7.6339 | 7.6635 | 16.1787 | 15.996 | 16.0216 | 15.8889 | 15.7869 | 15.3195 | 14.8358 | 12.7563 | 12.5185 | 12.4052
| ARDMORE / HARRIS GRID | TARBERT | MINIMUM HEADROOM | NB 15289 00157 | NO | YES | 0.216 | 0.1949 | 0.1551 | 0.14796 | 0.10204 | 0.055102 | -0.030612 | -0.11735 | -0.19592 | -0.28163 | -0.31531 | -0.49388 | -0.67959 | -0.83673 | 0.34286 | 0.3051 | 0.31837 | 0.32041 | 0.28673 | 0.27143 | 0.23571 | 0.21837 | 0.17857 | 0.13673 | -0.0010204 | -0.013265 | -0.055102 | 0.16429 | 0.12245 | 0.12959 | 0.1051 | 0.05 | -0.016327 | -0.052041 | -0.10612 | -0.16939 | -0.21735 | -0.34184 | -0.42959 | -0.52755
|  | TARBERT | EE |  |  |  |  | 0.19592 | 0.20204 | 0.14796 | 0.10714 | 0.076531 | -0.028571 | -0.11327 | -0.19388 | -0.28163 | -0.31224 | -0.49388 | -0.67959 | -0.82653 | 0.34286 | 0.3602 | 0.31837 | 0.32245 | 0.31531 | 0.27143 | 0.23571 | 0.21939 | 0.18061 | 0.13673 | 0.0040816 | 0.012245 | 0.013265 | 0.16429 | 0.17857 | 0.12959 | 0.10918 | 0.072449 | -0.016327 | -0.04898 | -0.10408 | -0.16837 | -0.21122 | -0.34184 | -0.42959 | -0.52143
|  | TARBERT | HT |  |  |  |  | 0.1949 | 0.1551 | 0.15 | 0.10612 | 0.055102 | -0.018367 | -0.10204 | -0.17653 | -0.2602 | -0.28673 | -0.42041 | -0.63673 | -0.83673 | 0.34286 | 0.3051 | 0.31939 | 0.32143 | 0.28673 | 0.27347 | 0.23878 | 0.22143 | 0.18367 | 0.13878 | -0.0010204 | -0.013265 | 0.0091837 | 0.16429 | 0.12245 | 0.12959 | 0.11122 | 0.05 | -0.0081633 | -0.041837 | -0.090816 | -0.15612 | -0.19898 | -0.2949 | -0.40204 | -0.52755
|  | TARBERT | HE |  |  |  |  | 0.1949 | 0.20102 | 0.14796 | 0.10204 | 0.070408 | -0.030612 | -0.11735 | -0.19592 | -0.28163 | -0.31531 | -0.43469 | -0.64796 | -0.78367 | 0.34286 | 0.36122 | 0.31837 | 0.32041 | 0.31429 | 0.27245 | 0.23571 | 0.21837 | 0.17857 | 0.13776 | 0.005102 | 0.0061224 | 0.0091837 | 0.16429 | 0.17857 | 0.12959 | 0.1051 | 0.068367 | 0.015306 | -0.052041 | -0.10612 | -0.16939 | -0.21735 | -0.30918 | -0.42245 | -0.50816
|  | TARBERT | FB |  |  |  |  | 0.21837 | 0.23673 | 0.25714 | 0.21429 | 0.21531 | 0.20714 | 0.17653 | 0.16122 | 0.15204 | 0.13571 | 0.081633 | -0.060204 | -0.094898 | 0.36429 | 0.38571 | 0.40408 | 0.36327 | 0.37551 | 0.36735 | 0.33163 | 0.31939 | 0.31327 | 0.29592 | 0.21224 | 0.052041 | -0.055102 | 0.19796 | 0.21531 | 0.23265 | 0.19388 | 0.20102 | 0.19286 | 0.16531 | 0.15306 | 0.14694 | 0.12959 | 0.036735 | -0.088776 | -0.091837
| PORT ANN | TARBERT JURA | MINIMUM HEADROOM | NR 60552 82166 | YES | YES | 0.092 | 0.16753 | 0.16753 | 0.16856 | 0.15835 | 0.15733 | 0.15325 | 0.15223 | 0.14815 | 0.14611 | 0.14611 | 0.14304 | 0.13896 | 0.13896 | 0.15566 | 0.15566 | 0.15566 | 0.14647 | 0.14545 | 0.14443 | 0.14341 | 0.14035 | 0.13831 | 0.13933 | 0.13729 | 0.13627 | 0.13321 | 0.16262 | 0.16262 | 0.16262 | 0.15343 | 0.15343 | 0.14935 | 0.14629 | 0.14221 | 0.14119 | 0.14221 | 0.13915 | 0.13609 | 0.13609
|  | TARBERT JURA | EE |  |  |  |  | 0.16753 | 0.16753 | 0.16856 | 0.15835 | 0.15733 | 0.15733 | 0.15223 | 0.14815 | 0.14713 | 0.14611 | 0.14304 | 0.13896 | 0.13998 | 0.15566 | 0.15566 | 0.15566 | 0.14647 | 0.14545 | 0.14647 | 0.14341 | 0.14035 | 0.14035 | 0.13933 | 0.13729 | 0.13627 | 0.13933 | 0.16262 | 0.16262 | 0.16262 | 0.15343 | 0.15343 | 0.15343 | 0.14629 | 0.14221 | 0.14323 | 0.14221 | 0.13915 | 0.13609 | 0.13813
|  | TARBERT JURA | HT |  |  |  |  | 0.16753 | 0.16753 | 0.16856 | 0.15835 | 0.15733 | 0.15835 | 0.15325 | 0.14917 | 0.14611 | 0.14713 | 0.14304 | 0.14304 | 0.13896 | 0.15566 | 0.15566 | 0.15566 | 0.14647 | 0.14545 | 0.14647 | 0.14443 | 0.14137 | 0.13831 | 0.14035 | 0.13729 | 0.13831 | 0.13729 | 0.16262 | 0.16262 | 0.16262 | 0.15343 | 0.15343 | 0.15343 | 0.14731 | 0.14323 | 0.14119 | 0.14323 | 0.13915 | 0.13915 | 0.13609
|  | TARBERT JURA | HE |  |  |  |  | 0.16753 | 0.16753 | 0.16856 | 0.15835 | 0.15733 | 0.15325 | 0.15223 | 0.14815 | 0.14713 | 0.14611 | 0.14304 | 0.141 | 0.13998 | 0.15566 | 0.15566 | 0.15566 | 0.14647 | 0.14545 | 0.14443 | 0.14341 | 0.14035 | 0.14035 | 0.13933 | 0.13729 | 0.13729 | 0.13729 | 0.16262 | 0.16262 | 0.16262 | 0.15343 | 0.15343 | 0.14935 | 0.14629 | 0.14221 | 0.14323 | 0.14221 | 0.13915 | 0.13711 | 0.13609
|  | TARBERT JURA | FB |  |  |  |  | 0.16753 | 0.16753 | 0.16856 | 0.16856 | 0.16856 | 0.15835 | 0.16141 | 0.16141 | 0.15835 | 0.15835 | 0.15121 | 0.14713 | 0.14509 | 0.15566 | 0.15566 | 0.15566 | 0.15668 | 0.15668 | 0.14443 | 0.14953 | 0.14953 | 0.14545 | 0.14545 | 0.14035 | 0.13831 | 0.13321 | 0.16262 | 0.16262 | 0.16262 | 0.16364 | 0.16364 | 0.15241 | 0.15649 | 0.15649 | 0.15343 | 0.15343 | 0.14731 | 0.14017 | 0.14017
| PORT ANN | TARBERT LOCH FYNE | MINIMUM HEADROOM | NR 86003 68479 | NO | YES | 1.694 | 0.95736 | 0.95226 | 0.9594 | 0.76858 | 0.57879 | 0.32369 | 0.085931 | -0.12529 | -0.26101 | -0.45999 | -1.0569 | -1.3753 | -1.6018 | 1.5859 | 1.5716 | 1.5655 | 1.2982 | 1.1737 | 0.94818 | 0.73083 | 0.5543 | 0.44205 | 0.25226 | -0.36611 | -0.54672 | -0.67631 | 1.3604 | 1.3482 | 1.3461 | 1.1339 | 0.9594 | 0.72777 | 0.50022 | 0.3043 | 0.17675 | -0.023253 | -0.62121 | -0.8906 | -1.0773
|  | TARBERT LOCH FYNE | EE |  |  |  |  | 0.96246 | 0.96246 | 0.96246 | 0.94511 | 0.58491 | 0.33287 | 0.10838 | -0.072233 | -0.26101 | -0.45999 | -1.0569 | -1.3753 | -1.6018 | 1.588 | 1.5767 | 1.5706 | 1.5543 | 1.1798 | 0.9543 | 0.76246 | 0.6145 | 0.45328 | 0.25226 | -0.32223 | -0.52631 | -0.67631 | 1.3645 | 1.3553 | 1.3492 | 1.3206 | 0.96552 | 0.73491 | 0.52573 | 0.36042 | 0.17981 | -0.023253 | -0.62019 | -0.8906 | -1.0773
|  | TARBERT LOCH FYNE | HT |  |  |  |  | 0.95736 | 0.95226 | 0.9594 | 0.94409 | 0.58185 | 0.32573 | 0.085931 | -0.075294 | -0.26101 | -0.44774 | -1.0345 | -1.3335 | -1.5386 | 1.5859 | 1.5716 | 1.5655 | 1.5492 | 1.1737 | 0.94818 | 0.73083 | 0.59818 | 0.44205 | 0.2543 | -0.36611 | -0.54672 | -0.62529 | 1.3604 | 1.3482 | 1.3461 | 1.3186 | 0.96144 | 0.72981 | 0.50022 | 0.35328 | 0.17675 | -0.01509 | -0.62121 | -0.86509 | -1.011
|  | TARBERT LOCH FYNE | HE |  |  |  |  | 0.96042 | 0.95736 | 0.96246 | 0.94205 | 0.57879 | 0.32369 | 0.1543 | -0.12529 | -0.22427 | -0.37223 | -0.74468 | -0.88448 | -0.95693 | 1.588 | 1.5747 | 1.5706 | 1.5523 | 1.1778 | 0.94818 | 0.81042 | 0.5543 | 0.48899 | 0.34511 | -0.031416 | -0.0406 | -0.026314 | 1.3625 | 1.3512 | 1.3502 | 1.3186 | 0.9594 | 0.72777 | 0.57369 | 0.3043 | 0.2196 | 0.070624 | -0.31101 | -0.38856 | -0.41917
|  | TARBERT LOCH FYNE | FB |  |  |  |  | 1.0063 | 1.0288 | 1.0451 | 0.76858 | 0.78083 | 0.77369 | 0.77369 | 0.76144 | 0.63287 | 0.59613 | 0.12879 | -0.29978 | -0.65999 | 1.6237 | 1.6318 | 1.6247 | 1.2982 | 1.2941 | 1.2737 | 1.2594 | 1.2278 | 1.0839 | 1.0359 | 0.55634 | 0.10838 | -0.31509 | 1.4043 | 1.4196 | 1.4247 | 1.1339 | 1.1359 | 1.1186 | 1.1114 | 1.0839 | 0.94716 | 0.9043 | 0.42981 | -0.097743 | -0.37733
| TAYNUILT | TAYNUILT | MINIMUM HEADROOM | NN 01856 31079 | NO | YES | 0.257 | 2.2051 | 2.1439 | 2.1265 | 2.0806 | 2.0653 | 1.998 | 1.9459 | 1.8857 | 1.8367 | 1.8194 | 1.5122 | 1.4469 | 1.3286 | 2.7306 | 2.6786 | 2.6643 | 2.6531 | 2.6388 | 2.6 | 2.5776 | 2.5378 | 2.5031 | 2.4969 | 2.1633 | 2.1643 | 2.0837 | 2.5796 | 2.5245 | 2.502 | 2.4684 | 2.4531 | 2.3847 | 2.3551 | 2.3092 | 2.2633 | 2.2531 | 1.9347 | 1.8929 | 1.7929
|  | TAYNUILT | EE |  |  |  |  | 2.2051 | 2.2102 | 2.1265 | 2.0806 | 2.0765 | 2.0031 | 1.9459 | 1.8857 | 1.8367 | 1.8194 | 1.5122 | 1.4469 | 1.3286 | 2.7306 | 2.7296 | 2.6643 | 2.6531 | 2.6388 | 2.6041 | 2.5776 | 2.5378 | 2.5041 | 2.4969 | 2.1633 | 2.1643 | 2.0837 | 2.5796 | 2.5776 | 2.502 | 2.4684 | 2.4531 | 2.3878 | 2.3663 | 2.3092 | 2.2633 | 2.2531 | 1.9347 | 1.8929 | 1.7929
|  | TAYNUILT | HT |  |  |  |  | 2.2051 | 2.1439 | 2.1306 | 2.0949 | 2.0653 | 2.0133 | 1.9694 | 1.9173 | 1.8684 | 1.849 | 1.7816 | 1.6878 | 1.599 | 2.7306 | 2.6786 | 2.6643 | 2.6541 | 2.6388 | 2.6 | 2.5796 | 2.5398 | 2.5031 | 2.498 | 2.4194 | 2.4194 | 2.4204 | 2.5796 | 2.5245 | 2.5061 | 2.4776 | 2.4612 | 2.3949 | 2.3551 | 2.3276 | 2.2806 | 2.2694 | 2.1827 | 2.1347 | 2.0796
|  | TAYNUILT | HE |  |  |  |  | 2.2082 | 2.2102 | 2.1286 | 2.0847 | 2.0796 | 1.998 | 1.9551 | 1.8969 | 1.848 | 1.8265 | 1.7582 | 1.6622 | 1.6286 | 2.7337 | 2.7296 | 2.6643 | 2.6531 | 2.6388 | 2.6 | 2.5776 | 2.5388 | 2.5041 | 2.4969 | 2.4153 | 2.4071 | 2.4112 | 2.5837 | 2.5786 | 2.5051 | 2.4714 | 2.4561 | 2.3847 | 2.3714 | 2.3153 | 2.2694 | 2.2561 | 2.1694 | 2.1051 | 2.0949
|  | TAYNUILT | FB |  |  |  |  | 2.2224 | 2.2327 | 2.2367 | 2.1633 | 2.1663 | 2.1592 | 2.1449 | 2.1398 | 2.1214 | 2.1153 | 2.0592 | 1.9571 | 1.9286 | 2.748 | 2.75 | 2.7429 | 2.6888 | 2.6837 | 2.6755 | 2.6561 | 2.6449 | 2.6255 | 2.6143 | 2.5367 | 2.398 | 2.3133 | 2.6051 | 2.6082 | 2.6061 | 2.5398 | 2.5388 | 2.5286 | 2.5163 | 2.5071 | 2.4878 | 2.4796 | 2.4031 | 2.2714 | 2.2571
| BURGHMUIR | THIMBLEROW | MINIMUM HEADROOM | NO 11356 23764 | NO | YES | 1.327 | 7.6908 | 7.6949 | 7.6582 | 7.5459 | 7.4061 | 7.1724 | 6.9735 | 6.6969 | 6.0082 | 5.7061 | 2.9082 | 0.66837 | -0.44592 | 13.401 | 13.399 | 13.3531 | 13.2765 | 13.1663 | 12.5041 | 12.1602 | 11.5969 | 10.8867 | 10.6133 | 8.4316 | 6.8908 | 5.0673 | 10.3663 | 10.3541 | 10.2959 | 10.1918 | 10.0551 | 9.8388 | 9.6571 | 9.4153 | 8.8286 | 8.5214 | 5.6357 | 3.5163 | 2.5245
|  | THIMBLEROW | EE |  |  |  |  | 7.6949 | 7.702 | 7.6694 | 7.5684 | 7.4296 | 7.1724 | 6.9735 | 6.6969 | 6.0082 | 5.7061 | 2.9082 | 0.66837 | -0.44592 | 13.4041 | 13.401 | 13.3602 | 13.2837 | 13.1724 | 12.5041 | 12.1602 | 11.6204 | 10.8867 | 10.6133 | 8.4316 | 6.8908 | 5.9041 | 10.3694 | 10.3612 | 10.3082 | 10.2102 | 10.0765 | 9.8388 | 9.6643 | 9.4245 | 8.8286 | 8.5214 | 5.6357 | 3.5163 | 2.5245
|  | THIMBLEROW | HT |  |  |  |  | 7.6969 | 7.7122 | 7.6837 | 7.5867 | 7.4541 | 7.2041 | 7.0051 | 6.7224 | 6.1684 | 5.8337 | 3.1163 | 1.1949 | 0.67551 | 13.401 | 13.399 | 13.3531 | 13.2765 | 13.1663 | 12.5755 | 12.2959 | 11.7337 | 11.0306 | 10.7092 | 8.6112 | 7.4459 | 7.299 | 10.3776 | 10.3755 | 10.3235 | 10.2286 | 10.0969 | 9.8673 | 9.698 | 9.4429 | 9.0051 | 8.6602 | 5.9194 | 4.0735 | 3.6408
|  | THIMBLEROW | HE |  |  |  |  | 7.6908 | 7.6949 | 7.6582 | 7.5459 | 7.4061 | 7.2071 | 6.9755 | 6.7092 | 6.3837 | 5.8929 | 4.0306 | 2.2847 | 1.9571 | 13.4031 | 13.401 | 13.3571 | 13.2786 | 13.1694 | 12.7469 | 12.1816 | 11.5969 | 11.1929 | 10.6571 | 9.1429 | 7.6653 | 7.4429 | 10.3663 | 10.3541 | 10.2959 | 10.1918 | 10.0551 | 9.8724 | 9.6571 | 9.4153 | 9.2082 | 8.6724 | 6.7735 | 5.0224 | 4.8684
|  | THIMBLEROW | FB |  |  |  |  | 7.7898 | 7.8684 | 7.9133 | 7.9092 | 7.9 | 7.85 | 7.7827 | 7.648 | 7.5653 | 7.4541 | 6.8857 | 4.8786 | 2.5102 | 13.4551 | 13.4949 | 13.5071 | 13.4969 | 13.4847 | 13.4316 | 13.3612 | 13.0653 | 12.8724 | 12.4837 | 10.8153 | 8.2816 | 5.0673 | 10.4582 | 10.5153 | 10.5408 | 10.5214 | 10.5041 | 10.4653 | 10.3969 | 10.2694 | 10.1908 | 10.0786 | 9.5102 | 6.9531 | 4.952
| TAYNUILT | TIRORAN BRIDGE | MINIMUM HEADROOM | NM 48666 28729 | YES | YES | 0 | 0.20131 | 0.19927 | 0.1962 | 0.19008 | 0.18396 | 0.17784 | 0.17273 | 0.16763 | 0.16457 | 0.16049 | 0.14824 | 0.13702 | 0.12988 | 0.19351 | 0.19147 | 0.18943 | 0.18535 | 0.18127 | 0.1782 | 0.17412 | 0.17106 | 0.16902 | 0.16596 | 0.15576 | 0.15269 | 0.15371 | 0.19639 | 0.19537 | 0.19129 | 0.18618 | 0.18108 | 0.17598 | 0.17292 | 0.16782 | 0.16476 | 0.16169 | 0.15149 | 0.14537 | 0.14027
|  | TIRORAN BRIDGE | EE |  |  |  |  | 0.20743 | 0.20233 | 0.19824 | 0.19212 | 0.18396 | 0.17988 | 0.17376 | 0.16763 | 0.16457 | 0.16049 | 0.14824 | 0.13702 | 0.13192 | 0.19963 | 0.19453 | 0.19147 | 0.18637 | 0.18127 | 0.18024 | 0.17616 | 0.1731 | 0.17004 | 0.168 | 0.15678 | 0.15473 | 0.15678 | 0.20353 | 0.19741 | 0.19333 | 0.1872 | 0.18108 | 0.17802 | 0.17292 | 0.16782 | 0.16476 | 0.16271 | 0.15149 | 0.14537 | 0.14129
|  | TIRORAN BRIDGE | HT |  |  |  |  | 0.20131 | 0.19927 | 0.1962 | 0.19008 | 0.18498 | 0.17784 | 0.17478 | 0.16967 | 0.16763 | 0.16253 | 0.15233 | 0.13906 | 0.12988 | 0.19351 | 0.19147 | 0.18943 | 0.18535 | 0.18229 | 0.1782 | 0.17412 | 0.17106 | 0.17004 | 0.16596 | 0.15576 | 0.15269 | 0.15371 | 0.19639 | 0.19537 | 0.19129 | 0.18618 | 0.18108 | 0.17598 | 0.17394 | 0.16884 | 0.1668 | 0.16169 | 0.15455 | 0.14537 | 0.14027
|  | TIRORAN BRIDGE | HE |  |  |  |  | 0.20743 | 0.20233 | 0.19824 | 0.19008 | 0.18498 | 0.17886 | 0.17273 | 0.16865 | 0.16457 | 0.16151 | 0.15335 | 0.13804 | 0.13294 | 0.19963 | 0.19453 | 0.19147 | 0.18637 | 0.18331 | 0.18024 | 0.17616 | 0.1731 | 0.16902 | 0.168 | 0.15678 | 0.15371 | 0.15473 | 0.20353 | 0.19741 | 0.19333 | 0.18618 | 0.1821 | 0.177 | 0.17292 | 0.16884 | 0.16476 | 0.16373 | 0.15455 | 0.14537 | 0.14129
|  | TIRORAN BRIDGE | FB |  |  |  |  | 0.20743 | 0.20845 | 0.20029 | 0.19722 | 0.19824 | 0.19927 | 0.19824 | 0.18804 | 0.18906 | 0.18396 | 0.17682 | 0.16355 | 0.15743 | 0.19963 | 0.20065 | 0.19249 | 0.18841 | 0.18841 | 0.18841 | 0.18739 | 0.18127 | 0.18229 | 0.1782 | 0.17106 | 0.15882 | 0.15371 | 0.20353 | 0.20455 | 0.19537 | 0.19231 | 0.19435 | 0.19435 | 0.19231 | 0.18414 | 0.18516 | 0.18006 | 0.17292 | 0.15965 | 0.15455
| BOAT OF GARTEN | TOMATIN | MINIMUM HEADROOM | NH 79106 29734 | YES | YES | 1.423 | -0.75278 | -0.75992 | -0.76809 | -0.78849 | -0.80686 | -1.0089 | -1.2273 | -1.414 | -1.4824 | -1.5344 | -1.6058 | -1.7018 | -1.765 | -0.39258 | -0.39768 | -0.40278 | -0.414 | -0.42217 | -0.57625 | -0.78033 | -0.93441 | -0.99156 | -1.0099 | -1.0395 | -1.0487 | -1.0405 | -0.58747 | -0.59462 | -0.60278 | -0.61911 | -0.63339 | -0.80686 | -1.0273 | -1.1977 | -1.2609 | -1.2854 | -1.3201 | -1.3814 | -1.4191
|  | TOMATIN | EE |  |  |  |  | -0.75278 | -0.75992 | -0.76809 | -0.78645 | -0.80278 | -0.84462 | -0.90788 | -1.1232 | -1.3242 | -1.4762 | -1.6058 | -1.7018 | -1.7558 | -0.39258 | -0.39768 | -0.40278 | -0.41298 | -0.42217 | -0.44666 | -0.48237 | -0.64156 | -0.81502 | -0.9589 | -1.0314 | -1.0487 | -1.0365 | -0.58747 | -0.59462 | -0.60278 | -0.61809 | -0.63135 | -0.66707 | -0.73237 | -0.92013 | -1.0987 | -1.2211 | -1.3201 | -1.3814 | -1.4109
|  | TOMATIN | HT |  |  |  |  | -0.75176 | -0.7589 | -0.76707 | -0.78543 | -0.80278 | -1.0089 | -1.2273 | -1.414 | -1.4824 | -1.513 | -1.5773 | -1.6671 | -1.765 | -0.39258 | -0.39666 | -0.40278 | -0.41298 | -0.42217 | -0.57625 | -0.78033 | -0.93441 | -0.99156 | -1.0099 | -1.0395 | -1.0324 | -1.0405 | -0.58747 | -0.5936 | -0.60176 | -0.61809 | -0.63033 | -0.80686 | -1.0273 | -1.1977 | -1.2609 | -1.2854 | -1.3099 | -1.3569 | -1.4191
|  | TOMATIN | HE |  |  |  |  | -0.75176 | -0.7589 | -0.76707 | -0.78849 | -0.80686 | -0.86809 | -0.92319 | -1.1477 | -1.3783 | -1.5344 | -1.5885 | -1.6936 | -1.7303 | -0.39258 | -0.39666 | -0.40278 | -0.414 | -0.42217 | -0.45176 | -0.48543 | -0.65278 | -0.85584 | -1.0028 | -1.0303 | -1.0477 | -1.0354 | -0.58747 | -0.5936 | -0.60176 | -0.61911 | -0.63339 | -0.68237 | -0.74053 | -0.93951 | -1.1211 | -1.2701 | -1.3109 | -1.3793 | -1.4018
|  | TOMATIN | FB |  |  |  |  | -0.72523 | -0.73237 | -0.73441 | -0.73849 | -0.74156 | -0.7538 | -0.80482 | -0.85686 | -0.97421 | -1.1201 | -1.3905 | -1.4507 | -1.4711 | -0.36911 | -0.37727 | -0.37931 | -0.38135 | -0.38441 | -0.39258 | -0.41911 | -0.43747 | -0.54462 | -0.69053 | -0.96911 | -1.0191 | -1.0395 | -0.56196 | -0.57115 | -0.57217 | -0.57523 | -0.57829 | -0.58849 | -0.63135 | -0.66809 | -0.77727 | -0.91298 | -1.1946 | -1.2487 | -1.2548
| LAIRG | TORBOLL | MINIMUM HEADROOM | NC 75779 00296 | YES | NO | 0 | 0.11086 | 0.11086 | 0.11086 | 0.11086 | 0.11086 | 0.098612 | 0.097592 | 0.097592 | 0.097592 | 0.097592 | 0.090449 | 0.089429 | 0.090449 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.089612 | 0.089612 | 0.089612 | 0.088592 | 0.088592 | 0.085531 | 0.08349 | 0.08451 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.094112 | 0.094112 | 0.094112 | 0.093092 | 0.093092 | 0.086969 | 0.085949 | 0.08799
|  | TORBOLL | EE |  |  |  |  | 0.11086 | 0.11086 | 0.11086 | 0.11086 | 0.11086 | 0.098612 | 0.097592 | 0.097592 | 0.098612 | 0.098612 | 0.091469 | 0.089429 | 0.091469 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.089612 | 0.089612 | 0.089612 | 0.090633 | 0.089612 | 0.085531 | 0.086551 | 0.089612 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.094112 | 0.094112 | 0.094112 | 0.094112 | 0.093092 | 0.086969 | 0.085949 | 0.08901
|  | TORBOLL | HT |  |  |  |  | 0.11086 | 0.11086 | 0.11086 | 0.11086 | 0.11086 | 0.098612 | 0.097592 | 0.097592 | 0.098612 | 0.098612 | 0.090449 | 0.090449 | 0.090449 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.089612 | 0.089612 | 0.089612 | 0.090633 | 0.089612 | 0.085531 | 0.085531 | 0.088592 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.094112 | 0.094112 | 0.094112 | 0.094112 | 0.094112 | 0.086969 | 0.085949 | 0.08799
|  | TORBOLL | HE |  |  |  |  | 0.11086 | 0.11086 | 0.11086 | 0.11086 | 0.11086 | 0.098612 | 0.097592 | 0.097592 | 0.098612 | 0.098612 | 0.091469 | 0.091469 | 0.090449 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.089612 | 0.089612 | 0.089612 | 0.090633 | 0.089612 | 0.085531 | 0.086551 | 0.086551 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.094112 | 0.094112 | 0.094112 | 0.094112 | 0.093092 | 0.08799 | 0.086969 | 0.08799
|  | TORBOLL | FB |  |  |  |  | 0.11086 | 0.11086 | 0.11086 | 0.11086 | 0.11086 | 0.11086 | 0.11188 | 0.11188 | 0.097592 | 0.097592 | 0.098612 | 0.09249 | 0.09351 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.088592 | 0.088592 | 0.089612 | 0.08349 | 0.08451 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.10738 | 0.093092 | 0.093092 | 0.094112 | 0.08901 | 0.08901
| KINTORE | TORRYBURN | MINIMUM HEADROOM | NJ 79129 15653 | NO | YES | 2.421 | 10.8307 | 10.4736 | 10.0532 | 9.4103 | 9.0144 | 8.4777 | 7.5287 | 6.4195 | 4.194 | 3.3144 | 0.16237 | -3.3519 | -6.6693 | 11.7164 | 11.3328 | 10.896 | 10.2838 | 9.8838 | 9.3583 | 8.3624 | 7.1348 | 4.494 | 3.6562 | 0.049102 | -4.1948 | -8.2315 | 11.3205 | 10.9573 | 10.546 | 9.9562 | 9.5981 | 9.1022 | 8.1226 | 6.8828 | 4.243 | 3.3256 | -0.19069 | -4.4458 | -8.5101
|  | TORRYBURN | EE |  |  |  |  | 10.9103 | 10.4736 | 10.0828 | 9.4634 | 9.0726 | 8.4777 | 7.5848 | 6.7858 | 5.5491 | 4.9185 | 2.8113 | -0.60702 | -2.0723 | 11.8032 | 11.3328 | 10.9164 | 10.3236 | 9.9256 | 9.3613 | 8.4246 | 7.5705 | 6.1767 | 5.6562 | 3.394 | -0.73967 | -2.558 | 11.4001 | 10.9573 | 10.5746 | 10.0073 | 9.6542 | 9.1022 | 8.1858 | 7.3236 | 5.9297 | 5.3338 | 3.1532 | -0.90294 | -2.7387
|  | TORRYBURN | HT |  |  |  |  | 10.8613 | 10.4807 | 10.0532 | 9.4103 | 9.0144 | 8.7073 | 7.8603 | 6.9675 | 5.3624 | 4.3695 | 1.9532 | -1.8652 | -5.0795 | 11.7501 | 11.342 | 10.896 | 10.2838 | 9.8838 | 9.6216 | 8.7022 | 7.7501 | 5.9052 | 5.0022 | 2.3818 | -2.3213 | -6.2682 | 11.3511 | 10.9664 | 10.546 | 9.9562 | 9.5981 | 9.3328 | 8.4093 | 7.446 | 5.6134 | 4.6542 | 2.1409 | -2.4938 | -6.4468
|  | TORRYBURN | HE |  |  |  |  | 10.8307 | 10.4746 | 10.0716 | 9.445 | 9.0522 | 8.4787 | 7.5287 | 6.4195 | 4.194 | 3.3144 | 0.16237 | -3.3519 | -6.6693 | 11.7164 | 11.3328 | 10.9103 | 10.3083 | 9.9113 | 9.3583 | 8.3624 | 7.1348 | 4.494 | 3.6562 | 0.049102 | -4.1948 | -8.2315 | 11.3205 | 10.9583 | 10.5644 | 9.9889 | 9.6358 | 9.1042 | 8.1226 | 6.8828 | 4.243 | 3.3256 | -0.19069 | -4.4458 | -8.5101
|  | TORRYBURN | FB |  |  |  |  | 11.192 | 10.8318 | 10.4522 | 10.0226 | 9.7246 | 9.2899 | 8.5838 | 7.7358 | 6.8318 | 6.2848 | 5.0971 | 3.7216 | 2.9756 | 12.096 | 11.6971 | 11.2889 | 10.8664 | 10.543 | 10.1175 | 9.3593 | 8.4522 | 7.4216 | 6.9093 | 5.7164 | 4.2256 | 3.3644 | 11.6746 | 11.3124 | 10.9338 | 10.5236 | 10.2338 | 9.8195 | 9.0879 | 8.194 | 7.1471 | 6.594 | 5.4338 | 3.796 | 3.2001
| LAIRG | TRESSADY | MINIMUM HEADROOM | NC 70537 03678 | YES | NO | 0.003 | 0.23694 | 0.23184 | 0.22673 | 0.20531 | 0.19306 | 0.15939 | 0.13184 | 0.097143 | 0.095102 | 0.06551 | -0.0079592 | -0.076327 | -0.14673 | 0.31745 | 0.31337 | 0.30724 | 0.29704 | 0.29398 | 0.27969 | 0.25622 | 0.24602 | 0.23378 | 0.21235 | 0.15724 | 0.16133 | 0.17051 | 0.2726 | 0.26648 | 0.26036 | 0.24199 | 0.23383 | 0.20423 | 0.17872 | 0.15526 | 0.13587 | 0.10934 | 0.049133 | 0.034847 | -0.0029082
|  | TRESSADY | EE |  |  |  |  | 0.23694 | 0.23184 | 0.22776 | 0.21449 | 0.20224 | 0.16449 | 0.13184 | 0.10633 | 0.10122 | 0.073673 | -0.0079592 | -0.076327 | -0.14673 | 0.31745 | 0.31337 | 0.30724 | 0.29806 | 0.295 | 0.27969 | 0.25724 | 0.24602 | 0.2348 | 0.21235 | 0.16847 | 0.17357 | 0.17051 | 0.2726 | 0.26648 | 0.26138 | 0.24709 | 0.23995 | 0.2073 | 0.17872 | 0.15832 | 0.13995 | 0.11648 | 0.049133 | 0.034847 | -0.0029082
|  | TRESSADY | HT |  |  |  |  | 0.24102 | 0.23286 | 0.22673 | 0.21245 | 0.20224 | 0.17265 | 0.1349 | 0.11041 | 0.10531 | 0.077755 | 0.0093878 | -0.05898 | -0.13857 | 0.32051 | 0.31439 | 0.30724 | 0.29806 | 0.295 | 0.28071 | 0.25622 | 0.24602 | 0.23582 | 0.21235 | 0.15724 | 0.16133 | 0.17663 | 0.27566 | 0.2675 | 0.26036 | 0.24709 | 0.23995 | 0.2124 | 0.18179 | 0.16138 | 0.14301 | 0.11954 | 0.059337 | 0.04199 | 0.0062755
|  | TRESSADY | HE |  |  |  |  | 0.24102 | 0.23286 | 0.22673 | 0.20531 | 0.19306 | 0.15939 | 0.13694 | 0.097143 | 0.095102 | 0.06551 | 0.013469 | -0.069184 | -0.12633 | 0.32051 | 0.31439 | 0.30724 | 0.29704 | 0.29398 | 0.27969 | 0.26847 | 0.24602 | 0.23378 | 0.21235 | 0.16847 | 0.17153 | 0.17561 | 0.27566 | 0.2675 | 0.26036 | 0.24199 | 0.23383 | 0.20423 | 0.18791 | 0.15526 | 0.13587 | 0.10934 | 0.064439 | 0.038929 | 0.0021939
|  | TRESSADY | FB |  |  |  |  | 0.25735 | 0.25429 | 0.25327 | 0.24816 | 0.25429 | 0.2451 | 0.23796 | 0.23184 | 0.21857 | 0.19816 | 0.14306 | 0.066531 | 0.067551 | 0.3348 | 0.32663 | 0.32459 | 0.31949 | 0.32357 | 0.31235 | 0.31031 | 0.30214 | 0.29194 | 0.27663 | 0.245 | 0.18276 | 0.19092 | 0.29301 | 0.28587 | 0.28281 | 0.27872 | 0.28281 | 0.27158 | 0.26852 | 0.25934 | 0.24607 | 0.23281 | 0.18383 | 0.12464 | 0.1175
| SHETLAND | TUMBLIN | MINIMUM HEADROOM | HU3334053363 | YES | YES | 0.036 | 5.0331 | 5.0341 | 5.0218 | 4.9637 | 4.8616 | 4.7576 | 4.6259 | 4.5004 | 4.3657 | 4.2739 | 4.0504 | 3.7861 | 3.581 | 5.3849 | 5.3869 | 5.3727 | 5.3553 | 5.3227 | 5.2869 | 5.1931 | 5.1227 | 5.0553 | 4.9624 | 4.8859 | 4.8869 | 4.8696 | 5.3131 | 5.309 | 5.2927 | 5.2233 | 5.1478 | 5.0794 | 4.9651 | 4.8702 | 4.7753 | 4.6876 | 4.5743 | 4.4131 | 4.2947
|  | TUMBLIN | EE |  |  |  |  | 5.0341 | 5.0351 | 5.0239 | 4.9729 | 4.8729 | 4.7667 | 4.6259 | 4.5004 | 4.3657 | 4.2739 | 4.0504 | 3.7861 | 3.5943 | 5.3869 | 5.3869 | 5.3747 | 5.3563 | 5.3237 | 5.2869 | 5.1931 | 5.1227 | 5.0553 | 4.9624 | 4.9237 | 4.9267 | 4.9645 | 5.3151 | 5.31 | 5.2947 | 5.2284 | 5.1569 | 5.0835 | 4.9651 | 4.8702 | 4.7753 | 4.6876 | 4.5743 | 4.4131 | 4.3049
|  | TUMBLIN | HT |  |  |  |  | 5.0331 | 5.0371 | 5.0259 | 4.9841 | 4.8861 | 4.7892 | 4.6504 | 4.5341 | 4.4208 | 4.3147 | 4.1606 | 3.8545 | 3.581 | 5.3849 | 5.3869 | 5.3737 | 5.3573 | 5.3257 | 5.288 | 5.1961 | 5.1257 | 5.0584 | 4.9645 | 4.8859 | 4.8869 | 4.9308 | 5.3131 | 5.312 | 5.2967 | 5.2386 | 5.1651 | 5.0947 | 4.9835 | 4.8916 | 4.8029 | 4.7151 | 4.6233 | 4.4549 | 4.2947
|  | TUMBLIN | HE |  |  |  |  | 5.0331 | 5.0341 | 5.0218 | 4.9637 | 4.8616 | 4.7576 | 4.628 | 4.5086 | 4.3861 | 4.2861 | 4.1576 | 3.8422 | 3.631 | 5.3849 | 5.3869 | 5.3727 | 5.3553 | 5.3227 | 5.289 | 5.1961 | 5.1247 | 5.0573 | 4.9635 | 4.9278 | 4.9073 | 4.9114 | 5.3131 | 5.309 | 5.2927 | 5.2233 | 5.1478 | 5.0794 | 4.9682 | 4.8753 | 4.7845 | 4.6957 | 4.6416 | 4.4406 | 4.312
|  | TUMBLIN | FB |  |  |  |  | 5.0759 | 5.0984 | 5.1096 | 5.1167 | 5.1137 | 5.1014 | 5.0586 | 5.0106 | 4.9933 | 4.9402 | 4.732 | 4.6137 | 4.5392 | 5.4267 | 5.4369 | 5.438 | 5.44 | 5.4329 | 5.4186 | 5.3869 | 5.3502 | 5.3308 | 5.2931 | 5.089 | 4.99 | 4.8696 | 5.3569 | 5.3712 | 5.3773 | 5.3722 | 5.3508 | 5.3335 | 5.3008 | 5.2569 | 5.2416 | 5.1957 | 5.009 | 4.9008 | 4.8702
| TUMMEL BRIDGE | TUMMEL BRIDGE | MINIMUM HEADROOM | NN 75906 59080 | YES | YES | 0.15 | -0.42959 | -0.43571 | -0.45102 | -0.47143 | -0.50408 | -0.5398 | -0.56531 | -0.5949 | -0.63469 | -0.66735 | -0.73469 | -0.91939 | -0.93061 | -0.43469 | -0.44184 | -0.45816 | -0.47449 | -0.50204 | -0.53469 | -0.55204 | -0.57449 | -0.60612 | -0.6398 | -0.70816 | -0.85612 | -0.83061 | -0.43265 | -0.43673 | -0.45102 | -0.47041 | -0.5 | -0.53469 | -0.55612 | -0.58163 | -0.61735 | -0.65408 | -0.72449 | -0.88163 | -0.87959
|  | TUMMEL BRIDGE | EE |  |  |  |  | -0.42959 | -0.43469 | -0.45102 | -0.47041 | -0.50102 | -0.5398 | -0.56429 | -0.5949 | -0.63265 | -0.6602 | -0.73469 | -0.91122 | -0.91531 | -0.43469 | -0.44184 | -0.45816 | -0.47347 | -0.50102 | -0.53469 | -0.55204 | -0.57449 | -0.60612 | -0.6398 | -0.69388 | -0.83878 | -0.81735 | -0.43265 | -0.43469 | -0.45102 | -0.46939 | -0.49796 | -0.53469 | -0.55408 | -0.58163 | -0.61633 | -0.65204 | -0.71939 | -0.87245 | -0.86531
|  | TUMMEL BRIDGE | HT |  |  |  |  | -0.42857 | -0.43469 | -0.45 | -0.47041 | -0.5 | -0.52143 | -0.5602 | -0.58878 | -0.62755 | -0.66735 | -0.73469 | -0.91939 | -0.93061 | -0.43367 | -0.44184 | -0.45816 | -0.47449 | -0.50204 | -0.51735 | -0.55102 | -0.57347 | -0.60612 | -0.6398 | -0.70816 | -0.85612 | -0.83061 | -0.43163 | -0.43469 | -0.45 | -0.46939 | -0.49694 | -0.51531 | -0.55306 | -0.57857 | -0.61224 | -0.64796 | -0.72449 | -0.88163 | -0.87959
|  | TUMMEL BRIDGE | HE |  |  |  |  | -0.42857 | -0.43571 | -0.45 | -0.47143 | -0.50408 | -0.52653 | -0.56531 | -0.59388 | -0.63469 | -0.66224 | -0.72449 | -0.91224 | -0.77551 | -0.43367 | -0.44184 | -0.45816 | -0.47449 | -0.50204 | -0.51837 | -0.55102 | -0.57347 | -0.60612 | -0.6398 | -0.69286 | -0.84694 | -0.68878 | -0.43163 | -0.43673 | -0.45102 | -0.47041 | -0.5 | -0.51837 | -0.55612 | -0.58163 | -0.61735 | -0.65408 | -0.71327 | -0.87653 | -0.72857
|  | TUMMEL BRIDGE | FB |  |  |  |  | -0.41122 | -0.41735 | -0.42551 | -0.44286 | -0.45816 | -0.46633 | -0.47755 | -0.49592 | -0.50102 | -0.52041 | -0.59592 | -0.65306 | -0.67143 | -0.41837 | -0.42551 | -0.43469 | -0.45306 | -0.47143 | -0.47959 | -0.49184 | -0.51122 | -0.51531 | -0.53469 | -0.60306 | -0.65306 | -0.67143 | -0.41327 | -0.41939 | -0.42755 | -0.44388 | -0.46224 | -0.46939 | -0.48061 | -0.49898 | -0.50204 | -0.52143 | -0.5898 | -0.65306 | -0.6602
| MACDUFF | TURRIFF | MINIMUM HEADROOM | NJ 72407 50271 | NO | NO | 0.933 | 4.2592 | 4.0327 | 3.8265 | 3.5143 | 2.75 | 1.7357 | 0.66122 | -0.010204 | -0.63367 | -1.1837 | -4.1092 | -5.5633 | -6.5337 | 7.1786 | 6.8 | 6.6918 | 6.5194 | 5.8276 | 5.102 | 4.3153 | 3.9786 | 3.6388 | 3.2531 | 1.2694 | 0.95918 | 0.62041 | 5.4444 | 5.076 | 4.9444 | 4.6985 | 3.9852 | 3.0913 | 2.1383 | 1.5801 | 1.1026 | 0.65867 | -1.8362 | -2.8291 | -3.4342
|  | TURRIFF | EE |  |  |  |  | 4.2939 | 4.0327 | 3.8265 | 3.5143 | 2.75 | 1.7357 | 0.66122 | 0.005102 | -0.61633 | -1.1837 | -4.1092 | -5.5633 | -6.5041 | 7.2184 | 6.801 | 6.6918 | 6.5194 | 5.8276 | 5.102 | 4.3153 | 3.9847 | 3.6388 | 3.2531 | 1.3133 | 0.95918 | 0.76939 | 5.473 | 5.076 | 4.9444 | 4.6985 | 3.9862 | 3.0913 | 2.1444 | 1.5883 | 1.1107 | 0.65867 | -1.8362 | -2.8291 | -3.424
|  | TURRIFF | HT |  |  |  |  | 4.2724 | 4.0398 | 3.8418 | 3.5337 | 2.7653 | 2.3582 | 1.6684 | 0.93776 | 0.04898 | -1.1112 | -3.8949 | -5.4 | -6.5337 | 7.1949 | 6.8061 | 6.6929 | 6.5204 | 5.8276 | 5.6173 | 5.2673 | 4.8969 | 4.2816 | 3.3102 | 1.2694 | 1.001 | 0.92551 | 5.4546 | 5.0821 | 4.9546 | 4.7138 | 3.9944 | 3.6495 | 3.1219 | 2.5638 | 1.8066 | 0.74235 | -1.7138 | -2.7179 | -3.4342
|  | TURRIFF | HE |  |  |  |  | 4.2592 | 4.0337 | 3.8357 | 3.5184 | 2.75 | 1.7418 | 0.66531 | -0.010204 | -0.63367 | -1.1602 | -3.6408 | -4.951 | -5.7276 | 7.1786 | 6.8 | 6.6929 | 6.5214 | 5.8296 | 5.1112 | 4.3153 | 3.9786 | 3.6398 | 3.3061 | 1.5857 | 1.3633 | 1.1918 | 5.4444 | 5.076 | 4.9495 | 4.7046 | 3.9852 | 3.0995 | 2.1383 | 1.5801 | 1.1026 | 0.6852 | -1.4781 | -2.3474 | -2.8515
|  | TURRIFF | FB |  |  |  |  | 4.4541 | 4.2469 | 4.1082 | 3.949 | 3.5378 | 2.9041 | 2.1347 | 1.2561 | 1.1357 | 1.0296 | -0.20204 | -2.1439 | -3.0592 | 7.3592 | 6.9551 | 6.8735 | 6.7653 | 6.401 | 5.9378 | 5.1714 | 4.2827 | 4.2112 | 4.149 | 3.2837 | 1.5827 | 0.62041 | 5.6413 | 5.2934 | 5.1913 | 5.0832 | 4.7209 | 4.2046 | 3.5454 | 2.7117 | 2.6301 | 2.5607 | 1.2893 | -0.58214 | -1.2066
| RANNOCH | TYNDRUM | MINIMUM HEADROOM | NN 32894 30860 | YES | YES | 0.476 | 0.49041 | 0.49551 | 0.49959 | 0.49857 | 0.49755 | 0.49653 | 0.49449 | 0.48531 | 0.47612 | 0.47816 | 0.45571 | 0.45061 | 0.44653 | 0.4751 | 0.4751 | 0.47204 | 0.46694 | 0.46184 | 0.45673 | 0.44755 | 0.4302 | 0.41592 | 0.41286 | 0.38122 | 0.37408 | 0.35571 | 0.57306 | 0.5751 | 0.57204 | 0.56592 | 0.5598 | 0.55673 | 0.54755 | 0.53429 | 0.52408 | 0.52102 | 0.48735 | 0.4802 | 0.4802
|  | TYNDRUM | EE |  |  |  |  | 0.49041 | 0.49551 | 0.49959 | 0.49959 | 0.49857 | 0.49959 | 0.49857 | 0.48939 | 0.4802 | 0.48224 | 0.46388 | 0.45673 | 0.45265 | 0.4751 | 0.4751 | 0.47204 | 0.46898 | 0.46388 | 0.45878 | 0.45061 | 0.43327 | 0.41796 | 0.41694 | 0.39041 | 0.38122 | 0.37918 | 0.57306 | 0.5751 | 0.57306 | 0.56694 | 0.56184 | 0.55776 | 0.55061 | 0.53837 | 0.52714 | 0.5251 | 0.49857 | 0.48735 | 0.48735
|  | TYNDRUM | HT |  |  |  |  | 0.49041 | 0.49551 | 0.49959 | 0.49857 | 0.49755 | 0.49653 | 0.49449 | 0.48531 | 0.47612 | 0.47816 | 0.45571 | 0.45061 | 0.44653 | 0.4751 | 0.4751 | 0.47204 | 0.46694 | 0.46184 | 0.45673 | 0.44755 | 0.4302 | 0.41592 | 0.41286 | 0.38122 | 0.37408 | 0.38122 | 0.57306 | 0.5751 | 0.57204 | 0.56592 | 0.5598 | 0.55673 | 0.54755 | 0.53429 | 0.52408 | 0.52102 | 0.48735 | 0.4802 | 0.48224
|  | TYNDRUM | HE |  |  |  |  | 0.49041 | 0.49551 | 0.49959 | 0.49959 | 0.49959 | 0.49959 | 0.49755 | 0.49041 | 0.48122 | 0.48327 | 0.4649 | 0.45673 | 0.44755 | 0.4751 | 0.4751 | 0.47204 | 0.46898 | 0.46388 | 0.45878 | 0.45163 | 0.43327 | 0.41898 | 0.41796 | 0.39143 | 0.37918 | 0.36796 | 0.57306 | 0.5751 | 0.57306 | 0.56694 | 0.56082 | 0.55878 | 0.55061 | 0.53939 | 0.52816 | 0.52612 | 0.49857 | 0.48837 | 0.4802
|  | TYNDRUM | FB |  |  |  |  | 0.49653 | 0.50265 | 0.50776 | 0.51286 | 0.51592 | 0.51592 | 0.51184 | 0.50776 | 0.51184 | 0.50571 | 0.49857 | 0.47816 | 0.4649 | 0.48531 | 0.48531 | 0.48429 | 0.48327 | 0.48429 | 0.48122 | 0.47408 | 0.4649 | 0.46388 | 0.45265 | 0.4302 | 0.38531 | 0.35571 | 0.57816 | 0.5802 | 0.5802 | 0.58224 | 0.58224 | 0.57816 | 0.57408 | 0.56898 | 0.56796 | 0.56184 | 0.54653 | 0.50367 | 0.49449
| DUNVEGAN | UIG | MINIMUM HEADROOM | NG 39131 64412 | YES | NO | 1.131 | 1.2023 | 1.1839 | 1.1645 | 1.1023 | 1.0635 | 0.82778 | 0.55738 | 0.32676 | 0.20431 | 0.11146 | -0.21813 | -0.44977 | -0.64569 | 1.113 | 1.1048 | 1.0987 | 1.0875 | 1.0752 | 0.92829 | 0.77421 | 0.62931 | 0.54972 | 0.51401 | 0.39054 | 0.39768 | 0.33238 | 1.1326 | 1.1204 | 1.1112 | 1.0775 | 1.0388 | 0.88161 | 0.68263 | 0.49998 | 0.38773 | 0.32753 | 0.096916 | -0.01839 | -0.14084
|  | UIG | EE |  |  |  |  | 1.2023 | 1.1839 | 1.1645 | 1.1064 | 1.0706 | 0.94819 | 0.84819 | 0.60227 | 0.33901 | 0.15023 | -0.21813 | -0.44977 | -0.61916 | 1.113 | 1.1048 | 1.0987 | 1.0875 | 1.0752 | 1.0252 | 0.9987 | 0.84666 | 0.66605 | 0.55278 | 0.40687 | 0.40993 | 0.42931 | 1.1326 | 1.1204 | 1.1112 | 1.0775 | 1.0428 | 0.97753 | 0.91426 | 0.71937 | 0.50304 | 0.36426 | 0.096916 | -0.01839 | -0.11941
|  | UIG | HT |  |  |  |  | 1.2023 | 1.1849 | 1.1666 | 1.1074 | 1.0717 | 0.82778 | 0.55738 | 0.32676 | 0.20431 | 0.11146 | -0.12426 | -0.3916 | -0.64569 | 1.113 | 1.1048 | 1.0987 | 1.0875 | 1.0752 | 0.92829 | 0.77421 | 0.62931 | 0.54972 | 0.51401 | 0.39054 | 0.39768 | 0.43646 | 1.1326 | 1.1204 | 1.1122 | 1.0785 | 1.0449 | 0.88161 | 0.68263 | 0.49998 | 0.38773 | 0.32753 | 0.13467 | 0.0071204 | -0.14084
|  | UIG | HE |  |  |  |  | 1.2023 | 1.1849 | 1.1655 | 1.1023 | 1.0635 | 0.94921 | 0.85125 | 0.59003 | 0.31146 | 0.11146 | -0.13038 | -0.40283 | -0.56507 | 1.115 | 1.1048 | 1.0987 | 1.0885 | 1.0763 | 1.0273 | 0.9987 | 0.83442 | 0.63952 | 0.52421 | 0.41299 | 0.40278 | 0.37625 | 1.1347 | 1.1204 | 1.1122 | 1.0775 | 1.0388 | 0.98059 | 0.91426 | 0.71018 | 0.47447 | 0.32957 | 0.14079 | -0.0051245 | -0.11227
|  | UIG | FB |  |  |  |  | 1.2257 | 1.2329 | 1.2421 | 1.2339 | 1.2237 | 1.2064 | 1.1859 | 1.1696 | 1.039 | 0.87778 | 0.50738 | 0.36656 | 0.3288 | 1.1405 | 1.1405 | 1.1528 | 1.1426 | 1.1456 | 1.1293 | 1.1028 | 1.0895 | 0.9834 | 0.85482 | 0.58136 | 0.41401 | 0.33238 | 1.1643 | 1.1745 | 1.1877 | 1.1826 | 1.1816 | 1.1643 | 1.1398 | 1.1265 | 1.0214 | 0.89386 | 0.58977 | 0.4459 | 0.43569
| GRUDIE BRIDGE | ULLAPOOL | MINIMUM HEADROOM | NH 13018 94588 | NO | NO | 0.139 | -1.0449 | -1.0378 | 3.0806 | 3.0469 | 3.0061 | 2.5582 | 2.0755 | 1.6184 | 1.3469 | 1.3255 | 1.1531 | 0.9949 | 0.8449 | -0.6398 | -0.63469 | 3.5276 | 3.5235 | 3.501 | 3.1439 | 2.6857 | 2.2531 | 2.0122 | 1.9969 | 1.9327 | 1.9255 | 1.9316 | -0.67245 | -0.66327 | 3.5622 | 3.5245 | 3.4204 | 3.0765 | 2.6245 | 2.1969 | 1.9531 | 1.9306 | 1.8184 | 1.7092 | 1.6184
|  | ULLAPOOL | EE |  |  |  |  | -1.0449 | -1.0378 | 3.0806 | 3.048 | 3.0102 | 2.9235 | 2.8898 | 2.4602 | 1.9724 | 1.5357 | 1.1531 | 0.9949 | 0.88163 | -0.63878 | -0.63469 | 3.5276 | 3.5245 | 3.5041 | 3.4806 | 3.4398 | 3.1163 | 2.649 | 2.2133 | 1.9388 | 1.9286 | 1.9439 | -0.67245 | -0.66327 | 3.5622 | 3.5265 | 3.4235 | 3.3643 | 3.3265 | 2.999 | 2.5622 | 2.1367 | 1.8184 | 1.7092 | 1.6357
|  | ULLAPOOL | HT |  |  |  |  | -1.0439 | -1.0367 | 3.0806 | 3.0469 | 3.0061 | 2.5582 | 2.0755 | 1.6184 | 1.3469 | 1.3255 | 1.1857 | 1.0041 | 0.8449 | -0.6398 | -0.63469 | 3.5276 | 3.5235 | 3.501 | 3.1439 | 2.6857 | 2.2531 | 2.0122 | 1.9969 | 1.9327 | 1.9255 | 1.9316 | -0.67245 | -0.66224 | 3.5622 | 3.5245 | 3.4204 | 3.0765 | 2.6245 | 2.1969 | 1.9531 | 1.9306 | 1.8408 | 1.7184 | 1.6184
|  | ULLAPOOL | HE |  |  |  |  | -1.0439 | -1.0367 | 3.0806 | 3.05 | 3.0153 | 2.9398 | 2.8847 | 2.4082 | 1.8684 | 1.3796 | 1.1806 | 1.0122 | 0.9051 | -0.6398 | -0.63469 | 3.5276 | 3.5235 | 3.5031 | 3.4816 | 3.4388 | 3.0704 | 2.5531 | 2.0745 | 1.9459 | 1.9418 | 1.9418 | -0.67245 | -0.66327 | 3.5622 | 3.5276 | 3.4255 | 3.3755 | 3.3255 | 2.9602 | 2.4653 | 1.998 | 1.8398 | 1.7184 | 1.6439
|  | ULLAPOOL | FB |  |  |  |  | -1.0255 | -1.0092 | 3.1459 | 3.1173 | 3.1296 | 3.1265 | 3.1143 | 3.1082 | 2.7908 | 2.4357 | 1.5796 | 1.452 | 1.401 | -0.61633 | -0.60918 | 3.5755 | 3.5694 | 3.5724 | 3.5673 | 3.55 | 3.5388 | 3.2724 | 2.9163 | 2.0602 | 1.9786 | 1.9592 | -0.64184 | -0.62755 | 3.6367 | 3.6173 | 3.5204 | 3.5122 | 3.4959 | 3.4878 | 3.2296 | 2.8816 | 2.0622 | 1.9459 | 1.9327
| SHETLAND | UNST | MINIMUM HEADROOM | HP6398113411 | YES | YES | 0.639 | 0.14041 | 0.12816 | 0.12612 | 0.086327 | 0.056735 | -0.0034694 | -0.065714 | -0.14122 | -0.20551 | -0.23306 | -0.33102 | -0.40449 | -0.49327 | 0.064898 | 0.061837 | 0.056735 | 0.037347 | 0.0036735 | -0.038163 | -0.072857 | -0.12898 | -0.17796 | -0.19429 | -0.31776 | -0.31776 | -0.30653 | -0.28816 | -0.29224 | -0.29837 | -0.32796 | -0.37082 | -0.42286 | -0.44633 | -0.50653 | -0.56163 | -0.57592 | -0.6749 | -0.71571 | -0.73612
|  | UNST | EE |  |  |  |  | 0.14449 | 0.13837 | 0.12612 | 0.087347 | 0.059796 | -0.0034694 | -0.065714 | -0.14122 | -0.20551 | -0.23306 | -0.32694 | -0.40449 | -0.47286 | 0.066939 | 0.067959 | 0.056735 | 0.037347 | 0.0036735 | -0.038163 | -0.072857 | -0.12898 | -0.17796 | -0.19429 | -0.29429 | -0.29224 | -0.27082 | -0.2851 | -0.28714 | -0.29837 | -0.32796 | -0.37082 | -0.42286 | -0.44633 | -0.50653 | -0.56163 | -0.57592 | -0.6698 | -0.70041 | -0.71265
|  | UNST | HT |  |  |  |  | 0.14551 | 0.13939 | 0.12714 | 0.091429 | 0.065918 | 0.0077551 | -0.046327 | -0.11571 | -0.17592 | -0.20143 | -0.33102 | -0.40143 | -0.49327 | 0.066939 | 0.066939 | 0.057755 | 0.037347 | 0.0057143 | -0.038163 | -0.070816 | -0.12796 | -0.17694 | -0.19122 | -0.31776 | -0.31776 | -0.29327 | -0.2851 | -0.28612 | -0.29735 | -0.32592 | -0.36673 | -0.41673 | -0.43816 | -0.49531 | -0.54939 | -0.56265 | -0.6749 | -0.71571 | -0.7351
|  | UNST | HE |  |  |  |  | 0.14041 | 0.12816 | 0.12714 | 0.086327 | 0.056735 | -0.0014286 | -0.058571 | -0.13204 | -0.19429 | -0.22286 | -0.31163 | -0.40347 | -0.48 | 0.064898 | 0.061837 | 0.058776 | 0.037347 | 0.0057143 | -0.038163 | -0.069796 | -0.12694 | -0.17694 | -0.1902 | -0.29122 | -0.30449 | -0.30653 | -0.28816 | -0.29224 | -0.29735 | -0.32796 | -0.37082 | -0.42082 | -0.44327 | -0.50245 | -0.55653 | -0.57082 | -0.65857 | -0.70653 | -0.73612
|  | UNST | FB |  |  |  |  | 0.17918 | 0.18429 | 0.19143 | 0.19041 | 0.17918 | 0.1751 | 0.15469 | 0.13939 | 0.11286 | 0.10367 | -0.00040816 | -0.12796 | -0.16265 | 0.083265 | 0.088367 | 0.093469 | 0.087347 | 0.07102 | 0.064898 | 0.040408 | 0.024082 | -0.0055102 | -0.017755 | -0.1249 | -0.25347 | -0.29837 | -0.26571 | -0.25959 | -0.25347 | -0.25857 | -0.27082 | -0.2749 | -0.29122 | -0.30143 | -0.3249 | -0.33 | -0.41776 | -0.54429 | -0.56163
| SHETLAND | VOE | MINIMUM HEADROOM | HU4117663079 | YES | YES | 0.196 | 6.241 | 6.2502 | 6.2329 | 6.1176 | 6.0012 | 5.8686 | 5.6737 | 5.4594 | 5.2655 | 5.1849 | 4.8237 | 4.5043 | 4.2573 | 6.5394 | 6.5496 | 6.5455 | 6.5139 | 6.5027 | 6.4506 | 6.3771 | 6.2873 | 6.2078 | 6.2476 | 5.9435 | 5.9506 | 5.8139 | 6.0749 | 6.081 | 6.0667 | 5.9953 | 5.9218 | 5.8361 | 5.7014 | 5.5514 | 5.4178 | 5.3596 | 5.0861 | 4.9055 | 4.7657
|  | VOE | EE |  |  |  |  | 6.2431 | 6.2502 | 6.2329 | 6.1278 | 6.0145 | 5.8737 | 5.6778 | 5.4716 | 5.2716 | 5.1931 | 4.8237 | 4.5043 | 4.2808 | 6.5414 | 6.5506 | 6.5455 | 6.5139 | 6.5027 | 6.4527 | 6.3792 | 6.2904 | 6.2078 | 6.2527 | 6.0027 | 6.0047 | 6.0578 | 6.0759 | 6.081 | 6.0667 | 6.0035 | 5.931 | 5.8412 | 5.7024 | 5.5576 | 5.4198 | 5.3657 | 5.0861 | 4.9055 | 4.7943
|  | VOE | HT |  |  |  |  | 6.241 | 6.2543 | 6.24 | 6.14 | 6.0329 | 5.888 | 5.6951 | 5.4941 | 5.3104 | 5.2369 | 4.9533 | 4.5747 | 4.2573 | 6.5394 | 6.5496 | 6.5465 | 6.5149 | 6.5037 | 6.4506 | 6.3771 | 6.2873 | 6.2088 | 6.2496 | 5.9435 | 5.9506 | 6.0139 | 6.0749 | 6.0831 | 6.0698 | 6.0086 | 5.9382 | 5.8473 | 5.7127 | 5.5708 | 5.4433 | 5.3892 | 5.1422 | 4.928 | 4.7657
|  | VOE | HE |  |  |  |  | 6.2431 | 6.2502 | 6.2349 | 6.1176 | 6.0012 | 5.8686 | 5.6737 | 5.4594 | 5.2655 | 5.1849 | 4.942 | 4.5349 | 4.3033 | 6.5414 | 6.5506 | 6.5486 | 6.5139 | 6.5037 | 6.4527 | 6.3792 | 6.2884 | 6.2108 | 6.2476 | 6.0037 | 5.9771 | 5.9792 | 6.0759 | 6.081 | 6.0688 | 5.9953 | 5.9218 | 5.8361 | 5.7014 | 5.5514 | 5.4178 | 5.3596 | 5.1555 | 4.9167 | 4.7912
|  | VOE | FB |  |  |  |  | 6.3369 | 6.3655 | 6.3869 | 6.389 | 6.3829 | 6.3594 | 6.3461 | 6.3349 | 6.3278 | 6.2971 | 6.088 | 5.7951 | 5.7033 | 6.5935 | 6.6169 | 6.6353 | 6.6414 | 6.6424 | 6.6108 | 6.5935 | 6.5486 | 6.5118 | 6.4761 | 6.3404 | 6.0006 | 5.8139 | 6.1371 | 6.1657 | 6.1861 | 6.1922 | 6.1902 | 6.1678 | 6.1596 | 6.1504 | 6.1208 | 6.0933 | 5.9463 | 5.6524 | 5.6157
| DUDHOPE | WALTON | MINIMUM HEADROOM | NO 38995 30333 | NO | NO | 0.673 | 17.5278 | 17.4104 | 17.1951 | 17.0309 | 16.6972 | 16.2207 | 14.6186 | 13.1788 | 10.6196 | 9.9604 | 6.0135 | -3.3814 | -10.2702 | 18.3482 | 18.2645 | 18.0758 | 17.9156 | 17.5135 | 17.0288 | 15.1064 | 13.3319 | 10.2696 | 9.5686 | 5.6064 | -4.9998 | -13.313 | 18.0737 | 17.9951 | 17.7809 | 17.5849 | 17.2329 | 16.7502 | 14.8737 | 13.1258 | 10.0462 | 9.3237 | 5.0237 | -6.0773 | -14.4998
|  | WALTON | EE |  |  |  |  | 17.5564 | 17.4104 | 17.1951 | 17.0309 | 16.6972 | 16.2207 | 14.9676 | 13.7778 | 11.6329 | 11.0247 | 7.3207 | -1.363 | -4.5457 | 18.4033 | 18.2676 | 18.0758 | 17.9156 | 17.5135 | 17.0288 | 15.6094 | 14.2084 | 11.5962 | 10.9553 | 7.4278 | -2.4314 | -6.2987 | 18.1186 | 17.9972 | 17.7809 | 17.5849 | 17.2329 | 16.7502 | 15.336 | 13.9278 | 11.336 | 10.687 | 6.6441 | -3.5222 | -7.2528
|  | WALTON | HT |  |  |  |  | 17.539 | 17.4309 | 17.2196 | 17.0472 | 16.7207 | 16.3053 | 14.6186 | 13.2329 | 10.6196 | 9.9604 | 6.0135 | -3.3814 | -10.2702 | 18.3686 | 18.2727 | 18.0768 | 17.9176 | 17.5145 | 17.0758 | 15.1064 | 13.4635 | 10.2696 | 9.5686 | 5.6298 | -4.9998 | -13.313 | 18.0941 | 18.0125 | 17.8053 | 17.6074 | 17.239 | 16.8258 | 14.8737 | 13.2339 | 10.0462 | 9.3237 | 5.0237 | -6.0773 | -14.4998
|  | WALTON | HE |  |  |  |  | 17.5278 | 17.4166 | 17.2207 | 17.0635 | 16.739 | 16.286 | 14.9594 | 13.1788 | 12.8043 | 11.7727 | 6.4523 | -1.4538 | -8.8998 | 18.3482 | 18.2645 | 18.089 | 17.9217 | 17.5166 | 17.0329 | 15.5002 | 13.3319 | 12.9104 | 11.688 | 5.6064 | -3.6651 | -12.9549 | 18.0737 | 17.9951 | 17.8033 | 17.6125 | 17.2523 | 16.8002 | 15.29 | 13.1258 | 12.7186 | 11.489 | 5.2492 | -4.2283 | -13.2865
|  | WALTON | FB |  |  |  |  | 17.7125 | 17.6849 | 17.6176 | 17.5676 | 17.5196 | 17.3564 | 16.7533 | 15.9176 | 14.237 | 13.7666 | 12.089 | 9.4278 | 6.5298 | 18.538 | 18.4349 | 18.3074 | 18.2115 | 18.089 | 17.8635 | 17.0798 | 16.0533 | 13.9921 | 13.3676 | 11.236 | 7.7645 | 3.7237 | 18.2951 | 18.2125 | 18.1615 | 18.1329 | 18.0513 | 17.8788 | 17.1492 | 16.1523 | 14.1074 | 13.5441 | 11.6594 | 8.0768 | 5.6696
| INVERNESS | WATERLOO PLACE | MINIMUM HEADROOM | NH 66301 45800 | NO | NO | 4.971 | 25.4345 | 25.2904 | 25.3093 | 25.189 | 25.0269 | 24.7276 | 24.3529 | 23.3038 | 22.0133 | 20.7937 | 18.6683 | 17.1787 | 16.7086 | 29.4413 | 29.4235 | 29.4312 | 29.4143 | 29.3908 | 29.3461 | 29.3033 | 29.2533 | 29.2162 | 29.1691 | 29.0359 | 28.9345 | 28.8652 | 29.6221 | 29.585 | 29.5889 | 29.5523 | 29.5057 | 29.4417 | 29.3754 | 29.3018 | 29.236 | 29.1489 | 28.7157 | 28.2301 | 28.2008
|  | WATERLOO PLACE | EE |  |  |  |  | 25.4345 | 25.2904 | 25.3093 | 25.189 | 25.0269 | 24.7276 | 24.3529 | 23.3038 | 22.0133 | 20.7937 | 18.6683 | 17.1787 | 16.7086 | 29.4413 | 29.4249 | 29.4321 | 29.4143 | 29.3913 | 29.3489 | 29.3033 | 29.2533 | 29.2162 | 29.1696 | 29.0359 | 28.9345 | 28.9407 | 29.6225 | 29.5865 | 29.5889 | 29.5528 | 29.5071 | 29.4446 | 29.3754 | 29.3018 | 29.236 | 29.1595 | 28.7157 | 28.2301 | 28.2008
|  | WATERLOO PLACE | HT |  |  |  |  | 30.3137 | 30.2031 | 30.2185 | 30.1439 | 30.0329 | 29.8703 | 29.7299 | 29.5794 | 29.4366 | 29.2318 | 28.6851 | 28.2394 | 28.1144 | 29.4417 | 29.4254 | 29.4326 | 29.4148 | 29.3908 | 29.3461 | 29.3062 | 29.26 | 29.2263 | 29.1691 | 29.0403 | 28.946 | 28.8652 | 29.6245 | 29.5908 | 29.5961 | 29.5591 | 29.5115 | 29.4441 | 29.3778 | 29.3052 | 29.2432 | 29.1489 | 28.7417 | 28.3296 | 28.2123
|  | WATERLOO PLACE | HE |  |  |  |  | 30.3141 | 30.2031 | 30.2204 | 30.1439 | 30.0401 | 29.8756 | 29.7448 | 29.5833 | 29.4491 | 29.303 | 28.8991 | 28.7289 | 28.5918 | 29.4417 | 29.4249 | 29.4326 | 29.4153 | 29.3917 | 29.347 | 29.3086 | 29.2586 | 29.2268 | 29.1864 | 29.0965 | 29.0835 | 29.0744 | 29.6221 | 29.586 | 29.5894 | 29.5523 | 29.5057 | 29.4417 | 29.3821 | 29.3086 | 29.2523 | 29.1888 | 28.9225 | 28.7917 | 28.6816
|  | WATERLOO PLACE | FB |  |  |  |  | 30.3247 | 30.1834 | 30.1973 | 30.1834 | 30.1502 | 30.093 | 30.0314 | 29.9694 | 29.8867 | 29.855 | 29.503 | 29.1799 | 28.8044 | 29.4466 | 29.4235 | 29.4312 | 29.4283 | 29.4235 | 29.4105 | 29.3937 | 29.3749 | 29.3489 | 29.3427 | 29.2427 | 29.1677 | 29.0855 | 29.6293 | 29.585 | 29.5932 | 29.5836 | 29.5663 | 29.5422 | 29.5153 | 29.4845 | 29.4466 | 29.4321 | 29.26 | 29.0739 | 28.8301
| LYNDHURST | WEST KIRKTON | MINIMUM HEADROOM | NO 39194 33796 | NO | YES | 2.858 | 13.0508 | 13.058 | 13.0355 | 12.8274 | 12.7192 | 12.5916 | 12.3814 | 12.1437 | 11.9182 | 11.7427 | 10.657 | 9.7151 | 9.2253 | 14.1202 | 14.1182 | 14.1039 | 13.96 | 13.8539 | 13.7274 | 13.4753 | 13.1314 | 12.76 | 12.4978 | 11.2743 | 10.8621 | 10.3763 | 13.686 | 13.682 | 13.6636 | 13.5177 | 13.4197 | 13.3075 | 13.0636 | 12.7911 | 12.5258 | 12.3228 | 11.1462 | 10.2095 | 9.7483
|  | WEST KIRKTON | EE |  |  |  |  | 13.0529 | 13.058 | 13.0488 | 12.8692 | 12.7733 | 12.6621 | 12.4274 | 12.1672 | 11.9692 | 11.7508 | 10.657 | 9.7151 | 9.2253 | 14.1253 | 14.1243 | 14.1253 | 13.9937 | 13.8876 | 13.7784 | 13.5161 | 13.1406 | 12.8467 | 12.51 | 11.3865 | 10.9253 | 10.7549 | 13.6871 | 13.682 | 13.6799 | 13.5422 | 13.4554 | 13.3666 | 13.0973 | 12.8064 | 12.585 | 12.3279 | 11.1462 | 10.2095 | 9.7483
|  | WEST KIRKTON | HT |  |  |  |  | 13.0508 | 13.0621 | 13.0355 | 12.8274 | 12.7192 | 12.5916 | 12.3814 | 12.1437 | 11.9692 | 11.7427 | 10.6906 | 9.9335 | 9.7335 | 14.1202 | 14.1182 | 14.1039 | 13.96 | 13.8539 | 13.7274 | 13.5018 | 13.1314 | 12.8406 | 12.4988 | 11.2743 | 10.8621 | 10.8406 | 13.686 | 13.6881 | 13.6636 | 13.5177 | 13.4197 | 13.3075 | 13.0656 | 12.7911 | 12.584 | 12.3228 | 11.1503 | 10.3871 | 10.1952
|  | WEST KIRKTON | HE |  |  |  |  | 13.059 | 13.0692 | 13.057 | 12.858 | 12.7539 | 12.6396 | 12.3896 | 12.1641 | 11.9182 | 11.7621 | 11.0906 | 10.6988 | 10.4172 | 14.1243 | 14.1223 | 14.1182 | 13.9753 | 13.8692 | 13.758 | 13.4753 | 13.1365 | 12.76 | 12.4978 | 11.6753 | 11.46 | 11.2825 | 13.6922 | 13.6922 | 13.6789 | 13.5371 | 13.4432 | 13.3513 | 13.0636 | 12.8126 | 12.5258 | 12.3442 | 11.6126 | 11.2309 | 10.9483
|  | WEST KIRKTON | FB |  |  |  |  | 13.1763 | 13.2274 | 13.26 | 13.0906 | 13.11 | 13.1182 | 13.0978 | 12.9988 | 12.9743 | 12.8661 | 12.3978 | 11.3447 | 10.5672 | 14.21 | 14.2223 | 14.2314 | 14.0702 | 14.0539 | 14.008 | 13.9365 | 13.7998 | 13.7365 | 13.5743 | 12.9223 | 11.6284 | 10.3763 | 13.8054 | 13.8452 | 13.8697 | 13.7197 | 13.734 | 13.7299 | 13.7075 | 13.632 | 13.6156 | 13.482 | 12.933 | 11.6166 | 11.0177
| KILLIN | WESTER DRUMMOND | MINIMUM HEADROOM | NN 72155 44784 | YES | YES | 0 | 0.090449 | 0.091469 | 0.089429 | 0.090449 | 0.083306 | 0.078204 | 0.075143 | 0.072082 | 0.06902 | 0.064939 | 0.057796 | 0.052694 | 0.048612 | 0.085531 | 0.086551 | 0.085531 | 0.08451 | 0.082469 | 0.078388 | 0.078388 | 0.074306 | 0.070224 | 0.067163 | 0.06002 | 0.06002 | 0.061041 | 0.08901 | 0.091051 | 0.08799 | 0.08901 | 0.082888 | 0.076765 | 0.075745 | 0.072684 | 0.070643 | 0.066561 | 0.059418 | 0.057378 | 0.055337
|  | WESTER DRUMMOND | EE |  |  |  |  | 0.090449 | 0.091469 | 0.089429 | 0.090449 | 0.085347 | 0.079224 | 0.075143 | 0.072082 | 0.06902 | 0.065959 | 0.057796 | 0.052694 | 0.053714 | 0.085531 | 0.086551 | 0.085531 | 0.08451 | 0.08349 | 0.079408 | 0.078388 | 0.074306 | 0.070224 | 0.067163 | 0.061041 | 0.061041 | 0.064102 | 0.08901 | 0.091051 | 0.08799 | 0.08901 | 0.083908 | 0.078806 | 0.075745 | 0.072684 | 0.070643 | 0.066561 | 0.059418 | 0.058398 | 0.058398
|  | WESTER DRUMMOND | HT |  |  |  |  | 0.090449 | 0.091469 | 0.089429 | 0.090449 | 0.085347 | 0.078204 | 0.076163 | 0.073102 | 0.070041 | 0.065959 | 0.059837 | 0.054735 | 0.050653 | 0.085531 | 0.086551 | 0.085531 | 0.08451 | 0.08349 | 0.078388 | 0.078388 | 0.074306 | 0.070224 | 0.067163 | 0.06002 | 0.061041 | 0.063082 | 0.08901 | 0.091051 | 0.08799 | 0.08901 | 0.083908 | 0.076765 | 0.076765 | 0.073704 | 0.070643 | 0.066561 | 0.060439 | 0.057378 | 0.057378
|  | WESTER DRUMMOND | HE |  |  |  |  | 0.090449 | 0.091469 | 0.089429 | 0.090449 | 0.083306 | 0.079224 | 0.076163 | 0.072082 | 0.06902 | 0.064939 | 0.059837 | 0.054735 | 0.048612 | 0.085531 | 0.086551 | 0.085531 | 0.08451 | 0.082469 | 0.079408 | 0.078388 | 0.074306 | 0.070224 | 0.067163 | 0.061041 | 0.06002 | 0.061041 | 0.08901 | 0.091051 | 0.08799 | 0.08901 | 0.082888 | 0.078806 | 0.076765 | 0.072684 | 0.070643 | 0.066561 | 0.060439 | 0.058398 | 0.055337
|  | WESTER DRUMMOND | FB |  |  |  |  | 0.10167 | 0.094531 | 0.095551 | 0.095551 | 0.09351 | 0.091469 | 0.09351 | 0.088408 | 0.088408 | 0.085347 | 0.074122 | 0.072082 | 0.06902 | 0.097776 | 0.089612 | 0.090633 | 0.091653 | 0.087571 | 0.08451 | 0.086551 | 0.080429 | 0.079408 | 0.078388 | 0.070224 | 0.068184 | 0.065122 | 0.10023 | 0.093092 | 0.094112 | 0.095133 | 0.092071 | 0.090031 | 0.092071 | 0.086969 | 0.085949 | 0.082888 | 0.072684 | 0.070643 | 0.066561
| THURSO | WESTRAY | MINIMUM HEADROOM | HY 50213 39413 | YES | NO | 0.079 | -0.15204 | -0.15204 | -0.16429 | -0.17857 | -0.46939 | -0.67653 | -0.8449 | -0.97143 | -1.0816 | -1.2071 | -1.5388 | -1.8827 | -2.0235 | 0.0071429 | 0.0010204 | -0.016327 | -0.028571 | -0.30714 | -0.49184 | -0.65204 | -0.76224 | -0.86633 | -0.98469 | -1.3255 | -1.5796 | -1.6571 | -0.11531 | -0.12041 | -0.1398 | -0.15918 | -0.43878 | -0.62755 | -0.79694 | -0.92041 | -1.0173 | -1.1357 | -1.4541 | -1.7459 | -1.8643
|  | WESTRAY | EE |  |  |  |  | -0.15204 | -0.15204 | -0.16429 | -0.17755 | -0.46531 | -0.66837 | -0.8449 | -0.94388 | -1.0735 | -1.1929 | -1.5245 | -1.8827 | -1.8735 | 0.0071429 | 0.0010204 | -0.016327 | -0.028571 | -0.30612 | -0.48571 | -0.65204 | -0.73776 | -0.84592 | -0.96224 | -1.2837 | -1.5694 | -1.5194 | -0.11531 | -0.12041 | -0.1398 | -0.15816 | -0.43571 | -0.61939 | -0.79694 | -0.89388 | -0.99388 | -1.1112 | -1.4286 | -1.7459 | -1.7163
|  | WESTRAY | HT |  |  |  |  | -0.15204 | -0.15204 | -0.16429 | -0.17857 | -0.46633 | -0.65816 | -0.80204 | -0.95102 | -1.0745 | -1.1959 | -1.5388 | -1.8663 | -2.0235 | 0.0071429 | 0.0010204 | -0.016327 | -0.028571 | -0.30714 | -0.47857 | -0.61633 | -0.75714 | -0.86633 | -0.98469 | -1.3255 | -1.5796 | -1.6571 | -0.11531 | -0.12041 | -0.1398 | -0.15816 | -0.43571 | -0.61224 | -0.75612 | -0.90306 | -1.0173 | -1.1357 | -1.4541 | -1.7408 | -1.8643
|  | WESTRAY | HE |  |  |  |  | -0.14898 | -0.15204 | -0.16429 | -0.17857 | -0.46939 | -0.67653 | -0.82959 | -0.97143 | -1.0816 | -1.2071 | -1.348 | -1.3827 | -1.452 | 0.010204 | 0.0010204 | -0.016327 | -0.028571 | -0.30714 | -0.49184 | -0.63469 | -0.76224 | -0.85102 | -0.97449 | -1.1306 | -1.1041 | -1.1367 | -0.11429 | -0.12041 | -0.1398 | -0.15918 | -0.43878 | -0.62755 | -0.78265 | -0.92041 | -0.99898 | -1.1235 | -1.2745 | -1.2847 | -1.3327
|  | WESTRAY | FB |  |  |  |  | -0.13367 | -0.13163 | -0.1449 | -0.1449 | -0.14796 | -0.15714 | -0.17143 | -0.17551 | -0.19286 | -0.53776 | -0.85102 | -1.1204 | -1.4194 | 0.02449 | 0.019388 | 0.0010204 | -0.0071429 | -0.016327 | -0.026531 | -0.04898 | -0.053061 | -0.07449 | -0.40714 | -0.71735 | -0.98878 | -1.2796 | -0.097959 | -0.10204 | -0.11735 | -0.12449 | -0.13469 | -0.14592 | -0.16735 | -0.17143 | -0.19184 | -0.51327 | -0.81735 | -1.1429 | -1.3612
| TARLAND | WHITEHOUSE | MINIMUM HEADROOM | NJ 61658 15058 | NO | NO | 1.11 | 2.9463 | 2.8238 | 2.6748 | 2.4555 | 2.3167 | 1.8493 | 1.4738 | 1.1504 | 0.79627 | 0.42382 | -0.46087 | -1.3343 | -1.9231 | 4.5595 | 4.4646 | 4.331 | 4.2014 | 4.1585 | 3.8779 | 3.6126 | 3.4483 | 3.2197 | 2.9585 | 2.3136 | 2.1106 | 2.0126 | 3.9555 | 3.8361 | 3.6646 | 3.5034 | 3.382 | 2.9167 | 2.5575 | 2.3034 | 2.0075 | 1.6657 | 0.90342 | 0.30342 | -0.054747
|  | WHITEHOUSE | EE |  |  |  |  | 2.9616 | 2.8483 | 2.6902 | 2.4738 | 2.3799 | 1.9728 | 1.6085 | 1.3075 | 0.94525 | 0.66056 | -0.46087 | -1.3343 | -1.9231 | 4.5779 | 4.4759 | 4.3442 | 4.2146 | 4.1708 | 3.8942 | 3.6299 | 3.4483 | 3.2197 | 3.0299 | 2.3493 | 2.1106 | 2.0126 | 3.9677 | 3.8514 | 3.6738 | 3.5167 | 3.4238 | 2.9912 | 2.6432 | 2.3973 | 2.0789 | 1.8412 | 0.90342 | 0.30342 | -0.054747
|  | WHITEHOUSE | HT |  |  |  |  | 2.9544 | 2.8238 | 2.6748 | 2.4585 | 2.3779 | 2.0055 | 1.683 | 1.3932 | 1.0493 | 0.76056 | -0.21699 | -1.1731 | -1.8711 | 4.5677 | 4.4646 | 4.331 | 4.2014 | 4.1585 | 3.9065 | 3.6463 | 3.4636 | 3.2208 | 3.0432 | 2.3136 | 2.1565 | 2.231 | 3.9616 | 3.8361 | 3.6646 | 3.5034 | 3.4177 | 3.0157 | 2.6953 | 2.4534 | 2.1473 | 1.9014 | 1.0167 | 0.39219 | 0.0095388
|  | WHITEHOUSE | HE |  |  |  |  | 2.9463 | 2.8585 | 2.6993 | 2.4555 | 2.3167 | 1.8493 | 1.4738 | 1.1504 | 0.79627 | 0.42382 | -0.1772 | -0.99352 | -1.5333 | 4.5595 | 4.4769 | 4.3453 | 4.2248 | 4.1636 | 3.8779 | 3.6126 | 3.4504 | 3.2371 | 2.9585 | 2.5106 | 2.4044 | 2.2687 | 3.9555 | 3.8585 | 3.681 | 3.5116 | 3.382 | 2.9167 | 2.5575 | 2.3034 | 2.0075 | 1.6657 | 1.1412 | 0.62178 | 0.26872
|  | WHITEHOUSE | FB |  |  |  |  | 3.1126 | 3.0759 | 3.0187 | 2.931 | 2.8677 | 2.5636 | 2.3973 | 2.335 | 2.3463 | 2.2677 | 1.7534 | 1.183 | 0.68505 | 4.7004 | 4.6371 | 4.5667 | 4.5004 | 4.4524 | 4.1218 | 4.0065 | 3.933 | 3.9402 | 3.8432 | 3.4279 | 2.8718 | 2.2738 | 4.1106 | 4.0646 | 4.0085 | 3.9075 | 3.8728 | 3.4238 | 3.285 | 3.2136 | 3.233 | 3.1473 | 2.6932 | 2.132 | 1.7412
| PERSLEY | WHITESTRIPES | MINIMUM HEADROOM | NJ 92850 11054 | NO | NO | 6.667 | 2.1905 | 2.0568 | 1.8732 | 1.5691 | -5.1258 | -5.7452 | -6.2176 | -6.6952 | -7.1534 | -7.4738 | -8.9197 | -10.0452 | -10.7993 | 3.566 | 3.4844 | 3.3987 | 3.2619 | 0.65786 | 0.48235 | 0.27521 | 0.051739 | -0.15847 | -0.36255 | -1.0789 | -1.3523 | -2.0238 | 3.2206 | 3.1298 | 2.9971 | 2.7767 | -1.7141 | -2.1794 | -2.5733 | -2.9835 | -3.3671 | -3.6722 | -4.9131 | -5.7029 | -6.2171
|  | WHITESTRIPES | EE |  |  |  |  | 2.1905 | 2.0568 | 1.8732 | 1.5834 | -4.2289 | -5.637 | -6.1105 | -6.6044 | -7.086 | -7.4738 | -8.9197 | -10.0452 | -10.7993 | 3.566 | 3.4875 | 3.4007 | 3.265 | 1.0977 | 0.4946 | 0.29256 | 0.060922 | -0.14826 | -0.35949 | -1.0646 | -1.3421 | -1.6115 | 3.2206 | 3.1298 | 2.9971 | 2.7859 | -1.0386 | -2.11 | -2.5069 | -2.9243 | -3.3243 | -3.6722 | -4.9131 | -5.7029 | -6.2171
|  | WHITESTRIPES | HT |  |  |  |  | 2.1915 | 2.0742 | 1.9058 | 1.614 | -5.1258 | -5.5187 | -5.9554 | -6.4105 | -6.8452 | -7.2921 | -8.8146 | -9.9258 | -10.6085 | 3.5681 | 3.4875 | 3.3987 | 3.263 | 0.65786 | 0.50276 | 0.30378 | 0.07929 | -0.12887 | -0.3503 | -1.0789 | -1.1503 | -1.1472 | 3.2227 | 3.139 | 3.0165 | 2.8043 | -1.7141 | -2.0386 | -2.411 | -2.8059 | -3.1753 | -3.561 | -4.8855 | -5.6447 | -6.06
|  | WHITESTRIPES | HE |  |  |  |  | 2.1926 | 2.063 | 1.8752 | 1.5691 | -4.2462 | -5.7452 | -6.2176 | -6.6952 | -7.1534 | -7.4472 | -8.6319 | -9.6125 | -10.187 | 3.5681 | 3.4844 | 3.3997 | 3.2619 | 1.0987 | 0.48235 | 0.27521 | 0.051739 | -0.15847 | -0.36255 | -1.0595 | -1.3523 | -1.6646 | 3.2247 | 3.1329 | 3.0002 | 2.7767 | -1.0508 | -2.1794 | -2.5733 | -2.9835 | -3.3671 | -3.6539 | -4.7212 | -5.411 | -5.8212
|  | WHITESTRIPES | FB |  |  |  |  | 2.3354 | 2.2834 | 2.1885 | 2.066 | -2.2421 | -4.1483 | -4.1268 | -4.2228 | -4.3197 | -4.437 | -5.036 | -6.0381 | -6.5309 | 3.6742 | 3.617 | 3.5579 | 3.4905 | 1.6497 | 0.7946 | 0.78745 | 0.67929 | 0.56398 | 0.43235 | -0.18193 | -1.2136 | -2.0238 | 3.3686 | 3.3278 | 3.2757 | 3.192 | 0.3798 | -1.0365 | -1.0253 | -1.1365 | -1.2508 | -1.3835 | -2.0284 | -3.1426 | -3.4314
| CARRADALE 1 | WHITING BAY | MINIMUM HEADROOM | NS 04169 26277 | YES | YES | 0.44 | 4.8898 | 4.8878 | 4.8918 | 4.85 | 4.8071 | 4.6929 | 4.5908 | 4.4908 | 4.3857 | 4.3245 | 4.0939 | 3.8694 | 3.6908 | 5.6531 | 5.65 | 5.6582 | 5.6357 | 5.6286 | 5.5786 | 5.5408 | 5.4969 | 5.4357 | 5.3796 | 5.1612 | 5.1837 | 5.2173 | 5.3378 | 5.3347 | 5.3408 | 5.2949 | 5.2633 | 5.199 | 5.1265 | 5.052 | 4.9694 | 4.9184 | 4.7388 | 4.6469 | 4.5612
|  | WHITING BAY | EE |  |  |  |  | 4.8908 | 4.8878 | 4.8918 | 4.851 | 4.8112 | 4.6959 | 4.5908 | 4.4908 | 4.3857 | 4.3245 | 4.0939 | 3.8694 | 3.701 | 5.6561 | 5.65 | 5.6582 | 5.6357 | 5.6286 | 5.5796 | 5.5418 | 5.499 | 5.4378 | 5.3816 | 5.2031 | 5.2224 | 5.2765 | 5.3398 | 5.3347 | 5.3408 | 5.2949 | 5.2673 | 5.201 | 5.1265 | 5.052 | 4.9694 | 4.9184 | 4.7388 | 4.6469 | 4.601
|  | WHITING BAY | HT |  |  |  |  | 4.8898 | 4.8908 | 4.898 | 4.8622 | 4.8235 | 4.7184 | 4.6265 | 4.5327 | 4.4235 | 4.3633 | 4.1745 | 3.9276 | 3.6908 | 5.6531 | 5.651 | 5.6582 | 5.6357 | 5.6296 | 5.5786 | 5.5439 | 5.501 | 5.4357 | 5.3796 | 5.1612 | 5.1837 | 5.2459 | 5.3378 | 5.3367 | 5.3449 | 5.302 | 5.2765 | 5.2163 | 5.149 | 5.0745 | 4.9929 | 4.9429 | 4.7796 | 4.6714 | 4.5949
|  | WHITING BAY | HE |  |  |  |  | 4.8908 | 4.8888 | 4.8949 | 4.85 | 4.8071 | 4.6929 | 4.5959 | 4.4969 | 4.3929 | 4.3265 | 4.1704 | 3.9051 | 3.7194 | 5.6561 | 5.651 | 5.6582 | 5.6357 | 5.6286 | 5.5796 | 5.5408 | 5.4969 | 5.4378 | 5.3806 | 5.2041 | 5.2051 | 5.2173 | 5.3408 | 5.3367 | 5.3429 | 5.2959 | 5.2633 | 5.199 | 5.1296 | 5.0531 | 4.9724 | 4.9194 | 4.7837 | 4.6469 | 4.5612
|  | WHITING BAY | FB |  |  |  |  | 4.9316 | 4.9561 | 4.9765 | 4.9857 | 4.9898 | 4.9755 | 4.9714 | 4.9561 | 4.9541 | 4.9327 | 4.8092 | 4.649 | 4.602 | 5.6959 | 5.7071 | 5.7153 | 5.7204 | 5.7235 | 5.701 | 5.6888 | 5.6592 | 5.649 | 5.6173 | 5.4745 | 5.299 | 5.2347 | 5.3867 | 5.4092 | 5.4265 | 5.4388 | 5.448 | 5.4265 | 5.4184 | 5.3918 | 5.3878 | 5.3612 | 5.2265 | 5.0806 | 5.0704
| MYBSTER 1 | WICK | MINIMUM HEADROOM | ND 35583 50947 | NO | NO | 2.666 | 5.7211 | 5.6956 | 5.7099 | 5.5477 | 5.2017 | 3.8415 | 2.4589 | 1.116 | 0.028278 | -0.70336 | -2.5952 | -4.1544 | -5.335 | 7.7742 | 7.7977 | 7.7987 | 7.8334 | 7.6273 | 6.6466 | 5.5191 | 4.4364 | 3.5813 | 3.1446 | 2.462 | 2.2711 | 1.6762 | 6.9354 | 6.9426 | 6.8946 | 6.9028 | 6.415 | 5.4477 | 4.3415 | 3.2426 | 2.3568 | 1.6813 | 0.00072653 | -1.2421 | -2.0278
|  | WICK | EE |  |  |  |  | 5.7211 | 5.6956 | 5.7099 | 5.5497 | 5.2089 | 4.8354 | 4.4038 | 2.9987 | 1.6313 | 0.33644 | -2.5952 | -4.1544 | -5.2217 | 7.7742 | 7.7977 | 7.8334 | 7.8334 | 7.6273 | 7.5864 | 7.4375 | 6.3671 | 5.2395 | 4.1273 | 2.512 | 2.2915 | 1.9273 | 6.9354 | 6.9426 | 6.9538 | 6.9028 | 6.4181 | 6.1915 | 5.8079 | 4.6773 | 3.5956 | 2.5456 | 0.00072653 | -1.2421 | -2.0278
|  | WICK | HT |  |  |  |  | 5.7232 | 5.6987 | 5.714 | 5.5538 | 5.214 | 3.8415 | 2.4589 | 1.116 | 0.028278 | -0.70336 | -2.4268 | -4.0401 | -5.335 | 7.7762 | 7.7977 | 7.8334 | 7.8334 | 7.6273 | 6.6466 | 5.5191 | 4.4364 | 3.5813 | 3.1446 | 2.462 | 2.2711 | 2.1507 | 6.9364 | 6.9436 | 6.9558 | 6.9079 | 6.4191 | 5.4477 | 4.3415 | 3.2426 | 2.3568 | 1.6813 | 0.14767 | -1.0411 | -1.8717
|  | WICK | HE |  |  |  |  | 5.7232 | 5.6997 | 5.715 | 5.5477 | 5.2017 | 4.8487 | 4.4303 | 2.9201 | 1.464 | 0.05889 | -2.1595 | -3.6003 | -4.4697 | 7.7752 | 7.7987 | 7.8334 | 7.8344 | 7.6273 | 7.5915 | 7.4477 | 6.2742 | 5.0242 | 3.8313 | 2.6017 | 2.5089 | 2.312 | 6.9375 | 6.9456 | 6.9558 | 6.9048 | 6.415 | 6.2028 | 5.8262 | 4.6171 | 3.465 | 2.3354 | 0.41501 | -0.50846 | -1.0891
|  | WICK | FB |  |  |  |  | 5.7987 | 5.8405 | 5.7436 | 5.7354 | 5.714 | 5.6375 | 5.5466 | 5.4548 | 4.5762 | 3.6844 | 0.36297 | -0.53499 | -1.0411 | 7.8334 | 7.8956 | 7.7987 | 7.8395 | 7.8558 | 7.8191 | 7.7548 | 7.713 | 6.964 | 6.1548 | 3.3966 | 2.5395 | 1.6762 | 6.9997 | 7.0528 | 6.8946 | 6.9068 | 6.9201 | 6.8609 | 6.7681 | 6.7007 | 6.0456 | 5.2579 | 2.3548 | 1.2589 | 0.6242
| WOODHILL | WOODHILL | MINIMUM HEADROOM | NJ 91259 07053 | NO | NO | 5.811 | 6.7213 | 6.7162 | 6.705 | 6.5264 | 6.1662 | 5.7846 | 5.3438 | 4.8693 | 4.3489 | 3.8662 | 0.92131 | -1.9052 | -3.4879 | 5.7407 | 5.7968 | 5.8366 | 5.8387 | 5.6815 | 5.4193 | 5.1397 | 4.7989 | 4.4182 | 4.1152 | 2.6519 | 1.3927 | -0.35624 | 6.6101 | 6.5887 | 6.558 | 6.4499 | 6.1723 | 5.8815 | 5.5325 | 5.0815 | 4.5489 | 4.1162 | 1.5284 | -0.88788 | -2.2175
|  | WOODHILL | EE |  |  |  |  | 6.7213 | 6.7162 | 6.705 | 6.5264 | 6.1662 | 5.7846 | 5.3438 | 4.8693 | 4.3489 | 3.8662 | 0.93355 | -1.9052 | -3.4879 | 5.7407 | 5.7968 | 5.8366 | 5.8387 | 5.6815 | 5.4284 | 5.1397 | 4.7989 | 4.4182 | 4.1152 | 2.6519 | 1.3927 | 0.46927 | 6.6101 | 6.5887 | 6.558 | 6.4499 | 6.1723 | 5.8815 | 5.5325 | 5.0815 | 4.5489 | 4.1162 | 1.5284 | -0.88788 | -2.2175
|  | WOODHILL | HT |  |  |  |  | 6.7438 | 6.7682 | 6.7836 | 6.5978 | 6.2356 | 5.8254 | 5.3968 | 4.9427 | 4.455 | 3.9244 | 0.92131 | -1.593 | -2.844 | 5.7407 | 5.7978 | 5.8387 | 5.8427 | 5.6887 | 5.4193 | 5.1468 | 4.8284 | 4.4611 | 4.1336 | 2.855 | 2.0917 | 1.8284 | 6.6346 | 6.6448 | 6.6366 | 6.5131 | 6.2213 | 5.9101 | 5.5642 | 5.1499 | 4.6346 | 4.1652 | 1.5652 | -0.44502 | -1.3093
|  | WOODHILL | HE |  |  |  |  | 6.7387 | 6.7468 | 6.756 | 6.5703 | 6.208 | 5.8754 | 5.4825 | 5.0642 | 4.6631 | 4.1305 | 1.9305 | 0.18967 | -0.9042 | 5.7407 | 5.7989 | 5.8397 | 5.8458 | 5.6948 | 5.4407 | 5.1397 | 4.8142 | 4.5223 | 4.1529 | 2.9448 | 2.0611 | 1.3091 | 6.6284 | 6.6264 | 6.6091 | 6.4917 | 6.2019 | 5.9376 | 5.6131 | 5.1999 | 4.7978 | 4.3244 | 2.3846 | 0.87845 | -0.064408
|  | WOODHILL | FB |  |  |  |  | 6.8478 | 6.9182 | 6.9662 | 6.8509 | 6.7774 | 6.6397 | 6.5427 | 6.3938 | 6.2376 | 6.0142 | 4.9723 | 2.4958 | 0.7662 | 5.7978 | 5.8672 | 5.9223 | 5.8795 | 5.8591 | 5.7172 | 5.6866 | 5.555 | 5.4101 | 5.1529 | 4.005 | 1.6795 | -0.35624 | 6.7376 | 6.7927 | 6.8295 | 6.7213 | 6.6733 | 6.5703 | 6.4999 | 6.3744 | 6.2427 | 6.0478 | 5.0958 | 2.4407 | 1.2427

## Primary Headroom Gen
#VALUE! | Grid Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Generation (MVA) | Generation Headroom Winter (MVA) | [12 empty] | Generation Headroom Summer (MVA) | [12 empty] | Generation Headroom Spring/Autumn (MVA)
[8 empty] | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2040 | 2045 | 2050 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2040 | 2045 | 2050
| FORT AUGUSTUS | ABERCHALDER | MINIMUM HEADROOM | NH 33843 03575 | YES | YES | 0 | 0.2 | 0.19895 | 0.19789 | 0.19789 | 0.19789 | 0.19789 | 0.19789 | 0.19684 | 0.19684 | 0.19684 | 0.19474 | 0.19368 | 0.19368 | 0.20211 | 0.20105 | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19789 | 0.19789 | 0.19579 | 0.19368 | 0.19368 | 0.20316 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.19684 | 0.19474 | 0.19474
|  | ABERCHALDER | EE |  |  |  |  | 0.2 | 0.19895 | 0.19789 | 0.19789 | 0.19789 | 0.19789 | 0.19789 | 0.19684 | 0.19684 | 0.19684 | 0.19474 | 0.19474 | 0.19368 | 0.20211 | 0.20105 | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19789 | 0.19789 | 0.19579 | 0.19474 | 0.19368 | 0.20316 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.19684 | 0.19579 | 0.19474
|  | ABERCHALDER | HT |  |  |  |  | 0.2 | 0.2 | 0.19789 | 0.19789 | 0.19789 | 0.19789 | 0.19789 | 0.19684 | 0.19684 | 0.19684 | 0.19474 | 0.19368 | 0.19368 | 0.20211 | 0.20211 | 0.2 | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19789 | 0.19789 | 0.19579 | 0.19368 | 0.19368 | 0.20316 | 0.20316 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.19684 | 0.19474 | 0.19474
|  | ABERCHALDER | HE |  |  |  |  | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19789 | 0.19789 | 0.19789 | 0.19789 | 0.19789 | 0.19684 | 0.19684 | 0.19684 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19789 | 0.19789 | 0.19789 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895
|  | ABERCHALDER | FB |  |  |  |  | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19789 | 0.19789 | 0.19789 | 0.19789 | 0.19789 | 0.19789 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2
| TUMMEL BRIDGE | ABERFELDY | MINIMUM HEADROOM | NN 84889 48876 | NO | YES | 0 | 6.7979 | 6.7716 | 6.7453 | 6.5968 | 6.4211 | 6.2137 | 6 | 5.8505 | 5.6811 | 5.4737 | 4.5474 | 3.7084 | 3.4747 | 6.4379 | 6.4168 | 6.3968 | 6.1747 | 5.9747 | 5.7516 | 5.5 | 5.3295 | 5.0653 | 4.8063 | 3.78 | 3.0347 | 2.8053 | 6.2632 | 6.2326 | 6.2 | 5.9905 | 5.7916 | 5.5558 | 5.3116 | 5.1421 | 4.9484 | 4.6947 | 3.5905 | 2.6789 | 2.4158
|  | ABERFELDY | EE |  |  |  |  | 6.7979 | 6.7716 | 6.7453 | 6.5968 | 6.4211 | 6.2137 | 6 | 5.8505 | 5.6811 | 5.6116 | 4.5474 | 3.7084 | 3.4747 | 6.4379 | 6.4168 | 6.3968 | 6.1968 | 5.9937 | 5.7516 | 5.5 | 5.3295 | 5.1326 | 5.0611 | 3.78 | 3.0347 | 2.8053 | 6.2632 | 6.2326 | 6.2 | 5.9905 | 5.7916 | 5.5558 | 5.3116 | 5.1421 | 4.9484 | 4.8695 | 3.5905 | 2.6789 | 2.4158
|  | ABERFELDY | HT |  |  |  |  | 6.8053 | 6.7863 | 6.7642 | 6.6053 | 6.4389 | 6.3074 | 6.14 | 5.9568 | 5.6874 | 5.4737 | 4.6463 | 3.9811 | 3.7958 | 6.4421 | 6.4242 | 6.4042 | 6.1747 | 5.9747 | 5.8189 | 5.6168 | 5.3947 | 5.0653 | 4.8063 | 3.8621 | 3.2568 | 3.0053 | 6.2737 | 6.2526 | 6.2158 | 5.9989 | 5.8105 | 5.6611 | 5.4695 | 5.2589 | 4.9484 | 4.6947 | 3.7611 | 3.0368 | 2.7758
|  | ABERFELDY | HE |  |  |  |  | 6.8147 | 6.7958 | 6.7821 | 6.7421 | 6.6095 | 6.4547 | 6.2168 | 6.0895 | 5.9211 | 5.8853 | 5.0432 | 4.6916 | 4.5779 | 6.4516 | 6.4337 | 6.4221 | 6.3411 | 6.1832 | 5.9968 | 5.7084 | 5.5547 | 5.3484 | 5.3095 | 4.2705 | 3.9537 | 3.8337 | 6.2832 | 6.2621 | 6.2474 | 6.1453 | 6.0053 | 5.8284 | 5.5558 | 5.4095 | 5.2137 | 5.1747 | 4.1621 | 3.7779 | 3.6463
|  | ABERFELDY | FB |  |  |  |  | 6.8242 | 6.8179 | 6.8116 | 6.8042 | 6.7958 | 6.7884 | 6.78 | 6.7211 | 6.6463 | 6.6105 | 6.1537 | 5.7463 | 5.6284 | 6.46 | 6.4537 | 6.4474 | 6.4411 | 6.4326 | 6.4253 | 6.4179 | 6.3063 | 6.2147 | 6.1726 | 5.6074 | 5.1042 | 4.9621 | 6.2937 | 6.2874 | 6.28 | 6.2726 | 6.2642 | 6.2558 | 6.24 | 6.1221 | 6.0421 | 6.0042 | 5.4758 | 5.0032 | 4.8632
| STRATHLEVEN | ABERFOYLE | MINIMUM HEADROOM | NS 53215 99705 | YES | YES | 0 | 4.3421 | 4.3168 | 4.2937 | 4.2674 | 4.2116 | 4.1379 | 4.0632 | 3.9905 | 3.9189 | 3.8463 | 3.5663 | 3.2695 | 2.9947 | 3.9958 | 3.9495 | 3.8989 | 3.8379 | 3.7747 | 3.7105 | 3.6453 | 3.5832 | 3.52 | 3.4568 | 3.1968 | 2.8768 | 2.5832 | 4.1568 | 4.1253 | 4.0705 | 3.9968 | 3.9168 | 3.8358 | 3.7526 | 3.6716 | 3.5916 | 3.5105 | 3.1979 | 2.8642 | 2.5547
|  | ABERFOYLE | EE |  |  |  |  | 4.3421 | 4.3168 | 4.2937 | 4.2674 | 4.2116 | 4.1379 | 4.0632 | 3.9905 | 3.9189 | 3.8463 | 3.5663 | 3.2695 | 2.9947 | 3.9958 | 3.9495 | 3.8989 | 3.8379 | 3.7747 | 3.7105 | 3.6453 | 3.5832 | 3.52 | 3.4568 | 3.1968 | 2.9074 | 2.6432 | 4.1568 | 4.1253 | 4.0705 | 3.9968 | 3.9168 | 3.8358 | 3.7526 | 3.6716 | 3.5916 | 3.5105 | 3.1979 | 2.8642 | 2.5547
|  | ABERFOYLE | HT |  |  |  |  | 4.3547 | 4.3432 | 4.3295 | 4.3158 | 4.2895 | 4.2263 | 4.1611 | 4.0937 | 4.0274 | 3.9568 | 3.6274 | 3.3432 | 3.1253 | 4.0105 | 3.9737 | 3.9284 | 3.8768 | 3.8137 | 3.7516 | 3.6884 | 3.6232 | 3.5589 | 3.4821 | 3.1979 | 2.8768 | 2.5832 | 4.1737 | 4.16 | 4.1305 | 4.0758 | 4.0032 | 3.9326 | 3.8589 | 3.7832 | 3.7095 | 3.6305 | 3.3358 | 3 | 2.6905
|  | ABERFOYLE | HE |  |  |  |  | 4.3579 | 4.3453 | 4.3358 | 4.3232 | 4.3074 | 4.2916 | 4.2632 | 4.2189 | 4.1705 | 4.1242 | 3.9379 | 3.7326 | 3.5442 | 4.0295 | 4 | 3.9674 | 3.9305 | 3.8863 | 3.8432 | 3.7937 | 3.7516 | 3.7053 | 3.6611 | 3.4779 | 3.2621 | 3.0653 | 4.1768 | 4.1621 | 4.1505 | 4.1284 | 4.0811 | 4.0326 | 3.9758 | 3.9263 | 3.8726 | 3.8189 | 3.6084 | 3.3758 | 3.1621
|  | ABERFOYLE | FB |  |  |  |  | 4.3653 | 4.3621 | 4.3568 | 4.3516 | 4.3474 | 4.3421 | 4.3368 | 4.3316 | 4.3263 | 4.3211 | 4.2147 | 4.0811 | 3.9684 | 4.0411 | 4.0263 | 4.0095 | 3.9905 | 3.9716 | 3.9505 | 3.9284 | 3.9053 | 3.8789 | 3.8474 | 3.7305 | 3.5958 | 3.4663 | 4.1842 | 4.1811 | 4.1758 | 4.1705 | 4.1653 | 4.1589 | 4.1368 | 4.1126 | 4.0842 | 4.0495 | 3.9168 | 3.7663 | 3.6389
| KEITH 2 | ABERLOUR | MINIMUM HEADROOM | NJ 24809 40878 | NO | YES | 0 | 5.5989 | 5.5411 | 5.4789 | 5.34 | 5.2779 | 5.2168 | 5.1495 | 5.0779 | 5.0179 | 4.9758 | 4.3916 | 4.2137 | 4.0705 | 4.8 | 4.7389 | 4.6737 | 4.5221 | 4.4568 | 4.3926 | 4.3211 | 4.2453 | 4.1832 | 4.1337 | 3.5053 | 3.3211 | 3.1737 | 5.7589 | 5.6989 | 5.6358 | 5.4958 | 5.4316 | 5.3695 | 5.3 | 5.2253 | 5.1653 | 5.1211 | 4.4621 | 4.2632 | 4.1032
|  | ABERLOUR | EE |  |  |  |  | 5.5989 | 5.5411 | 5.4789 | 5.34 | 5.2779 | 5.2168 | 5.1495 | 5.0779 | 5.0179 | 4.9758 | 4.3916 | 4.2137 | 4.0705 | 4.8 | 4.7389 | 4.6737 | 4.5221 | 4.4568 | 4.3926 | 4.3211 | 4.2453 | 4.1832 | 4.1368 | 3.5053 | 3.3211 | 3.1737 | 5.7589 | 5.6989 | 5.6358 | 5.4958 | 5.4316 | 5.3695 | 5.3 | 5.2253 | 5.1653 | 5.1211 | 4.4621 | 4.2632 | 4.1032
|  | ABERLOUR | HT |  |  |  |  | 5.6221 | 5.5705 | 5.5211 | 5.3926 | 5.3421 | 5.3063 | 5.2632 | 5.2221 | 5.1326 | 4.9832 | 4.5884 | 4.4526 | 4.3484 | 4.8242 | 4.7695 | 4.7189 | 4.5779 | 4.5232 | 4.4853 | 4.44 | 4.3968 | 4.2979 | 4.1337 | 3.7453 | 3.5989 | 3.4642 | 5.7832 | 5.7305 | 5.68 | 5.5505 | 5.4989 | 5.4632 | 5.4211 | 5.38 | 5.2905 | 5.1442 | 4.7137 | 4.5558 | 4.4074
|  | ABERLOUR | HE |  |  |  |  | 5.6716 | 5.6526 | 5.6358 | 5.5463 | 5.5263 | 5.5053 | 5.4811 | 5.46 | 5.4368 | 5.4221 | 4.9768 | 4.9232 | 4.8874 | 4.8768 | 4.8568 | 4.8389 | 4.7389 | 4.7179 | 4.6968 | 4.6716 | 4.6484 | 4.6242 | 4.6084 | 4.1126 | 4.0558 | 4.0189 | 5.8347 | 5.8158 | 5.8 | 5.7105 | 5.6916 | 5.6705 | 5.6463 | 5.6253 | 5.6021 | 5.5874 | 5.1095 | 5.0474 | 5.0063
|  | ABERLOUR | FB |  |  |  |  | 5.7116 | 5.7 | 5.6874 | 5.6453 | 5.6326 | 5.6211 | 5.6074 | 5.4621 | 5.4474 | 5.4305 | 5.3326 | 5.22 | 5.1705 | 4.9211 | 4.9074 | 4.8947 | 4.8474 | 4.8337 | 4.8211 | 4.8074 | 4.6453 | 4.6295 | 4.6105 | 4.5042 | 4.38 | 4.3253 | 5.8611 | 5.8579 | 5.8505 | 5.8084 | 5.7958 | 5.7842 | 5.7716 | 5.6284 | 5.6147 | 5.5968 | 5.5011 | 5.3905 | 5.3421
| ABERNETHY | ABERNETHY | MINIMUM HEADROOM | NO 20094 17132 | YES | YES | 0 | 2.3026 | 2.2963 | 2.2889 | 2.2805 | 2.2711 | 2.2616 | 2.2521 | 2.2426 | 5.2889 | 5.2321 | 5.0816 | 5.57 | 5.5237 | 2.1226 | 2.1016 | 2.0826 | 2.0595 | 2.0395 | 2.0163 | 1.9921 | 1.9711 | 4.95 | 4.8805 | 4.7153 | 5.1889 | 5.1174 | 2.1711 | 2.1553 | 2.1405 | 2.1226 | 2.1068 | 2.0858 | 2.0616 | 2.0405 | 5.2584 | 5.1889 | 5.0216 | 5.5363 | 5.4647
|  | ABERNETHY | EE |  |  |  |  | 2.3026 | 2.2963 | 2.2911 | 2.2847 | 2.2774 | 2.2668 | 2.2553 | 2.2458 | 5.3026 | 5.2879 | 5.0963 | 5.5921 | 5.5405 | 2.1226 | 2.1016 | 2.0826 | 2.0595 | 2.0395 | 2.0163 | 1.9921 | 1.9711 | 4.9647 | 4.9479 | 4.7153 | 5.1942 | 5.1321 | 2.1711 | 2.1553 | 2.1405 | 2.1226 | 2.1068 | 2.0858 | 2.0616 | 2.0405 | 5.2742 | 5.2574 | 5.0216 | 5.5416 | 5.4795
|  | ABERNETHY | HT |  |  |  |  | 2.3026 | 2.2963 | 2.2889 | 2.2805 | 2.2711 | 2.2616 | 2.2521 | 2.2426 | 5.2889 | 5.2321 | 5.0816 | 5.57 | 5.5237 | 2.1279 | 2.1089 | 2.09 | 2.0689 | 2.0458 | 2.0237 | 2.0026 | 1.9805 | 4.95 | 4.8805 | 4.7174 | 5.1889 | 5.1174 | 2.1753 | 2.1605 | 2.1447 | 2.1279 | 2.11 | 2.0921 | 2.0732 | 2.0511 | 5.2584 | 5.1889 | 5.0237 | 5.5363 | 5.4647
|  | ABERNETHY | HE |  |  |  |  | 2.3068 | 2.3005 | 2.2963 | 2.29 | 2.2837 | 2.2721 | 2.2626 | 2.2563 | 5.3374 | 5.3332 | 5.1984 | 5.7184 | 5.6858 | 2.1447 | 2.1311 | 2.1195 | 2.1068 | 2.0942 | 2.0774 | 2.0626 | 2.05 | 5.0489 | 5.0384 | 4.8363 | 5.3416 | 5.3026 | 2.1795 | 2.1732 | 2.1668 | 2.1563 | 2.1458 | 2.1311 | 2.1174 | 2.1068 | 5.3584 | 5.3479 | 5.1437 | 5.6911 | 5.6511
|  | ABERNETHY | FB |  |  |  |  | 2.31 | 2.3079 | 2.3058 | 2.3037 | 2.3005 | 2.2974 | 2.2942 | 2.2911 | 5.3742 | 5.3711 | 5.3374 | 5.8026 | 5.7658 | 2.1521 | 2.1437 | 2.1353 | 2.1268 | 2.1174 | 2.1079 | 2.0984 | 2.0889 | 5.0942 | 5.0837 | 4.9995 | 5.4384 | 5.3942 | 2.1826 | 2.1805 | 2.1784 | 2.1742 | 2.1668 | 2.1595 | 2.1521 | 2.1447 | 5.4037 | 5.3932 | 5.3089 | 5.7879 | 5.7437
| TARLAND | ABOYNE | MINIMUM HEADROOM | NO 52048 98716 | NO | YES | 0 | 15.9174 | 15.7721 | 15.5953 | 15.3668 | 15.1816 | 14.8216 | 14.5089 | 14.3574 | 14.2574 | 14.1574 | 13.5374 | 13.1342 | 12.8532 | 14.0884 | 13.9137 | 13.6968 | 13.4158 | 13.1926 | 12.7516 | 12.3916 | 12.2189 | 12.1084 | 11.9947 | 11.3821 | 10.9221 | 10.5168 | 14.5561 | 14.4013 | 14.2129 | 13.9613 | 13.7434 | 13.3139 | 12.9624 | 12.7929 | 12.6834 | 12.5729 | 11.975 | 11.5255 | 11.1297
|  | ABOYNE | EE |  |  |  |  | 15.9174 | 15.7721 | 15.5953 | 15.3668 | 15.1816 | 14.8216 | 14.5089 | 14.3574 | 14.2574 | 14.1574 | 13.6184 | 13.2563 | 12.9721 | 14.0884 | 13.9137 | 13.6968 | 13.4158 | 13.1926 | 12.7516 | 12.3916 | 12.2189 | 12.1084 | 11.9947 | 11.3821 | 10.9705 | 10.6442 | 14.5561 | 14.4013 | 14.2129 | 13.9613 | 13.7434 | 13.3139 | 12.9624 | 12.7929 | 12.6834 | 12.5729 | 11.975 | 11.5729 | 11.255
|  | ABOYNE | HT |  |  |  |  | 15.9437 | 15.7911 | 15.6132 | 15.3942 | 15.2005 | 14.9879 | 14.7742 | 14.5974 | 14.4426 | 14.2289 | 13.5374 | 13.1342 | 12.8532 | 14.1211 | 13.9358 | 13.72 | 13.4537 | 13.2189 | 12.9611 | 12.7042 | 12.5032 | 12.3274 | 12.0842 | 11.4095 | 10.9221 | 10.5168 | 14.5845 | 14.4213 | 14.2318 | 13.9982 | 13.7687 | 13.5171 | 13.2666 | 13.0697 | 12.8982 | 12.6603 | 12.0013 | 11.5255 | 11.1297
|  | ABOYNE | HE |  |  |  |  | 16.0058 | 15.8984 | 15.7637 | 15.5889 | 15.4447 | 15.1321 | 14.8679 | 14.7395 | 14.6721 | 14.6121 | 14.2363 | 14.0468 | 13.8858 | 14.1958 | 14.0684 | 13.9032 | 13.6895 | 13.5168 | 13.1337 | 12.8137 | 12.6632 | 12.5884 | 12.52 | 12.0863 | 11.8716 | 11.6853 | 14.6497 | 14.5371 | 14.3929 | 14.2055 | 14.0529 | 13.6855 | 13.3729 | 13.2266 | 13.1539 | 13.0866 | 12.6634 | 12.4539 | 12.2718
|  | ABOYNE | FB |  |  |  |  | 16.0658 | 16.0089 | 15.9416 | 15.8584 | 15.7995 | 15.6753 | 15.5174 | 15.3911 | 15.3447 | 15.2847 | 15.0511 | 14.8026 | 14.6205 | 14.2674 | 14.1989 | 14.1168 | 14.0147 | 13.9442 | 13.7916 | 13.5958 | 13.44 | 13.3853 | 13.3126 | 13.0337 | 12.7337 | 12.5242 | 14.7139 | 14.6529 | 14.5824 | 14.4929 | 14.4308 | 14.2971 | 14.1276 | 13.9855 | 13.9318 | 13.8613 | 13.5887 | 13.2961 | 13.0908
| GRUDIE BRIDGE | ACHILTIBUIE | MINIMUM HEADROOM | NC 01618 09557 | YES | NO | 0 | 0.4 | 0.39368 | 0.38947 | 0.38421 | 0.37789 | 0.37158 | 0.36526 | 0.35895 | 0.35368 | 0.34947 | 0.32947 | 0.29158 | 0.26211 | -0.61158 | -0.62316 | -0.63474 | -0.64842 | -0.66316 | -0.67789 | -0.69158 | -0.70421 | -0.71684 | -0.72737 | -0.76947 | -0.80947 | -0.84105 | 0.42316 | 0.41474 | 0.40737 | 0.39895 | 0.39053 | 0.38 | 0.37158 | 0.36316 | 0.35474 | 0.34842 | 0.31579 | 0.27263 | 0.23789
|  | ACHILTIBUIE | EE |  |  |  |  | 0.4 | 0.39368 | 0.38947 | 0.38421 | 0.37789 | 0.37158 | 0.36526 | 0.35895 | 0.35368 | 0.34947 | 0.32947 | 0.29158 | 0.26211 | -0.61158 | -0.62316 | -0.63474 | -0.64842 | -0.66316 | -0.67789 | -0.69158 | -0.70421 | -0.71684 | -0.72737 | -0.76947 | -0.80947 | -0.84105 | 0.42316 | 0.41474 | 0.40737 | 0.39895 | 0.39053 | 0.38 | 0.37158 | 0.36316 | 0.35474 | 0.34842 | 0.31579 | 0.27263 | 0.23789
|  | ACHILTIBUIE | HT |  |  |  |  | 0.4 | 0.39579 | 0.39158 | 0.38737 | 0.38316 | 0.37684 | 0.37263 | 0.36737 | 0.36105 | 0.35579 | 0.33474 | 0.30211 | 0.27684 | -0.60737 | -0.61895 | -0.62842 | -0.63895 | -0.65053 | -0.66526 | -0.67789 | -0.69053 | -0.70316 | -0.71579 | -0.75684 | -0.79789 | -0.83158 | 0.42421 | 0.41789 | 0.41263 | 0.40632 | 0.4 | 0.39053 | 0.38316 | 0.37684 | 0.36842 | 0.36105 | 0.33474 | 0.29263 | 0.25684
|  | ACHILTIBUIE | HE |  |  |  |  | 0.40316 | 0.39895 | 0.39579 | 0.39263 | 0.38842 | 0.38316 | 0.37789 | 0.37474 | 0.36947 | 0.36842 | 0.35895 | 0.35368 | 0.34842 | -0.6 | -0.60737 | -0.61474 | -0.62 | -0.62632 | -0.63368 | -0.64211 | -0.64947 | -0.65789 | -0.66421 | -0.68632 | -0.70737 | -0.72211 | 0.42842 | 0.42421 | 0.41895 | 0.41579 | 0.41053 | 0.40421 | 0.39789 | 0.39263 | 0.38737 | 0.38421 | 0.36947 | 0.35895 | 0.34947
|  | ACHILTIBUIE | FB |  |  |  |  | 0.40526 | 0.40316 | 0.40211 | 0.4 | 0.39789 | 0.39684 | 0.39474 | 0.39263 | 0.39158 | 0.38947 | 0.38211 | 0.37579 | 0.37053 | -0.59684 | -0.60105 | -0.60526 | -0.60947 | -0.61474 | -0.61789 | -0.62316 | -0.62737 | -0.63263 | -0.63895 | -0.66632 | -0.69053 | -0.71158 | 0.43053 | 0.42842 | 0.42737 | 0.42316 | 0.42105 | 0.41895 | 0.41579 | 0.41368 | 0.41053 | 0.40842 | 0.39474 | 0.38421 | 0.37368
| BEAULY | AIGAS | MINIMUM HEADROOM | NH 45362 40529 | YES | YES | 0 | 0.51579 | 0.51474 | 0.51368 | 0.51368 | 0.51263 | 0.51053 | 0.50947 | 0.50842 | 0.50632 | 0.50526 | 0.49895 | 0.49368 | 0.49158 | 0.50421 | 0.50316 | 0.50211 | 0.5 | 0.49789 | 0.49263 | 0.49158 | 0.48842 | 0.48632 | 0.48421 | 0.47895 | 0.47368 | 0.47053 | 0.50526 | 0.50421 | 0.50316 | 0.50316 | 0.50211 | 0.49789 | 0.49684 | 0.49368 | 0.49263 | 0.49053 | 0.48526 | 0.48 | 0.47684
|  | AIGAS | EE |  |  |  |  | 0.51579 | 0.51474 | 0.51474 | 0.51368 | 0.51263 | 0.51053 | 0.51053 | 0.50842 | 0.50632 | 0.50526 | 0.49895 | 0.49368 | 0.49158 | 0.50421 | 0.50316 | 0.50316 | 0.5 | 0.49789 | 0.49263 | 0.49158 | 0.48842 | 0.48632 | 0.48421 | 0.47895 | 0.47368 | 0.47053 | 0.50526 | 0.50421 | 0.50421 | 0.50316 | 0.50211 | 0.49789 | 0.49684 | 0.49368 | 0.49263 | 0.49053 | 0.48526 | 0.48 | 0.47684
|  | AIGAS | HT |  |  |  |  | 0.51579 | 0.51474 | 0.51474 | 0.51368 | 0.51263 | 0.51158 | 0.50947 | 0.50842 | 0.50737 | 0.50632 | 0.5 | 0.49474 | 0.49158 | 0.50421 | 0.50316 | 0.50316 | 0.50211 | 0.49895 | 0.49684 | 0.49368 | 0.49158 | 0.48947 | 0.48842 | 0.48105 | 0.47579 | 0.47053 | 0.50526 | 0.50421 | 0.50421 | 0.50316 | 0.50211 | 0.50105 | 0.49789 | 0.49684 | 0.49474 | 0.49263 | 0.48737 | 0.48211 | 0.47684
|  | AIGAS | HE |  |  |  |  | 0.51579 | 0.51579 | 0.51368 | 0.51368 | 0.51263 | 0.51263 | 0.51053 | 0.50947 | 0.50947 | 0.50842 | 0.50737 | 0.50632 | 0.50632 | 0.50421 | 0.50421 | 0.50211 | 0.50211 | 0.50105 | 0.50105 | 0.49895 | 0.49789 | 0.49789 | 0.49579 | 0.49368 | 0.49053 | 0.48947 | 0.50526 | 0.50526 | 0.50316 | 0.50316 | 0.50211 | 0.50211 | 0.5 | 0.49895 | 0.49895 | 0.49789 | 0.49684 | 0.49474 | 0.49474
|  | AIGAS | FB |  |  |  |  | 0.51684 | 0.51579 | 0.51579 | 0.51579 | 0.51579 | 0.51474 | 0.51474 | 0.51474 | 0.51368 | 0.51368 | 0.51263 | 0.51158 | 0.51053 | 0.50526 | 0.50421 | 0.50421 | 0.50421 | 0.50421 | 0.50316 | 0.50316 | 0.50316 | 0.50211 | 0.50211 | 0.49895 | 0.49474 | 0.49263 | 0.50632 | 0.50526 | 0.50526 | 0.50526 | 0.50526 | 0.50421 | 0.50421 | 0.50421 | 0.50316 | 0.50316 | 0.50211 | 0.5 | 0.49684
| ARDMORE | AIRD | MINIMUM HEADROOM | NF 79163 53853 | NO | YES | 0 | 7.5453 | 7.5179 | 7.4895 | 7.4558 | 7.3189 | 7.2674 | 7.2337 | 7.2032 | 7.1737 | 7.1484 | 5.0937 | 5.0021 | 4.9347 | 7.2979 | 7.2663 | 7.2358 | 7.1979 | 7.0389 | 6.9789 | 6.9432 | 6.9084 | 6.8758 | 6.8474 | 5.12 | 5.0232 | 4.9505 | 7.5432 | 7.5295 | 7.4989 | 7.4611 | 7.3011 | 7.2421 | 7.2063 | 7.1716 | 7.1389 | 7.1105 | 4.9768 | 4.8768 | 4.8011
|  | AIRD | EE |  |  |  |  | 7.5453 | 7.5179 | 7.4895 | 7.4558 | 7.4242 | 7.2674 | 7.2337 | 7.2032 | 7.1737 | 7.1484 | 5.0937 | 5.0021 | 4.9347 | 7.2979 | 7.2663 | 7.2358 | 7.1979 | 7.1621 | 6.9789 | 6.9432 | 6.9084 | 6.8758 | 6.8474 | 5.12 | 5.0232 | 4.9505 | 7.5432 | 7.5295 | 7.4989 | 7.4611 | 7.4253 | 7.2421 | 7.2063 | 7.1716 | 7.1389 | 7.1105 | 4.9768 | 4.8768 | 4.8011
|  | AIRD | HT |  |  |  |  | 7.5526 | 7.5274 | 7.5021 | 7.4758 | 7.3189 | 7.2884 | 7.2579 | 7.2274 | 7.1968 | 7.1663 | 5.48 | 5.3895 | 5.3263 | 7.3063 | 7.2789 | 7.2505 | 7.22 | 7.0389 | 7.0042 | 6.9705 | 6.9368 | 6.9032 | 6.8695 | 5.4726 | 5.3695 | 5.2842 | 7.5442 | 7.5337 | 7.5137 | 7.4832 | 7.3011 | 7.2674 | 7.2337 | 7.2 | 7.1663 | 7.1326 | 5.4095 | 5.3032 | 5.2147
|  | AIRD | HE |  |  |  |  | 7.5705 | 7.5537 | 7.5368 | 7.52 | 7.5 | 7.3558 | 7.3337 | 7.3158 | 7.2968 | 7.2832 | 6.4484 | 6.4 | 6.3674 | 7.3274 | 7.3084 | 7.2895 | 7.2716 | 7.2505 | 7.0821 | 7.0589 | 7.04 | 7.0189 | 7.0032 | 6.3063 | 6.2547 | 6.22 | 7.5484 | 7.54 | 7.5305 | 7.5221 | 7.5095 | 7.3453 | 7.3221 | 7.3032 | 7.2821 | 7.2663 | 6.4063 | 6.3516 | 6.3137
|  | AIRD | FB |  |  |  |  | 7.5821 | 7.5695 | 7.5589 | 7.5463 | 7.5347 | 7.5221 | 7.4537 | 7.4421 | 7.4274 | 7.4105 | 7.3484 | 7.2853 | 7.2379 | 7.3389 | 7.3263 | 7.3137 | 7.3 | 7.2863 | 7.2716 | 7.1926 | 7.18 | 7.1632 | 7.1442 | 7.0747 | 7.0032 | 6.9474 | 7.5537 | 7.5495 | 7.5463 | 7.5411 | 7.5368 | 7.5316 | 7.4558 | 7.4432 | 7.4263 | 7.4074 | 7.3379 | 7.2653 | 7.2105
| PORT ANN | AIRIGH-NA-BRODAIG | MINIMUM HEADROOM | NR 85849 74792 | YES | YES | 0 | 0.32026 | 0.32026 | 0.31921 | 0.31921 | 0.31921 | 0.31816 | 0.31816 | 0.31816 | 0.31711 | 0.31605 | 0.315 | 0.315 | 0.31289 | 0.32132 | 0.32132 | 0.31921 | 0.31921 | 0.31921 | 0.31816 | 0.31816 | 0.31816 | 0.31711 | 0.31711 | 0.315 | 0.315 | 0.31289 | 0.31816 | 0.31816 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.315 | 0.31395 | 0.31184 | 0.31184 | 0.30974
|  | AIRIGH-NA-BRODAIG | EE |  |  |  |  | 0.32026 | 0.32026 | 0.31921 | 0.31921 | 0.31921 | 0.31816 | 0.31816 | 0.31816 | 0.31711 | 0.31605 | 0.315 | 0.315 | 0.31395 | 0.32132 | 0.32132 | 0.31921 | 0.31921 | 0.31921 | 0.31816 | 0.31816 | 0.31816 | 0.31711 | 0.31711 | 0.315 | 0.315 | 0.31395 | 0.31816 | 0.31816 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.315 | 0.31395 | 0.31184 | 0.31184 | 0.31079
|  | AIRIGH-NA-BRODAIG | HT |  |  |  |  | 0.32026 | 0.32026 | 0.31921 | 0.31921 | 0.31921 | 0.31921 | 0.31816 | 0.31816 | 0.31711 | 0.31711 | 0.315 | 0.315 | 0.31289 | 0.32132 | 0.32132 | 0.31921 | 0.31921 | 0.31921 | 0.31921 | 0.31816 | 0.31816 | 0.31711 | 0.31711 | 0.31605 | 0.315 | 0.31289 | 0.31816 | 0.31816 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.315 | 0.315 | 0.31289 | 0.31184 | 0.30974
|  | AIRIGH-NA-BRODAIG | HE |  |  |  |  | 0.32132 | 0.32026 | 0.32026 | 0.31921 | 0.31921 | 0.31921 | 0.31921 | 0.31921 | 0.31921 | 0.31921 | 0.31711 | 0.31711 | 0.31711 | 0.32132 | 0.32132 | 0.32132 | 0.32026 | 0.32026 | 0.32026 | 0.31921 | 0.31921 | 0.31921 | 0.31921 | 0.31711 | 0.31711 | 0.31711 | 0.31921 | 0.31816 | 0.31816 | 0.31711 | 0.31711 | 0.31711 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.315 | 0.315 | 0.315
|  | AIRIGH-NA-BRODAIG | FB |  |  |  |  | 0.32132 | 0.32132 | 0.32026 | 0.32026 | 0.32026 | 0.32026 | 0.31921 | 0.31921 | 0.31921 | 0.31921 | 0.31816 | 0.31816 | 0.31605 | 0.32132 | 0.32132 | 0.32132 | 0.32132 | 0.32132 | 0.32132 | 0.32026 | 0.31921 | 0.31921 | 0.31921 | 0.31816 | 0.31816 | 0.31711 | 0.31921 | 0.31921 | 0.31816 | 0.31816 | 0.31816 | 0.31816 | 0.31711 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.31395
| COUPAR ANGUS | ALYTH | MINIMUM HEADROOM | NO 23579 48311 | NO | YES | 0.2 | 4.7463 | 4.6832 | 4.4926 | 4.1895 | 4.0137 | 3.7747 | 3.5863 | 3.3947 | 3.1726 | 3.0421 | 2.0621 | 1.8284 | 1.6663 | 4.6842 | 4.4558 | 4.1958 | 3.7832 | 3.5463 | 3.2232 | 2.9737 | 2.7495 | 2.4863 | 2.3347 | 1.4074 | 1.1368 | 0.94842 | 4.7316 | 4.5326 | 4.2874 | 3.8842 | 3.6537 | 3.3379 | 3.0947 | 2.8747 | 2.6179 | 2.4663 | 1.4137 | 1.1421 | 0.95368
|  | ALYTH | EE |  |  |  |  | 4.7463 | 4.6832 | 4.5158 | 4.2758 | 4.1105 | 3.8695 | 3.6863 | 3.4926 | 3.2453 | 3.1968 | 2.0621 | 1.8284 | 1.6663 | 4.6842 | 4.4558 | 4.2274 | 3.8989 | 3.6758 | 3.3516 | 3.1074 | 2.8653 | 2.5716 | 2.5168 | 1.4074 | 1.1368 | 0.94842 | 4.7316 | 4.5326 | 4.3179 | 3.9979 | 3.78 | 3.4632 | 3.2253 | 2.9874 | 2.7021 | 2.6484 | 1.4137 | 1.1421 | 0.95368
|  | ALYTH | HT |  |  |  |  | 4.7484 | 4.6947 | 4.4926 | 4.1895 | 4.0137 | 3.7747 | 3.5863 | 3.3947 | 3.1726 | 3.0421 | 2.1263 | 1.9168 | 1.7716 | 4.6937 | 4.4705 | 4.1958 | 3.7832 | 3.5463 | 3.2232 | 2.9737 | 2.7495 | 2.4863 | 2.3347 | 1.5011 | 1.2537 | 1.04 | 4.74 | 4.5463 | 4.2874 | 3.8842 | 3.6537 | 3.3379 | 3.0947 | 2.8747 | 2.6179 | 2.4663 | 1.5316 | 1.2842 | 1.0705
|  | ALYTH | HE |  |  |  |  | 4.76 | 4.7263 | 4.5821 | 4.3463 | 4.2011 | 3.9611 | 3.7242 | 3.5474 | 3.2937 | 3.2674 | 2.7011 | 2.5874 | 2.4905 | 4.7389 | 4.5358 | 4.3137 | 3.9916 | 3.7968 | 3.4737 | 3.1547 | 2.9263 | 2.6232 | 2.5937 | 2.0158 | 1.8842 | 1.7705 | 4.78 | 4.6032 | 4.4032 | 4.0884 | 3.8989 | 3.5832 | 3.2716 | 3.0484 | 2.7537 | 2.7232 | 2.0979 | 1.9653 | 1.8526
|  | ALYTH | FB |  |  |  |  | 4.7789 | 4.7663 | 4.7526 | 4.7368 | 4.7211 | 4.6295 | 4.5484 | 4.4432 | 4.3305 | 4.3011 | 3.9863 | 3.7474 | 3.6579 | 4.8632 | 4.7853 | 4.6926 | 4.5853 | 4.5042 | 4.3789 | 4.2705 | 4.1263 | 3.9716 | 3.9358 | 3.5095 | 3.1884 | 3.0684 | 4.8874 | 4.82 | 4.74 | 4.6463 | 4.5758 | 4.4663 | 4.36 | 4.22 | 4.0695 | 4.0337 | 3.6179 | 3.3042 | 3.1874
| FORT WILLIAM | ANNAT | MINIMUM HEADROOM | NN 08452 76751 | YES | NO | 0 | 6.9263 | 6.8863 | 6.8505 | 6.8074 | 6.7653 | 4.9368 | 2.7432 | 0.44316 | -0.72632 | -1.1379 | -2.3074 | -2.4537 | -2.5589 | 6.62 | 6.5779 | 6.5379 | 6.4916 | 6.4453 | 4.2568 | 1.6789 | -1.0242 | -2.3947 | -2.8758 | -4.2021 | -4.3768 | -4.4874 | 6.4253 | 6.3926 | 6.3621 | 6.3253 | 6.2895 | 4.2084 | 1.6337 | -1.0642 | -2.4347 | -2.9137 | -4.2421 | -4.4432 | -4.5621
|  | ANNAT | EE |  |  |  |  | 6.9263 | 6.8863 | 6.8505 | 6.8074 | 6.7653 | 6.7189 | 6.6737 | 4.8989 | 2.6905 | 0.30632 | -2.0947 | -2.4537 | -2.5589 | 6.62 | 6.5779 | 6.5379 | 6.4916 | 6.4453 | 6.3947 | 6.3463 | 4.2347 | 1.64 | -1.1621 | -3.9695 | -4.3768 | -4.4874 | 6.4253 | 6.3926 | 6.3621 | 6.3253 | 6.2895 | 6.2484 | 6.2095 | 4.1716 | 1.5789 | -1.2179 | -4.0274 | -4.4432 | -4.5621
|  | ANNAT | HT |  |  |  |  | 6.9389 | 6.9042 | 6.8716 | 6.8358 | 6.7926 | 4.9368 | 2.7432 | 0.44316 | -0.72632 | -1.1379 | -2.3074 | -2.4337 | -2.52 | 6.6347 | 6.5968 | 6.5611 | 6.5221 | 6.4737 | 4.2568 | 1.6789 | -1.0242 | -2.3947 | -2.8758 | -4.2021 | -4.3516 | -4.4716 | 6.4368 | 6.4074 | 6.3811 | 6.3516 | 6.3147 | 4.2084 | 1.6337 | -1.0642 | -2.4347 | -2.9137 | -4.2421 | -4.3937 | -4.5147
|  | ANNAT | HE |  |  |  |  | 6.9611 | 6.9347 | 6.9126 | 6.8874 | 6.86 | 6.8316 | 6.8 | 4.8368 | 2.3895 | -0.25789 | -1.8474 | -2.1495 | -2.2074 | 6.6589 | 6.6305 | 6.6063 | 6.58 | 6.5495 | 6.52 | 6.4874 | 4.1442 | 1.2674 | -1.8453 | -3.7084 | -4.0579 | -4.1221 | 6.4537 | 6.4295 | 6.4116 | 6.3905 | 6.3653 | 6.34 | 6.3126 | 4.0937 | 1.2221 | -1.8853 | -3.7484 | -4.1 | -4.1663
|  | ANNAT | FB |  |  |  |  | 6.9726 | 6.9589 | 6.9432 | 6.9284 | 6.9105 | 6.8926 | 6.8779 | 6.86 | 6.0547 | 5.0063 | 1.7042 | 1.3284 | 1.2653 | 6.6737 | 6.6579 | 6.64 | 6.6232 | 6.6032 | 6.5842 | 6.5674 | 6.5474 | 5.6095 | 4.3316 | 0.45053 | 0.012632 | -0.06 | 6.4642 | 6.4526 | 6.44 | 6.4284 | 6.4137 | 6.4 | 6.3874 | 6.3716 | 5.56 | 4.2842 | 0.40947 | -0.028421 | -0.1
| KILLIN | ARDCHYLE | MINIMUM HEADROOM | NN 52734 29223 | YES | YES | 0 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947
|  | ARDCHYLE | EE |  |  |  |  | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947
|  | ARDCHYLE | HT |  |  |  |  | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947
|  | ARDCHYLE | HE |  |  |  |  | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.098947
|  | ARDCHYLE | FB |  |  |  |  | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1
| NAIRN | ARDERSIER | MINIMUM HEADROOM | NH 80475 55905 | NO | YES | 0 | 5.0874 | 5.0716 | 5.0589 | 5.0442 | 5.0274 | 4.9063 | 4.4389 | 3.4358 | 2.2063 | 1.3695 | 0.28526 | 0.18947 | 0.12421 | 5.2316 | 5.1989 | 5.1705 | 5.1379 | 5.1042 | 4.6305 | 3.8611 | 2.6811 | 1.2326 | 0.24737 | -1.0021 | -1.1105 | -1.2042 | 5.3032 | 5.2726 | 5.2453 | 5.2147 | 5.1821 | 4.7421 | 3.9979 | 2.8242 | 1.3758 | 0.39053 | -0.86 | -0.96842 | -1.0621
|  | ARDERSIER | EE |  |  |  |  | 5.0874 | 5.0716 | 5.0589 | 5.0442 | 5.0274 | 5.0063 | 4.9853 | 4.8695 | 4.3305 | 3.3147 | 0.30421 | 0.21158 | 0.13895 | 5.2316 | 5.1989 | 5.1705 | 5.1379 | 5.1042 | 5.0632 | 5.0263 | 4.5653 | 3.7389 | 2.5421 | -1.0021 | -1.1063 | -1.1884 | 5.3032 | 5.2726 | 5.2453 | 5.2147 | 5.1821 | 5.1432 | 5.1074 | 4.68 | 3.8789 | 2.6863 | -0.86 | -0.96421 | -1.0463
|  | ARDERSIER | HT |  |  |  |  | 5.0905 | 5.0768 | 5.0621 | 5.0474 | 5.0295 | 4.9063 | 4.4389 | 3.4358 | 2.2063 | 1.3695 | 0.28526 | 0.18947 | 0.12421 | 5.2411 | 5.2116 | 5.1842 | 5.1568 | 5.1179 | 4.6305 | 3.8611 | 2.6811 | 1.2326 | 0.24737 | -0.99158 | -1.1105 | -1.2042 | 5.3126 | 5.2853 | 5.2589 | 5.2316 | 5.1958 | 4.7421 | 3.9979 | 2.8242 | 1.3758 | 0.39053 | -0.84842 | -0.96842 | -1.0621
|  | ARDERSIER | HE |  |  |  |  | 5.0989 | 5.0853 | 5.0768 | 5.0653 | 5.0505 | 5.0337 | 5.0158 | 4.8916 | 4.3116 | 3.1158 | 0.46526 | 0.40737 | 0.36526 | 5.2611 | 5.2411 | 5.2242 | 5.2053 | 5.1811 | 5.1579 | 5.1305 | 4.6274 | 3.7137 | 2.3042 | -0.82 | -0.88526 | -0.93368 | 5.3337 | 5.3116 | 5.2958 | 5.2779 | 5.2547 | 5.2316 | 5.2053 | 4.7389 | 3.8537 | 2.4474 | -0.67789 | -0.74316 | -0.79053
|  | ARDERSIER | FB |  |  |  |  | 5.1053 | 5.1 | 5.0937 | 5.0884 | 5.0821 | 5.0747 | 5.0674 | 5.0611 | 4.9989 | 4.9084 | 2.5042 | 2.3347 | 2.2842 | 5.2716 | 5.26 | 5.2474 | 5.2347 | 5.22 | 5.2053 | 5.1895 | 5.1747 | 4.9242 | 4.5505 | 1.5747 | 1.3779 | 1.32 | 5.3432 | 5.3316 | 5.3189 | 5.3074 | 5.2926 | 5.2779 | 5.2642 | 5.2495 | 5.0168 | 4.6705 | 1.7179 | 1.52 | 1.4632
| FORT AUGUSTUS | ARDOCHY | MINIMUM HEADROOM | NH 47714 12561 | YES | YES | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.097895
|  | ARDOCHY | EE |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947
|  | ARDOCHY | HT |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.097895
|  | ARDOCHY | HE |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | ARDOCHY | FB |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1
| FORT WILLIAM | ARISAIG | MINIMUM HEADROOM | NM 66564 86619 | YES | NO | 0 | 2.4263 | 2.4137 | 2.4042 | 2.3895 | 2.3758 | 2.3621 | 2.3474 | 2.3347 | 2.3242 | 2.3116 | 2.2695 | 2.2316 | 2.2084 | 2.4147 | 2.4 | 2.3884 | 2.3726 | 2.3579 | 2.3421 | 2.3263 | 2.3126 | 2.3011 | 2.2874 | 2.2432 | 2.2021 | 2.1726 | 2.4137 | 2.3989 | 2.3884 | 2.3716 | 2.3568 | 2.3411 | 2.3263 | 2.3116 | 2.3 | 2.2863 | 2.2421 | 2.2021 | 2.1726
|  | ARISAIG | EE |  |  |  |  | 2.4263 | 2.4137 | 2.4042 | 2.3895 | 2.3758 | 2.3621 | 2.3474 | 2.3347 | 2.3242 | 2.3116 | 2.2726 | 2.2358 | 2.2105 | 2.4147 | 2.4 | 2.3884 | 2.3726 | 2.3579 | 2.3421 | 2.3263 | 2.3126 | 2.3011 | 2.2874 | 2.2432 | 2.2021 | 2.1737 | 2.4137 | 2.3989 | 2.3884 | 2.3716 | 2.3568 | 2.3411 | 2.3263 | 2.3116 | 2.3 | 2.2863 | 2.2421 | 2.2021 | 2.1726
|  | ARISAIG | HT |  |  |  |  | 2.4295 | 2.4189 | 2.4084 | 2.3958 | 2.3832 | 2.3695 | 2.3568 | 2.3442 | 2.3326 | 2.32 | 2.2695 | 2.2316 | 2.2084 | 2.4179 | 2.4053 | 2.3937 | 2.3811 | 2.3663 | 2.3505 | 2.3379 | 2.3242 | 2.3105 | 2.2968 | 2.2505 | 2.2074 | 2.1726 | 2.4168 | 2.4053 | 2.3937 | 2.38 | 2.3653 | 2.3505 | 2.3368 | 2.3232 | 2.3095 | 2.2958 | 2.2505 | 2.2063 | 2.1726
|  | ARISAIG | HE |  |  |  |  | 2.4368 | 2.4305 | 2.4232 | 2.4158 | 2.4095 | 2.4 | 2.3905 | 2.3821 | 2.3758 | 2.3705 | 2.3474 | 2.3274 | 2.3147 | 2.4263 | 2.4189 | 2.4105 | 2.4032 | 2.3968 | 2.3863 | 2.3768 | 2.3674 | 2.36 | 2.3547 | 2.3284 | 2.3063 | 2.2916 | 2.4253 | 2.4179 | 2.4105 | 2.4021 | 2.3958 | 2.3853 | 2.3758 | 2.3674 | 2.3589 | 2.3537 | 2.3274 | 2.3053 | 2.2916
|  | ARISAIG | FB |  |  |  |  | 2.4421 | 2.4379 | 2.4337 | 2.4284 | 2.4232 | 2.4168 | 2.4126 | 2.4074 | 2.4021 | 2.3947 | 2.3705 | 2.3453 | 2.3253 | 2.4326 | 2.4263 | 2.4221 | 2.4158 | 2.4105 | 2.4042 | 2.3989 | 2.3937 | 2.3863 | 2.3789 | 2.3516 | 2.3221 | 2.3 | 2.4316 | 2.4263 | 2.4211 | 2.4158 | 2.4095 | 2.4032 | 2.3979 | 2.3926 | 2.3863 | 2.3779 | 2.3505 | 2.3221 | 2.3
| ELGIN | ASHGROVE | MINIMUM HEADROOM | NJ 22458 62130 | YES | YES | 0 | 8.6379 | 35.6842 | 34.7726 | 34.0653 | 33.3284 | 32.6674 | 31.5916 | 31.1432 | 30.1526 | 28.0958 | 17.4368 | 17.0495 | 16.7611 | 8.4074 | 33.9737 | 32.9063 | 32.08 | 31.22 | 30.4526 | 29.1979 | 28.6779 | 27.52 | 25.1063 | 13.5284 | 12.2337 | 11.8232 | 10.5411 | 37.1411 | 36.1042 | 35.3011 | 34.4579 | 33.6937 | 32.4432 | 31.9242 | 30.7695 | 28.3642 | 16.82 | 15.5284 | 15.12
|  | ASHGROVE | EE |  |  |  |  | 8.6379 | 35.6842 | 34.7726 | 34.0653 | 33.3284 | 32.6674 | 31.5916 | 31.1432 | 30.6421 | 30.2305 | 23.2789 | 20.2716 | 19.9705 | 8.4074 | 33.9737 | 32.9063 | 32.08 | 31.22 | 30.4526 | 29.1979 | 28.6779 | 28.0968 | 27.6189 | 19.4589 | 15.9347 | 15.5926 | 10.5411 | 37.1411 | 36.1042 | 35.3011 | 34.4579 | 33.6937 | 32.4432 | 31.9242 | 31.3453 | 30.8684 | 22.7337 | 19.2189 | 18.8779
|  | ASHGROVE | HT |  |  |  |  | 8.66 | 35.7516 | 34.8337 | 34.1347 | 33.3789 | 32.9158 | 32.2716 | 31.5726 | 30.1526 | 28.0958 | 17.4368 | 17.0495 | 16.7611 | 8.4326 | 34.0516 | 32.9779 | 32.1621 | 31.2821 | 30.7453 | 29.9958 | 29.1821 | 27.52 | 25.1063 | 13.5284 | 12.2337 | 11.8232 | 10.5653 | 37.2168 | 36.1737 | 35.38 | 34.5211 | 33.9853 | 33.2389 | 32.4274 | 30.7695 | 28.3642 | 16.82 | 15.5284 | 15.12
|  | ASHGROVE | HE |  |  |  |  | 8.7284 | 35.8611 | 34.9958 | 34.3389 | 33.6411 | 33.2053 | 32.1432 | 31.6832 | 31.1526 | 30.7589 | 20.7705 | 17.9832 | 17.8432 | 8.5095 | 34.1768 | 33.1632 | 32.3968 | 31.5832 | 31.08 | 29.8411 | 29.3074 | 28.6884 | 28.2274 | 16.4747 | 13.2011 | 13.0421 | 10.64 | 37.34 | 36.3547 | 35.6095 | 34.8189 | 34.32 | 33.0842 | 32.5516 | 31.9347 | 31.4758 | 19.7579 | 16.4937 | 16.3358
|  | ASHGROVE | FB |  |  |  |  | 9.4126 | 37.1621 | 36.8189 | 36.5779 | 36.3589 | 36.0316 | 35.6084 | 35.2937 | 35.0558 | 34.8516 | 31.7747 | 26.2884 | 26.0947 | 9.3126 | 35.7032 | 35.3011 | 35.02 | 34.7653 | 34.3832 | 33.8884 | 33.5211 | 33.2453 | 33.0084 | 29.3979 | 22.9474 | 22.7253 | 11.4211 | 38.8221 | 38.4316 | 38.1579 | 37.9105 | 37.5389 | 37.0579 | 36.7011 | 36.4326 | 36.2011 | 32.6432 | 26.2116 | 25.9905
| MILTON OF CRAIGIE | ASHLUDIE | MINIMUM HEADROOM | NO 49222 33584 | NO | YES | 0 | 12.4589 | 12.1358 | 30.9274 | 30.6642 | 30.4158 | 30.1684 | 29.8884 | 29.5989 | 29.3547 | 29.1537 | 28.2653 | 27.5895 | 27.0979 | 11.3074 | 10.9463 | 28.2021 | 27.9147 | 27.6442 | 27.3789 | 27.0779 | 26.7642 | 26.4958 | 26.2768 | 25.3 | 24.5568 | 24.0126 | 11.5453 | 11.1947 | 29.21 | 28.9268 | 28.6605 | 28.3984 | 28.1005 | 27.79 | 27.5216 | 27.2984 | 26.3079 | 25.5532 | 25.0005
|  | ASHLUDIE | EE |  |  |  |  | 12.4589 | 12.1358 | 30.9274 | 30.6642 | 30.4158 | 30.1684 | 29.8884 | 29.5989 | 29.3547 | 29.1537 | 28.2653 | 27.5895 | 27.0979 | 11.3074 | 10.9463 | 28.2021 | 27.9147 | 27.6442 | 27.3789 | 27.0779 | 26.7642 | 26.4958 | 26.2768 | 25.3 | 24.5568 | 24.0126 | 11.5453 | 11.1947 | 29.21 | 28.9268 | 28.6605 | 28.3984 | 28.1005 | 27.79 | 27.5216 | 27.2984 | 26.3079 | 25.5532 | 25.0005
|  | ASHLUDIE | HT |  |  |  |  | 12.5526 | 12.2611 | 31.0853 | 30.8505 | 30.6474 | 30.4884 | 30.2874 | 30.0768 | 29.8568 | 29.6695 | 28.8832 | 28.3526 | 27.9611 | 11.4105 | 11.0832 | 28.3758 | 28.1221 | 27.8989 | 27.7242 | 27.4989 | 27.2632 | 27.0147 | 26.8074 | 26.0905 | 25.4568 | 24.9084 | 11.6474 | 11.3305 | 29.3816 | 29.1321 | 28.9153 | 28.7447 | 28.5289 | 28.3047 | 28.0637 | 27.8553 | 27.1363 | 26.4963 | 25.9437
|  | ASHLUDIE | HE |  |  |  |  | 12.7653 | 12.6011 | 31.5663 | 31.4684 | 31.3653 | 31.2463 | 31.1253 | 31.0179 | 30.8947 | 30.8137 | 30.4105 | 30.1884 | 30.0253 | 11.6432 | 11.4547 | 28.8979 | 28.7916 | 28.6789 | 28.5505 | 28.4211 | 28.3011 | 28.1621 | 28.0705 | 27.6063 | 27.3526 | 27.1642 | 11.8768 | 11.6989 | 29.9016 | 29.7984 | 29.6911 | 29.5658 | 29.4405 | 29.3258 | 29.1932 | 29.1058 | 28.6679 | 28.4237 | 28.2363
|  | ASHLUDIE | FB |  |  |  |  | 12.8526 | 12.7632 | 31.7747 | 31.7095 | 31.64 | 31.5695 | 31.4989 | 31.4337 | 31.3558 | 31.2716 | 30.9179 | 30.6 | 30.3926 | 11.7432 | 11.6389 | 29.1368 | 29.0621 | 28.9832 | 28.9032 | 28.8232 | 28.7495 | 28.66 | 28.5653 | 28.1589 | 27.7947 | 27.5526 | 11.9716 | 11.8737 | 30.1279 | 30.0563 | 29.9826 | 29.9058 | 29.83 | 29.7595 | 29.6753 | 29.5858 | 29.2016 | 28.8574 | 28.6247
| GRUDIE BRIDGE | AULTBEA | MINIMUM HEADROOM | NG 87458 88885 | YES | NO | 0 | 0.55158 | 0.52316 | 0.49579 | 0.46316 | 0.43053 | 0.28 | 0.16947 | 0.083158 | 0.031579 | -0.0031579 | -0.13263 | -0.22632 | -0.29684 | 0.91263 | 0.89053 | 0.86632 | 0.84211 | 0.81474 | 0.70842 | 0.62842 | 0.53158 | 0.47053 | 0.43474 | 0.28211 | 0.17368 | 0.083158 | 0.93684 | 0.91789 | 0.89895 | 0.87895 | 0.85684 | 0.78211 | 0.64316 | 0.53579 | 0.47474 | 0.43263 | 0.27684 | 0.16526 | 0.085263
|  | AULTBEA | EE |  |  |  |  | 0.55158 | 0.52316 | 0.49579 | 0.46316 | 0.43053 | 0.39368 | 0.35789 | 0.19368 | 0.081053 | -0.0031579 | -0.13263 | -0.22632 | -0.29158 | 0.91263 | 0.89053 | 0.86632 | 0.84211 | 0.81474 | 0.78526 | 0.75474 | 0.63684 | 0.53895 | 0.43474 | 0.28211 | 0.17368 | 0.097895 | 0.93684 | 0.91789 | 0.89895 | 0.87895 | 0.85684 | 0.83053 | 0.80526 | 0.67895 | 0.53789 | 0.43263 | 0.27684 | 0.16526 | 0.087368
|  | AULTBEA | HT |  |  |  |  | 0.56 | 0.53579 | 0.51158 | 0.48316 | 0.45053 | 0.28 | 0.16947 | 0.083158 | 0.031579 | 0.0052632 | -0.12737 | -0.22526 | -0.29684 | 0.91895 | 0.9 | 0.88 | 0.85684 | 0.83053 | 0.70842 | 0.62842 | 0.53158 | 0.47053 | 0.44 | 0.31368 | 0.18947 | 0.083158 | 0.94211 | 0.92632 | 0.90947 | 0.89053 | 0.86842 | 0.78211 | 0.64316 | 0.53579 | 0.47474 | 0.44316 | 0.31684 | 0.19158 | 0.085263
|  | AULTBEA | HE |  |  |  |  | 0.57684 | 0.55895 | 0.54421 | 0.52737 | 0.50526 | 0.48421 | 0.46526 | 0.29579 | 0.18632 | 0.11684 | 0.053684 | 0.0031579 | -0.029474 | 0.93158 | 0.91789 | 0.90526 | 0.88947 | 0.87158 | 0.85263 | 0.83474 | 0.71368 | 0.63579 | 0.57684 | 0.50211 | 0.44105 | 0.40316 | 0.95158 | 0.93895 | 0.92947 | 0.91579 | 0.89895 | 0.88105 | 0.86526 | 0.78526 | 0.66842 | 0.58 | 0.50421 | 0.44316 | 0.40421
|  | AULTBEA | FB |  |  |  |  | 0.58737 | 0.57789 | 0.56526 | 0.55474 | 0.54211 | 0.53053 | 0.51895 | 0.50842 | 0.43368 | 0.37158 | 0.23895 | 0.17789 | 0.13474 | 0.94211 | 0.93474 | 0.92421 | 0.91579 | 0.90632 | 0.89579 | 0.88737 | 0.87895 | 0.82526 | 0.78105 | 0.68421 | 0.63789 | 0.59368 | 0.96 | 0.95474 | 0.94632 | 0.94 | 0.93158 | 0.92421 | 0.91684 | 0.90947 | 0.87474 | 0.84421 | 0.72526 | 0.65158 | 0.59895
| BOAT OF GARTEN | AVIEMORE | MINIMUM HEADROOM | NH 89856 11394 | NO | YES | 0 | 18.1253 | 18.0916 | 18.06 | 17.9242 | 17.8126 | 17.6884 | 17.5684 | 17.4663 | 17.36 | 17.2705 | 16.8674 | 16.5126 | 16.2653 | 17.3442 | 17.2084 | 17.0874 | 16.9263 | 16.7926 | 16.6484 | 16.5095 | 16.3884 | 16.2674 | 16.1653 | 15.7411 | 15.3421 | 15.0211 | 17.1526 | 17.0021 | 16.8926 | 16.7474 | 16.6274 | 16.4968 | 16.3705 | 16.2611 | 16.1516 | 16.06 | 15.6779 | 15.3221 | 15.0326
|  | AVIEMORE | EE |  |  |  |  | 18.1253 | 18.0916 | 18.06 | 17.9242 | 17.8126 | 17.6884 | 17.5684 | 17.4663 | 17.36 | 17.2705 | 16.8968 | 16.5505 | 16.2916 | 17.3442 | 17.2084 | 17.0874 | 16.9263 | 16.7926 | 16.6484 | 16.5095 | 16.3884 | 16.2674 | 16.1653 | 15.7411 | 15.3421 | 15.0411 | 17.1526 | 17.0021 | 16.8926 | 16.7474 | 16.6274 | 16.4968 | 16.3705 | 16.2611 | 16.1516 | 16.06 | 15.6779 | 15.3221 | 15.0568
|  | AVIEMORE | HT |  |  |  |  | 18.1295 | 18.0989 | 18.0674 | 17.9853 | 17.8705 | 17.7642 | 17.6589 | 17.5537 | 17.4537 | 17.3474 | 16.8674 | 16.5126 | 16.2653 | 17.3495 | 17.2484 | 17.1389 | 17.0042 | 16.8695 | 16.7442 | 16.6211 | 16.4989 | 16.3821 | 16.26 | 15.8137 | 15.38 | 15.0211 | 17.1789 | 17.0389 | 16.9379 | 16.8147 | 16.6916 | 16.5789 | 16.4684 | 16.3568 | 16.2505 | 16.14 | 15.7389 | 15.3526 | 15.0326
|  | AVIEMORE | HE |  |  |  |  | 18.1379 | 18.1063 | 18.0853 | 18.0558 | 18.0168 | 17.9705 | 17.9105 | 17.8484 | 17.78 | 17.7337 | 17.5305 | 17.3432 | 17.2084 | 17.3611 | 17.3242 | 17.2568 | 17.1663 | 17.0905 | 17.0158 | 16.9379 | 16.8674 | 16.7895 | 16.7347 | 16.4905 | 16.2621 | 16.1042 | 17.2347 | 17.1158 | 17.0442 | 16.9621 | 16.8905 | 16.8189 | 16.7432 | 16.6779 | 16.6053 | 16.5568 | 16.3379 | 16.1368 | 15.9979
|  | AVIEMORE | FB |  |  |  |  | 18.1589 | 18.1484 | 18.1368 | 18.1242 | 18.1105 | 18.0968 | 18.0821 | 18.0674 | 18.0526 | 18.0358 | 17.84 | 17.6179 | 17.4442 | 17.3863 | 17.3726 | 17.3589 | 17.3442 | 17.3295 | 17.3 | 17.2547 | 17.2105 | 17.1579 | 17.0884 | 16.8347 | 16.5632 | 16.3516 | 17.34 | 17.2726 | 17.22 | 17.1705 | 17.1284 | 17.0842 | 17.0432 | 17.0011 | 16.9526 | 16.8905 | 16.66 | 16.4211 | 16.2358
| ALNESS | BALALDIE | MINIMUM HEADROOM | NH 87017 79720 | YES | YES | 0 | 0.64316 | 0.6 | 0.56 | 0.51684 | 0.46842 | 0.18842 | -0.12421 | -0.37579 | -0.50316 | -0.56842 | -0.98211 | -1.1116 | -1.2084 | 0.44526 | 0.39053 | 0.34 | 0.28526 | 0.22632 | -0.15789 | -0.58632 | -0.93158 | -1.1011 | -1.1832 | -1.6095 | -1.7737 | -1.9126 | 0.44947 | 0.39579 | 0.34526 | 0.29053 | 0.23158 | -0.15158 | -0.57895 | -0.92316 | -1.0926 | -1.1737 | -1.6505 | -1.8147 | -1.9432
|  | BALALDIE | EE |  |  |  |  | 0.64316 | 0.6 | 0.56 | 0.51684 | 0.46842 | 0.41579 | 0.36 | 0.071579 | -0.24211 | -0.49263 | -0.98211 | -1.1116 | -1.2074 | 0.44526 | 0.39053 | 0.34 | 0.28526 | 0.22632 | 0.16211 | 0.093684 | -0.30211 | -0.73263 | -1.0789 | -1.6095 | -1.7737 | -1.8958 | 0.44947 | 0.39579 | 0.34526 | 0.29053 | 0.23158 | 0.16737 | 0.1 | -0.29579 | -0.72526 | -1.0705 | -1.6505 | -1.8147 | -1.9368
|  | BALALDIE | HT |  |  |  |  | 0.65474 | 0.61684 | 0.57789 | 0.53579 | 0.48737 | 0.18842 | -0.12421 | -0.37579 | -0.50316 | -0.56842 | -0.97053 | -1.1084 | -1.2084 | 0.46105 | 0.41158 | 0.36421 | 0.31368 | 0.25368 | -0.15789 | -0.58632 | -0.93158 | -1.1011 | -1.1832 | -1.5642 | -1.7526 | -1.9126 | 0.46526 | 0.41684 | 0.36947 | 0.31789 | 0.25789 | -0.15158 | -0.57895 | -0.92316 | -1.0926 | -1.1737 | -1.5958 | -1.7842 | -1.9432
|  | BALALDIE | HE |  |  |  |  | 0.67789 | 0.64842 | 0.62211 | 0.59368 | 0.55895 | 0.51895 | 0.47684 | 0.17684 | -0.15158 | -0.39789 | -0.63684 | -0.71263 | -0.76526 | 0.49158 | 0.45579 | 0.42421 | 0.39053 | 0.34947 | 0.30316 | 0.25474 | -0.16 | -0.61368 | -0.95684 | -1.2295 | -1.3284 | -1.3968 | 0.49684 | 0.46105 | 0.42947 | 0.39579 | 0.35474 | 0.30842 | 0.25895 | -0.15368 | -0.60526 | -0.94842 | -1.2421 | -1.34 | -1.4084
|  | BALALDIE | FB |  |  |  |  | 0.69895 | 0.68211 | 0.66421 | 0.64526 | 0.62526 | 0.60526 | 0.58211 | 0.55789 | 0.42211 | 0.26737 | -0.10526 | -0.19579 | -0.26105 | 0.51684 | 0.49474 | 0.47158 | 0.44737 | 0.42316 | 0.39684 | 0.36842 | 0.33684 | 0.15053 | -0.064211 | -0.57368 | -0.69053 | -0.77579 | 0.52105 | 0.49895 | 0.47684 | 0.45263 | 0.42737 | 0.40211 | 0.37263 | 0.34211 | 0.15579 | -0.057895 | -0.56526 | -0.68211 | -0.76737
| ABERNETHY | BALBEGGIE | MINIMUM HEADROOM | NO 17499 29606 | YES | YES | 0.14796 | 6.6284 | 6.5747 | 6.5189 | 6.4337 | 6.3579 | 6.2895 | 6.2095 | 6.1242 | 5.9958 | 5.9305 | 4.7463 | 4.3979 | 4.2632 | 5.6874 | 5.6105 | 5.5295 | 5.4021 | 5.2916 | 5.1926 | 5.0747 | 4.9505 | 4.8 | 4.7274 | 4.4011 | 3.4358 | 3.2811 | 5.7705 | 5.7421 | 5.7116 | 5.6726 | 5.6326 | 5.5779 | 5.4589 | 5.3347 | 5.1832 | 5.1095 | 4.7832 | 3.5211 | 3.3642
|  | BALBEGGIE | EE |  |  |  |  | 6.6284 | 6.5747 | 6.5242 | 6.4589 | 6.3874 | 6.3063 | 6.2411 | 6.1632 | 6.0284 | 5.9874 | 5.6568 | 4.3979 | 4.2632 | 5.6874 | 5.6105 | 5.5347 | 5.4368 | 5.3305 | 5.2126 | 5.1242 | 5.0074 | 4.8358 | 4.7895 | 4.4074 | 3.4358 | 3.2811 | 5.7705 | 5.7421 | 5.7168 | 5.6863 | 5.6526 | 5.5979 | 5.5084 | 5.3916 | 5.2189 | 5.1726 | 4.7895 | 3.5211 | 3.3642
|  | BALBEGGIE | HT |  |  |  |  | 6.6368 | 6.5842 | 6.5189 | 6.4337 | 6.3579 | 6.2895 | 6.2095 | 6.1242 | 5.9958 | 5.9305 | 4.7463 | 4.5537 | 4.4179 | 5.7 | 5.6242 | 5.5295 | 5.4021 | 5.2916 | 5.1926 | 5.0747 | 4.9505 | 4.8 | 4.7274 | 4.4011 | 3.5737 | 3.3758 | 5.7726 | 5.7453 | 5.7116 | 5.6726 | 5.6326 | 5.5779 | 5.4589 | 5.3347 | 5.1832 | 5.1095 | 4.7832 | 3.7179 | 3.5189
|  | BALBEGGIE | HE |  |  |  |  | 6.6663 | 6.6274 | 6.5853 | 6.5295 | 6.4705 | 6.4032 | 6.3242 | 6.2632 | 6.1863 | 6.1674 | 5.9421 | 5.4137 | 5.3305 | 5.7442 | 5.6895 | 5.6284 | 5.5442 | 5.4589 | 5.3632 | 5.2505 | 5.1589 | 5.04 | 5.0137 | 4.7337 | 4.3168 | 4.22 | 5.7884 | 5.7653 | 5.7453 | 5.7179 | 5.6874 | 5.6495 | 5.6074 | 5.5432 | 5.4242 | 5.3979 | 5.1168 | 4.58 | 4.4832
|  | BALBEGGIE | FB |  |  |  |  | 6.6937 | 6.6758 | 6.6568 | 6.6337 | 6.6095 | 6.58 | 6.5537 | 6.5189 | 6.4726 | 6.4516 | 6.28 | 6.1316 | 6.0379 | 5.7842 | 5.7589 | 5.7295 | 5.6968 | 5.66 | 5.6158 | 5.5779 | 5.5242 | 5.4526 | 5.4221 | 5.1568 | 4.9463 | 4.8379 | 5.8021 | 5.7926 | 5.7832 | 5.7716 | 5.76 | 5.7453 | 5.7326 | 5.7168 | 5.6989 | 5.6863 | 5.5411 | 5.3295 | 5.22
| MILTON OF CRAIGIE | BALDOVIE | MINIMUM HEADROOM | NO 45279 32147 | NO | YES | 0.029592 | 20.1474 | 19.3463 | 18.5642 | 17.16 | 15.5 | 13.8168 | 12.1432 | 12.0221 | 11.9021 | 11.7632 | 5.6737 | 5.4095 | 5.2463 | 19.8747 | 18.9389 | 18.0232 | 16.3726 | 14.4242 | 12.4495 | 10.4884 | 10.3547 | 10.2221 | 10.0663 | 4.2726 | 3.9726 | 3.7874 | 19.9189 | 18.9821 | 18.0663 | 16.4158 | 14.4653 | 12.4905 | 10.5295 | 10.3958 | 10.2642 | 10.1074 | 3.4768 | 3.1768 | 2.9916
|  | BALDOVIE | EE |  |  |  |  | 20.1558 | 19.3463 | 18.5642 | 17.16 | 15.5 | 13.8168 | 12.1432 | 12.0221 | 11.9021 | 11.7632 | 8.4042 | 7.9874 | 7.6895 | 19.8853 | 18.9389 | 18.0232 | 16.3726 | 14.4242 | 12.4495 | 10.4884 | 10.3547 | 10.2221 | 10.0663 | 6.1232 | 5.6526 | 5.3158 | 19.9305 | 18.9821 | 18.0663 | 16.4158 | 14.4653 | 12.4905 | 10.5295 | 10.3958 | 10.2642 | 10.1074 | 6.1768 | 5.7074 | 5.3705
|  | BALDOVIE | HT |  |  |  |  | 20.1474 | 19.4568 | 18.6442 | 17.2453 | 15.5737 | 15.4432 | 15.3179 | 15.1926 | 14.3579 | 12.3958 | 8.2379 | 7.8032 | 7.5116 | 19.8747 | 19.0674 | 18.1179 | 16.4758 | 14.5137 | 14.3684 | 14.2316 | 14.0937 | 13.1189 | 10.8168 | 6.0768 | 5.5358 | 5.1211 | 19.9189 | 19.1116 | 18.1611 | 16.5189 | 14.5558 | 14.4105 | 14.2737 | 14.1358 | 13.1611 | 10.8579 | 6.1284 | 5.5884 | 5.1758
|  | BALDOVIE | HE |  |  |  |  | 20.2021 | 19.5716 | 18.8347 | 17.4779 | 15.8558 | 14.2116 | 12.5937 | 12.5147 | 12.4326 | 12.3411 | 5.6737 | 5.4095 | 5.2463 | 19.9358 | 19.2 | 18.3368 | 16.7421 | 14.8379 | 12.9095 | 11.0137 | 10.9263 | 10.8379 | 10.7337 | 4.2726 | 3.9726 | 3.7874 | 19.98 | 19.2442 | 18.38 | 16.7853 | 14.88 | 12.9516 | 11.0547 | 10.9674 | 10.8789 | 10.7747 | 3.4768 | 3.1768 | 2.9916
|  | BALDOVIE | FB |  |  |  |  | 20.6937 | 20.5011 | 20.2221 | 19.9189 | 19.3579 | 18.6558 | 17.7789 | 16.9274 | 16.8642 | 16.7779 | 15.8263 | 14.5768 | 14.3663 | 20.5284 | 20.2926 | 19.9611 | 19.6095 | 18.9505 | 18.1263 | 17.0958 | 16.0947 | 16.0253 | 15.9274 | 14.8211 | 13.3611 | 13.12 | 20.5716 | 20.3368 | 20.0063 | 19.6526 | 18.9947 | 18.1695 | 17.1389 | 16.1368 | 16.0674 | 15.9695 | 14.8632 | 13.4032 | 13.1621
| TARLAND | BALLATER | MINIMUM HEADROOM | NO 37542 97131 | NO | YES | 0 | 12.0895 | 12.0653 | 12.0337 | 11.8958 | 11.7947 | 11.6347 | 11.4589 | 11.3179 | 11.1842 | 11.0884 | 10.6474 | 10.3105 | 10.0516 | 12.0232 | 11.9232 | 11.8295 | 11.6621 | 11.5411 | 11.3453 | 11.1284 | 10.9547 | 10.7937 | 10.68 | 10.1516 | 9.7389 | 9.4232 | 11.8253 | 11.8011 | 11.7274 | 11.5695 | 11.4558 | 11.2726 | 11.0705 | 10.9084 | 10.7579 | 10.6495 | 10.1253 | 9.7116 | 9.3958
|  | BALLATER | EE |  |  |  |  | 12.0895 | 12.0653 | 12.0368 | 11.9147 | 11.8179 | 11.7126 | 11.5758 | 11.4 | 11.2358 | 11.1463 | 10.6495 | 10.3105 | 10.0516 | 12.0232 | 11.9232 | 11.8368 | 11.6884 | 11.5716 | 11.4484 | 11.2853 | 11.0684 | 10.8663 | 10.76 | 10.1516 | 9.7389 | 9.4232 | 11.8253 | 11.8011 | 11.7305 | 11.5916 | 11.4811 | 11.3632 | 11.2095 | 11.0074 | 10.8168 | 10.7168 | 10.1253 | 9.7116 | 9.3958
|  | BALLATER | HT |  |  |  |  | 12.0937 | 12.0716 | 12.0337 | 11.8958 | 11.7947 | 11.6347 | 11.4589 | 11.3179 | 11.1842 | 11.0884 | 10.6474 | 10.3137 | 10.08 | 12.0463 | 11.9474 | 11.8295 | 11.6621 | 11.5411 | 11.3453 | 11.1284 | 10.9547 | 10.7937 | 10.68 | 10.2463 | 9.8189 | 9.4579 | 11.8295 | 11.8084 | 11.7274 | 11.5695 | 11.4558 | 11.2726 | 11.0705 | 10.9084 | 10.7579 | 10.6495 | 10.2263 | 9.8032 | 9.4442
|  | BALLATER | HE |  |  |  |  | 12.1021 | 12.0821 | 12.0663 | 12.0453 | 12.0179 | 11.9695 | 11.8411 | 11.7074 | 11.5726 | 11.5221 | 11.2411 | 11.0716 | 10.9316 | 12.1011 | 12.0284 | 11.9642 | 11.8758 | 11.8242 | 11.7684 | 11.6116 | 11.4463 | 11.28 | 11.2189 | 10.8726 | 10.6653 | 10.4937 | 11.8379 | 11.8189 | 11.8032 | 11.7684 | 11.7189 | 11.6632 | 11.5168 | 11.3632 | 11.2095 | 11.1505 | 10.8274 | 10.6337 | 10.4695
|  | BALLATER | FB |  |  |  |  | 12.1137 | 12.1053 | 12.0968 | 12.0884 | 12.0779 | 12.0674 | 12.0568 | 12.0453 | 11.9747 | 11.92 | 11.6063 | 11.3389 | 11.1726 | 12.1347 | 12.1032 | 12.0674 | 12.0326 | 11.9968 | 11.9632 | 11.9284 | 11.8621 | 11.7579 | 11.6916 | 11.3021 | 10.9705 | 10.7621 | 11.8505 | 11.8421 | 11.8326 | 11.8242 | 11.8137 | 11.8032 | 11.7926 | 11.7558 | 11.66 | 11.5979 | 11.2368 | 10.9274 | 10.7347
| CARRADALE 1 | BALLIEKINE | MINIMUM HEADROOM | NR 87179 38819 | YES | YES | 0 | 0.97579 | 0.96 | 0.94421 | 0.92842 | 0.91263 | 0.89579 | 0.88 | 0.86526 | 0.85053 | 0.83474 | 0.78211 | 0.72842 | 0.68 | 0.98526 | 0.97053 | 0.95579 | 0.93895 | 0.92316 | 0.90526 | 0.89053 | 0.87474 | 0.86 | 0.84421 | 0.78947 | 0.73368 | 0.68211 | 0.97474 | 0.95789 | 0.94 | 0.92316 | 0.90526 | 0.88632 | 0.86947 | 0.85368 | 0.83789 | 0.82105 | 0.76316 | 0.70421 | 0.65158
|  | BALLIEKINE | EE |  |  |  |  | 0.97579 | 0.96 | 0.94421 | 0.92842 | 0.91263 | 0.89579 | 0.88 | 0.86526 | 0.85053 | 0.83474 | 0.78211 | 0.72842 | 0.68 | 0.98526 | 0.97053 | 0.95579 | 0.93895 | 0.92316 | 0.90526 | 0.89053 | 0.87474 | 0.86 | 0.84421 | 0.78947 | 0.73368 | 0.68211 | 0.97474 | 0.95789 | 0.94 | 0.92316 | 0.90526 | 0.88632 | 0.86947 | 0.85368 | 0.83789 | 0.82105 | 0.76316 | 0.70421 | 0.65158
|  | BALLIEKINE | HT |  |  |  |  | 0.98421 | 0.97474 | 0.96421 | 0.95368 | 0.94211 | 0.93368 | 0.92211 | 0.91263 | 0.90211 | 0.89158 | 0.84737 | 0.81368 | 0.78737 | 0.99053 | 0.98211 | 0.97158 | 0.96105 | 0.95053 | 0.94105 | 0.92947 | 0.92 | 0.91053 | 0.9 | 0.86421 | 0.82842 | 0.79684 | 0.98421 | 0.97368 | 0.96316 | 0.95158 | 0.94 | 0.92947 | 0.91789 | 0.90737 | 0.89684 | 0.88526 | 0.84632 | 0.80632 | 0.77368
|  | BALLIEKINE | HE |  |  |  |  | 0.99053 | 0.98316 | 0.97684 | 0.96737 | 0.96 | 0.95368 | 0.94316 | 0.93684 | 0.93053 | 0.92316 | 0.89895 | 0.87368 | 0.85579 | 0.99789 | 0.99158 | 0.98526 | 0.97684 | 0.96947 | 0.96316 | 0.95368 | 0.94737 | 0.94105 | 0.93263 | 0.90947 | 0.88421 | 0.86526 | 0.99158 | 0.98211 | 0.97579 | 0.96632 | 0.95895 | 0.95158 | 0.94105 | 0.93368 | 0.92737 | 0.91895 | 0.89263 | 0.86421 | 0.84526
|  | BALLIEKINE | FB |  |  |  |  | 0.99474 | 0.99053 | 0.98632 | 0.98316 | 0.97789 | 0.97368 | 0.96947 | 0.96526 | 0.96105 | 0.95579 | 0.93895 | 0.91895 | 0.90316 | 1.0042 | 0.99789 | 0.99474 | 0.99053 | 0.98526 | 0.98 | 0.97579 | 0.97263 | 0.96737 | 0.96211 | 0.94316 | 0.92316 | 0.90632 | 0.99579 | 0.99158 | 0.98632 | 0.98316 | 0.97789 | 0.97263 | 0.96842 | 0.96526 | 0.95895 | 0.95368 | 0.93579 | 0.91474 | 0.89789
| BOAT OF GARTEN | BALLINDALLOCH | MINIMUM HEADROOM | NJ 19279 34652 | NO | YES | 0.10204 | 13.2271 | 13.2166 | 13.2071 | 13.1945 | 13.1797 | 13.1661 | 13.1482 | 13.1355 | 13.1218 | 13.0945 | 9.7482 | 9.6376 | 9.5576 | 12.1021 | 12.0684 | 12.0347 | 11.9832 | 11.9411 | 11.8905 | 11.8411 | 11.8 | 11.7579 | 11.7221 | 9.0463 | 8.9168 | 8.82 | 12.7062 | 12.6757 | 12.6451 | 12.5988 | 12.5609 | 12.5146 | 12.4693 | 12.4314 | 12.3936 | 12.3609 | 9.0062 | 8.8851 | 8.7936
|  | BALLINDALLOCH | EE |  |  |  |  | 13.2271 | 13.2166 | 13.2082 | 13.1966 | 13.185 | 13.1661 | 13.1482 | 13.1355 | 13.1218 | 13.0945 | 9.7555 | 9.6429 | 9.5576 | 12.1021 | 12.0684 | 12.0347 | 11.9832 | 11.9411 | 11.8905 | 11.8411 | 11.8 | 11.7579 | 11.7221 | 9.0463 | 8.9168 | 8.82 | 12.7062 | 12.6757 | 12.6451 | 12.5988 | 12.5609 | 12.5146 | 12.4693 | 12.4314 | 12.3936 | 12.3609 | 9.0062 | 8.8851 | 8.7936
|  | BALLINDALLOCH | HT |  |  |  |  | 13.2282 | 13.2176 | 13.2071 | 13.1945 | 13.1797 | 13.1671 | 13.1513 | 13.1376 | 13.1218 | 13.105 | 9.7482 | 9.6376 | 9.5618 | 12.1116 | 12.0811 | 12.0516 | 12.0137 | 11.9684 | 11.9253 | 11.8768 | 11.8305 | 11.7842 | 11.7411 | 9.0716 | 8.9368 | 8.8284 | 12.7146 | 12.6862 | 12.6599 | 12.6251 | 12.5841 | 12.5441 | 12.5009 | 12.4578 | 12.4157 | 12.3767 | 9.0283 | 8.902 | 8.7999
|  | BALLINDALLOCH | HE |  |  |  |  | 13.2313 | 13.2197 | 13.2145 | 13.2039 | 13.1924 | 13.1766 | 13.1597 | 13.1482 | 13.1376 | 13.1345 | 9.9829 | 9.9229 | 9.8818 | 12.1337 | 12.1095 | 12.0937 | 12.0726 | 12.0526 | 12.0274 | 12.0021 | 11.9779 | 11.9484 | 11.9305 | 9.3095 | 9.24 | 9.1926 | 12.7336 | 12.7114 | 12.6967 | 12.6778 | 12.6578 | 12.6346 | 12.6104 | 12.5872 | 12.5609 | 12.5451 | 9.2514 | 9.1872 | 9.142
|  | BALLINDALLOCH | FB |  |  |  |  | 13.2387 | 13.2366 | 13.2324 | 13.2292 | 13.2239 | 13.2197 | 13.2155 | 13.2113 | 13.2061 | 13.2008 | 10.0576 | 9.9787 | 9.9197 | 12.1474 | 12.1358 | 12.1211 | 12.1084 | 12.0926 | 12.0789 | 12.0653 | 12.0526 | 12.0347 | 12.0116 | 9.3863 | 9.2947 | 9.2253 | 12.7462 | 12.7367 | 12.723 | 12.7114 | 12.6978 | 12.6851 | 12.6725 | 12.6609 | 12.6441 | 12.623 | 9.3272 | 9.242 | 9.1778
| CARRADALE 1 | BALLURE | MINIMUM HEADROOM | NR 71425 49944 | YES | YES | 0 | 2.4737 | 2.1695 | 1.9747 | 1.7537 | 1.5632 | 1.5474 | 1.5326 | 1.5211 | 1.5074 | 1.4958 | -0.54632 | -0.58737 | -0.61579 | 2.4768 | 2.1453 | 1.9168 | 1.6568 | 1.4326 | 1.4168 | 1.4 | 1.3863 | 1.3726 | 1.36 | -0.24105 | -0.28526 | -0.31579 | 2.4716 | 2.1284 | 1.9084 | 1.6589 | 1.4442 | 1.4274 | 1.4116 | 1.3989 | 1.3842 | 1.3726 | -0.66947 | -0.71368 | -0.74421
|  | BALLURE | EE |  |  |  |  | 2.4737 | 2.46 | 2.0632 | 1.8232 | 1.5632 | 1.5474 | 1.5326 | 1.5211 | 1.5074 | 1.4958 | -0.54632 | -0.58737 | -0.61579 | 2.4768 | 2.4642 | 2.0211 | 1.7389 | 1.4326 | 1.4168 | 1.4 | 1.3863 | 1.3726 | 1.36 | -0.24105 | -0.28526 | -0.31579 | 2.4716 | 2.4568 | 2.0084 | 1.7379 | 1.4442 | 1.4274 | 1.4116 | 1.3989 | 1.3842 | 1.3726 | -0.66947 | -0.71368 | -0.74421
|  | BALLURE | HT |  |  |  |  | 2.4768 | 2.1695 | 1.9747 | 1.7537 | 1.74 | 1.7274 | 1.7126 | 1.7 | 1.6853 | 1.6726 | 0.016842 | -0.023158 | -0.048421 | 2.4789 | 2.1453 | 1.9168 | 1.6568 | 1.6421 | 1.6274 | 1.6126 | 1.5979 | 1.5821 | 1.5674 | 0.27684 | 0.23263 | 0.19579 | 2.4747 | 2.1284 | 1.9084 | 1.6589 | 1.6442 | 1.6305 | 1.6158 | 1.6011 | 1.5863 | 1.5716 | -0.069474 | -0.11368 | -0.14947
|  | BALLURE | HE |  |  |  |  | 2.4863 | 2.4779 | 2.0863 | 1.8537 | 1.5979 | 1.5884 | 1.5779 | 1.5705 | 1.5611 | 1.5558 | 0.73368 | 0.71474 | 0.7 | 2.4884 | 2.4811 | 2.0474 | 1.7737 | 1.4737 | 1.4632 | 1.4526 | 1.4442 | 1.4347 | 1.4274 | 0.79368 | 0.77263 | 0.75684 | 2.4863 | 2.4779 | 2.0347 | 1.7716 | 1.4832 | 1.4737 | 1.4621 | 1.4537 | 1.4442 | 1.4379 | 0.61684 | 0.59579 | 0.57895
|  | BALLURE | FB |  |  |  |  | 2.4905 | 2.4853 | 2.48 | 2.3137 | 2.2168 | 2.1116 | 2.1063 | 2.1 | 2.0937 | 2.0863 | 2.0579 | 2.0295 | 2.0095 | 2.4926 | 2.4884 | 2.4821 | 2.3147 | 2.2 | 2.0779 | 2.0716 | 2.0642 | 2.0579 | 2.0495 | 2.0179 | 1.9853 | 1.9621 | 2.4905 | 2.4853 | 2.4789 | 2.2916 | 2.1821 | 2.0632 | 2.0568 | 2.0505 | 2.0442 | 2.0358 | 2.0053 | 1.9737 | 1.9505
| DYCE | BALMEDIE | MINIMUM HEADROOM | NJ 95546 18627 | NO | YES | 0 | 8.3726 | 7.9811 | 7.2316 | 6.2105 | 5.2347 | 3.9758 | 2.3284 | 1.9389 | 1.5758 | 1.5347 | -0.99789 | -1.3105 | -1.5011 | 7.1747 | 6.6368 | 5.7358 | 4.5063 | 3.3316 | 1.8242 | -0.11158 | -0.56526 | -0.98842 | -1.08 | -4.0495 | -4.4074 | -4.6253 | 8.0147 | 7.3979 | 6.4989 | 5.2737 | 4.1032 | 2.5989 | 0.66947 | 0.21789 | -0.20421 | -0.27684 | -3.2379 | -3.5968 | -3.8137
|  | BALMEDIE | EE |  |  |  |  | 8.3726 | 8.1147 | 7.4863 | 6.6337 | 5.6758 | 3.9758 | 2.3284 | 1.9389 | 1.5758 | 1.7463 | -0.99789 | -1.3105 | -1.5011 | 7.1747 | 6.8 | 6.0432 | 5.0168 | 3.8632 | 1.8242 | -0.11158 | -0.56526 | -0.98842 | -0.83263 | -4.0495 | -4.4074 | -4.6253 | 8.0147 | 7.56 | 6.8063 | 5.7821 | 4.6326 | 2.5989 | 0.66947 | 0.21789 | -0.20421 | -0.031579 | -3.2379 | -3.5968 | -3.8137
|  | BALMEDIE | HT |  |  |  |  | 8.3758 | 7.9811 | 7.2316 | 6.2105 | 5.2347 | 4.1789 | 3.6274 | 3.2737 | 2.4474 | 1.5347 | -0.93684 | -1.2011 | -1.3853 | 7.1768 | 6.6368 | 5.7358 | 4.5063 | 3.3316 | 2.0642 | 1.4189 | 1.0074 | 0.038947 | -1.08 | -3.8937 | -4.2158 | -4.4811 | 8.0179 | 7.3979 | 6.4989 | 5.2737 | 4.1032 | 2.8389 | 2.1958 | 1.7853 | 0.81895 | -0.27684 | -3.0832 | -3.4042 | -3.6684
|  | BALMEDIE | HE |  |  |  |  | 8.3842 | 8.2158 | 7.6779 | 6.9158 | 5.9789 | 4.6663 | 3.0937 | 2.5495 | 2.0526 | 2.0716 | -0.72421 | -0.84526 | -0.96105 | 7.1958 | 6.9221 | 6.2716 | 5.3547 | 4.2263 | 2.6453 | 0.78526 | 0.14947 | -0.43368 | -0.45789 | -3.7442 | -3.8821 | -4.0158 | 8.0263 | 7.6821 | 7.0337 | 6.1189 | 4.9937 | 3.4189 | 1.5642 | 0.92947 | 0.34842 | 0.34316 | -2.9337 | -3.0705 | -3.2042
|  | BALMEDIE | FB |  |  |  |  | 8.3947 | 8.3874 | 8.38 | 8.2926 | 8.0495 | 7.5442 | 6.9 | 6.1411 | 5.8589 | 5.9842 | 4.6853 | 3.7705 | 3.6611 | 7.3084 | 7.2653 | 7.1811 | 7.0189 | 6.7189 | 6.1095 | 5.3326 | 4.4168 | 4.0779 | 4.1758 | 2.6137 | 1.5368 | 1.4095 | 8.0368 | 8.0295 | 8.0221 | 7.7789 | 7.48 | 6.8716 | 6.0968 | 5.1853 | 4.8463 | 4.9632 | 3.4053 | 2.3316 | 2.2053
| CLAYHILLS | BALNAGASK | MINIMUM HEADROOM | NJ 96055 05234 | YES | YES | 0.96633 | 10.7632 | 10.7474 | 10.7326 | 10.7147 | 10.6947 | 10.6716 | 10.6474 | 10.6263 | 10.6074 | 10.5842 | 10.4916 | 10.4 | 10.2895 | 10.4621 | 10.4389 | 10.4168 | 10.3895 | 10.3589 | 10.3274 | 10.2968 | 10.2653 | 10.2389 | 10.2042 | 10.0968 | 9.9916 | 9.8779 | 10.4884 | 10.4789 | 10.4695 | 10.4579 | 10.4453 | 10.4295 | 10.4126 | 10.4011 | 10.3874 | 10.3705 | 10.3032 | 10.1579 | 9.9884
|  | BALNAGASK | EE |  |  |  |  | 10.7632 | 10.7474 | 10.7326 | 10.7147 | 10.6947 | 10.6716 | 10.6474 | 10.6263 | 10.6074 | 10.5842 | 10.5063 | 10.4284 | 10.3242 | 10.4621 | 10.4389 | 10.4168 | 10.3895 | 10.3589 | 10.3274 | 10.2968 | 10.2653 | 10.2389 | 10.2042 | 10.0968 | 9.9989 | 9.9095 | 10.4884 | 10.4789 | 10.4705 | 10.4611 | 10.4495 | 10.4337 | 10.4168 | 10.4032 | 10.3905 | 10.3779 | 10.3032 | 10.16 | 10.0242
|  | BALNAGASK | HT |  |  |  |  | 10.7653 | 10.7516 | 10.7358 | 10.7179 | 10.6958 | 10.6747 | 10.6547 | 10.6347 | 10.6126 | 10.5853 | 10.4916 | 10.4 | 10.2895 | 10.4663 | 10.4463 | 10.4242 | 10.4 | 10.3663 | 10.3368 | 10.3105 | 10.2832 | 10.2547 | 10.2147 | 10.1105 | 9.9916 | 9.8779 | 10.4884 | 10.48 | 10.4695 | 10.4579 | 10.4453 | 10.4316 | 10.4179 | 10.4032 | 10.3874 | 10.3705 | 10.3179 | 10.1579 | 9.9884
|  | BALNAGASK | HE |  |  |  |  | 10.7716 | 10.7579 | 10.7463 | 10.7326 | 10.7126 | 10.6926 | 10.6705 | 10.6547 | 10.6389 | 10.6263 | 10.5832 | 10.5484 | 10.5189 | 10.4779 | 10.46 | 10.4442 | 10.4263 | 10.4011 | 10.3768 | 10.3495 | 10.3295 | 10.3095 | 10.2895 | 10.2274 | 10.1758 | 10.1274 | 10.4905 | 10.48 | 10.4716 | 10.4611 | 10.4463 | 10.4295 | 10.4126 | 10.4011 | 10.3884 | 10.3832 | 10.3568 | 10.3368 | 10.3232
|  | BALNAGASK | FB |  |  |  |  | 10.7768 | 10.7684 | 10.76 | 10.7505 | 10.7411 | 10.7305 | 10.72 | 10.7095 | 10.6979 | 10.6842 | 10.6379 | 10.5926 | 10.5611 | 10.4842 | 10.4726 | 10.4611 | 10.4484 | 10.4337 | 10.42 | 10.4063 | 10.3916 | 10.3758 | 10.3558 | 10.2895 | 10.2232 | 10.1716 | 10.4937 | 10.4884 | 10.4832 | 10.4768 | 10.4705 | 10.4632 | 10.4558 | 10.4495 | 10.4421 | 10.4337 | 10.4042 | 10.3779 | 10.3642
| KINTORE | BANCHORY | MINIMUM HEADROOM | NO 69262 96297 | NO | YES | 2.0449 | 15.2789 | 14.8884 | 39.0926 | 38.7137 | 38.1884 | 36.1453 | 35.5453 | 35.2305 | 34.9295 | 34.7421 | 33.1137 | 32.3926 | 31.9211 | 13.0453 | 12.6032 | 36.1653 | 35.7463 | 35.1495 | 32.7905 | 32.1105 | 31.7568 | 31.4211 | 31.2147 | 29.4811 | 28.7116 | 28.0253 | -4.5753 | -4.6384 | 19.8747 | 19.8168 | 19.7432 | 19.6905 | 19.5947 | 19.5179 | 19.4379 | 19.3568 | 19.12 | 18.9432 | 18.8295
|  | BANCHORY | EE |  |  |  |  | 15.2789 | 14.8884 | 39.1053 | 38.7337 | 38.2189 | 36.1453 | 35.5453 | 35.2305 | 34.9295 | 34.7537 | 33.2221 | 32.5474 | 32.06 | 13.0453 | 12.6032 | 36.1789 | 35.7579 | 35.1716 | 32.7905 | 32.1105 | 31.7568 | 31.4211 | 31.2253 | 29.4811 | 28.7242 | 28.1663 | -4.5753 | -4.6384 | 19.8789 | 19.8168 | 19.7432 | 19.6937 | 19.5947 | 19.5179 | 19.44 | 19.3874 | 19.1632 | 19.0116 | 18.9537
|  | BANCHORY | HT |  |  |  |  | 15.3147 | 14.9484 | 39.0926 | 38.7137 | 38.1884 | 36.3958 | 36.0484 | 35.7632 | 35.3137 | 34.7421 | 33.1137 | 32.3926 | 31.9211 | 13.0863 | 12.6705 | 36.1653 | 35.7463 | 35.1495 | 33.0821 | 32.6916 | 32.3737 | 31.8663 | 31.2147 | 29.5726 | 28.7116 | 28.0253 | -4.5689 | -4.6289 | 19.8747 | 19.8495 | 19.7695 | 19.6905 | 19.6095 | 19.5253 | 19.4379 | 19.3568 | 19.12 | 18.9432 | 18.8295
|  | BANCHORY | HE |  |  |  |  | 15.4137 | 15.1347 | 39.3926 | 39.0979 | 38.6568 | 36.5726 | 36.0137 | 35.7684 | 35.5337 | 35.4305 | 34.2684 | 33.9368 | 33.6642 | 13.1989 | 12.8842 | 36.5074 | 36.1747 | 35.6747 | 33.2705 | 32.6368 | 32.3611 | 32.0979 | 31.9811 | 30.6484 | 30.2747 | 29.96 | -4.5532 | -4.6121 | 19.9147 | 19.8547 | 19.7832 | 19.6916 | 19.5979 | 19.5358 | 19.4758 | 19.4568 | 19.3611 | 19.2895 | 19.2821
|  | BANCHORY | FB |  |  |  |  | 15.8295 | 15.6621 | 40.0379 | 39.9042 | 39.7674 | 39.5495 | 39.2726 | 38.9726 | 38.8263 | 38.7158 | 38.0453 | 37.3895 | 37.1074 | 13.6726 | 13.4811 | 37.2379 | 37.0863 | 36.9316 | 36.6821 | 36.3642 | 36.02 | 35.8547 | 35.7316 | 34.9705 | 34.2232 | 33.8958 | -4.5047 | -4.5226 | 20.0274 | 20.0063 | 19.9832 | 19.9579 | 19.9337 | 19.9084 | 19.8821 | 19.8526 | 19.7495 | 19.6621 | 19.6568
| TAYNUILT | BARCALDINE | MINIMUM HEADROOM | NM 96356 42181 | YES | YES | 0.53061 | -0.98421 | -1.1411 | -1.3105 | -1.4979 | -1.6979 | -1.9758 | -2.1863 | -2.3284 | -2.4042 | -2.3411 | -4.5221 | -4.6484 | -4.7389 | -0.54211 | -0.67263 | -0.85263 | -1.0621 | -1.2895 | -1.6084 | -1.8211 | -1.9789 | -2.0589 | -2.0147 | -3.66 | -3.7958 | -3.9095 | -1.2421 | -1.2653 | -1.2874 | -1.3295 | -1.5589 | -1.8811 | -2.12 | -2.2821 | -2.3674 | -2.2947 | -4.4579 | -4.6042 | -4.7305
|  | BARCALDINE | EE |  |  |  |  | -0.98421 | -1.0032 | -1.2916 | -1.4832 | -1.6916 | -1.9463 | -2.1863 | -2.3284 | -2.4042 | -0.64316 | -3.4 | -3.5579 | -3.6853 | -0.54211 | -0.55789 | -0.82947 | -1.0305 | -1.2632 | -1.5516 | -1.8211 | -1.9789 | -2.0589 | 0.31368 | -2.0326 | -2.1768 | -2.2874 | -1.2421 | -1.2653 | -1.2874 | -1.3116 | -1.5505 | -1.8442 | -2.12 | -2.2821 | -2.3674 | -0.34632 | -3.1884 | -3.3632 | -3.5042
|  | BARCALDINE | HT |  |  |  |  | -0.97684 | -1.1411 | -1.3105 | -1.4979 | -1.6979 | -1.9758 | -2.1147 | -2.2063 | -2.2832 | -2.3411 | -4.5221 | -4.6484 | -4.7389 | -0.53789 | -0.67263 | -0.85263 | -1.0621 | -1.2895 | -1.6084 | -1.7653 | -1.8674 | -1.9516 | -2.0147 | -3.66 | -3.7958 | -3.9095 | -1.2316 | -1.2463 | -1.2642 | -1.3295 | -1.5589 | -1.8811 | -2.04 | -2.1432 | -2.2305 | -2.2947 | -4.4579 | -4.6042 | -4.7305
|  | BARCALDINE | HE |  |  |  |  | -0.97158 | -0.98526 | -1.2063 | -1.3726 | -1.5547 | -1.7958 | -2.0263 | -2.1442 | -2.2 | -2.22 | -3.3905 | -3.4684 | -3.5274 | -0.53263 | -0.54526 | -0.74211 | -0.92 | -1.1263 | -1.4021 | -1.6653 | -1.7989 | -1.86 | -1.88 | -2.8021 | -2.8811 | -2.9389 | -1.2274 | -1.2421 | -1.2516 | -1.2663 | -1.3958 | -1.6747 | -1.9389 | -2.0737 | -2.1379 | -2.1589 | -3.3537 | -3.44 | -3.5053
|  | BARCALDINE | FB |  |  |  |  | -0.96421 | -0.96842 | -0.97474 | -1.0368 | -1.1021 | -1.1905 | -1.2968 | -1.4063 | -1.4726 | -1.4947 | -1.6242 | -1.7463 | -1.8084 | -0.52632 | -0.53053 | -0.53579 | -0.55579 | -0.62842 | -0.72737 | -0.83895 | -0.96316 | -1.0368 | -1.0611 | -1.2074 | -1.3442 | -1.4137 | -1.2189 | -1.2232 | -1.2284 | -1.2347 | -1.24 | -1.2474 | -1.2526 | -1.2589 | -1.3021 | -1.3274 | -1.4747 | -1.6137 | -1.6842
| STORNOWAY | BARVAS | MINIMUM HEADROOM | NB 35613 48891 | NO | YES | 0 | 2.4642 | 6.2421 | 6.2179 | 6.1958 | 6.1705 | 6.1411 | 6.1105 | 6.0853 | 6.06 | 6.0379 | 4.0032 | 3.9726 | 3.9568 | 2.5379 | 6.32 | 6.3053 | 6.2853 | 6.2411 | 6.1832 | 6.1253 | 6.0737 | 6.0221 | 5.9758 | 4.3189 | 4.2411 | 4.1916 | 2.4642 | 6.2411 | 6.2137 | 6.1905 | 6.1642 | 6.1337 | 6.1032 | 6.0768 | 6.0505 | 6.0284 | 3.8589 | 3.7832 | 3.7347
|  | BARVAS | EE |  |  |  |  | 2.4642 | 6.2421 | 6.2179 | 6.1958 | 6.1705 | 6.1411 | 6.1105 | 6.0853 | 6.06 | 6.0389 | 5.9547 | 5.8947 | 5.8547 | 2.5379 | 6.32 | 6.3053 | 6.2874 | 6.2411 | 6.1832 | 6.1253 | 6.0737 | 6.0221 | 5.9758 | 5.8011 | 5.6484 | 5.5368 | 2.4642 | 6.2411 | 6.2137 | 6.1905 | 6.1642 | 6.1337 | 6.1032 | 6.0768 | 6.0505 | 6.0284 | 5.8905 | 5.7421 | 5.6337
|  | BARVAS | HT |  |  |  |  | 2.4695 | 6.2442 | 6.2221 | 6.1989 | 6.1737 | 6.1484 | 6.1221 | 6.0947 | 6.0674 | 6.0379 | 5.9326 | 5.8716 | 5.8253 | 2.5411 | 6.3242 | 6.3053 | 6.2853 | 6.2632 | 6.2326 | 6.1789 | 6.1263 | 6.0747 | 6.0189 | 5.8389 | 5.6789 | 5.5421 | 2.4695 | 6.2421 | 6.2189 | 6.1947 | 6.1684 | 6.1421 | 6.1147 | 6.0874 | 6.0589 | 6.0284 | 5.9263 | 5.7705 | 5.6368
|  | BARVAS | HE |  |  |  |  | 2.4779 | 6.2589 | 6.2379 | 6.2189 | 6.1979 | 6.1695 | 6.1432 | 6.1221 | 6.1032 | 6.0947 | 4.0032 | 3.9726 | 3.9568 | 2.5463 | 6.3295 | 6.3158 | 6.2989 | 6.2789 | 6.2526 | 6.2274 | 6.2084 | 6.1916 | 6.1842 | 4.3189 | 4.2411 | 4.1916 | 2.4768 | 6.2589 | 6.2358 | 6.2168 | 6.1947 | 6.1663 | 6.1389 | 6.1179 | 6.0989 | 6.0895 | 3.8589 | 3.7832 | 3.7347
|  | BARVAS | FB |  |  |  |  | 2.4884 | 6.2811 | 6.2726 | 6.2611 | 6.2505 | 6.2421 | 6.2316 | 6.2211 | 6.2116 | 6.1989 | 6.1568 | 6.12 | 6.0989 | 2.5558 | 6.3495 | 6.3432 | 6.3358 | 6.3274 | 6.32 | 6.3116 | 6.3032 | 6.2947 | 6.2842 | 6.2389 | 6.1326 | 6.0516 | 2.4874 | 6.28 | 6.2716 | 6.26 | 6.2495 | 6.24 | 6.2295 | 6.2179 | 6.2074 | 6.1947 | 6.1505 | 6.1116 | 6.0884
| STORNOWAY | BATTERY POINT | MINIMUM HEADROOM | NB 43147 32182 | NO | YES | 0 | 15.4242 | 28.6832 | 28.38 | 28.0663 | 27.7389 | 27.4158 | 27.0558 | 26.6147 | 25.6316 | 24.2421 | 20.3832 | 19.8547 | 19.4895 | 6.7021 | 19.3874 | 19.1968 | 19.0021 | 18.7937 | 18.5779 | 18.3516 | 17.9642 | 16.9221 | 15.5453 | 11.3747 | 10.7484 | 10.2347 | 6.4621 | 19.3605 | 19.0037 | 18.6342 | 18.2511 | 17.8405 | 17.3584 | 16.7658 | 15.4005 | 13.7416 | 9.4489 | 8.8205 | 8.3047
|  | BATTERY POINT | EE |  |  |  |  | 15.4242 | 28.8074 | 28.4284 | 28.0663 | 27.7389 | 27.4158 | 27.0895 | 26.7295 | 26.3547 | 40.9937 | 35.0379 | 34.4326 | 34.0453 | 6.7021 | 19.4474 | 19.2221 | 19.0021 | 18.7937 | 18.5779 | 18.36 | 18.0863 | 17.6916 | 36.3263 | 29.8726 | 29.1937 | 28.76 | 6.4621 | 19.5026 | 19.0626 | 18.6342 | 18.2511 | 17.8405 | 17.4153 | 16.9332 | 16.4321 | 32.7511 | 25.9868 | 25.3016 | 24.8647
|  | BATTERY POINT | HT |  |  |  |  | 15.4632 | 28.6832 | 28.38 | 28.0821 | 27.7726 | 27.4695 | 27.0558 | 26.6147 | 25.6316 | 24.2421 | 20.3832 | 19.8547 | 19.4895 | 6.7242 | 19.3874 | 19.1968 | 19.0063 | 18.8053 | 18.6084 | 18.3516 | 17.9642 | 16.9221 | 15.5453 | 11.3747 | 10.7484 | 10.2347 | 6.4989 | 19.3605 | 19.0037 | 18.6553 | 18.2953 | 17.9142 | 17.3584 | 16.7658 | 15.4005 | 13.7416 | 9.4489 | 8.8205 | 8.3047
|  | BATTERY POINT | HE |  |  |  |  | 15.5653 | 29.0053 | 28.6737 | 28.3758 | 28.1032 | 27.8379 | 27.5632 | 27.2663 | 26.9389 | 26.7274 | 21.6421 | 21.2453 | 21.0568 | 6.7737 | 19.5663 | 19.3716 | 19.1853 | 19.0074 | 18.8242 | 18.6358 | 18.4495 | 18.2474 | 18.0863 | 12.5684 | 12.1158 | 11.9021 | 6.5958 | 19.6911 | 19.3532 | 19.0037 | 18.6858 | 18.3816 | 18.0658 | 17.6721 | 17.2321 | 16.9405 | 10.6984 | 10.2447 | 10.03
|  | BATTERY POINT | FB |  |  |  |  | 15.6642 | 29.1768 | 29.1105 | 28.9432 | 28.8011 | 28.6663 | 28.5326 | 28.0337 | 27.8474 | 27.6726 | 26.3358 | 24.4958 | 24.2179 | 6.8337 | 19.6726 | 19.6347 | 19.5453 | 19.4579 | 19.3726 | 19.2884 | 19.0095 | 18.8968 | 18.7874 | 17.6537 | 15.7968 | 15.4779 | 6.6958 | 19.8563 | 19.7932 | 19.6342 | 19.4984 | 19.3416 | 19.1858 | 18.5826 | 18.3616 | 18.1395 | 16.2847 | 13.9921 | 13.6732
| DOUNREAY | BETTYHILL | MINIMUM HEADROOM | NC 70763 61645 | YES | YES | 0 | 0.94526 | 0.92737 | 0.91263 | 0.89684 | 0.88 | 0.86105 | 0.84316 | 0.82737 | 0.81053 | 0.79789 | 0.74 | 0.69579 | 0.65684 | 1.0705 | 1.0537 | 1.0368 | 1.0189 | 1.0021 | 0.98211 | 0.96316 | 0.94632 | 0.92947 | 0.91474 | 0.85684 | 0.80632 | 0.76211 | 1.0737 | 1.0547 | 1.0389 | 1.0211 | 1.0021 | 0.98211 | 0.96316 | 0.94632 | 0.92842 | 0.91368 | 0.85263 | 0.80105 | 0.75895
|  | BETTYHILL | EE |  |  |  |  | 0.94526 | 0.92737 | 0.91263 | 0.89684 | 0.88 | 0.86105 | 0.84316 | 0.82737 | 0.81053 | 0.79789 | 0.74211 | 0.69579 | 0.65684 | 1.0705 | 1.0537 | 1.0368 | 1.0189 | 1.0021 | 0.98211 | 0.96316 | 0.94632 | 0.92947 | 0.91474 | 0.85684 | 0.80632 | 0.76632 | 1.0737 | 1.0547 | 1.0389 | 1.0211 | 1.0021 | 0.98211 | 0.96316 | 0.94632 | 0.92842 | 0.91368 | 0.85263 | 0.80105 | 0.75895
|  | BETTYHILL | HT |  |  |  |  | 0.94842 | 0.93474 | 0.92211 | 0.90737 | 0.88737 | 0.87263 | 0.85789 | 0.84211 | 0.82632 | 0.80947 | 0.74 | 0.69579 | 0.66316 | 1.0758 | 1.0611 | 1.0453 | 1.0295 | 1.0084 | 0.99158 | 0.97684 | 0.95789 | 0.94 | 0.92421 | 0.85789 | 0.80632 | 0.76211 | 1.0789 | 1.0632 | 1.0495 | 1.0337 | 1.0116 | 0.99579 | 0.98 | 0.96105 | 0.94421 | 0.92842 | 0.86211 | 0.81053 | 0.76632
|  | BETTYHILL | HE |  |  |  |  | 0.95895 | 0.94947 | 0.94211 | 0.93158 | 0.92211 | 0.91053 | 0.89895 | 0.89053 | 0.88105 | 0.87474 | 0.84737 | 0.82105 | 0.80316 | 1.0874 | 1.0768 | 1.0684 | 1.0568 | 1.0474 | 1.0358 | 1.0242 | 1.0137 | 1.0042 | 0.99684 | 0.96632 | 0.93895 | 0.92105 | 1.0895 | 1.0789 | 1.0716 | 1.06 | 1.0505 | 1.0379 | 1.0263 | 1.0158 | 1.0063 | 1 | 0.96842 | 0.94105 | 0.92105
|  | BETTYHILL | FB |  |  |  |  | 0.96526 | 0.95895 | 0.95263 | 0.94632 | 0.94105 | 0.93474 | 0.92737 | 0.92211 | 0.91474 | 0.90842 | 0.87895 | 0.84842 | 0.82632 | 1.0926 | 1.0863 | 1.08 | 1.0737 | 1.0663 | 1.06 | 1.0526 | 1.0453 | 1.0379 | 1.0295 | 0.99684 | 0.96316 | 0.93789 | 1.0958 | 1.0895 | 1.0821 | 1.0758 | 1.0695 | 1.0632 | 1.0547 | 1.0484 | 1.0411 | 1.0337 | 1.0021 | 0.96842 | 0.94316
| GRUDIE BRIDGE | BIDEN CLAN RAONAILD | MINIMUM HEADROOM | NH 06927 58342 | YES | NO | 0 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474
|  | BIDEN CLAN RAONAILD | EE |  |  |  |  | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474
|  | BIDEN CLAN RAONAILD | HT |  |  |  |  | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474
|  | BIDEN CLAN RAONAILD | HE |  |  |  |  | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474
|  | BIDEN CLAN RAONAILD | FB |  |  |  |  | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474 | 0.089474
| ELGIN | BILBOHALL | MINIMUM HEADROOM | NJ 20782 61556 | YES | YES | 0.071429 | 12.2189 | 23.4842 | 23.4716 | 23.4537 | 23.4358 | 23.4168 | 23.3937 | 23.2884 | 23.1189 | 23.0821 | 22.7632 | 22.64 | 22.5474 | 11.8011 | 21.8305 | 21.7832 | 21.7305 | 21.6832 | 21.6295 | 21.5147 | 21.3526 | 21.1189 | 21.0758 | 20.7526 | 20.5968 | 20.4737 | 11.7937 | 22.4242 | 22.3779 | 22.3263 | 22.2811 | 22.2284 | 22.1168 | 21.96 | 21.7337 | 21.6916 | 21.3832 | 21.2316 | 21.1116
|  | BILBOHALL | EE |  |  |  |  | 12.2189 | 23.4842 | 23.4716 | 23.4568 | 23.4411 | 23.4179 | 23.3937 | 23.3768 | 23.2979 | 23.2674 | 22.8305 | 22.66 | 22.5611 | 11.8011 | 21.8305 | 21.7832 | 21.7305 | 21.6832 | 21.6295 | 21.5789 | 21.4895 | 21.3758 | 21.3368 | 20.7905 | 20.5968 | 20.4853 | 11.7937 | 22.4242 | 22.3779 | 22.3263 | 22.2811 | 22.2284 | 22.1789 | 22.0916 | 21.9811 | 21.9432 | 21.42 | 21.2316 | 21.1221
|  | BILBOHALL | HT |  |  |  |  | 12.2211 | 23.4874 | 23.4716 | 23.4537 | 23.4358 | 23.4168 | 23.3979 | 23.2884 | 23.1189 | 23.0821 | 22.7632 | 22.64 | 22.5474 | 11.8158 | 21.8505 | 21.8053 | 21.7558 | 21.7074 | 21.6589 | 21.5147 | 21.3526 | 21.1189 | 21.0758 | 20.7526 | 20.6042 | 20.4737 | 11.8074 | 22.4432 | 22.3989 | 22.3516 | 22.3042 | 22.2558 | 22.1168 | 21.96 | 21.7337 | 21.6916 | 21.3832 | 21.2389 | 21.1116
|  | BILBOHALL | HE |  |  |  |  | 12.2253 | 23.4926 | 23.4821 | 23.4684 | 23.4505 | 23.4295 | 23.4074 | 23.3937 | 23.3789 | 23.3737 | 23.02 | 22.9347 | 22.8937 | 11.8474 | 21.8947 | 21.8653 | 21.8337 | 21.8 | 21.7621 | 21.7232 | 21.6421 | 21.5326 | 21.5126 | 21.0032 | 20.9011 | 20.8547 | 11.8379 | 22.4863 | 22.4579 | 22.4274 | 22.3937 | 22.3568 | 22.3189 | 22.2389 | 22.1326 | 22.1137 | 21.6263 | 21.5221 | 21.4779
|  | BILBOHALL | FB |  |  |  |  | 12.2337 | 23.5084 | 23.5032 | 23.4968 | 23.4905 | 23.4842 | 23.4768 | 23.4705 | 23.4632 | 23.4547 | 23.3516 | 23.1821 | 23.1305 | 11.8653 | 21.9253 | 21.9042 | 21.8811 | 21.86 | 21.8389 | 21.8179 | 21.7979 | 21.7568 | 21.7316 | 21.4221 | 21.1916 | 21.1221 | 11.8558 | 22.5158 | 22.4958 | 22.4737 | 22.4526 | 22.4326 | 22.4116 | 22.3926 | 22.3526 | 22.3284 | 22.0284 | 21.8053 | 21.7379
| RANNOCH | BLACKMOUNT | MINIMUM HEADROOM | NN 30077 41404 | YES | YES | 0 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.035263 | 0.045789 | 0.045789 | 0.044737 | 0.044737 | 0.044737 | 0.044737 | 0.044737 | 0.044737 | 0.043684 | 0.043684 | 0.043684 | 0.042632 | 0.042632
|  | BLACKMOUNT | EE |  |  |  |  | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.035263 | 0.045789 | 0.045789 | 0.044737 | 0.044737 | 0.044737 | 0.044737 | 0.044737 | 0.044737 | 0.043684 | 0.043684 | 0.043684 | 0.042632 | 0.042632
|  | BLACKMOUNT | HT |  |  |  |  | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.035263 | 0.045789 | 0.045789 | 0.045789 | 0.044737 | 0.044737 | 0.044737 | 0.044737 | 0.044737 | 0.043684 | 0.043684 | 0.043684 | 0.042632 | 0.042632
|  | BLACKMOUNT | HE |  |  |  |  | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.045789 | 0.045789 | 0.045789 | 0.045789 | 0.045789 | 0.045789 | 0.044737 | 0.044737 | 0.044737 | 0.044737 | 0.043684 | 0.043684 | 0.043684
|  | BLACKMOUNT | FB |  |  |  |  | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.045789 | 0.045789 | 0.045789 | 0.045789 | 0.045789 | 0.045789 | 0.045789 | 0.044737 | 0.044737 | 0.044737 | 0.044737 | 0.044737 | 0.044737
| BEAULY | BLACKSTAND | MINIMUM HEADROOM | NH 71036 59151 | YES | YES | 0 | 5.8474 | 5.7958 | 5.7495 | 5.6968 | 5.6453 | 5.5853 | 5.5326 | 5.4863 | 5.4411 | 5.4042 | 5.2042 | 5.0432 | 4.9326 | 5.8842 | 5.8411 | 5.8021 | 5.7589 | 5.7147 | 5.6621 | 5.6158 | 5.5758 | 5.5368 | 5.5042 | 5.3632 | 5.2221 | 5.1053 | 5.8263 | 5.7684 | 5.7168 | 5.6589 | 5.6011 | 5.5347 | 5.4779 | 5.4263 | 5.3779 | 5.3368 | 5.1547 | 4.9705 | 4.8137
|  | BLACKSTAND | EE |  |  |  |  | 5.8474 | 5.7958 | 5.7495 | 5.6968 | 5.6453 | 5.5853 | 5.5326 | 5.4863 | 5.4411 | 5.4042 | 5.2389 | 5.0947 | 4.9905 | 5.8842 | 5.8411 | 5.8021 | 5.7589 | 5.7147 | 5.6621 | 5.6158 | 5.5758 | 5.5368 | 5.5042 | 5.3632 | 5.2432 | 5.1579 | 5.8263 | 5.7684 | 5.7168 | 5.6589 | 5.6011 | 5.5347 | 5.4779 | 5.4263 | 5.3779 | 5.3368 | 5.1547 | 4.9926 | 4.8747
|  | BLACKSTAND | HT |  |  |  |  | 5.8621 | 5.8147 | 5.7695 | 5.7221 | 5.6663 | 5.6179 | 5.5674 | 5.5189 | 5.4726 | 5.4232 | 5.2042 | 5.0432 | 4.9326 | 5.8958 | 5.8558 | 5.8168 | 5.7768 | 5.7295 | 5.6874 | 5.6442 | 5.6011 | 5.5611 | 5.5168 | 5.3653 | 5.2221 | 5.1053 | 5.8432 | 5.7905 | 5.74 | 5.6884 | 5.6263 | 5.5737 | 5.5179 | 5.4653 | 5.4158 | 5.3611 | 5.1653 | 4.9705 | 4.8137
|  | BLACKSTAND | HE |  |  |  |  | 5.8937 | 5.8589 | 5.8284 | 5.7968 | 5.7579 | 5.7189 | 5.6779 | 5.6453 | 5.6158 | 5.5968 | 5.5011 | 5.4137 | 5.3547 | 5.9211 | 5.8916 | 5.8653 | 5.8368 | 5.8032 | 5.7674 | 5.7305 | 5.7011 | 5.6747 | 5.6589 | 5.5789 | 5.5084 | 5.46 | 5.8789 | 5.8421 | 5.8084 | 5.7737 | 5.7316 | 5.6895 | 5.6453 | 5.6105 | 5.5779 | 5.5568 | 5.4495 | 5.3505 | 5.2842
|  | BLACKSTAND | FB |  |  |  |  | 5.9126 | 5.8926 | 5.8737 | 5.8505 | 5.8274 | 5.8042 | 5.7821 | 5.7589 | 5.7379 | 5.7105 | 5.6116 | 5.5116 | 5.4368 | 5.9379 | 5.9211 | 5.9053 | 5.8863 | 5.8674 | 5.8484 | 5.8295 | 5.8095 | 5.7916 | 5.7695 | 5.6863 | 5.6042 | 5.5453 | 5.9 | 5.8768 | 5.8558 | 5.8295 | 5.8042 | 5.7779 | 5.7537 | 5.7274 | 5.7042 | 5.6737 | 5.5632 | 5.4495 | 5.3642
| COUPAR ANGUS | BLAIRGOWRIE | MINIMUM HEADROOM | NO 18741 44551 | NO | YES | 0.64082 | 21.9732 | 21.9026 | 21.8395 | 21.7458 | 21.6605 | 21.5574 | 21.4521 | 21.1321 | 20.6216 | 20.4405 | 19.1195 | 18.4447 | 18.0605 | 21.2758 | 21.0253 | 20.7832 | 20.4105 | 20.18 | 19.7095 | 19.2147 | 18.6895 | 18.1 | 17.9011 | 16.6884 | 15.7432 | 15.1916 | 11.7792 | 11.6771 | 11.5876 | 11.4424 | 11.3318 | 11.1666 | 10.9939 | 10.8108 | 10.6108 | 10.5013 | 10.0297 | 9.6655 | 9.4192
|  | BLAIRGOWRIE | EE |  |  |  |  | 21.9732 | 21.9026 | 21.8437 | 21.7689 | 21.6963 | 21.5837 | 21.4732 | 21.3447 | 20.9205 | 20.7784 | 19.6668 | 18.5974 | 18.1837 | 21.2758 | 21.0253 | 20.7832 | 20.4263 | 20.2095 | 19.7558 | 19.3663 | 18.9432 | 18.4526 | 18.2937 | 17.0179 | 15.7821 | 15.3147 | 11.7792 | 11.6771 | 11.5876 | 11.4624 | 11.3645 | 11.1939 | 11.0361 | 10.8845 | 10.7192 | 10.6445 | 10.1782 | 9.7666 | 9.5739
|  | BLAIRGOWRIE | HT |  |  |  |  | 21.9784 | 21.9121 | 21.8395 | 21.7458 | 21.6605 | 21.5574 | 21.4521 | 21.1321 | 20.6216 | 20.4405 | 19.1195 | 18.4447 | 18.0605 | 21.3168 | 21.0842 | 20.8432 | 20.4105 | 20.18 | 19.7095 | 19.2147 | 18.6895 | 18.1 | 17.9011 | 16.6884 | 15.7432 | 15.1916 | 11.7908 | 11.695 | 11.5929 | 11.4424 | 11.3318 | 11.1666 | 10.9939 | 10.8108 | 10.6108 | 10.5013 | 10.0297 | 9.6655 | 9.4192
|  | BLAIRGOWRIE | HE |  |  |  |  | 22.0121 | 21.9542 | 21.9111 | 21.8405 | 21.7742 | 21.6774 | 21.57 | 21.4942 | 21.3353 | 21.2437 | 20.3605 | 19.6921 | 19.45 | 21.4326 | 21.2442 | 21.0684 | 20.7632 | 20.6084 | 20.2726 | 19.8316 | 19.4305 | 18.9221 | 18.8158 | 17.7895 | 17.0126 | 16.7358 | 11.8382 | 11.7571 | 11.6918 | 11.5813 | 11.4992 | 11.3624 | 11.1961 | 11.0645 | 10.9087 | 10.8676 | 10.5476 | 10.3055 | 10.2013
|  | BLAIRGOWRIE | FB |  |  |  |  | 22.0426 | 22.0163 | 21.9879 | 21.9605 | 21.9311 | 21.8963 | 21.8595 | 21.8195 | 21.7753 | 21.7416 | 21.5953 | 20.9889 | 20.7142 | 21.5179 | 21.4147 | 21.3063 | 21.1874 | 21.0989 | 20.9326 | 20.7579 | 20.56 | 20.2989 | 20.1958 | 19.5442 | 18.5 | 18.1842 | 11.8782 | 11.8392 | 11.7971 | 11.7529 | 11.7139 | 11.6561 | 11.5961 | 11.5287 | 11.4466 | 11.4013 | 11.1676 | 10.8518 | 10.7382
| STRATHLEVEN | BLAIRLINNANS | MINIMUM HEADROOM | NS 40709 85121 | YES | YES | 0.95 | -2.8295 | -2.8305 | -2.8337 | -2.8368 | -2.84 | -2.8432 | -2.8463 | -2.8495 | -2.8526 | -2.8547 | -2.8674 | -2.8758 | -2.8842 | -3.5042 | -3.5063 | -3.5095 | -3.5126 | -3.5168 | -3.52 | -3.5232 | -3.5274 | -3.5305 | -3.5337 | -3.5442 | -3.5558 | -3.5653 | -3.4768 | -3.4789 | -3.4821 | -3.4853 | -3.4895 | -3.4926 | -3.4958 | -3.5 | -3.5032 | -3.5053 | -3.5168 | -3.5284 | -3.5379
|  | BLAIRLINNANS | EE |  |  |  |  | -2.8295 | -2.8305 | -2.8337 | -2.8368 | -2.84 | -2.8432 | -2.8463 | -2.8495 | -2.8526 | -2.8547 | -2.8653 | -2.8737 | -2.8821 | -3.5042 | -3.5063 | -3.5095 | -3.5126 | -3.5168 | -3.52 | -3.5232 | -3.5274 | -3.5305 | -3.5337 | -3.5442 | -3.5547 | -3.5642 | -3.4768 | -3.4789 | -3.4821 | -3.4853 | -3.4895 | -3.4926 | -3.4958 | -3.5 | -3.5032 | -3.5053 | -3.5168 | -3.5274 | -3.5368
|  | BLAIRLINNANS | HT |  |  |  |  | -2.8274 | -2.8295 | -2.8326 | -2.8347 | -2.8389 | -2.8411 | -2.8453 | -2.8484 | -2.8505 | -2.8537 | -2.8674 | -2.8758 | -2.8842 | -3.5021 | -3.5053 | -3.5084 | -3.5116 | -3.5147 | -3.5179 | -3.5232 | -3.5253 | -3.5284 | -3.5326 | -3.5442 | -3.5558 | -3.5653 | -3.4747 | -3.4779 | -3.4811 | -3.4842 | -3.4874 | -3.4905 | -3.4947 | -3.4979 | -3.5011 | -3.5053 | -3.5158 | -3.5284 | -3.5379
|  | BLAIRLINNANS | HE |  |  |  |  | -2.8263 | -2.8274 | -2.8284 | -2.8305 | -2.8326 | -2.8337 | -2.8368 | -2.8389 | -2.8411 | -2.8411 | -2.8474 | -2.8495 | -2.8526 | -3.5011 | -3.5032 | -3.5032 | -3.5053 | -3.5084 | -3.5095 | -3.5126 | -3.5147 | -3.5168 | -3.5168 | -3.5242 | -3.5263 | -3.5295 | -3.4737 | -3.4758 | -3.4758 | -3.4779 | -3.4811 | -3.4821 | -3.4853 | -3.4874 | -3.4895 | -3.4895 | -3.4968 | -3.4989 | -3.5021
|  | BLAIRLINNANS | FB |  |  |  |  | 0.27789 | 0.27684 | 0.27579 | 0.27368 | 0.27368 | 0.27263 | 0.27053 | 0.26947 | 0.26842 | 0.26632 | 0.25895 | 0.25368 | 0.25053 | 0.15368 | 0.15263 | 0.15158 | 0.14947 | 0.14947 | 0.14842 | 0.14632 | 0.14526 | 0.14316 | 0.14105 | 0.13263 | 0.12632 | 0.12421 | 0.17158 | 0.17053 | 0.16947 | 0.16737 | 0.16632 | 0.16526 | 0.16316 | 0.16316 | 0.16105 | 0.15895 | 0.15053 | 0.14421 | 0.14105
| BOAT OF GARTEN | BOAT OF GARTEN | MINIMUM HEADROOM | NH 95609 19427 | NO | YES | 0 | 8.2768 | 8.2232 | 8.1947 | 8.16 | 8.1232 | 8.0811 | 8.0389 | 8.0053 | 7.9716 | 7.9442 | 7.8042 | 7.6979 | 7.6263 | 8.2716 | 8.1811 | 8.1358 | 8.0821 | 8.0274 | 7.9663 | 7.9063 | 7.8589 | 7.8105 | 7.7684 | 7.5937 | 7.4305 | 7.2874 | 8.2474 | 8.1621 | 8.1189 | 8.0674 | 8.0158 | 7.9568 | 7.9 | 7.8547 | 7.8084 | 7.7684 | 7.6032 | 7.4484 | 7.3074
|  | BOAT OF GARTEN | EE |  |  |  |  | 8.2768 | 8.2232 | 8.1947 | 8.16 | 8.1232 | 8.0811 | 8.0389 | 8.0053 | 7.9716 | 7.9442 | 7.8274 | 7.7263 | 7.6505 | 8.2716 | 8.1811 | 8.1358 | 8.0821 | 8.0274 | 7.9663 | 7.9063 | 7.8589 | 7.8105 | 7.7684 | 7.5937 | 7.4305 | 7.3032 | 8.2474 | 8.1621 | 8.1189 | 8.0674 | 8.0158 | 7.9568 | 7.9 | 7.8547 | 7.8084 | 7.7684 | 7.6032 | 7.4484 | 7.3242
|  | BOAT OF GARTEN | HT |  |  |  |  | 8.2842 | 8.2337 | 8.2053 | 8.1737 | 8.1337 | 8.0968 | 8.0621 | 8.0263 | 7.9905 | 7.9547 | 7.8042 | 7.6979 | 7.6263 | 8.2853 | 8.1989 | 8.1579 | 8.1116 | 8.0526 | 7.9989 | 7.9495 | 7.8989 | 7.8495 | 7.7989 | 7.6116 | 7.4326 | 7.2874 | 8.26 | 8.1789 | 8.14 | 8.0947 | 8.0389 | 7.9874 | 7.94 | 7.8926 | 7.8442 | 7.7958 | 7.6189 | 7.4495 | 7.3074
|  | BOAT OF GARTEN | HE |  |  |  |  | 8.3011 | 8.2579 | 8.2411 | 8.2189 | 8.1937 | 8.1663 | 8.1347 | 8.1137 | 8.0905 | 8.0758 | 8.0126 | 7.9547 | 7.9137 | 8.3158 | 8.2421 | 8.2179 | 8.1884 | 8.1558 | 8.1232 | 8.0832 | 8.0537 | 8.0232 | 8 | 7.9011 | 7.8053 | 7.7337 | 8.2884 | 8.2189 | 8.1958 | 8.1674 | 8.1358 | 8.1032 | 8.0653 | 8.0368 | 8.0074 | 7.9853 | 7.8916 | 7.8011 | 7.7347
|  | BOAT OF GARTEN | FB |  |  |  |  | 8.3168 | 8.2958 | 8.2821 | 8.2695 | 8.2568 | 8.2421 | 8.2274 | 8.2137 | 8.2 | 8.1821 | 8.1147 | 8.0484 | 7.9979 | 8.3347 | 8.2989 | 8.2768 | 8.2568 | 8.2368 | 8.2147 | 8.1926 | 8.1716 | 8.1505 | 8.1232 | 8.0158 | 7.9053 | 7.8158 | 8.3074 | 8.2737 | 8.2526 | 8.2337 | 8.2137 | 8.1937 | 8.1726 | 8.1526 | 8.1326 | 8.1063 | 8.0053 | 7.9 | 7.8168
| PETERHEAD SHELL | BODDAM | MINIMUM HEADROOM | NK 12219 42512 | YES | NO | 0.05102 | 5.9937 | 5.9221 | 5.8516 | 5.7579 | 4.5453 | 3.3337 | 2.1232 | 2.0947 | 2.0653 | 2.0358 | -4.6168 | -7.2442 | -9.2747 | 5.9516 | 5.8716 | 5.7905 | 5.6842 | 4.2726 | 2.8495 | 1.4274 | 1.3947 | 1.3621 | 1.3295 | -5.4905 | -9.1884 | -11.9905 | 5.9074 | 5.8253 | 5.7432 | 5.6347 | 4.2126 | 2.7916 | 1.3716 | 1.3389 | 1.3074 | 1.2737 | -5.5337 | -9.2221 | -12.0158
|  | BODDAM | EE |  |  |  |  | 5.9937 | 5.9221 | 5.8516 | 5.7579 | 4.5453 | 3.3337 | 2.1232 | 2.0947 | 2.0653 | 2.0358 | -1.2789 | -1.9979 | -2.9537 | 5.9516 | 5.8716 | 5.7905 | 5.6842 | 4.2726 | 2.8495 | 1.4274 | 1.3947 | 1.3621 | 1.3295 | -2.5653 | -3.4074 | -4.5284 | 5.9074 | 5.8253 | 5.7432 | 5.6347 | 4.2126 | 2.7916 | 1.3716 | 1.3389 | 1.3074 | 1.2737 | -2.6137 | -3.4537 | -4.5737
|  | BODDAM | HT |  |  |  |  | 5.9968 | 5.9358 | 5.8663 | 5.7811 | 4.5684 | 4.5379 | 4.5063 | 4.4716 | 3.7758 | 2.3653 | -4.6168 | -7.2442 | -8.5674 | 5.9558 | 5.8853 | 5.8063 | 5.7095 | 4.2989 | 4.2653 | 4.2295 | 4.1916 | 3.3747 | 1.7168 | -5.4905 | -9.1884 | -11.1368 | 5.9116 | 5.84 | 5.76 | 5.6611 | 4.2389 | 4.2053 | 4.1695 | 4.1316 | 3.3158 | 1.6611 | -5.5337 | -9.2221 | -11.1642
|  | BODDAM | HE |  |  |  |  | 6.0074 | 5.9547 | 5.8926 | 5.82 | 4.6232 | 3.4284 | 2.2326 | 2.2158 | 2.1979 | 2.18 | -1.0863 | -1.7547 | -2.6737 | 5.9674 | 5.9074 | 5.8368 | 5.7537 | 4.3611 | 2.96 | 1.5547 | 1.5358 | 1.5158 | 1.4958 | -2.3442 | -3.1295 | -4.2095 | 5.9232 | 5.8611 | 5.7905 | 5.7063 | 4.3021 | 2.9011 | 1.4989 | 1.48 | 1.46 | 1.44 | -2.3937 | -3.1758 | -4.2547
|  | BODDAM | FB |  |  |  |  | 6.0726 | 6.0526 | 6.0263 | 6.0053 | 5.7916 | 5.4074 | 4.8495 | 4.1179 | 4.1063 | 4.0874 | -0.54842 | -6.06 | -9.2747 | 6.0411 | 6.02 | 5.9895 | 5.9653 | 5.7189 | 5.2758 | 4.6242 | 3.7663 | 3.7537 | 3.7316 | -1.72 | -8.2042 | -11.9905 | 5.9989 | 5.9758 | 5.9463 | 5.9211 | 5.6705 | 5.22 | 4.5653 | 3.7063 | 3.6937 | 3.6716 | -1.7695 | -8.2411 | -12.0158
| TUMMEL BRIDGE | BONSKEID | MINIMUM HEADROOM | NN 90919 60658 | YES | YES | 0 | 0.89263 | 0.84947 | 0.79579 | 0.70842 | 0.67158 | 0.60421 | 0.51789 | 0.43474 | 0.33789 | 0.30105 | 0.064211 | -0.069474 | -0.17053 | 0.87368 | 0.82421 | 0.76316 | 0.66316 | 0.62105 | 0.54421 | 0.44526 | 0.34947 | 0.23684 | 0.19684 | -0.062105 | -0.23263 | -0.34842 | 0.87368 | 0.82526 | 0.76421 | 0.66421 | 0.62211 | 0.54526 | 0.44632 | 0.35158 | 0.23895 | 0.19895 | -0.06 | -0.22947 | -0.34526
|  | BONSKEID | EE |  |  |  |  | 0.89263 | 0.85158 | 0.82526 | 0.76842 | 0.73263 | 0.69263 | 0.63474 | 0.54421 | 0.44316 | 0.41263 | 0.077895 | -0.069474 | -0.17053 | 0.87368 | 0.82737 | 0.79684 | 0.73263 | 0.69158 | 0.64737 | 0.58211 | 0.47684 | 0.36 | 0.32526 | -0.062105 | -0.23263 | -0.34842 | 0.87368 | 0.82842 | 0.79789 | 0.73263 | 0.69263 | 0.64842 | 0.58316 | 0.47895 | 0.36105 | 0.32632 | -0.06 | -0.22947 | -0.34526
|  | BONSKEID | HT |  |  |  |  | 0.89474 | 0.84947 | 0.79579 | 0.70842 | 0.67158 | 0.60421 | 0.51789 | 0.43474 | 0.33789 | 0.30105 | 0.064211 | -0.061053 | -0.14947 | 0.87579 | 0.82421 | 0.76316 | 0.66316 | 0.62105 | 0.54421 | 0.44526 | 0.34947 | 0.23684 | 0.19684 | -0.042105 | -0.18947 | -0.31684 | 0.87684 | 0.82526 | 0.76421 | 0.66421 | 0.62211 | 0.54526 | 0.44632 | 0.35158 | 0.23895 | 0.19895 | -0.04 | -0.18632 | -0.31368
|  | BONSKEID | HE |  |  |  |  | 0.91579 | 0.88421 | 0.85474 | 0.81053 | 0.79474 | 0.77474 | 0.68947 | 0.61474 | 0.52105 | 0.50421 | 0.28526 | 0.21684 | 0.15789 | 0.90105 | 0.86526 | 0.83158 | 0.78 | 0.76316 | 0.74211 | 0.64421 | 0.55789 | 0.44842 | 0.42947 | 0.17474 | 0.095789 | 0.027368 | 0.90105 | 0.86526 | 0.83158 | 0.78 | 0.76421 | 0.74316 | 0.64526 | 0.55895 | 0.44947 | 0.43158 | 0.17684 | 0.097895 | 0.030526
|  | BONSKEID | FB |  |  |  |  | 0.94105 | 0.93053 | 0.91789 | 0.90421 | 0.89263 | 0.88211 | 0.87158 | 0.84526 | 0.79684 | 0.77789 | 0.55895 | 0.39789 | 0.32842 | 0.92947 | 0.91789 | 0.90316 | 0.88737 | 0.87474 | 0.86316 | 0.85053 | 0.82105 | 0.76526 | 0.74316 | 0.48842 | 0.30211 | 0.22 | 0.92947 | 0.91895 | 0.90316 | 0.88737 | 0.87474 | 0.86421 | 0.85158 | 0.82211 | 0.76526 | 0.74421 | 0.49053 | 0.30316 | 0.22211
| PORT ANN | BOWMORE | MINIMUM HEADROOM | NR 32021 60211 | NO | YES | 0 | 3.7 | 3.6863 | 3.6747 | 3.6621 | 3.6432 | 3.6253 | 3.6032 | 3.5863 | 3.5695 | 3.5337 | 2 | 1.8337 | 1.7147 | 4.8295 | 4.7695 | 4.6368 | 4.5568 | 4.4958 | 4.3621 | 4.2568 | 4.1979 | 3.9737 | 3.4547 | 1.9421 | 1.7411 | 1.5716 | 4.6168 | 4.5695 | 4.4684 | 4.4063 | 4.3579 | 4.2526 | 4.1695 | 4.1211 | 3.9516 | 3.5632 | 2.0811 | 1.88 | 1.7116
|  | BOWMORE | EE |  |  |  |  | 3.7 | 3.6863 | 3.6747 | 3.6632 | 3.6484 | 3.6253 | 3.6032 | 3.5863 | 3.5695 | 6.7442 | 5.9726 | 5.8 | 5.6695 | 4.8295 | 4.7695 | 4.6368 | 4.5568 | 4.4958 | 4.3621 | 4.2568 | 4.1979 | 4.14 | 9.2958 | 7.0253 | 6.8337 | 6.6842 | 4.6168 | 4.5695 | 4.4684 | 4.4063 | 4.3579 | 4.2526 | 4.1695 | 4.1211 | 4.0747 | 8.8253 | 6.5295 | 6.3379 | 6.1926
|  | BOWMORE | HT |  |  |  |  | 3.7032 | 3.6895 | 3.6758 | 3.6621 | 3.6432 | 3.6263 | 3.6084 | 3.5905 | 3.5716 | 3.5337 | 2 | 1.8337 | 1.7147 | 4.8442 | 4.7895 | 4.6642 | 4.6011 | 4.5379 | 4.3979 | 4.3137 | 4.2547 | 3.9737 | 3.4547 | 1.9421 | 1.7411 | 1.5716 | 4.6295 | 4.5853 | 4.4895 | 4.4389 | 4.3874 | 4.28 | 4.2126 | 4.1642 | 3.9516 | 3.5632 | 2.0811 | 1.88 | 1.7116
|  | BOWMORE | HE |  |  |  |  | 3.7074 | 3.6947 | 3.6874 | 3.6737 | 3.6579 | 3.6379 | 3.6158 | 3.6042 | 3.5916 | 3.5853 | 2.6189 | 2.5253 | 2.46 | 4.8758 | 4.8326 | 4.7253 | 4.6842 | 4.6547 | 4.5411 | 4.4821 | 4.4505 | 4.4137 | 4.3832 | 2.4926 | 2.3863 | 2.3116 | 4.6537 | 4.6189 | 4.5368 | 4.5032 | 4.4768 | 4.3884 | 4.3389 | 4.3126 | 4.2821 | 4.2579 | 2.6874 | 2.5926 | 2.5179
|  | BOWMORE | FB |  |  |  |  | 3.7137 | 3.7084 | 3.7032 | 3.6968 | 3.6905 | 3.6832 | 3.6768 | 3.6695 | 3.6621 | 3.6537 | 3.6253 | 3.46 | 3.3674 | 4.9063 | 4.88 | 4.8232 | 4.7979 | 4.7779 | 4.7358 | 4.6853 | 4.6642 | 4.6379 | 4.6032 | 4.0705 | 3.3589 | 3.2516 | 4.6768 | 4.6568 | 4.6137 | 4.5926 | 4.5768 | 4.5432 | 4.5053 | 4.4874 | 4.4663 | 4.4379 | 4.0379 | 3.5053 | 3.4147
| SHETLAND | BRAE | MINIMUM HEADROOM | HU3604068816 | YES | YES | 0 | 0.93158 | 0.89684 | 0.86632 | 0.38316 | -0.18211 | -0.75053 | -1.3189 | -1.3505 | -1.3789 | -1.4053 | -5.4389 | -8.5789 | -8.6368 | 0.92632 | 0.88947 | 0.85684 | 0.32737 | -0.29368 | -0.91895 | -1.5421 | -1.5747 | -1.6074 | -1.6379 | -5.1705 | -7.8411 | -7.92 | 0.97684 | 0.96211 | 0.95053 | 0.73579 | 0.035789 | -0.66842 | -1.3705 | -1.4053 | -1.4379 | -1.4674 | -5.6705 | -8.9411 | -9.0263
|  | BRAE | EE |  |  |  |  | 0.93158 | 0.89684 | 0.86632 | 0.38316 | -0.18211 | -0.75053 | -1.3189 | -1.3505 | -1.3789 | -1.4053 | -2.4568 | -2.5411 | -2.6042 | 0.92632 | 0.88947 | 0.85684 | 0.32737 | -0.29368 | -0.91895 | -1.5421 | -1.5747 | -1.6074 | -1.6379 | -2.7389 | -2.8358 | -2.9105 | 0.97684 | 0.96211 | 0.95053 | 0.73579 | 0.035789 | -0.66842 | -1.3705 | -1.4053 | -1.4379 | -1.4674 | -2.6611 | -2.7579 | -2.8316
|  | BRAE | HT |  |  |  |  | 0.94211 | 0.90947 | 0.88 | 0.39895 | -0.16632 | -0.19789 | -0.22947 | -0.26 | -0.52105 | -1.02 | -5.4389 | -8.5789 | -8.6368 | 0.93789 | 0.90316 | 0.87158 | 0.34421 | -0.27684 | -0.30947 | -0.34316 | -0.37579 | -0.66 | -1.2084 | -5.1705 | -7.8411 | -7.92 | 0.97895 | 0.96526 | 0.95053 | 0.75474 | 0.054737 | 0.02 | -0.015789 | -0.050526 | -0.36947 | -0.98737 | -5.6705 | -8.9411 | -9.0263
|  | BRAE | HE |  |  |  |  | 0.96316 | 0.93895 | 0.92 | 0.44842 | -0.10737 | -0.66842 | -1.2284 | -1.2495 | -1.2705 | -1.2842 | -3.5632 | -5.1326 | -5.1621 | 0.96105 | 0.93579 | 0.91579 | 0.39789 | -0.21368 | -0.82842 | -1.4432 | -1.4653 | -1.4874 | -1.5021 | -3.5716 | -4.9032 | -4.9358 | 0.98316 | 0.97053 | 0.96105 | 0.81474 | 0.12526 | -0.56842 | -1.2611 | -1.2842 | -1.3074 | -1.3232 | -3.7505 | -5.3621 | -5.3968
|  | BRAE | FB |  |  |  |  | 0.97684 | 0.96316 | 0.94737 | 0.87895 | 0.72211 | 0.50526 | 0.22105 | -0.13158 | -0.14737 | -0.16421 | -0.30211 | -0.47368 | -0.51474 | 0.97474 | 0.96105 | 0.94421 | 0.86947 | 0.69684 | 0.45895 | 0.14632 | -0.24211 | -0.25895 | -0.27579 | -0.42632 | -0.61158 | -0.65684 | 0.99158 | 0.98632 | 0.98 | 0.97158 | 0.95474 | 0.88211 | 0.52842 | 0.090526 | 0.072632 | 0.053684 | -0.11263 | -0.32 | -0.37053
| BRIDGE OF DUN | BRECHIN | MINIMUM HEADROOM | NO 60998 59682 | NO | YES | 0.41327 | 12.8524 | 12.7239 | 12.5039 | 12.1776 | 11.5587 | 11.345 | 11.1492 | 10.9345 | 10.4397 | 9.8955 | 5.7482 | 4.7229 | 4.4355 | 11.2484 | 11.0811 | 10.8105 | 10.4274 | 9.7095 | 9.4653 | 9.2442 | 9.0011 | 8.4284 | 7.7989 | 4.7853 | 2.7179 | 2.3926 | 10.0251 | 9.7704 | 9.5178 | 9.1588 | 8.4893 | 8.2609 | 8.0525 | 7.823 | 7.2883 | 6.7009 | 3.7862 | 1.2199 | 0.91355
|  | BRECHIN | EE |  |  |  |  | 12.8524 | 12.7239 | 12.5429 | 12.3071 | 11.6934 | 11.5155 | 11.3534 | 11.1629 | 10.8324 | 10.7239 | 7.3029 | 4.7229 | 4.4355 | 11.2484 | 11.0811 | 10.86 | 10.5779 | 9.8642 | 9.6653 | 9.4853 | 9.2695 | 8.8895 | 8.7684 | 4.9526 | 2.7179 | 2.3926 | 10.0251 | 9.7704 | 9.563 | 9.2999 | 8.6346 | 8.4462 | 8.2746 | 8.0714 | 7.7157 | 7.5999 | 3.9136 | 1.2199 | 0.91355
|  | BRECHIN | HT |  |  |  |  | 12.8597 | 12.7597 | 12.5039 | 12.1776 | 11.5587 | 11.345 | 11.1492 | 10.9345 | 10.4397 | 9.8955 | 5.7482 | 5.2018 | 4.9229 | 11.2568 | 11.1242 | 10.8105 | 10.4274 | 9.7095 | 9.4653 | 9.2442 | 9.0011 | 8.4284 | 7.7989 | 4.7853 | 3.1811 | 2.7874 | 10.0578 | 9.8114 | 9.5178 | 9.1588 | 8.4893 | 8.2609 | 8.0525 | 7.823 | 7.2883 | 6.7009 | 3.7862 | 1.7967 | 1.4241
|  | BRECHIN | HE |  |  |  |  | 12.8692 | 12.8366 | 12.6797 | 12.4661 | 11.9029 | 11.7566 | 11.5797 | 11.4208 | 11.0797 | 11.0176 | 8.205 | 6.9776 | 6.8282 | 11.2695 | 11.2284 | 11.0263 | 10.7674 | 10.1063 | 9.9453 | 9.7474 | 9.5674 | 9.1726 | 9.1032 | 5.8842 | 4.7611 | 4.5926 | 10.1346 | 9.9209 | 9.7199 | 9.4757 | 8.8609 | 8.7072 | 8.5199 | 8.3493 | 7.982 | 7.9157 | 4.8704 | 3.5809 | 3.422
|  | BRECHIN | FB |  |  |  |  | 12.8861 | 12.8713 | 12.8555 | 12.8261 | 12.7018 | 12.5924 | 12.4987 | 12.4134 | 12.2503 | 12.1808 | 11.1997 | 9.7376 | 9.5376 | 11.2895 | 11.2684 | 11.2484 | 11.2032 | 11.0526 | 10.9189 | 10.8063 | 10.7042 | 10.5126 | 10.4358 | 9.2979 | 7.5937 | 7.3642 | 10.2167 | 10.0767 | 9.9809 | 9.8851 | 9.7441 | 9.6188 | 9.5125 | 9.4167 | 9.2378 | 9.1641 | 8.1041 | 6.5188 | 6.3041
| PERSLEY | BRIDGE OF DON | MINIMUM HEADROOM | NJ 94130 10184 | NO | NO | 0.2602 | 16.81 | 15.7711 | 15.0753 | 14.3184 | 14.0289 | 13.5974 | 13.0974 | 12.5342 | 13.3563 | 13.0647 | 11.0479 | 11.1742 | 11.4142 | 13.3632 | 12.1589 | 11.3537 | 10.48 | 10.1558 | 9.6611 | 9.0905 | 8.4453 | 9.1179 | 8.7916 | 6.7368 | 6.78 | 6.9242 | 15.8613 | 14.6539 | 13.8245 | 12.9255 | 12.5929 | 12.0855 | 11.4971 | 10.835 | 11.6003 | 11.2666 | 9.0339 | 9.1361 | 9.3245
|  | BRIDGE OF DON | EE |  |  |  |  | 16.8268 | 15.7711 | 15.1037 | 14.3805 | 14.1195 | 13.5974 | 13.2247 | 12.7879 | 13.8132 | 13.5626 | 11.0479 | 11.1742 | 11.4142 | 13.3842 | 12.1589 | 11.3874 | 10.5505 | 10.2568 | 9.6611 | 9.2421 | 8.7421 | 9.6516 | 9.3674 | 6.7368 | 6.78 | 6.9242 | 15.8782 | 14.6539 | 13.8592 | 12.9961 | 12.695 | 12.0855 | 11.655 | 11.1424 | 12.1518 | 11.8613 | 9.0339 | 9.1361 | 9.3245
|  | BRIDGE OF DON | HT |  |  |  |  | 16.81 | 15.8132 | 15.0753 | 14.3184 | 14.0289 | 13.6079 | 13.0974 | 12.5342 | 13.3563 | 13.0647 | 11.9805 | 11.2868 | 11.5384 | 13.3632 | 12.2063 | 11.3537 | 10.48 | 10.1558 | 9.6747 | 9.0905 | 8.4453 | 9.1179 | 8.7916 | 7.0505 | 7.0211 | 7.0368 | 15.8613 | 14.7024 | 13.8245 | 12.9255 | 12.5929 | 12.0982 | 11.4971 | 10.835 | 11.6003 | 11.2666 | 9.3971 | 9.4108 | 9.4676
|  | BRIDGE OF DON | HE |  |  |  |  | 16.8721 | 16.0353 | 15.4511 | 14.8268 | 14.6332 | 14.2995 | 13.9121 | 13.5479 | 14.6437 | 14.4784 | 13.5721 | 13.6016 | 13.6563 | 13.4326 | 12.4632 | 11.7863 | 11.0653 | 10.8495 | 10.4737 | 10.0358 | 9.6189 | 10.6074 | 10.4179 | 9.4874 | 9.3653 | 9.2842 | 15.9245 | 14.9666 | 14.2687 | 13.5276 | 13.3066 | 12.9213 | 12.4729 | 12.0445 | 13.1361 | 12.9413 | 11.9361 | 11.8424 | 11.7961
|  | BRIDGE OF DON | FB |  |  |  |  | 17.6405 | 17.3374 | 17.0258 | 16.7784 | 16.5795 | 16.35 | 16.1405 | 15.9079 | 17.1595 | 16.9668 | 16.4479 | 16.5626 | 16.7311 | 14.3253 | 13.9747 | 13.6137 | 13.3295 | 13.1021 | 12.8379 | 12.5979 | 12.3305 | 13.4968 | 13.2768 | 12.6895 | 12.6821 | 12.7358 | 16.7171 | 16.4045 | 16.0834 | 15.8287 | 15.6245 | 15.3539 | 15.1066 | 14.8329 | 16.1076 | 15.8813 | 15.2792 | 15.3118 | 15.4045
| BRIDGE OF DUN | BRIDGE OF DUN | MINIMUM HEADROOM | NO 66018 58883 | YES | YES | 0.67347 | 0.28 | 0.27053 | 0.26 | 0.24737 | 0.23684 | 0.22316 | 0.20842 | 0.19474 | 0.18211 | 0.17053 | -1.1274 | -1.1611 | -1.1884 | 0.26526 | 0.25158 | 0.23895 | 0.22211 | 0.20842 | 0.19053 | 0.17579 | 0.16211 | 0.14842 | 0.13579 | -0.89579 | -0.93895 | -0.96947 | 0.31789 | 0.30526 | 0.29053 | 0.27368 | 0.25895 | 0.24105 | 0.22632 | 0.21158 | 0.19789 | 0.18421 | -1.1137 | -1.1568 | -1.1916
|  | BRIDGE OF DUN | EE |  |  |  |  | 0.28 | 0.27053 | 0.26 | 0.24737 | 0.23684 | 0.22316 | 0.20842 | 0.19474 | 0.18211 | 0.17053 | -1.1274 | -1.1611 | -1.1884 | 0.26526 | 0.25158 | 0.23895 | 0.22211 | 0.20842 | 0.19053 | 0.17579 | 0.16211 | 0.14842 | 0.13579 | -0.89579 | -0.93895 | -0.96947 | 0.31789 | 0.30526 | 0.29053 | 0.27368 | 0.25895 | 0.24105 | 0.22632 | 0.21158 | 0.19789 | 0.18421 | -1.1137 | -1.1568 | -1.1916
|  | BRIDGE OF DUN | HT |  |  |  |  | 0.28316 | 0.27474 | 0.26842 | 0.25789 | 0.24632 | 0.23579 | 0.22632 | 0.21474 | 0.20105 | 0.18947 | -0.86316 | -0.89368 | -0.91684 | 0.26947 | 0.25789 | 0.24842 | 0.23579 | 0.22 | 0.20632 | 0.19368 | 0.17895 | 0.16526 | 0.15158 | -0.68 | -0.72105 | -0.75789 | 0.32316 | 0.31158 | 0.30211 | 0.28947 | 0.27368 | 0.26 | 0.24842 | 0.23263 | 0.22 | 0.20526 | -0.83684 | -0.87684 | -0.91263
|  | BRIDGE OF DUN | HE |  |  |  |  | 0.28842 | 0.28316 | 0.27895 | 0.27158 | 0.26632 | 0.25789 | 0.24842 | 0.24421 | 0.23684 | 0.23368 | -0.29474 | -0.31158 | -0.32421 | 0.27895 | 0.26947 | 0.26421 | 0.25579 | 0.24947 | 0.23895 | 0.22947 | 0.22316 | 0.21474 | 0.20947 | -0.20316 | -0.22526 | -0.24 | 0.33053 | 0.32316 | 0.31789 | 0.30947 | 0.30211 | 0.29263 | 0.28105 | 0.27579 | 0.26737 | 0.26211 | -0.25895 | -0.28105 | -0.29684
|  | BRIDGE OF DUN | FB |  |  |  |  | 0.29263 | 0.28947 | 0.28526 | 0.28211 | 0.27789 | 0.27368 | 0.27053 | 0.26632 | 0.26211 | 0.25684 | 0.23789 | 0.21263 | 0.19263 | 0.28211 | 0.27789 | 0.27263 | 0.26842 | 0.26211 | 0.25684 | 0.25158 | 0.24632 | 0.24 | 0.23158 | 0.20421 | 0.17579 | 0.15158 | 0.33579 | 0.33158 | 0.32526 | 0.32105 | 0.31579 | 0.30947 | 0.30526 | 0.3 | 0.29368 | 0.28632 | 0.26 | 0.23053 | 0.20842
| ABERNETHY | BRIDGE OF EARN | MINIMUM HEADROOM | NO 13343 17764 | NO | YES | 0.067347 | 14.6826 | 14.4879 | 14.2753 | 14.0721 | 13.9468 | 13.6258 | 13.3658 | 13.1374 | 12.9037 | 12.75 | 6.7784 | 2.5395 | -1.3447 | 13.3832 | 13.1568 | 12.9095 | 12.6737 | 12.5316 | 12.16 | 11.86 | 11.5947 | 11.3263 | 11.1484 | 5.5284 | -0.85368 | -5.4189 | 13.8297 | 13.6066 | 13.3634 | 13.1297 | 12.9897 | 12.6224 | 12.3255 | 12.0645 | 11.7982 | 11.6234 | 6.0466 | -0.33868 | -4.8966
|  | BRIDGE OF EARN | EE |  |  |  |  | 14.6826 | 14.4879 | 14.2753 | 14.0721 | 13.9468 | 13.6258 | 13.3658 | 13.1374 | 12.9037 | 12.75 | 10.9647 | 9.9184 | 8.7384 | 13.3832 | 13.1568 | 12.9095 | 12.6737 | 12.5316 | 12.16 | 11.86 | 11.5947 | 11.3263 | 11.1484 | 9.0653 | 7.8463 | 6.4663 | 13.8297 | 13.6066 | 13.3634 | 13.1297 | 12.9897 | 12.6224 | 12.3255 | 12.0645 | 11.7982 | 11.6234 | 9.5655 | 8.3624 | 6.9845
|  | BRIDGE OF EARN | HT |  |  |  |  | 14.6974 | 14.5089 | 14.2921 | 14.0911 | 13.9489 | 13.7121 | 13.4753 | 13.2374 | 12.9816 | 12.7784 | 6.7784 | 3.5763 | 1.9668 | 13.3989 | 13.1821 | 12.9305 | 12.6989 | 12.5368 | 12.2642 | 11.9895 | 11.7158 | 11.4211 | 11.1874 | 5.5284 | 0.88842 | -1.4695 | 13.8466 | 13.6318 | 13.3834 | 13.155 | 12.9939 | 12.7245 | 12.4539 | 12.1824 | 11.8918 | 11.6613 | 6.0466 | 1.4045 | -0.95342
|  | BRIDGE OF EARN | HE |  |  |  |  | 14.7353 | 14.5637 | 14.37 | 14.1879 | 14.0805 | 13.8311 | 13.5805 | 13.3616 | 13.1374 | 12.9974 | 11.2626 | 10.2763 | 9.1511 | 13.4421 | 13.2432 | 13.0189 | 12.8074 | 12.6853 | 12.3979 | 12.1084 | 11.8547 | 11.5947 | 11.4316 | 9.4011 | 8.2474 | 6.9295 | 13.8887 | 13.6929 | 13.4708 | 13.2624 | 13.1413 | 12.8571 | 12.5708 | 12.3203 | 12.0634 | 11.9024 | 9.8992 | 8.7603 | 7.4466
|  | BRIDGE OF EARN | FB |  |  |  |  | 14.8279 | 14.7468 | 14.65 | 14.5658 | 14.5205 | 14.4037 | 14.2805 | 14.1426 | 14.0026 | 13.9279 | 8.5426 | 2.5395 | -1.3447 | 13.5505 | 13.4558 | 13.3432 | 13.2453 | 13.1926 | 13.0579 | 12.9137 | 12.7537 | 12.5905 | 12.5053 | 6.1895 | -0.85368 | -5.4189 | 13.9961 | 13.9024 | 13.7918 | 13.6939 | 13.6424 | 13.5097 | 13.3666 | 13.2097 | 13.0476 | 12.9634 | 6.7076 | -0.33868 | -4.8966
| RANNOCH | BRIDGE OF GAUR | MINIMUM HEADROOM | NN 50676 57767 | YES | YES | 0 | 0.88947 | 0.88211 | 0.87368 | 0.86316 | 0.85263 | 0.84316 | 0.83368 | 0.82316 | 0.81263 | 0.80316 | 0.76737 | 0.72737 | 0.69053 | 0.88737 | 0.87789 | 0.86842 | 0.85789 | 0.84737 | 0.83684 | 0.82632 | 0.81579 | 0.80526 | 0.79474 | 0.75895 | 0.71895 | 0.68 | 0.95684 | 0.94526 | 0.93368 | 0.92421 | 0.91263 | 0.90211 | 0.89158 | 0.88 | 0.86947 | 0.85895 | 0.81895 | 0.77684 | 0.73474
|  | BRIDGE OF GAUR | EE |  |  |  |  | 0.88947 | 0.88211 | 0.87368 | 0.86316 | 0.85263 | 0.84316 | 0.83368 | 0.82316 | 0.81263 | 0.80316 | 0.76737 | 0.72737 | 0.69053 | 0.88737 | 0.87789 | 0.86842 | 0.85789 | 0.84737 | 0.83684 | 0.82632 | 0.81579 | 0.80526 | 0.79474 | 0.75895 | 0.71895 | 0.68 | 0.95684 | 0.94526 | 0.93368 | 0.92421 | 0.91263 | 0.90211 | 0.89158 | 0.88 | 0.86947 | 0.85895 | 0.81895 | 0.77684 | 0.73474
|  | BRIDGE OF GAUR | HT |  |  |  |  | 0.89368 | 0.89158 | 0.88737 | 0.88421 | 0.88105 | 0.87684 | 0.87158 | 0.86737 | 0.86105 | 0.85579 | 0.83368 | 0.81474 | 0.79789 | 0.89263 | 0.88947 | 0.88316 | 0.88 | 0.87579 | 0.87158 | 0.86737 | 0.86316 | 0.85579 | 0.85053 | 0.83368 | 0.81263 | 0.79263 | 0.96211 | 0.95789 | 0.95053 | 0.94632 | 0.94211 | 0.93579 | 0.93158 | 0.92632 | 0.91895 | 0.91368 | 0.89368 | 0.86947 | 0.84842
|  | BRIDGE OF GAUR | HE |  |  |  |  | 0.89368 | 0.89263 | 0.88947 | 0.88526 | 0.88316 | 0.88 | 0.87579 | 0.87474 | 0.87053 | 0.86737 | 0.85684 | 0.84105 | 0.82842 | 0.89368 | 0.89158 | 0.88737 | 0.88316 | 0.87895 | 0.87684 | 0.87158 | 0.86947 | 0.86526 | 0.86105 | 0.84947 | 0.83474 | 0.82105 | 0.96316 | 0.96 | 0.95579 | 0.95158 | 0.94737 | 0.94316 | 0.93895 | 0.93579 | 0.93158 | 0.92737 | 0.91579 | 0.89895 | 0.88737
|  | BRIDGE OF GAUR | FB |  |  |  |  | 0.89579 | 0.89474 | 0.89474 | 0.89368 | 0.89263 | 0.89263 | 0.89053 | 0.89053 | 0.89053 | 0.88842 | 0.88316 | 0.87789 | 0.87368 | 0.89579 | 0.89368 | 0.89263 | 0.89263 | 0.89053 | 0.88842 | 0.88632 | 0.88526 | 0.88421 | 0.88105 | 0.87474 | 0.87053 | 0.86632 | 0.96526 | 0.96421 | 0.96211 | 0.96211 | 0.96 | 0.95789 | 0.95474 | 0.95368 | 0.95263 | 0.95053 | 0.94211 | 0.93789 | 0.93158
| BROADFORD | BROADFORD | MINIMUM HEADROOM | NG 62656 24360 | YES | YES | 0.0081633 | 4.8663 | 4.8053 | 4.7316 | 4.6979 | 4.6621 | 3.0768 | 1.2042 | -0.87789 | -2.4895 | -2.9326 | -3.0768 | -3.1863 | -3.2642 | 4.8484 | 4.78 | 4.6947 | 4.6568 | 4.6179 | 2.7821 | 0.61158 | -1.8011 | -3.6684 | -4.18 | -4.3295 | -4.4421 | -4.5495 | 4.8484 | 4.7789 | 4.6937 | 4.6558 | 4.6168 | 2.7747 | 0.59684 | -1.8253 | -3.6989 | -4.2126 | -4.3632 | -4.4747 | -4.5832
|  | BROADFORD | EE |  |  |  |  | 4.8663 | 4.8053 | 4.7316 | 4.6979 | 4.6621 | 4.6232 | 4.5126 | 3.0137 | 1.1768 | -0.94421 | -3.0663 | -3.1663 | -3.2368 | 4.8484 | 4.78 | 4.6947 | 4.6568 | 4.6179 | 4.5747 | 4.4484 | 2.7116 | 0.58316 | -1.8747 | -4.3295 | -4.4421 | -4.5211 | 4.8484 | 4.7789 | 4.6937 | 4.6558 | 4.6168 | 4.5737 | 4.4474 | 2.7042 | 0.56842 | -1.8989 | -4.3632 | -4.4747 | -4.5547
|  | BROADFORD | HT |  |  |  |  | 4.8747 | 4.8158 | 4.7453 | 4.7158 | 4.68 | 3.0768 | 1.2042 | -0.87789 | -2.4895 | -2.9326 | -3.0768 | -3.1863 | -3.2642 | 4.8579 | 4.7916 | 4.7116 | 4.6779 | 4.6389 | 2.7821 | 0.61158 | -1.8011 | -3.6684 | -4.18 | -4.3105 | -4.4389 | -4.5495 | 4.8579 | 4.7905 | 4.7105 | 4.6768 | 4.6379 | 2.7747 | 0.59684 | -1.8253 | -3.6989 | -4.2126 | -4.3432 | -4.4726 | -4.5832
|  | BROADFORD | HE |  |  |  |  | 4.8926 | 4.8411 | 4.7789 | 4.7611 | 4.74 | 4.7053 | 4.6221 | 2.9611 | 0.91895 | -1.4768 | -2.8726 | -2.9284 | -2.9621 | 4.8789 | 4.82 | 4.7484 | 4.7295 | 4.7074 | 4.6684 | 4.5747 | 2.6505 | 0.28316 | -2.4947 | -4.1116 | -4.1737 | -4.2126 | 4.8789 | 4.8189 | 4.7484 | 4.7284 | 4.7063 | 4.6674 | 4.5737 | 2.6421 | 0.26632 | -2.5211 | -4.1442 | -4.2063 | -4.2453
|  | BROADFORD | FB |  |  |  |  | 4.9105 | 4.8863 | 4.8516 | 4.84 | 4.8274 | 4.8137 | 4.7821 | 4.7505 | 4.0474 | 3.1463 | 0.11053 | 0.042105 | -0.0084211 | 4.8989 | 4.8705 | 4.8316 | 4.8179 | 4.8042 | 4.7895 | 4.7526 | 4.7168 | 3.9032 | 2.8579 | -0.66 | -0.73684 | -0.79368 | 4.8979 | 4.8695 | 4.8305 | 4.8179 | 4.8042 | 4.7884 | 4.7526 | 4.7168 | 3.8989 | 2.8505 | -0.68 | -0.75789 | -0.81474
| CARRADALE 1 | BRODICK | MINIMUM HEADROOM | NS 01976 35459 | NO | YES | 0 | 4.8032 | 4.6874 | 4.4505 | 4.3568 | 4.2684 | 4.1737 | 4.0768 | 3.9926 | 3.9105 | 3.8368 | 3.5558 | 3.2958 | 3.0968 | 4.1989 | 4.0716 | 3.8747 | 3.7747 | 3.6811 | 3.5811 | 3.4789 | 3.3926 | 3.3053 | 3.2284 | 2.9358 | 2.6642 | 2.4589 | 4.5495 | 4.4168 | 4.1495 | 4.0442 | 3.9453 | 3.8389 | 3.7337 | 3.6389 | 3.5484 | 3.4663 | 3.1537 | 2.8611 | 2.6358
|  | BRODICK | EE |  |  |  |  | 4.8032 | 4.6874 | 4.4505 | 4.3568 | 4.2684 | 4.1737 | 4.0768 | 3.9926 | 3.9105 | 3.8368 | 3.5558 | 3.2958 | 3.0968 | 4.1989 | 4.0716 | 3.8747 | 3.7747 | 3.6811 | 3.5811 | 3.4789 | 3.3926 | 3.3053 | 3.2284 | 2.9358 | 2.6642 | 2.4589 | 4.5495 | 4.4168 | 4.1495 | 4.0442 | 3.9453 | 3.8389 | 3.7337 | 3.6389 | 3.5484 | 3.4663 | 3.1537 | 2.8611 | 2.6358
|  | BRODICK | HT |  |  |  |  | 4.8295 | 4.7295 | 4.6032 | 4.5263 | 4.4421 | 4.3611 | 4.28 | 4.1979 | 4.1179 | 4.0347 | 3.7084 | 3.4695 | 3.3032 | 4.2253 | 4.1137 | 3.9716 | 3.8884 | 3.7979 | 3.7095 | 3.6211 | 3.5316 | 3.4453 | 3.3568 | 3.0653 | 2.7916 | 2.5653 | 4.58 | 4.4653 | 4.3211 | 4.2347 | 4.1421 | 4.0526 | 3.9621 | 3.8705 | 3.7821 | 3.6916 | 3.3937 | 3.1095 | 2.8737
|  | BRODICK | HE |  |  |  |  | 4.8937 | 4.8284 | 4.7053 | 4.6295 | 4.58 | 4.5221 | 4.4621 | 4.4126 | 4.3611 | 4.3221 | 4.1747 | 4.0389 | 3.9432 | 4.2979 | 4.2274 | 4.0863 | 4.0053 | 3.9537 | 3.8916 | 3.8305 | 3.7779 | 3.7221 | 3.68 | 3.5221 | 3.3768 | 3.2758 | 4.6537 | 4.58 | 4.4368 | 4.3526 | 4.3 | 4.2358 | 4.1726 | 4.1189 | 4.0621 | 4.0179 | 3.8526 | 3.6989 | 3.5916
|  | BRODICK | FB |  |  |  |  | 7.7432 | 7.7337 | 4.8326 | 4.7874 | 4.7547 | 4.7211 | 4.6874 | 4.6537 | 4.6168 | 4.5737 | 4.4168 | 4.2568 | 4.1337 | 7.6495 | 7.64 | 4.2274 | 4.1779 | 4.1421 | 4.1032 | 4.0674 | 4.0305 | 3.9895 | 3.9421 | 3.7674 | 3.5895 | 3.4495 | 8.1621 | 8.1537 | 4.5832 | 4.5316 | 4.4947 | 4.4558 | 4.42 | 4.3832 | 4.34 | 4.2926 | 4.1158 | 3.9337 | 3.7926
| BRORA | BRORA | MINIMUM HEADROOM | NC 90482 04236 | NO | YES | 0 | 1.9674 | 1.9516 | 1.9379 | 1.9211 | 1.9032 | 1.8137 | 1.7326 | 1.6737 | 1.6379 | 1.6147 | 1.5347 | 1.4874 | 1.4526 | 4.8442 | 4.8137 | 4.7853 | 4.7516 | 4.7168 | 3.9842 | 3.1716 | 2.62 | 2.3811 | 2.3095 | 2.0747 | 1.9421 | 1.8305 | 1.8747 | 1.8411 | 1.8084 | 1.7716 | 1.7347 | 1.0063 | 0.38316 | -0.043158 | -0.22947 | -0.28947 | -0.48842 | -0.60211 | -0.69053
|  | BRORA | EE |  |  |  |  | 1.9674 | 1.9516 | 1.9379 | 1.9211 | 1.9032 | 1.88 | 1.8558 | 1.7663 | 1.6821 | 1.6221 | 1.5358 | 1.4874 | 1.4526 | 4.8442 | 4.8137 | 4.7853 | 4.7516 | 4.7168 | 4.6768 | 4.6368 | 3.9137 | 3.0905 | 2.5137 | 2.0747 | 1.9421 | 1.8368 | 1.8747 | 1.8411 | 1.8084 | 1.7716 | 1.7347 | 1.6905 | 1.6484 | 0.93684 | 0.30526 | -0.13895 | -0.48842 | -0.60211 | -0.69053
|  | BRORA | HT |  |  |  |  | 1.9716 | 1.9579 | 1.9442 | 1.9274 | 1.9084 | 1.8137 | 1.7326 | 1.6737 | 1.6379 | 1.6147 | 1.5347 | 1.4905 | 1.4568 | 4.8537 | 4.8274 | 4.8011 | 4.7716 | 4.7347 | 3.9842 | 3.1716 | 2.62 | 2.3811 | 2.3095 | 2.0947 | 1.9484 | 1.8305 | 1.8853 | 1.8558 | 1.8274 | 1.7947 | 1.7547 | 1.0063 | 0.38316 | -0.043158 | -0.22947 | -0.28947 | -0.46526 | -0.58632 | -0.68632
|  | BRORA | HE |  |  |  |  | 1.9779 | 1.9663 | 1.9568 | 1.9421 | 1.9274 | 1.9084 | 1.8874 | 1.7958 | 1.7105 | 1.6611 | 1.6211 | 1.5968 | 1.5811 | 4.8726 | 4.8537 | 4.8368 | 4.8158 | 4.7937 | 4.7684 | 4.74 | 3.9653 | 3.0779 | 2.5221 | 2.3232 | 2.2421 | 2.1821 | 1.9074 | 1.8863 | 1.8684 | 1.8453 | 1.8211 | 1.7947 | 1.7653 | 0.98632 | 0.30632 | -0.11895 | -0.27789 | -0.34421 | -0.39263
|  | BRORA | FB |  |  |  |  | 1.9863 | 1.9811 | 1.9747 | 1.9684 | 1.9621 | 1.9558 | 1.9495 | 1.9432 | 1.9021 | 1.8621 | 1.7758 | 1.7505 | 1.7347 | 4.8863 | 4.8737 | 4.8611 | 4.8484 | 4.8347 | 4.8211 | 4.8074 | 4.7937 | 4.5095 | 4.18 | 3.3768 | 3.2863 | 3.2158 | 1.9211 | 1.9074 | 1.8937 | 1.8789 | 1.8632 | 1.8484 | 1.8337 | 1.8189 | 1.4832 | 1.1642 | 0.54632 | 0.47158 | 0.41579
| MILTON OF CRAIGIE | BROUGHTY FERRY | MINIMUM HEADROOM | NO 46658 30758 | NO | YES | 0 | 11.6411 | 11.5947 | 11.5579 | 11.5105 | 11.4547 | 11.3947 | 11.3263 | 11.2716 | 11.2179 | 11.1558 | 10.9105 | 10.7547 | 10.4958 | 11.3432 | 11.2989 | 11.2642 | 11.2168 | 11.1632 | 11.1074 | 11.0411 | 10.9895 | 10.9368 | 10.8495 | 10.3316 | 9.8221 | 9.4358 | 9.6232 | 9.4989 | 9.3832 | 9.2526 | 9.1095 | 8.9453 | 8.7937 | 8.6716 | 8.5505 | 8.4137 | 7.9126 | 7.4305 | 7.0642
|  | BROUGHTY FERRY | EE |  |  |  |  | 11.6411 | 11.5947 | 11.5579 | 11.5158 | 11.4632 | 11.3947 | 11.3263 | 11.2716 | 11.2179 | 11.1705 | 10.9821 | 10.8453 | 10.6474 | 11.3432 | 11.2989 | 11.2642 | 11.2242 | 11.1737 | 11.1074 | 11.0411 | 10.9895 | 10.9368 | 10.8495 | 10.3926 | 9.9389 | 9.6063 | 9.6232 | 9.4989 | 9.3832 | 9.2526 | 9.1095 | 8.9453 | 8.7937 | 8.6716 | 8.5505 | 8.4137 | 7.9716 | 7.5432 | 7.2284
|  | BROUGHTY FERRY | HT |  |  |  |  | 11.6495 | 11.6063 | 11.5611 | 11.5105 | 11.4547 | 11.3989 | 11.3421 | 11.2832 | 11.2232 | 11.1558 | 10.9105 | 10.7547 | 10.4958 | 11.3505 | 11.3095 | 11.2663 | 11.2168 | 11.1632 | 11.1095 | 11.0558 | 10.9979 | 10.9389 | 10.8747 | 10.3316 | 9.8221 | 9.4358 | 9.66 | 9.5463 | 9.4379 | 9.3158 | 9.1653 | 9.0337 | 8.9074 | 8.7811 | 8.6505 | 8.48 | 7.9126 | 7.4305 | 7.0642
|  | BROUGHTY FERRY | HE |  |  |  |  | 11.6684 | 11.6284 | 11.6 | 11.56 | 11.5116 | 11.4495 | 11.3863 | 11.3463 | 11.3063 | 11.2821 | 11.1842 | 11.1126 | 11.0642 | 11.3674 | 11.3295 | 11.3021 | 11.2632 | 11.2158 | 11.1558 | 11.0926 | 11.0537 | 11.0147 | 10.9916 | 10.8989 | 10.8326 | 10.6684 | 9.7411 | 9.66 | 9.5926 | 9.5158 | 9.4168 | 9.3011 | 9.2053 | 9.1284 | 9.0463 | 8.9568 | 8.6789 | 8.4126 | 8.2368
|  | BROUGHTY FERRY | FB |  |  |  |  | 11.6863 | 11.6684 | 11.6505 | 11.6305 | 11.6084 | 11.5853 | 11.5621 | 11.5379 | 11.5147 | 11.4874 | 11.3895 | 11.3032 | 11.2537 | 11.3863 | 11.3695 | 11.3516 | 11.3326 | 11.3116 | 11.2905 | 11.2674 | 11.2442 | 11.2221 | 11.1958 | 11.1032 | 11.0221 | 10.8779 | 9.7811 | 9.7284 | 9.6758 | 9.6189 | 9.5558 | 9.4895 | 9.4189 | 9.3621 | 9.3011 | 9.2137 | 8.94 | 8.6589 | 8.4453
| DUNOON | BRUCHAG | MINIMUM HEADROOM | NS 11372 57191 | NO | YES | 3.5714 | 11.7532 | 11.71 | 11.6711 | 11.6216 | 11.5774 | 11.5268 | 11.4742 | 11.43 | 11.3858 | 11.3437 | 11.1826 | 11.0363 | 10.9226 | 11.0474 | 11 | 10.9558 | 10.9 | 10.8505 | 10.7947 | 10.7379 | 10.6884 | 10.6389 | 10.5926 | 10.4158 | 10.2495 | 10.1211 | -20.465 | -20.5113 | -20.5555 | -20.6103 | -20.6597 | -20.7145 | -20.7713 | -20.8208 | -20.8692 | -20.9155 | -21.0903 | -21.2545 | -21.3808
|  | BRUCHAG | EE |  |  |  |  | 11.7532 | 11.71 | 11.6711 | 11.6216 | 11.5774 | 11.5268 | 11.4742 | 11.43 | 11.3858 | 11.3437 | 11.1837 | 11.0363 | 10.9226 | 11.0474 | 11 | 10.9558 | 10.9 | 10.8505 | 10.7947 | 10.7379 | 10.6884 | 10.6389 | 10.5926 | 10.4158 | 10.2495 | 10.1211 | -20.465 | -20.5113 | -20.5555 | -20.6103 | -20.6597 | -20.7145 | -20.7713 | -20.8208 | -20.8692 | -20.9155 | -21.0903 | -21.2545 | -21.3808
|  | BRUCHAG | HT |  |  |  |  | 11.7658 | 11.7289 | 11.6911 | 11.6511 | 11.6047 | 11.5595 | 11.5142 | 11.4679 | 11.4237 | 11.3763 | 11.1826 | 11.0374 | 10.9332 | 11.0632 | 11.0221 | 10.98 | 10.9347 | 10.8832 | 10.8326 | 10.7832 | 10.7316 | 10.6832 | 10.6316 | 10.4547 | 10.2821 | 10.1358 | -20.4503 | -20.4903 | -20.5324 | -20.5766 | -20.6271 | -20.6776 | -20.7271 | -20.7776 | -20.8261 | -20.8766 | -21.0513 | -21.2218 | -21.3671
|  | BRUCHAG | HE |  |  |  |  | 11.7921 | 11.7637 | 11.7395 | 11.7132 | 11.6868 | 11.6532 | 11.6174 | 11.59 | 11.5605 | 11.5384 | 11.4511 | 11.3711 | 11.3163 | 11.0937 | 11.0611 | 11.0358 | 11.0074 | 10.9779 | 10.9421 | 10.9053 | 10.8758 | 10.8421 | 10.8179 | 10.72 | 10.6305 | 10.5684 | -20.4197 | -20.4513 | -20.4776 | -20.505 | -20.5334 | -20.5692 | -20.6061 | -20.6355 | -20.6682 | -20.6934 | -20.7892 | -20.8776 | -20.9397
|  | BRUCHAG | FB |  |  |  |  | 11.8047 | 11.7858 | 11.7668 | 11.7468 | 11.7268 | 11.7068 | 11.6868 | 11.6658 | 11.6437 | 11.6163 | 11.5153 | 11.4132 | 11.3311 | 11.1063 | 11.0863 | 11.0642 | 11.0421 | 11.02 | 10.9979 | 10.9758 | 10.9526 | 10.9274 | 10.8968 | 10.7842 | 10.6684 | 10.5737 | -20.4061 | -20.4271 | -20.4492 | -20.4703 | -20.4924 | -20.5145 | -20.5355 | -20.5587 | -20.5839 | -20.6145 | -20.725 | -20.8397 | -20.9324
| KEITH 1 | BUCKIE | MINIMUM HEADROOM | NJ 43291 64802 | NO | YES | 2.4184 | 22.9779 | 22.92 | 22.8558 | 22.6642 | 22.2211 | 19.6916 | 18.9074 | 18.0842 | 17.3453 | 16.5621 | 14.1432 | 13.54 | 13.1305 | 21.2705 | 21.1474 | 20.5916 | 19.9305 | 19.4242 | 16.5263 | 15.6389 | 14.7084 | 13.8747 | 12.9895 | 10.5547 | 9.5937 | 9.0863 | 21.9663 | 21.8537 | 21.2958 | 20.6305 | 20.1221 | 17.2116 | 16.3211 | 15.3863 | 14.5495 | 13.6611 | 11.2968 | 10.3347 | 9.8284
|  | BUCKIE | EE |  |  |  |  | 22.9779 | 22.92 | 22.8558 | 22.6642 | 22.2211 | 19.7221 | 19.0168 | 18.3474 | 17.8337 | 17.5495 | 14.4958 | 13.5916 | 13.1547 | 21.2705 | 21.1474 | 20.5916 | 19.9305 | 19.4242 | 16.56 | 15.7653 | 15.0095 | 14.4326 | 14.1147 | 10.5926 | 9.5937 | 9.0979 | 21.9663 | 21.8537 | 21.2958 | 20.6305 | 20.1221 | 17.2453 | 16.4474 | 15.6884 | 15.1095 | 14.7905 | 11.3095 | 10.3347 | 9.8389
|  | BUCKIE | HT |  |  |  |  | 22.9863 | 22.9326 | 22.8579 | 22.6947 | 22.2411 | 19.6916 | 18.9074 | 18.0842 | 17.3453 | 16.5621 | 14.1432 | 13.54 | 13.1305 | 21.2789 | 21.22 | 20.6505 | 19.9674 | 19.4495 | 16.5263 | 15.6389 | 14.7084 | 13.8747 | 12.9895 | 10.5547 | 9.6726 | 9.0863 | 21.9747 | 21.9211 | 21.3547 | 20.6684 | 20.1474 | 17.2116 | 16.3211 | 15.3863 | 14.5495 | 13.6611 | 11.2968 | 10.4137 | 9.8284
|  | BUCKIE | HE |  |  |  |  | 23.0042 | 22.9516 | 22.9126 | 22.8211 | 22.6168 | 20.1968 | 19.4716 | 18.7937 | 18.2905 | 18.0726 | 15.3126 | 14.7705 | 14.5695 | 21.2968 | 21.2442 | 20.8916 | 20.3063 | 19.8779 | 17.0958 | 16.2789 | 15.5105 | 14.9432 | 14.6968 | 11.5116 | 10.8884 | 10.66 | 21.9926 | 21.94 | 21.5958 | 21.0084 | 20.5779 | 17.7832 | 16.9632 | 16.1916 | 15.6221 | 15.3747 | 12.2221 | 11.6053 | 11.3768
|  | BUCKIE | FB |  |  |  |  | 23.0358 | 23.0158 | 22.9947 | 22.9726 | 22.9474 | 22.9189 | 22.8674 | 22.82 | 22.6295 | 22.4789 | 21.2484 | 19.8011 | 19.5189 | 21.3284 | 21.3084 | 21.2874 | 21.2653 | 21.1779 | 20.8789 | 20.4979 | 20.1884 | 19.8853 | 19.7137 | 18.3011 | 16.6579 | 16.3421 | 22.0242 | 22.0042 | 21.9832 | 21.9611 | 21.8832 | 21.5832 | 21.2 | 20.8884 | 20.5842 | 20.4126 | 18.9937 | 17.3442 | 17.0274
| FORT AUGUSTUS | BUNOICH | MINIMUM HEADROOM | NH 37662 09672 | YES | YES | 0 | 2.0126 | 2.0053 | 1.9989 | 1.9874 | 1.98 | 1.9695 | 1.96 | 1.9516 | 1.9432 | 1.9358 | 1.9032 | 1.8768 | 1.8558 | 1.9863 | 1.9789 | 1.9716 | 1.9589 | 1.9495 | 1.9389 | 1.9284 | 1.92 | 1.9105 | 1.9021 | 1.8684 | 1.8379 | 1.8137 | 2.0042 | 1.9968 | 1.9895 | 1.9768 | 1.9684 | 1.9579 | 1.9463 | 1.9379 | 1.9284 | 1.9211 | 1.8874 | 1.8579 | 1.8337
|  | BUNOICH | EE |  |  |  |  | 2.0126 | 2.0053 | 1.9989 | 1.9874 | 1.98 | 1.9695 | 1.96 | 1.9516 | 1.9432 | 1.9358 | 1.9053 | 1.8779 | 1.8568 | 1.9863 | 1.9789 | 1.9716 | 1.9589 | 1.9495 | 1.9389 | 1.9284 | 1.92 | 1.9105 | 1.9021 | 1.8684 | 1.8379 | 1.8137 | 2.0042 | 1.9968 | 1.9895 | 1.9768 | 1.9684 | 1.9579 | 1.9463 | 1.9379 | 1.9284 | 1.9211 | 1.8874 | 1.8579 | 1.8337
|  | BUNOICH | HT |  |  |  |  | 2.0137 | 2.0074 | 2.0021 | 1.9926 | 1.9842 | 1.9758 | 1.9663 | 1.9579 | 1.9505 | 1.94 | 1.9032 | 1.8768 | 1.8558 | 1.9874 | 1.9811 | 1.9747 | 1.9653 | 1.9558 | 1.9463 | 1.9358 | 1.9263 | 1.9179 | 1.9063 | 1.8726 | 1.8421 | 1.8137 | 2.0053 | 1.9989 | 1.9926 | 1.9832 | 1.9737 | 1.9642 | 1.9547 | 1.9453 | 1.9368 | 1.9253 | 1.8926 | 1.8621 | 1.8337
|  | BUNOICH | HE |  |  |  |  | 2.0189 | 2.0147 | 2.0095 | 2.0053 | 2.0011 | 1.9958 | 1.9916 | 1.9874 | 1.9821 | 1.9779 | 1.9611 | 1.9453 | 1.9347 | 1.9937 | 1.9884 | 1.9842 | 1.9789 | 1.9737 | 1.9695 | 1.9642 | 1.9589 | 1.9537 | 1.9495 | 1.9305 | 1.9126 | 1.9021 | 2.0105 | 2.0063 | 2.0011 | 1.9968 | 1.9916 | 1.9874 | 1.9821 | 1.9768 | 1.9716 | 1.9674 | 1.9484 | 1.9316 | 1.9211
|  | BUNOICH | FB |  |  |  |  | 2.0211 | 2.0179 | 2.0147 | 2.0116 | 2.0084 | 2.0063 | 2.0032 | 2 | 1.9968 | 1.9926 | 1.9747 | 1.9558 | 1.9411 | 1.9958 | 1.9926 | 1.9884 | 1.9863 | 1.9821 | 1.9789 | 1.9768 | 1.9726 | 1.9695 | 1.9642 | 1.9453 | 1.9242 | 1.9063 | 2.0137 | 2.0105 | 2.0063 | 2.0032 | 2 | 1.9968 | 1.9947 | 1.9905 | 1.9874 | 1.9821 | 1.9632 | 1.9421 | 1.9253
| THURSO | BURGARHILL | MINIMUM HEADROOM | HY 34441 26078 | YES | YES | 0 | -1.4674 | -1.4768 | -1.4842 | -1.4937 | -1.5042 | -1.5158 | -1.5305 | -1.5421 | -1.5526 | -1.5653 | -1.6253 | -2.76 | -2.8242 | -1.7811 | -1.8032 | -1.8221 | -1.8442 | -1.8684 | -1.8958 | -1.9232 | -1.9442 | -1.9663 | -1.9905 | -2.0737 | -3.0032 | -3.0726 | -3.4568 | -3.4832 | -3.5074 | -3.5358 | -3.5642 | -3.5979 | -3.6305 | -3.6547 | -3.6821 | -3.7126 | -3.8137 | -4.9747 | -5.0474
|  | BURGARHILL | EE |  |  |  |  | -1.4674 | -1.4768 | -1.4842 | -1.4926 | -1.5032 | -1.5158 | -1.5305 | -1.5421 | -1.5526 | -1.5621 | -1.6126 | -2.76 | -2.8242 | -1.7811 | -1.8032 | -1.8221 | -1.8442 | -1.8684 | -1.8958 | -1.9232 | -1.9442 | -1.9663 | -1.9905 | -2.0737 | -3.0032 | -3.0726 | -3.4568 | -3.4832 | -3.5074 | -3.5358 | -3.5642 | -3.5979 | -3.6305 | -3.6547 | -3.6821 | -3.7126 | -3.8137 | -4.9747 | -5.0474
|  | BURGARHILL | HT |  |  |  |  | -1.4642 | -1.4726 | -1.4832 | -1.4937 | -1.5042 | -1.5158 | -1.5284 | -1.5389 | -1.5505 | -1.5653 | -1.6253 | -2.5674 | -2.6242 | -1.7737 | -1.7926 | -1.8126 | -1.8347 | -1.8589 | -1.8874 | -1.9126 | -1.9358 | -1.9589 | -1.9895 | -2.0653 | -2.8358 | -2.9147 | -3.4474 | -3.4716 | -3.4947 | -3.5221 | -3.5505 | -3.5863 | -3.6158 | -3.6442 | -3.6726 | -3.7095 | -3.8 | -4.7653 | -4.8474
|  | BURGARHILL | HE |  |  |  |  | -1.4611 | -1.4695 | -1.4737 | -1.4821 | -1.4926 | -1.5053 | -1.5189 | -1.5263 | -1.5337 | -1.5389 | -1.5579 | -1.9558 | -1.9947 | -1.7611 | -1.7758 | -1.7863 | -1.8011 | -1.8189 | -1.84 | -1.86 | -1.8737 | -1.8884 | -1.9053 | -1.9526 | -2.34 | -2.3747 | -3.4316 | -3.4474 | -3.4611 | -3.4789 | -3.4989 | -3.5242 | -3.5474 | -3.5621 | -3.5811 | -3.6011 | -3.6611 | -4.1474 | -4.1926
|  | BURGARHILL | FB |  |  |  |  | -1.4568 | -1.46 | -1.4642 | -1.4674 | -1.4716 | -1.4768 | -1.4811 | -1.4853 | -1.4905 | -1.4958 | -1.5147 | -1.5305 | -1.5411 | -1.7537 | -1.7621 | -1.7716 | -1.78 | -1.7905 | -1.8032 | -1.8126 | -1.8242 | -1.8347 | -1.8484 | -1.8968 | -1.9453 | -1.9842 | -3.4221 | -3.4326 | -3.4442 | -3.4558 | -3.4684 | -3.4842 | -3.4958 | -3.5095 | -3.5221 | -3.54 | -3.6011 | -3.6621 | -3.7116
| ELGIN | BURGHEAD | MINIMUM HEADROOM | NJ 12666 68781 | NO | YES | 0 | 16.9532 | 16.9174 | 16.8889 | 16.8479 | 16.8047 | 16.7532 | 16.6984 | 16.6553 | 16.6111 | 16.5711 | 16.0289 | 15.6858 | 15.4247 | 15.2368 | 15.1284 | 15.0242 | 14.8568 | 14.7358 | 14.56 | 14.3968 | 14.2495 | 14.1105 | 14.0095 | 13.3779 | 12.9168 | 12.6179 | 13.8624 | 13.7508 | 13.6413 | 13.4676 | 13.3424 | 13.1592 | 12.9897 | 12.8361 | 12.6929 | 12.5855 | 11.9276 | 11.4476 | 11.1361
|  | BURGHEAD | EE |  |  |  |  | 16.9532 | 16.9174 | 16.8889 | 16.8479 | 16.8089 | 16.7532 | 16.6984 | 16.6553 | 16.6111 | 16.5816 | 16.1005 | 15.69 | 15.4247 | 15.2368 | 15.1284 | 15.0242 | 14.8568 | 14.7358 | 14.56 | 14.3968 | 14.2495 | 14.1105 | 14.0095 | 13.3779 | 12.9168 | 12.6179 | 13.8624 | 13.7508 | 13.6413 | 13.4676 | 13.3424 | 13.1592 | 12.9897 | 12.8361 | 12.6929 | 12.5855 | 11.9276 | 11.4476 | 11.1361
|  | BURGHEAD | HT |  |  |  |  | 16.9574 | 16.9247 | 16.89 | 16.8489 | 16.8047 | 16.7595 | 16.7111 | 16.6616 | 16.6142 | 16.5711 | 16.0289 | 15.6858 | 15.4416 | 15.26 | 15.16 | 15.0547 | 14.9116 | 14.7884 | 14.6253 | 14.4495 | 14.28 | 14.1274 | 14.0137 | 13.4211 | 12.9926 | 12.6453 | 13.8866 | 13.7834 | 13.6739 | 13.5255 | 13.3982 | 13.2276 | 13.0445 | 12.8687 | 12.7097 | 12.5918 | 11.9739 | 11.5287 | 11.1666
|  | BURGHEAD | HE |  |  |  |  | 16.97 | 16.9384 | 16.9174 | 16.8858 | 16.8553 | 16.81 | 16.7616 | 16.7289 | 16.6953 | 16.6826 | 16.5984 | 16.5121 | 16.3879 | 15.3116 | 15.2326 | 15.1632 | 15.0758 | 15.0221 | 14.9242 | 14.8032 | 14.6979 | 14.5874 | 14.5316 | 14.0853 | 13.84 | 13.7 | 13.9413 | 13.8603 | 13.7876 | 13.6971 | 13.6424 | 13.5413 | 13.4161 | 13.3055 | 13.1918 | 13.1329 | 12.6666 | 12.4097 | 12.2645
|  | BURGHEAD | FB |  |  |  |  | 16.99 | 16.9784 | 16.9647 | 16.9521 | 16.9374 | 16.9226 | 16.9068 | 16.8911 | 16.8732 | 16.8553 | 16.7732 | 16.6984 | 16.6553 | 15.3547 | 15.3147 | 15.2705 | 15.2253 | 15.1874 | 15.1389 | 15.0863 | 15.0326 | 14.9737 | 14.9105 | 14.5526 | 14.1916 | 13.9884 | 13.9855 | 13.9434 | 13.8982 | 13.8508 | 13.8118 | 13.7613 | 13.7066 | 13.6508 | 13.5887 | 13.5234 | 13.1497 | 12.7729 | 12.5613
| BURGHMUIR | BURGHMUIR | MINIMUM HEADROOM | NO 08256 23702 | NO | YES | 1.4163 | 12.9376 | 12.7524 | 12.5734 | 12.2113 | 10.9955 | 10.3955 | 9.625 | 9.3797 | 9.1018 | 8.7303 | 2.0303 | -3.5413 | -9.3045 | 11.9042 | 11.6968 | 11.4979 | 11.0874 | 9.6768 | 8.9747 | 8.0811 | 7.8042 | 7.4884 | 7.0747 | -0.80947 | -7.3758 | -14.14 | 12.4051 | 12.2483 | 12.0957 | 11.7483 | 10.4493 | 9.7651 | 8.8925 | 8.6209 | 8.3062 | 7.8925 | 0.0072368 | -6.5412 | -13.2843
|  | BURGHMUIR | EE |  |  |  |  | 12.9376 | 12.7524 | 12.6071 | 12.3387 | 11.1355 | 10.3955 | 9.625 | 9.3797 | 9.1018 | 8.9818 | 2.0303 | -3.5413 | -8.4729 | 11.9042 | 11.6968 | 11.5347 | 11.2295 | 9.8337 | 8.9747 | 8.0811 | 7.8042 | 7.4884 | 7.3558 | -0.80947 | -7.3758 | -13.1958 | 12.4051 | 12.2483 | 12.1262 | 11.8746 | 10.603 | 9.7651 | 8.8925 | 8.6209 | 8.3062 | 8.1746 | 0.0072368 | -6.5412 | -12.3433
|  | BURGHMUIR | HT |  |  |  |  | 12.9776 | 12.7997 | 12.5734 | 12.2113 | 10.9955 | 10.7334 | 10.3966 | 10.0261 | 9.3724 | 8.7303 | 4.8197 | -2.4508 | -9.3045 | 11.9505 | 11.7516 | 11.4979 | 11.0874 | 9.6768 | 9.3811 | 8.9958 | 8.5737 | 7.8168 | 7.0747 | 3.2326 | -4.0168 | -14.14 | 12.4367 | 12.2862 | 12.0957 | 11.7483 | 10.4493 | 10.1599 | 9.783 | 9.3683 | 8.6293 | 7.8925 | 4.0483 | -3.1917 | -13.2843
|  | BURGHMUIR | HE |  |  |  |  | 13.0882 | 12.9566 | 12.8334 | 12.5839 | 11.4197 | 10.725 | 9.845 | 9.6092 | 9.3082 | 9.245 | 2.2071 | -2.5371 | -7.3192 | 12.0747 | 11.9284 | 11.7916 | 11.5084 | 10.16 | 9.3558 | 8.3316 | 8.0632 | 7.7168 | 7.6453 | -0.64 | -6.2411 | -11.8947 | 12.5293 | 12.4157 | 12.3114 | 12.1062 | 10.923 | 10.1367 | 9.1378 | 8.8746 | 8.5346 | 8.4641 | 0.17671 | -5.4086 | -11.0443
|  | BURGHMUIR | FB |  |  |  |  | 13.1587 | 13.0924 | 13.0218 | 12.9397 | 12.8418 | 12.6376 | 12.3334 | 12.0703 | 11.9387 | 11.8618 | 10.8924 | 5.8671 | 5.6082 | 12.1526 | 12.0779 | 11.9989 | 11.9063 | 11.7958 | 11.5621 | 11.2116 | 10.9084 | 10.76 | 10.6747 | 9.5547 | 3.6421 | 3.3453 | 12.5904 | 12.5336 | 12.4746 | 12.4062 | 12.3241 | 12.1599 | 11.8693 | 11.6041 | 11.4714 | 11.3936 | 10.3314 | 4.4599 | 4.163
| CLACHAN | BUTTERBRIDGE | MINIMUM HEADROOM | NN 19306 09936 | YES | YES | 0 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947
|  | BUTTERBRIDGE | EE |  |  |  |  | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947
|  | BUTTERBRIDGE | HT |  |  |  |  | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947
|  | BUTTERBRIDGE | HE |  |  |  |  | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947
|  | BUTTERBRIDGE | FB |  |  |  |  | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947
| BRACO | CALLANDER | MINIMUM HEADROOM | NN 62995 07081 | NO | YES | 0 | 7.5495 | 7.4821 | 7.3653 | 7.2768 | 7.1821 | 7.08 | 6.9274 | 6.7558 | 6.5789 | 6.3947 | 5.5253 | 4.7768 | 4.2063 | 7.0874 | 6.9842 | 6.7674 | 6.6179 | 6.44 | 6.26 | 6.0674 | 5.8779 | 5.6821 | 5.4726 | 4.6779 | 3.7779 | 2.9547 | 7.2242 | 7.1632 | 6.9642 | 6.8242 | 6.6684 | 6.4937 | 6.3084 | 6.1221 | 5.9337 | 5.7232 | 4.9242 | 4.02 | 3.1926
|  | CALLANDER | EE |  |  |  |  | 7.5495 | 7.4821 | 7.3653 | 7.2768 | 7.1821 | 7.08 | 6.9474 | 6.8011 | 6.6526 | 6.5042 | 5.9179 | 5.2705 | 4.6884 | 7.0874 | 6.9842 | 6.7674 | 6.6179 | 6.46 | 6.2937 | 6.1168 | 5.9579 | 5.7979 | 5.6358 | 4.9779 | 4.2453 | 3.5853 | 7.2242 | 7.1632 | 6.9642 | 6.8242 | 6.6705 | 6.5053 | 6.3305 | 6.1716 | 6.0126 | 5.8526 | 5.1789 | 4.4316 | 3.7558
|  | CALLANDER | HT |  |  |  |  | 7.5653 | 7.5053 | 7.3832 | 7.2916 | 7.1905 | 7.0874 | 6.9274 | 6.7558 | 6.5789 | 6.3947 | 5.5253 | 4.7768 | 4.2063 | 7.1063 | 7.0063 | 6.7789 | 6.6189 | 6.44 | 6.26 | 6.0674 | 5.8779 | 5.6821 | 5.4726 | 4.6779 | 3.7779 | 2.9547 | 7.2337 | 7.1905 | 6.9853 | 6.8389 | 6.6684 | 6.4937 | 6.3084 | 6.1221 | 5.9337 | 5.7232 | 4.9242 | 4.02 | 3.1926
|  | CALLANDER | HE |  |  |  |  | 7.5937 | 7.5453 | 7.4474 | 7.3821 | 7.3084 | 7.2253 | 7.1379 | 7.0653 | 6.9705 | 6.8547 | 6.3853 | 5.8495 | 5.3589 | 7.1547 | 7.0832 | 6.8958 | 6.7863 | 6.6611 | 6.5274 | 6.3874 | 6.2589 | 6.1253 | 5.9958 | 5.4653 | 4.8463 | 4.2811 | 7.2411 | 7.2179 | 7.0905 | 6.9895 | 6.8747 | 6.7505 | 6.6126 | 6.4884 | 6.3579 | 6.2326 | 5.7095 | 5.0853 | 4.5147
|  | CALLANDER | FB |  |  |  |  | 7.6147 | 7.5916 | 7.5558 | 7.5211 | 7.4842 | 7.4484 | 7.4074 | 7.3674 | 7.3242 | 7.2737 | 7.0695 | 6.7063 | 6.3853 | 7.1853 | 7.1474 | 7.0842 | 7.0221 | 6.9579 | 6.8905 | 6.8179 | 6.7463 | 6.6684 | 6.5758 | 6.2189 | 5.8116 | 5.4411 | 7.2526 | 7.2453 | 7.2368 | 7.2074 | 7.1484 | 7.0884 | 7.0232 | 6.9589 | 6.8863 | 6.8042 | 6.4589 | 6.0674 | 5.6989
| STORNOWAY | CALLANISH | MINIMUM HEADROOM | NB 22040 33554 | YES | YES | 0 | 2.0958 | 2.0284 | 1.9726 | 1.9453 | 1.9189 | 1.8895 | 1.86 | 1.8358 | 1.8084 | 1.7853 | -0.21895 | -0.29263 | -0.34632 | 2.0947 | 2.0011 | 1.9337 | 1.9021 | 1.8716 | 1.8379 | 1.8053 | 1.7779 | 1.7463 | 1.7189 | 0.087368 | 0.0031579 | -0.056842 | 2.0358 | 1.9411 | 1.8737 | 1.8421 | 1.8116 | 1.7779 | 1.7453 | 1.7168 | 1.6863 | 1.6589 | -0.36842 | -0.45263 | -0.51474
|  | CALLANISH | EE |  |  |  |  | 2.0958 | 2.0779 | 1.9726 | 1.9453 | 1.9189 | 1.8895 | 1.86 | 1.8358 | 1.8084 | 1.7853 | -0.21895 | -0.29263 | -0.34632 | 2.0947 | 2.0632 | 1.9337 | 1.9021 | 1.8716 | 1.8379 | 1.8053 | 1.7779 | 1.7463 | 1.7189 | 0.087368 | 0.0031579 | -0.056842 | 2.0358 | 2.0042 | 1.8737 | 1.8421 | 1.8116 | 1.7779 | 1.7453 | 1.7168 | 1.6863 | 1.6589 | -0.36842 | -0.45263 | -0.51474
|  | CALLANISH | HT |  |  |  |  | 2.0968 | 2.0284 | 2.0032 | 1.9779 | 1.9505 | 1.9242 | 1.8979 | 1.8716 | 1.8442 | 1.8168 | 0.18421 | 0.10947 | 0.058947 | 2.1032 | 2.0011 | 1.9726 | 1.9432 | 1.9116 | 1.8821 | 1.8526 | 1.8221 | 1.7916 | 1.76 | 0.43474 | 0.34421 | 0.27263 | 2.0453 | 1.9411 | 1.9126 | 1.8832 | 1.8516 | 1.8221 | 1.7926 | 1.7621 | 1.7316 | 1.7 | 0.058947 | -0.033684 | -0.10737
|  | CALLANISH | HE |  |  |  |  | 2.1 | 2.0905 | 2.0179 | 2.0011 | 1.9811 | 1.9611 | 1.94 | 1.9211 | 1.9053 | 1.8926 | 1.0989 | 1.0611 | 1.0337 | 2.1095 | 2.1 | 1.9884 | 1.9705 | 1.9484 | 1.9263 | 1.9042 | 1.8832 | 1.8653 | 1.8505 | 1.1895 | 1.1463 | 1.1158 | 2.0663 | 2.0453 | 1.9284 | 1.9105 | 1.8884 | 1.8663 | 1.8442 | 1.8232 | 1.8042 | 1.7905 | 0.96842 | 0.92421 | 0.89263
|  | CALLANISH | FB |  |  |  |  | 2.1053 | 2.1021 | 2.0989 | 2.0737 | 2.0621 | 2.0495 | 2.0379 | 2.0263 | 2.0137 | 1.9989 | 1.9463 | 1.8947 | 1.8568 | 2.1147 | 2.1116 | 2.1084 | 2.0558 | 2.0432 | 2.0295 | 2.0147 | 2.0011 | 1.9874 | 1.9695 | 1.9084 | 1.8474 | 1.8011 | 2.0779 | 2.0653 | 2.0526 | 1.9968 | 1.9832 | 1.9695 | 1.9547 | 1.9411 | 1.9274 | 1.9095 | 1.8484 | 1.7863 | 1.7411
| TUMMEL BRIDGE | CALVINE | MINIMUM HEADROOM | NN 80186 65270 | YES | YES | 0 | 0.87789 | 0.86842 | 0.86211 | 0.85053 | 0.83895 | 0.82842 | 0.81789 | 0.80737 | 0.79895 | 0.78842 | 0.75368 | 0.72211 | 0.69263 | 1.1305 | 1.1274 | 1.1263 | 1.1211 | 1.1179 | 1.1137 | 1.1095 | 1.1053 | 1.1032 | 1.0989 | 1.0863 | 1.0779 | 1.0621 | 0.86526 | 0.85579 | 0.84737 | 0.83579 | 0.82421 | 0.81263 | 0.80105 | 0.79053 | 0.78105 | 0.76947 | 0.73263 | 0.69789 | 0.66632
|  | CALVINE | EE |  |  |  |  | 0.87789 | 0.86842 | 0.86211 | 0.85053 | 0.83895 | 0.82842 | 0.81789 | 0.80737 | 0.79895 | 0.78842 | 0.75368 | 0.72211 | 0.69263 | 1.1305 | 1.1274 | 1.1263 | 1.1221 | 1.1179 | 1.1137 | 1.1095 | 1.1053 | 1.1032 | 1.0989 | 1.0863 | 1.0779 | 1.0621 | 0.86526 | 0.85579 | 0.84737 | 0.83579 | 0.82421 | 0.81263 | 0.80105 | 0.79053 | 0.78105 | 0.76947 | 0.73263 | 0.69789 | 0.66632
|  | CALVINE | HT |  |  |  |  | 0.87895 | 0.87263 | 0.86737 | 0.85789 | 0.84947 | 0.84 | 0.83053 | 0.82316 | 0.81263 | 0.80421 | 0.76316 | 0.73368 | 0.71263 | 1.1305 | 1.1284 | 1.1263 | 1.1211 | 1.1179 | 1.1147 | 1.1116 | 1.1084 | 1.1042 | 1.1011 | 1.0884 | 1.0779 | 1.0705 | 0.86737 | 0.86105 | 0.85474 | 0.84526 | 0.83579 | 0.82632 | 0.81579 | 0.80737 | 0.79684 | 0.78737 | 0.75263 | 0.71895 | 0.68947
|  | CALVINE | HE |  |  |  |  | 0.88526 | 0.88105 | 0.87579 | 0.87053 | 0.86632 | 0.86105 | 0.85579 | 0.85158 | 0.84526 | 0.84105 | 0.82316 | 0.80632 | 0.79368 | 1.1326 | 1.1305 | 1.1284 | 1.1253 | 1.1221 | 1.12 | 1.1158 | 1.1137 | 1.1105 | 1.1095 | 1.1042 | 1.0989 | 1.0968 | 0.87368 | 0.86842 | 0.86421 | 0.85789 | 0.85368 | 0.84842 | 0.84211 | 0.83684 | 0.83158 | 0.82632 | 0.80842 | 0.78947 | 0.77579
|  | CALVINE | FB |  |  |  |  | 0.88737 | 0.88526 | 0.88105 | 0.87789 | 0.87474 | 0.87263 | 0.86947 | 0.86632 | 0.86316 | 0.85895 | 0.84211 | 0.82211 | 0.80737 | 1.1337 | 1.1326 | 1.1316 | 1.1305 | 1.1295 | 1.1284 | 1.1274 | 1.1263 | 1.1253 | 1.1232 | 1.1189 | 1.1126 | 1.1095 | 0.87579 | 0.87368 | 0.86842 | 0.86632 | 0.86211 | 0.86 | 0.85684 | 0.85368 | 0.84947 | 0.84526 | 0.82842 | 0.80632 | 0.79053
| CARRADALE 1 | CAMPBELTOWN | MINIMUM HEADROOM | NR 71509 20746 | NO | YES | 0 | 14.0079 | 13.9405 | 13.8774 | 13.8037 | 13.7268 | 13.5837 | 13.4311 | 13.2689 | 13.1121 | 12.9647 | 12.0479 | 11.5026 | 11.0511 | 13.4968 | 13.4537 | 13.4189 | 13.3705 | 13.2453 | 13.0179 | 12.8232 | 12.5979 | 12.3853 | 12.2389 | 11.3516 | 10.8063 | 10.3674 | 13.5771 | 13.5013 | 13.3613 | 13.1613 | 12.9824 | 12.7392 | 12.5276 | 12.2855 | 12.0561 | 11.8929 | 10.8897 | 10.2792 | 9.7739
|  | CAMPBELTOWN | EE |  |  |  |  | 14.0079 | 13.9405 | 13.8774 | 13.8037 | 13.7268 | 13.5837 | 13.4311 | 13.2689 | 13.1121 | 12.9647 | 12.0479 | 11.5026 | 11.0511 | 13.4968 | 13.4537 | 13.4189 | 13.3705 | 13.2453 | 13.0179 | 12.8232 | 12.5979 | 12.3853 | 12.2389 | 11.3516 | 10.8063 | 10.3674 | 13.5771 | 13.5013 | 13.3613 | 13.1613 | 12.9824 | 12.7392 | 12.5276 | 12.2855 | 12.0561 | 11.8929 | 10.8897 | 10.2792 | 9.7739
|  | CAMPBELTOWN | HT |  |  |  |  | 14.0384 | 13.9953 | 13.9489 | 13.8974 | 13.8416 | 13.7816 | 13.6732 | 13.5163 | 13.35 | 13.1953 | 12.4132 | 11.97 | 11.65 | 13.5116 | 13.4789 | 13.4442 | 13.4053 | 13.3632 | 13.2084 | 13.0011 | 12.7505 | 12.5432 | 12.3789 | 11.7074 | 11.2158 | 10.7916 | 13.6118 | 13.5666 | 13.495 | 13.3518 | 13.2045 | 13.0003 | 12.7876 | 12.5318 | 12.3192 | 12.1497 | 11.4118 | 10.8939 | 10.4424
|  | CAMPBELTOWN | HE |  |  |  |  | 14.0542 | 14.0121 | 13.9805 | 13.9384 | 13.8911 | 13.83 | 13.7637 | 13.7153 | 13.6679 | 13.6174 | 13.2489 | 12.9932 | 12.7826 | 13.5232 | 13.4895 | 13.4674 | 13.4337 | 13.3947 | 13.3453 | 13.2905 | 13.2442 | 13.0726 | 12.9989 | 12.5095 | 12.2347 | 12.0253 | 13.6276 | 13.5824 | 13.5497 | 13.5045 | 13.4561 | 13.3455 | 13.2045 | 13.0287 | 12.8508 | 12.7718 | 12.2392 | 11.9392 | 11.7024
|  | CAMPBELTOWN | FB |  |  |  |  | 14.0753 | 14.0584 | 14.0395 | 14.0205 | 13.9995 | 13.9774 | 13.9553 | 13.9311 | 13.9068 | 13.8805 | 13.7468 | 13.4921 | 13.2679 | 13.5368 | 13.5242 | 13.5095 | 13.4947 | 13.4779 | 13.4611 | 13.4432 | 13.4242 | 13.4074 | 13.3863 | 13.0568 | 12.6737 | 12.4232 | 13.6487 | 13.6318 | 13.6139 | 13.5939 | 13.5729 | 13.5508 | 13.5003 | 13.4224 | 13.3287 | 13.2476 | 12.8624 | 12.4739 | 12.2192
| COUPAR ANGUS | CAPUTH | MINIMUM HEADROOM | NO 09277 40265 | NO | YES | 0 | 11.9379 | 11.8537 | 11.7758 | 11.6295 | 11.4989 | 11.3189 | 11.1568 | 11.0295 | 10.9021 | 10.7832 | 10.1274 | 9.8253 | 9.5853 | 11.3737 | 11.28 | 11.1905 | 11.0179 | 10.8663 | 10.6547 | 10.4684 | 10.32 | 10.1716 | 10.0337 | 9.3474 | 9.0011 | 8.7137 | 11.4989 | 11.4242 | 11.3368 | 11.1663 | 11.0147 | 10.8021 | 10.6158 | 10.4674 | 10.3179 | 10.1779 | 9.4389 | 9.0874 | 8.8063
|  | CAPUTH | EE |  |  |  |  | 11.9379 | 11.8537 | 11.7758 | 11.6295 | 11.4989 | 11.3189 | 11.1568 | 11.0295 | 10.9021 | 10.7832 | 10.1274 | 9.8253 | 9.5853 | 11.3737 | 11.28 | 11.1905 | 11.0179 | 10.8663 | 10.6547 | 10.4684 | 10.32 | 10.1716 | 10.0337 | 9.3474 | 9.0011 | 8.7242 | 11.4989 | 11.4242 | 11.3368 | 11.1663 | 11.0147 | 10.8021 | 10.6158 | 10.4674 | 10.3179 | 10.1779 | 9.4389 | 9.0874 | 8.8063
|  | CAPUTH | HT |  |  |  |  | 11.9589 | 11.8863 | 11.8126 | 11.6832 | 11.5495 | 11.4147 | 11.2811 | 11.1463 | 10.9926 | 10.82 | 10.14 | 9.8253 | 9.6053 | 11.3968 | 11.3158 | 11.2316 | 11.0789 | 10.9242 | 10.7663 | 10.6084 | 10.4526 | 10.2705 | 10.0684 | 9.4158 | 9.0411 | 8.7137 | 11.5032 | 11.4621 | 11.38 | 11.2326 | 11.08 | 10.9232 | 10.7663 | 10.6105 | 10.4305 | 10.2295 | 9.5389 | 9.1642 | 8.8379
|  | CAPUTH | HE |  |  |  |  | 12.0126 | 11.96 | 11.9147 | 11.8189 | 11.7274 | 11.6053 | 11.4811 | 11.3853 | 11.2832 | 11.2011 | 10.8042 | 10.6389 | 10.5053 | 11.4126 | 11.3853 | 11.3516 | 11.2389 | 11.1347 | 10.9926 | 10.8484 | 10.7379 | 10.6168 | 10.5179 | 10.0779 | 9.8832 | 9.7274 | 11.5168 | 11.4905 | 11.4705 | 11.3874 | 11.2863 | 11.1463 | 11.0042 | 10.8926 | 10.7726 | 10.6737 | 10.2158 | 10.02 | 9.8632
|  | CAPUTH | FB |  |  |  |  | 12.0411 | 12.0095 | 11.9768 | 11.9347 | 11.8916 | 11.8284 | 11.7632 | 11.7032 | 11.64 | 11.5768 | 11.3211 | 11.0937 | 10.9368 | 11.4274 | 11.4168 | 11.4042 | 11.3674 | 11.3179 | 11.2432 | 11.1642 | 11.0926 | 11.0179 | 10.9432 | 10.6358 | 10.3653 | 10.1758 | 11.5305 | 11.5211 | 11.5105 | 11.5 | 11.4663 | 11.3937 | 11.32 | 11.2484 | 11.1747 | 11.1011 | 10.7968 | 10.5284 | 10.3421
| ARBROATH | CARNOUSTIE | MINIMUM HEADROOM | NO 55631 35403 | NO | YES | 0.17857 | 16.3289 | 15.7363 | 15.2763 | 14.7237 | 14.5837 | 14.4268 | 14.2574 | 14.0889 | 13.93 | 13.8016 | 13.2458 | 12.8216 | 12.5163 | 14.6842 | 14.0011 | 13.4695 | 12.8316 | 12.6789 | 12.5074 | 12.3232 | 12.1379 | 11.9621 | 11.82 | 11.2653 | 10.7916 | 10.4011 | 15.4592 | 14.7992 | 14.2539 | 13.5982 | 13.4413 | 13.2676 | 13.0803 | 12.8897 | 12.7108 | 12.5655 | 12.0034 | 11.5297 | 11.1382
|  | CARNOUSTIE | EE |  |  |  |  | 16.3289 | 15.7363 | 15.2763 | 14.7237 | 14.5837 | 14.4268 | 14.2574 | 14.0889 | 13.93 | 13.8016 | 13.2921 | 12.8742 | 12.55 | 14.6842 | 14.0011 | 13.4695 | 12.8316 | 12.6789 | 12.5074 | 12.3232 | 12.1379 | 11.9621 | 11.82 | 11.2653 | 10.7916 | 10.4189 | 15.4592 | 14.7992 | 14.2539 | 13.5982 | 13.4413 | 13.2676 | 13.0803 | 12.8897 | 12.7108 | 12.5655 | 12.0034 | 11.5297 | 11.1571
|  | CARNOUSTIE | HT |  |  |  |  | 16.3542 | 15.8237 | 15.3079 | 14.7289 | 14.5858 | 14.4426 | 14.2942 | 14.1458 | 14.0026 | 13.8574 | 13.2458 | 12.8216 | 12.5163 | 14.7116 | 14.1 | 13.5063 | 12.84 | 12.6832 | 12.5263 | 12.3642 | 12.2032 | 12.0463 | 11.8937 | 11.3484 | 10.8379 | 10.4011 | 15.4845 | 14.8982 | 14.2918 | 13.6066 | 13.4466 | 13.2876 | 13.1213 | 12.9571 | 12.7992 | 12.6466 | 12.0908 | 11.5761 | 11.1382
|  | CARNOUSTIE | HE |  |  |  |  | 16.3837 | 15.9647 | 15.5384 | 15.0247 | 14.93 | 14.8174 | 14.6805 | 14.5689 | 14.4616 | 14.3879 | 14.1121 | 13.8984 | 13.7311 | 14.8084 | 14.2621 | 13.7684 | 13.1768 | 13.0747 | 12.9558 | 12.8095 | 12.6874 | 12.5695 | 12.4874 | 12.1832 | 11.9442 | 11.7568 | 15.5718 | 15.0603 | 14.5624 | 13.9529 | 13.8497 | 13.7287 | 13.5803 | 13.4561 | 13.335 | 13.2508 | 12.9413 | 12.6971 | 12.5045
|  | CARNOUSTIE | FB |  |  |  |  | 16.4068 | 16.3889 | 16.3689 | 16.2553 | 16.1005 | 15.9753 | 15.8732 | 15.7753 | 15.6868 | 15.6068 | 15.2732 | 14.9574 | 14.7416 | 15.1947 | 14.9832 | 14.7768 | 14.5989 | 14.4221 | 14.28 | 14.1642 | 14.0558 | 13.9558 | 13.8663 | 13.4947 | 13.14 | 12.8947 | 15.8571 | 15.7276 | 15.5424 | 15.3834 | 15.2213 | 15.0792 | 14.9634 | 14.8539 | 14.7539 | 14.6645 | 14.2855 | 13.9224 | 13.6708
| KILLIN | CASHLIE | MINIMUM HEADROOM | NN 50711 42144 | YES | YES | 0 | 1.0189 | 1.0189 | 1.0179 | 1.0147 | 1.0126 | 1.0084 | 1.0053 | 1.0021 | 0.99895 | 0.99684 | 0.98421 | 0.97579 | 0.96947 | 1.02 | 1.02 | 1.0189 | 1.0179 | 1.0168 | 1.0116 | 1.0095 | 1.0053 | 1.0011 | 0.99895 | 0.98526 | 0.97474 | 0.96737 | 1.0221 | 1.0211 | 1.0179 | 1.0137 | 1.0116 | 1.0063 | 1.0042 | 1 | 0.99579 | 0.99368 | 0.98 | 0.96947 | 0.96211
|  | CASHLIE | EE |  |  |  |  | 1.0189 | 1.0189 | 1.0179 | 1.0147 | 1.0126 | 1.0084 | 1.0053 | 1.0021 | 0.99895 | 0.99684 | 0.98526 | 0.97579 | 0.96947 | 1.02 | 1.02 | 1.0189 | 1.0179 | 1.0168 | 1.0116 | 1.0095 | 1.0053 | 1.0011 | 0.99895 | 0.98526 | 0.97474 | 0.96737 | 1.0221 | 1.0211 | 1.0179 | 1.0137 | 1.0116 | 1.0063 | 1.0042 | 1 | 0.99579 | 0.99368 | 0.98 | 0.96947 | 0.96211
|  | CASHLIE | HT |  |  |  |  | 1.0189 | 1.0189 | 1.0179 | 1.0179 | 1.0137 | 1.0105 | 1.0074 | 1.0042 | 1.0011 | 0.99789 | 0.98421 | 0.97579 | 0.96947 | 1.02 | 1.02 | 1.0189 | 1.0189 | 1.0168 | 1.0147 | 1.0105 | 1.0084 | 1.0042 | 1 | 0.98842 | 0.97579 | 0.96737 | 1.0221 | 1.0221 | 1.02 | 1.0179 | 1.0126 | 1.0095 | 1.0053 | 1.0032 | 0.99895 | 0.99474 | 0.98316 | 0.97053 | 0.96211
|  | CASHLIE | HE |  |  |  |  | 1.02 | 1.02 | 1.0189 | 1.0179 | 1.0179 | 1.0158 | 1.0158 | 1.0147 | 1.0137 | 1.0116 | 1.0063 | 1.0011 | 0.99579 | 1.02 | 1.02 | 1.02 | 1.0189 | 1.0189 | 1.0168 | 1.0168 | 1.0158 | 1.0158 | 1.0147 | 1.0095 | 1.0042 | 0.99789 | 1.0232 | 1.0232 | 1.0221 | 1.0211 | 1.0211 | 1.0179 | 1.0179 | 1.0147 | 1.0137 | 1.0105 | 1.0042 | 0.99895 | 0.99263
|  | CASHLIE | FB |  |  |  |  | 1.0211 | 1.02 | 1.02 | 1.0189 | 1.0189 | 1.0189 | 1.0179 | 1.0179 | 1.0179 | 1.0158 | 1.0095 | 1.0032 | 0.99789 | 1.0211 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.0189 | 1.0189 | 1.0189 | 1.0179 | 1.0137 | 1.0063 | 1 | 1.0242 | 1.0232 | 1.0232 | 1.0221 | 1.0221 | 1.0221 | 1.02 | 1.0189 | 1.0179 | 1.0147 | 1.0084 | 1.0011 | 0.99474
| KILLIN | CHAORACH | MINIMUM HEADROOM | NN 45400 27553 | YES | YES | 0 | -3.2863 | -3.2884 | -3.2895 | -3.2905 | -3.2926 | -3.2926 | -3.2947 | -3.2968 | -3.2968 | -3.2989 | -3.3042 | -3.3084 | -3.3137 | -3.1095 | -3.1105 | -3.1105 | -3.1116 | -3.1126 | -3.1168 | -3.1211 | -3.1263 | -3.1305 | -3.1337 | -3.1516 | -3.1726 | -3.1926 | -3.1474 | -3.1495 | -3.1516 | -3.1537 | -3.1547 | -3.1568 | -3.1589 | -3.1611 | -3.1621 | -3.1642 | -3.1716 | -3.18 | -3.2042
|  | CHAORACH | EE |  |  |  |  | -3.2863 | -3.2884 | -3.2895 | -3.2905 | -3.2926 | -3.2926 | -3.2947 | -3.2968 | -3.2968 | -3.2989 | -3.3042 | -3.3084 | -3.3137 | -3.1095 | -3.1105 | -3.1105 | -3.1116 | -3.1116 | -3.1126 | -3.1137 | -3.1147 | -3.1179 | -3.1242 | -3.1432 | -3.1653 | -3.1874 | -3.1474 | -3.1495 | -3.1516 | -3.1537 | -3.1547 | -3.1568 | -3.1589 | -3.1611 | -3.1621 | -3.1642 | -3.1716 | -3.18 | -3.2042
|  | CHAORACH | HT |  |  |  |  | -3.2853 | -3.2863 | -3.2874 | -3.2874 | -3.2884 | -3.2884 | -3.2895 | -3.2895 | -3.2905 | -3.2905 | -3.2937 | -3.2958 | -3.2968 | -3.1084 | -3.1084 | -3.1095 | -3.1105 | -3.1126 | -3.1168 | -3.1211 | -3.1263 | -3.1305 | -3.1337 | -3.1516 | -3.1726 | -3.1926 | -3.1463 | -3.1463 | -3.1474 | -3.1484 | -3.1484 | -3.1495 | -3.1505 | -3.1516 | -3.1516 | -3.1526 | -3.1558 | -3.1737 | -3.1937
|  | CHAORACH | HE |  |  |  |  | -3.2853 | -3.2863 | -3.2863 | -3.2874 | -3.2884 | -3.2884 | -3.2884 | -3.2884 | -3.2916 | -3.2905 | -3.2916 | -3.2947 | -3.2958 | -3.1084 | -3.1084 | -3.1084 | -3.1105 | -3.1105 | -3.1105 | -3.1105 | -3.1105 | -3.1137 | -3.1168 | -3.1326 | -3.1526 | -3.1726 | -3.1463 | -3.1463 | -3.1463 | -3.1484 | -3.1484 | -3.1495 | -3.1505 | -3.1505 | -3.1526 | -3.1526 | -3.1547 | -3.1579 | -3.1747
|  | CHAORACH | FB |  |  |  |  | -3.2853 | -3.2853 | -3.2853 | -3.2853 | -3.2853 | -3.2863 | -3.2863 | -3.2863 | -3.2874 | -3.2874 | -3.2874 | -3.2884 | -3.2895 | -3.1084 | -3.1084 | -3.1084 | -3.1084 | -3.1084 | -3.1095 | -3.1095 | -3.1095 | -3.1095 | -3.1095 | -3.1095 | -3.1116 | -3.1116 | -3.1453 | -3.1453 | -3.1463 | -3.1463 | -3.1463 | -3.1474 | -3.1474 | -3.1474 | -3.1474 | -3.1474 | -3.1474 | -3.1495 | -3.1495
| ARBROATH | CHARLES AVENUE | MINIMUM HEADROOM | NO 62954 41097 | NO | YES | 0 | 12.5379 | 12.4232 | 12.3147 | 12.1779 | 12.0537 | 11.6589 | 11.2695 | 11.1442 | 11.02 | 10.8979 | 9.5526 | 9.1495 | 8.8516 | 11.5368 | 11.3926 | 11.2632 | 11.1116 | 10.9747 | 10.5411 | 10.0989 | 9.9632 | 9.8263 | 9.6947 | 8.2168 | 7.7747 | 7.3926 | 11.7453 | 11.6074 | 11.4832 | 11.3389 | 11.2074 | 10.8063 | 10.3874 | 10.2516 | 10.1168 | 9.9863 | 8.5274 | 8.0916 | 7.7126
|  | CHARLES AVENUE | EE |  |  |  |  | 12.5379 | 12.4232 | 12.3147 | 12.1779 | 12.0537 | 11.6589 | 11.2695 | 11.1442 | 11.02 | 10.9 | 9.6011 | 9.2032 | 8.8821 | 11.5368 | 11.3926 | 11.2632 | 11.1116 | 10.9747 | 10.5411 | 10.0989 | 9.9632 | 9.8263 | 9.6947 | 8.2168 | 7.7747 | 7.4158 | 11.7453 | 11.6074 | 11.4832 | 11.3389 | 11.2074 | 10.8063 | 10.3874 | 10.2516 | 10.1168 | 9.9863 | 8.5274 | 8.0916 | 7.7358
|  | CHARLES AVENUE | HT |  |  |  |  | 12.5705 | 12.4674 | 12.3674 | 12.2853 | 12.1579 | 12.0337 | 11.9032 | 11.7758 | 11.4495 | 10.8979 | 9.5526 | 9.1495 | 8.8516 | 11.58 | 11.4516 | 11.3274 | 11.2505 | 11.1105 | 10.9747 | 10.8326 | 10.6926 | 10.3232 | 9.6947 | 8.2842 | 7.8084 | 7.3926 | 11.7863 | 11.6621 | 11.5432 | 11.4779 | 11.3432 | 11.2137 | 11.0768 | 10.9421 | 10.5916 | 9.9874 | 8.5937 | 8.1242 | 7.7126
|  | CHARLES AVENUE | HE |  |  |  |  | 12.64 | 12.5632 | 12.4989 | 12.4242 | 12.3463 | 12.0074 | 11.6558 | 11.5379 | 11.4537 | 11.3853 | 10.2811 | 10.0747 | 9.9063 | 11.6726 | 11.58 | 11.5011 | 11.4137 | 11.3242 | 10.94 | 10.5432 | 10.4 | 10.3084 | 10.2316 | 8.9663 | 8.7368 | 8.5474 | 11.8726 | 11.7842 | 11.7084 | 11.6232 | 11.5368 | 11.1821 | 10.8063 | 10.6589 | 10.5705 | 10.4979 | 9.2611 | 9.0337 | 8.8463
|  | CHARLES AVENUE | FB |  |  |  |  | 12.6758 | 12.6284 | 12.58 | 12.5284 | 12.4768 | 12.3758 | 12.2147 | 12.0989 | 12.0337 | 11.9579 | 11.4505 | 10.8432 | 10.6295 | 11.7158 | 11.6558 | 11.5947 | 11.5305 | 11.4663 | 11.3326 | 11.1484 | 11.0179 | 10.9463 | 10.8621 | 10.2884 | 9.5958 | 9.3537 | 11.9147 | 11.8568 | 11.7989 | 11.7379 | 11.6758 | 11.5495 | 11.3758 | 11.2516 | 11.1832 | 11.1021 | 10.5589 | 9.8832 | 9.6442
| CHARLESTON | CHARLESTON | MINIMUM HEADROOM | NO 35734 31818 | NO | YES | 0 | 16.1205 | 16.1016 | 16.0774 | 16.0447 | 16.0237 | 15.9932 | 15.9437 | 15.9111 | 15.8805 | 15.85 | 15.6026 | 15.4668 | 15.3584 | 15.32 | 15.3042 | 15.2884 | 15.2653 | 15.2474 | 15.1895 | 14.96 | 14.8358 | 14.7326 | 14.6305 | 14.3105 | 14.1158 | 13.9832 | 15.8371 | 15.8087 | 15.7382 | 15.6024 | 15.5497 | 15.435 | 15.2213 | 15.1045 | 15.0076 | 14.9108 | 14.6108 | 14.4266 | 14.2971
|  | CHARLESTON | EE |  |  |  |  | 16.1205 | 16.1016 | 16.0858 | 16.0658 | 16.0458 | 16.0216 | 15.9868 | 15.9426 | 15.9037 | 15.8868 | 15.6268 | 15.4753 | 15.3584 | 15.32 | 15.3042 | 15.2916 | 15.2758 | 15.2589 | 15.2379 | 15.2116 | 15.0705 | 14.9 | 14.8495 | 14.3105 | 14.1158 | 13.9832 | 15.8371 | 15.8087 | 15.7876 | 15.7203 | 15.6708 | 15.615 | 15.5013 | 15.3213 | 15.1624 | 15.115 | 14.6108 | 14.4266 | 14.2971
|  | CHARLESTON | HT |  |  |  |  | 16.1226 | 16.1037 | 16.0774 | 16.0447 | 16.0237 | 15.9932 | 15.9437 | 15.9111 | 15.8805 | 15.85 | 15.6026 | 15.4668 | 15.3616 | 15.3221 | 15.3063 | 15.2884 | 15.2653 | 15.2474 | 15.1895 | 14.96 | 14.8358 | 14.7326 | 14.6305 | 14.3263 | 14.1389 | 13.9895 | 15.8392 | 15.8108 | 15.7382 | 15.6024 | 15.5497 | 15.435 | 15.2213 | 15.1045 | 15.0076 | 14.9108 | 14.6266 | 14.4487 | 14.3045
|  | CHARLESTON | HE |  |  |  |  | 16.1289 | 16.1132 | 16.0974 | 16.0753 | 16.0574 | 16.0374 | 15.99 | 15.9532 | 15.9205 | 15.91 | 15.8258 | 15.7458 | 15.6879 | 15.3263 | 15.3137 | 15.3011 | 15.2832 | 15.2674 | 15.2484 | 15.2147 | 15.0895 | 14.9442 | 14.9116 | 14.5716 | 14.4663 | 14.3905 | 15.8413 | 15.8287 | 15.8055 | 15.7529 | 15.7213 | 15.6845 | 15.5034 | 15.3403 | 15.2045 | 15.1739 | 14.8561 | 14.7571 | 14.6866
|  | CHARLESTON | FB |  |  |  |  | 16.1416 | 16.1342 | 16.1268 | 16.1174 | 16.1089 | 16.1005 | 16.09 | 16.0742 | 16.0511 | 16.0384 | 15.9626 | 15.9005 | 15.8763 | 15.3358 | 15.3295 | 15.3232 | 15.3147 | 15.3074 | 15.3 | 15.2916 | 15.28 | 15.2642 | 15.2537 | 15.0842 | 14.8116 | 14.7284 | 15.8466 | 15.8413 | 15.8361 | 15.8297 | 15.8234 | 15.8171 | 15.8034 | 15.775 | 15.6761 | 15.6455 | 15.3361 | 15.0813 | 15.0034
| ARDMORE | CLACHAN | MINIMUM HEADROOM | NF 81863 64360 | NO | YES | 0 | 2.4189 | 2.2558 | 2.1705 | 2.1389 | 2.0768 | 1.9821 | 1.9495 | 1.92 | 1.8905 | 1.8632 | 1.7621 | -1.5453 | -1.6053 | 2.4074 | 2.2168 | 2.1179 | 2.0821 | 2.0116 | 1.9042 | 1.8674 | 1.8347 | 1.8021 | 1.7726 | 1.6611 | -0.95684 | -1.04 | 2.4179 | 2.2411 | 2.1474 | 2.1116 | 2.0411 | 1.9326 | 1.8968 | 1.8642 | 1.8316 | 1.8021 | 1.6916 | -1.6168 | -1.7
|  | CLACHAN | EE |  |  |  |  | 2.4189 | 2.3874 | 2.1705 | 2.1389 | 2.1063 | 1.9821 | 1.9495 | 1.92 | 1.8905 | 1.8632 | 1.7621 | 1.6737 | 1.6084 | 2.4074 | 2.3716 | 2.1179 | 2.0821 | 2.0463 | 1.9042 | 1.8674 | 1.8347 | 1.8021 | 1.7726 | 1.6611 | 1.5621 | 1.4895 | 2.4179 | 2.3842 | 2.1474 | 2.1116 | 2.0758 | 1.9326 | 1.8968 | 1.8642 | 1.8316 | 1.8021 | 1.6916 | 1.5926 | 1.52
|  | CLACHAN | HT |  |  |  |  | 2.4274 | 2.2558 | 2.2274 | 2.1979 | 2.0768 | 2.0453 | 2.0137 | 1.9832 | 1.9526 | 1.9221 | 1.7958 | -1.5453 | -1.6053 | 2.4179 | 2.2168 | 2.1842 | 2.1516 | 2.0116 | 1.9768 | 1.9432 | 1.9095 | 1.8758 | 1.8421 | 1.7284 | -0.95684 | -1.04 | 2.4274 | 2.2411 | 2.2105 | 2.18 | 2.0411 | 2.0063 | 1.9726 | 1.9389 | 1.9053 | 1.8716 | 1.7579 | -1.6168 | -1.7
|  | CLACHAN | HE |  |  |  |  | 2.4484 | 2.4274 | 2.2242 | 2.2042 | 2.1832 | 2.0684 | 2.0453 | 2.0263 | 2.0053 | 1.9916 | 1.9379 | 0.28 | 0.25158 | 2.4411 | 2.4189 | 2.1789 | 2.1579 | 2.1347 | 2.0032 | 1.9789 | 1.9579 | 1.9358 | 1.92 | 1.8611 | 0.53474 | 0.50211 | 2.4495 | 2.4284 | 2.2063 | 2.1853 | 2.1642 | 2.0326 | 2.0074 | 1.9874 | 1.9642 | 1.9495 | 1.8905 | 0.20737 | 0.17474
|  | CLACHAN | FB |  |  |  |  | 2.46 | 2.4474 | 2.4337 | 2.3432 | 2.3295 | 2.3158 | 2.26 | 2.2463 | 2.2316 | 2.2158 | 2.1558 | 2.0926 | 2.0463 | 2.4547 | 2.4389 | 2.4242 | 2.3179 | 2.3021 | 2.2874 | 2.2232 | 2.2074 | 2.1916 | 2.1726 | 2.1063 | 2.0358 | 1.9821 | 2.4621 | 2.4484 | 2.4337 | 2.3347 | 2.3211 | 2.3063 | 2.2463 | 2.2316 | 2.2158 | 2.1989 | 2.1358 | 2.0642 | 2.0116
| CARRADALE 1 | CLAONAIG | MINIMUM HEADROOM | NR 86915 56467 | YES | YES | 0 | 0.32763 | 0.32763 | 0.32658 | 0.32447 | 0.32342 | 0.32026 | 0.31816 | 0.31605 | 0.31289 | 0.31184 | 0.30342 | 0.295 | 0.28868 | 0.31079 | 0.30868 | 0.30553 | 0.30237 | 0.30026 | 0.29711 | 0.29395 | 0.29289 | 0.28868 | 0.28763 | 0.27816 | 0.26868 | 0.26132 | 0.32132 | 0.31921 | 0.31605 | 0.31289 | 0.31079 | 0.30763 | 0.30553 | 0.30342 | 0.29921 | 0.29816 | 0.28868 | 0.27921 | 0.27184
|  | CLAONAIG | EE |  |  |  |  | 0.32763 | 0.32763 | 0.32658 | 0.32447 | 0.32342 | 0.32026 | 0.31816 | 0.31605 | 0.31289 | 0.31184 | 0.30342 | 0.295 | 0.28868 | 0.31079 | 0.30868 | 0.30553 | 0.30237 | 0.30026 | 0.29711 | 0.29395 | 0.29289 | 0.28868 | 0.28763 | 0.27816 | 0.26868 | 0.26132 | 0.32132 | 0.31921 | 0.31605 | 0.31289 | 0.31079 | 0.30763 | 0.30553 | 0.30342 | 0.29921 | 0.29816 | 0.28868 | 0.27921 | 0.27184
|  | CLAONAIG | HT |  |  |  |  | 0.32763 | 0.32763 | 0.32658 | 0.32553 | 0.32447 | 0.32237 | 0.31921 | 0.31711 | 0.315 | 0.31395 | 0.30342 | 0.295 | 0.28974 | 0.31079 | 0.30974 | 0.30658 | 0.30342 | 0.30237 | 0.29921 | 0.29605 | 0.29289 | 0.29184 | 0.28974 | 0.27921 | 0.26974 | 0.26237 | 0.32132 | 0.32026 | 0.31711 | 0.31395 | 0.31289 | 0.30974 | 0.30658 | 0.30447 | 0.30237 | 0.30026 | 0.28974 | 0.28026 | 0.27289
|  | CLAONAIG | HE |  |  |  |  | 0.32763 | 0.32763 | 0.32763 | 0.32658 | 0.32658 | 0.32447 | 0.32447 | 0.32342 | 0.32342 | 0.32237 | 0.31711 | 0.30974 | 0.30974 | 0.31184 | 0.31184 | 0.31079 | 0.30868 | 0.30763 | 0.30553 | 0.30447 | 0.30342 | 0.30132 | 0.30026 | 0.29289 | 0.28553 | 0.28447 | 0.32237 | 0.32237 | 0.32132 | 0.31921 | 0.31816 | 0.31605 | 0.315 | 0.31395 | 0.31184 | 0.31079 | 0.30342 | 0.29605 | 0.295
|  | CLAONAIG | FB |  |  |  |  | 0.32868 | 0.32763 | 0.32763 | 0.32763 | 0.32763 | 0.32658 | 0.32658 | 0.32658 | 0.32658 | 0.32553 | 0.32026 | 0.31289 | 0.30763 | 0.31289 | 0.31184 | 0.31079 | 0.31079 | 0.30974 | 0.30763 | 0.30763 | 0.30658 | 0.30553 | 0.30342 | 0.29711 | 0.28868 | 0.28237 | 0.32342 | 0.32237 | 0.32132 | 0.32132 | 0.32026 | 0.31816 | 0.31816 | 0.31711 | 0.31605 | 0.31395 | 0.30763 | 0.29921 | 0.29289
| CLAYHILLS | CLAYHILLS | MINIMUM HEADROOM | NJ 94047 05518 | NO | YES | 0 | 25.0958 | 25.0495 | 25.0105 | 24.9579 | 24.8968 | 24.8358 | 24.7579 | 24.7011 | 24.6337 | 24.5568 | 24.2758 | 23.9853 | 23.4695 | 24.2684 | 24.2168 | 24.1747 | 24.1168 | 24.0484 | 23.9779 | 23.8895 | 23.82 | 23.7453 | 23.6568 | 22.9189 | 22.1537 | 21.3674 | 24.3474 | 24.3011 | 24.2611 | 24.2084 | 24.1484 | 24.0874 | 23.9989 | 23.9295 | 23.8537 | 23.7663 | 23.1663 | 22.4021 | 21.6189
|  | CLAYHILLS | EE |  |  |  |  | 25.0958 | 25.0495 | 25.0147 | 24.9695 | 24.9147 | 24.84 | 24.76 | 24.7011 | 24.6358 | 24.5832 | 24.3505 | 24.0979 | 23.5611 | 24.2684 | 24.2168 | 24.1758 | 24.1242 | 24.0611 | 23.9779 | 23.8895 | 23.82 | 23.7453 | 23.6758 | 22.9189 | 22.1537 | 21.4579 | 24.3474 | 24.3011 | 24.2653 | 24.2211 | 24.1663 | 24.0874 | 23.9989 | 23.9295 | 23.8537 | 23.7905 | 23.1663 | 22.4021 | 21.7074
|  | CLAYHILLS | HT |  |  |  |  | 25.1032 | 25.0579 | 25.0105 | 24.9579 | 24.8968 | 24.8358 | 24.7716 | 24.7053 | 24.6337 | 24.5568 | 24.2758 | 23.9853 | 23.4695 | 24.2779 | 24.2274 | 24.1747 | 24.1168 | 24.0484 | 23.9811 | 23.9074 | 23.8305 | 23.7474 | 23.6568 | 23.0695 | 22.1968 | 21.3674 | 24.3547 | 24.3095 | 24.2611 | 24.2084 | 24.1484 | 24.0874 | 24.0168 | 23.94 | 23.8558 | 23.7663 | 23.3168 | 22.4463 | 21.6189
|  | CLAYHILLS | HE |  |  |  |  | 25.1116 | 25.0632 | 25.0284 | 24.9779 | 24.9168 | 24.84 | 24.7579 | 24.7084 | 24.6579 | 24.6326 | 24.5116 | 24.4263 | 24.3695 | 24.2895 | 24.2389 | 24.2011 | 24.1484 | 24.0832 | 24.0032 | 23.9179 | 23.8642 | 23.8084 | 23.7758 | 23.6263 | 23.5126 | 23.2863 | 24.3632 | 24.3147 | 24.28 | 24.2295 | 24.1684 | 24.0916 | 24.0095 | 23.96 | 23.9095 | 23.8842 | 23.7358 | 23.6326 | 23.5326
|  | CLAYHILLS | FB |  |  |  |  | 25.1305 | 25.1074 | 25.0832 | 25.0568 | 25.0284 | 24.9989 | 24.9684 | 24.9368 | 24.9053 | 24.8695 | 24.7421 | 24.6326 | 24.5747 | 24.3095 | 24.2842 | 24.2579 | 24.2295 | 24.1979 | 24.1653 | 24.1326 | 24.0979 | 24.0632 | 24.0221 | 23.8726 | 23.7389 | 23.5989 | 24.3821 | 24.3589 | 24.3347 | 24.3084 | 24.28 | 24.2505 | 24.22 | 24.1884 | 24.1568 | 24.1211 | 23.9821 | 23.8474 | 23.7684
| DOUNREAY | COLDBACKIE | MINIMUM HEADROOM | NC 62182 59590 | YES | YES | 0 | 0.92 | 0.84632 | 0.77368 | 0.69579 | 0.61684 | 0.54316 | 0.47053 | 0.36421 | 0.26947 | 0.17895 | -0.088421 | -0.36842 | -0.64526 | 0.92737 | 0.86316 | 0.80105 | 0.73158 | 0.66421 | 0.6 | 0.53579 | 0.42526 | 0.33053 | 0.24421 | 0.012632 | -0.24737 | -0.56 | 1.1168 | 1.0358 | 0.95158 | 0.86105 | 0.76947 | 0.68526 | 0.60105 | 0.50211 | 0.40632 | 0.30842 | 0.0052632 | -0.32 | -0.64737
|  | COLDBACKIE | EE |  |  |  |  | 0.92 | 0.84632 | 0.77368 | 0.69579 | 0.61684 | 0.54316 | 0.47053 | 0.36421 | 0.26947 | 0.17895 | -0.088421 | -0.36842 | -0.64526 | 0.92737 | 0.86316 | 0.80105 | 0.73158 | 0.66421 | 0.6 | 0.53579 | 0.42526 | 0.33053 | 0.24421 | 0.012632 | -0.24737 | -0.56 | 1.1168 | 1.0358 | 0.95158 | 0.86105 | 0.76947 | 0.68526 | 0.60105 | 0.50211 | 0.40632 | 0.30842 | 0.0052632 | -0.32 | -0.64737
|  | COLDBACKIE | HT |  |  |  |  | 0.96526 | 0.93789 | 0.91053 | 0.88 | 0.85263 | 0.78632 | 0.73684 | 0.69263 | 0.65684 | 0.62632 | 0.48632 | 0.35789 | 0.25684 | 0.96421 | 0.93789 | 0.91158 | 0.88316 | 0.85474 | 0.77368 | 0.71579 | 0.66737 | 0.62947 | 0.60105 | 0.49368 | 0.37474 | 0.25895 | 1.1558 | 1.1358 | 1.1063 | 1.0737 | 1.0421 | 0.95263 | 0.88526 | 0.82947 | 0.78737 | 0.75368 | 0.62842 | 0.48632 | 0.34842
|  | COLDBACKIE | HE |  |  |  |  | 0.97158 | 0.94632 | 0.92211 | 0.89684 | 0.87368 | 0.84421 | 0.81789 | 0.75579 | 0.70947 | 0.67158 | 0.57579 | 0.46316 | 0.35263 | 0.97158 | 0.94947 | 0.92737 | 0.90421 | 0.88316 | 0.85789 | 0.83474 | 0.75789 | 0.70316 | 0.66211 | 0.57579 | 0.47684 | 0.38211 | 1.1568 | 1.1379 | 1.1179 | 1.0958 | 1.0684 | 1.0368 | 1.0063 | 0.92947 | 0.86737 | 0.82 | 0.71579 | 0.59684 | 0.48105
|  | COLDBACKIE | FB |  |  |  |  | 0.98842 | 0.98 | 0.97158 | 0.96316 | 0.95474 | 0.94737 | 0.93789 | 0.93053 | 0.90632 | 0.88632 | 0.83158 | 0.79474 | 0.76526 | 0.98842 | 0.97895 | 0.96947 | 0.96105 | 0.95263 | 0.94421 | 0.93579 | 0.92842 | 0.89579 | 0.86947 | 0.80316 | 0.76211 | 0.72947 | 1.1726 | 1.1663 | 1.1611 | 1.1547 | 1.1505 | 1.1442 | 1.1368 | 1.1263 | 1.0916 | 1.0632 | 0.98947 | 0.94316 | 0.90421
| DUNOON | COLINTRAIVE | MINIMUM HEADROOM | NS 03209 74814 | YES | YES | 0 | 0.51789 | 0.51368 | 0.50632 | 0.49789 | 0.49053 | 0.48316 | 0.47368 | 0.46632 | 0.45789 | 0.44947 | 0.42211 | 0.39368 | 0.36211 | 0.50316 | 0.5 | 0.49474 | 0.48316 | 0.47474 | 0.46737 | 0.45789 | 0.44947 | 0.44105 | 0.43263 | 0.40421 | 0.37263 | 0.34211 | 0.50316 | 0.49684 | 0.48947 | 0.47895 | 0.47053 | 0.46211 | 0.45263 | 0.44526 | 0.43684 | 0.42842 | 0.39789 | 0.36632 | 0.33368
|  | COLINTRAIVE | EE |  |  |  |  | 0.51789 | 0.51368 | 0.50632 | 0.49789 | 0.49053 | 0.48316 | 0.47368 | 0.46632 | 0.45789 | 0.44947 | 0.42211 | 0.39368 | 0.36211 | 0.50316 | 0.5 | 0.49474 | 0.48316 | 0.47474 | 0.46737 | 0.45789 | 0.44947 | 0.44105 | 0.43263 | 0.40421 | 0.37263 | 0.34211 | 0.50316 | 0.49684 | 0.48947 | 0.47895 | 0.47053 | 0.46211 | 0.45263 | 0.44526 | 0.43684 | 0.42842 | 0.39789 | 0.36632 | 0.33368
|  | COLINTRAIVE | HT |  |  |  |  | 0.52105 | 0.51895 | 0.51684 | 0.51474 | 0.51158 | 0.50947 | 0.50632 | 0.50211 | 0.49895 | 0.49474 | 0.47684 | 0.46316 | 0.45263 | 0.50421 | 0.50316 | 0.50105 | 0.49789 | 0.49368 | 0.48947 | 0.48737 | 0.48316 | 0.48 | 0.47684 | 0.46211 | 0.44842 | 0.43474 | 0.50632 | 0.50421 | 0.50105 | 0.49895 | 0.49474 | 0.48947 | 0.48632 | 0.48211 | 0.47789 | 0.47263 | 0.45895 | 0.44316 | 0.42842
|  | COLINTRAIVE | HE |  |  |  |  | 0.52105 | 0.52 | 0.51789 | 0.51579 | 0.51368 | 0.51158 | 0.50842 | 0.50526 | 0.50211 | 0.5 | 0.49158 | 0.47895 | 0.46842 | 0.50421 | 0.50421 | 0.50316 | 0.50105 | 0.5 | 0.49789 | 0.49368 | 0.49158 | 0.48842 | 0.48737 | 0.47684 | 0.46421 | 0.45263 | 0.50632 | 0.50526 | 0.50211 | 0.5 | 0.49789 | 0.49474 | 0.49053 | 0.48737 | 0.48526 | 0.48211 | 0.47263 | 0.46 | 0.44737
|  | COLINTRAIVE | FB |  |  |  |  | 0.52316 | 0.52211 | 0.52105 | 0.52105 | 0.52 | 0.51895 | 0.51895 | 0.51789 | 0.51789 | 0.51684 | 0.51368 | 0.51053 | 0.50737 | 0.50632 | 0.50526 | 0.50526 | 0.50421 | 0.50316 | 0.50316 | 0.50316 | 0.50211 | 0.50105 | 0.49895 | 0.49263 | 0.48737 | 0.48421 | 0.50842 | 0.50737 | 0.50737 | 0.50632 | 0.50526 | 0.50526 | 0.50421 | 0.50316 | 0.50316 | 0.50211 | 0.49579 | 0.48947 | 0.48526
| STORNOWAY | COLL | MINIMUM HEADROOM | NB 47510 40182 | YES | YES | 0 | 2.4263 | 6.1842 | 6.1453 | 6.1063 | 6.0705 | 6.0274 | 5.9863 | 5.9505 | 5.9147 | 5.8821 | 3.8263 | 3.7284 | 3.6568 | 2.4126 | 6.1642 | 6.1211 | 6.0758 | 6.0368 | 5.9895 | 5.9442 | 5.9053 | 5.8653 | 5.8305 | 4.1663 | 4.0568 | 3.9768 | 2.4074 | 6.1589 | 6.1158 | 6.0716 | 6.0326 | 5.9853 | 5.9411 | 5.9021 | 5.8632 | 5.8284 | 3.7674 | 3.6589 | 3.5779
|  | COLL | EE |  |  |  |  | 2.4263 | 6.1842 | 6.1453 | 6.1063 | 6.0705 | 6.0274 | 5.9863 | 5.9505 | 5.9147 | 5.8821 | 3.8263 | 3.7284 | 3.6568 | 2.4126 | 6.1642 | 6.1211 | 6.0758 | 6.0368 | 5.9895 | 5.9442 | 5.9053 | 5.8653 | 5.8305 | 4.1663 | 4.0568 | 3.9768 | 2.4074 | 6.1589 | 6.1158 | 6.0716 | 6.0326 | 5.9853 | 5.9411 | 5.9021 | 5.8632 | 5.8284 | 3.7674 | 3.6589 | 3.5779
|  | COLL | HT |  |  |  |  | 2.4379 | 6.2 | 6.1642 | 6.1263 | 6.0874 | 6.0505 | 6.0126 | 5.9768 | 5.9389 | 5.9 | 4.2053 | 4.1042 | 4.0316 | 2.4263 | 6.1832 | 6.1432 | 6.1 | 6.0579 | 6.0168 | 5.9747 | 5.9358 | 5.8947 | 5.8526 | 4.4937 | 4.3758 | 4.2768 | 2.42 | 6.1768 | 6.1379 | 6.0958 | 6.0537 | 6.0126 | 5.9716 | 5.9316 | 5.8916 | 5.8495 | 4.1758 | 4.0558 | 3.9547
|  | COLL | HE |  |  |  |  | 2.4642 | 6.2379 | 6.2137 | 6.1863 | 6.16 | 6.1284 | 6.0968 | 6.0726 | 6.0474 | 6.0305 | 5.1958 | 5.1442 | 5.1095 | 2.4568 | 6.2274 | 6.2021 | 6.1716 | 6.1432 | 6.1084 | 6.0747 | 6.0484 | 6.0211 | 6.0021 | 5.3242 | 5.2674 | 5.2295 | 2.4505 | 6.2211 | 6.1958 | 6.1653 | 6.1368 | 6.1032 | 6.0695 | 6.0432 | 6.0158 | 5.9968 | 5.1642 | 5.1063 | 5.0674
|  | COLL | FB |  |  |  |  | 2.48 | 6.2642 | 6.2463 | 6.2295 | 6.2105 | 6.1916 | 6.1747 | 6.1558 | 6.1379 | 6.1179 | 6.0442 | 5.9705 | 5.9179 | 2.4747 | 6.2558 | 6.2368 | 6.2168 | 6.1958 | 6.1747 | 6.1547 | 6.1337 | 6.1137 | 6.0905 | 6.0084 | 5.9232 | 5.8642 | 2.4684 | 6.2495 | 6.2295 | 6.2105 | 6.1895 | 6.1684 | 6.1484 | 6.1284 | 6.1084 | 6.0853 | 6.0042 | 5.9211 | 5.8621
| CLAYHILLS | COMMERCE STREET | MINIMUM HEADROOM | NJ 94816 06282 | NO | YES | 0 | 26.2068 | 26.1974 | 26.1889 | 26.1763 | 26.1647 | 26.1511 | 26.1342 | 26.1216 | 26.1089 | 26.0932 | 26.0342 | 25.9605 | 25.7816 | 24.3 | 24.2663 | 24.2221 | 24.1442 | 24.0674 | 23.9926 | 23.9179 | 23.8463 | 23.78 | 23.7053 | 23.4516 | 23.1979 | 22.9811 | 25.2276 | 25.2182 | 25.2097 | 25.1971 | 25.1855 | 25.1718 | 25.155 | 25.1424 | 25.1297 | 25.1139 | 25.0634 | 25.0266 | 24.9918
|  | COMMERCE STREET | EE |  |  |  |  | 26.2068 | 26.1974 | 26.1889 | 26.1795 | 26.1668 | 26.1521 | 26.1363 | 26.1216 | 26.1089 | 26.0963 | 26.0479 | 25.97 | 25.7816 | 24.3 | 24.2663 | 24.2221 | 24.1442 | 24.0674 | 23.9926 | 23.9179 | 23.8463 | 23.78 | 23.7053 | 23.4516 | 23.1979 | 22.9811 | 25.2276 | 25.2182 | 25.2097 | 25.2003 | 25.1876 | 25.1729 | 25.1571 | 25.1424 | 25.1297 | 25.1171 | 25.0687 | 25.0339 | 25.0108
|  | COMMERCE STREET | HT |  |  |  |  | 26.2079 | 26.1995 | 26.1889 | 26.1763 | 26.1647 | 26.1511 | 26.1384 | 26.1237 | 26.1089 | 26.0932 | 26.0342 | 25.9605 | 25.7879 | 24.3095 | 24.2789 | 24.2463 | 24.1958 | 24.1179 | 24.0495 | 23.9842 | 23.9168 | 23.8526 | 23.7705 | 23.5211 | 23.2432 | 22.9905 | 25.2287 | 25.2203 | 25.2097 | 25.1971 | 25.1855 | 25.1718 | 25.1592 | 25.1445 | 25.1297 | 25.1139 | 25.0634 | 25.0266 | 24.9918
|  | COMMERCE STREET | HE |  |  |  |  | 26.21 | 26.2005 | 26.1921 | 26.1816 | 26.1689 | 26.1521 | 26.1342 | 26.1237 | 26.1132 | 26.1089 | 26.0826 | 26.0658 | 26.0532 | 24.3295 | 24.3084 | 24.2874 | 24.2674 | 24.2379 | 24.2074 | 24.1737 | 24.1368 | 24.0947 | 24.0495 | 23.9011 | 23.7632 | 23.6474 | 25.2308 | 25.2213 | 25.2129 | 25.2024 | 25.1897 | 25.1729 | 25.155 | 25.1445 | 25.1339 | 25.1297 | 25.1034 | 25.0866 | 25.0739
|  | COMMERCE STREET | FB |  |  |  |  | 26.2142 | 26.21 | 26.2047 | 26.1984 | 26.1932 | 26.1868 | 26.1805 | 26.1732 | 26.1668 | 26.1595 | 26.1332 | 26.11 | 26.0974 | 24.4158 | 24.4011 | 24.3853 | 24.3684 | 24.3505 | 24.3305 | 24.3147 | 24.2937 | 24.2621 | 24.2179 | 24.0579 | 23.8895 | 23.7411 | 25.235 | 25.2308 | 25.2255 | 25.2192 | 25.2139 | 25.2076 | 25.2013 | 25.1939 | 25.1876 | 25.1803 | 25.1539 | 25.1308 | 25.1182
| ST FILLANS | COMRIE | MINIMUM HEADROOM | NN 76887 22417 | YES | YES | 0 | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.053158 | 0.053158 | 0.052105 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.052105 | 0.052105 | 0.051053 | 0.05 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.052105 | 0.052105 | 0.051053 | 0.051053
|  | COMRIE | EE |  |  |  |  | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.053158 | 0.052105 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.052105 | 0.052105 | 0.051053 | 0.05 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.052105 | 0.052105 | 0.051053 | 0.051053
|  | COMRIE | HT |  |  |  |  | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.053158 | 0.053158 | 0.052105 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.052105 | 0.051053 | 0.05 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.052105 | 0.051053 | 0.051053
|  | COMRIE | HE |  |  |  |  | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.053158
|  | COMRIE | FB |  |  |  |  | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.053158 | 0.053158 | 0.052105 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.053158 | 0.053158 | 0.052105
| TAYNUILT | CONNEL | MINIMUM HEADROOM | NM 91213 33970 | YES | YES | 0 | 0.97263 | 0.90526 | 0.83684 | 0.80842 | 0.78421 | 0.75579 | 0.72526 | 0.70211 | 0.67895 | 0.56737 | 0.23789 | 0.16526 | 0.10842 | 0.99579 | 0.84737 | 0.77053 | 0.74 | 0.71263 | 0.68316 | 0.65053 | 0.62526 | 0.60105 | 0.46737 | 0.093684 | 0.015789 | -0.044211 | 0.91789 | 0.77053 | 0.69053 | 0.65895 | 0.63263 | 0.60105 | 0.56947 | 0.54316 | 0.51789 | 0.38842 | 0.0073684 | -0.073684 | -0.13789
|  | CONNEL | EE |  |  |  |  | 0.97263 | 0.95895 | 0.83684 | 0.80842 | 0.78421 | 0.75579 | 0.72526 | 0.70211 | 0.67895 | 0.65684 | 0.23789 | 0.16526 | 0.10842 | 0.99579 | 0.96737 | 0.77053 | 0.74 | 0.71263 | 0.68316 | 0.65053 | 0.62526 | 0.60105 | 0.57789 | 0.093684 | 0.015789 | -0.044211 | 0.91789 | 0.88947 | 0.69053 | 0.65895 | 0.63263 | 0.60105 | 0.56947 | 0.54316 | 0.51789 | 0.49263 | 0.0073684 | -0.073684 | -0.13789
|  | CONNEL | HT |  |  |  |  | 0.97579 | 0.90526 | 0.88211 | 0.86 | 0.83474 | 0.81053 | 0.78842 | 0.76421 | 0.69158 | 0.56737 | 0.27789 | 0.20842 | 0.15789 | 1.0042 | 0.84737 | 0.82211 | 0.79789 | 0.77053 | 0.74421 | 0.71895 | 0.69368 | 0.61053 | 0.46737 | 0.15474 | 0.071579 | 0.0021053 | 0.92632 | 0.77053 | 0.74526 | 0.72105 | 0.69263 | 0.66737 | 0.64211 | 0.61474 | 0.53263 | 0.38842 | 0.074737 | -0.0084211 | -0.077895
|  | CONNEL | HE |  |  |  |  | 0.98105 | 0.97158 | 0.88105 | 0.86526 | 0.85053 | 0.83053 | 0.81368 | 0.79895 | 0.78316 | 0.77263 | 0.39158 | 0.35474 | 0.32737 | 1.0232 | 1.0053 | 0.81895 | 0.80316 | 0.78737 | 0.76632 | 0.74842 | 0.73263 | 0.71579 | 0.70421 | 0.26 | 0.21895 | 0.18947 | 0.94526 | 0.92842 | 0.74211 | 0.72526 | 0.70947 | 0.68947 | 0.66947 | 0.65474 | 0.63789 | 0.62421 | 0.18105 | 0.14 | 0.10842
|  | CONNEL | FB |  |  |  |  | 0.98526 | 0.98211 | 0.97684 | 0.96211 | 0.95789 | 0.95158 | 0.94211 | 0.93158 | 0.92211 | 0.90947 | 0.77579 | 0.60211 | 0.56737 | 1.0316 | 1.0211 | 1.0095 | 0.92737 | 0.91579 | 0.90316 | 0.89263 | 0.88105 | 0.86947 | 0.85474 | 0.70105 | 0.5 | 0.46 | 0.95474 | 0.94421 | 0.93158 | 0.84947 | 0.83789 | 0.82632 | 0.81579 | 0.80421 | 0.79263 | 0.77789 | 0.62526 | 0.42316 | 0.38316
| BEAULY | CONON BRIDGE | MINIMUM HEADROOM | NH 54996 55499 | NO | YES | 0 | 6.4214 | 14.6953 | 14.5005 | 14.2921 | 14.1995 | 13.5595 | 12.8879 | 12.5805 | 12.4089 | 12.3153 | 11.2521 | 10.8542 | 10.6479 | 5.4932 | 13.2832 | 13.0453 | 12.7895 | 12.6853 | 11.9316 | 11.1547 | 10.8042 | 10.6116 | 10.5116 | 10.1242 | 9.1653 | 8.94 | 5.3684 | 13.3832 | 13.1463 | 12.8926 | 12.7874 | 12.0505 | 11.2832 | 10.9368 | 10.7474 | 10.6453 | 10.2421 | 9.0779 | 8.8484
|  | CONON BRIDGE | EE |  |  |  |  | 6.4214 | 14.6953 | 14.5005 | 14.2921 | 14.1995 | 14.0953 | 13.5626 | 13.0826 | 12.6595 | 12.3563 | 11.9511 | 10.8542 | 10.6479 | 5.4932 | 13.2832 | 13.0453 | 12.7895 | 12.6853 | 12.5663 | 11.9526 | 11.4021 | 10.9158 | 10.5695 | 10.1242 | 9.1653 | 8.94 | 5.3684 | 13.3832 | 13.1463 | 12.8926 | 12.7874 | 12.6684 | 12.06 | 11.5147 | 11.0347 | 10.6905 | 10.2421 | 9.0779 | 8.8484
|  | CONON BRIDGE | HT |  |  |  |  | 6.4467 | 14.7321 | 14.5384 | 14.3363 | 14.2353 | 13.5595 | 12.8879 | 12.5805 | 12.4089 | 12.3153 | 11.2521 | 10.9795 | 10.7911 | 5.5216 | 13.3242 | 13.0895 | 12.8411 | 12.7253 | 11.9316 | 11.1547 | 10.8042 | 10.6116 | 10.5116 | 10.1442 | 9.2926 | 9.0295 | 5.3989 | 13.4274 | 13.1937 | 12.9484 | 12.8326 | 12.0505 | 11.2832 | 10.9368 | 10.7474 | 10.6453 | 10.2811 | 9.2684 | 9.0053
|  | CONON BRIDGE | HE |  |  |  |  | 6.4857 | 14.8068 | 14.6416 | 14.4637 | 14.3932 | 14.2416 | 13.8353 | 13.3342 | 12.9058 | 12.6384 | 12.4332 | 11.9384 | 11.8142 | 5.5879 | 13.4158 | 13.2137 | 12.9947 | 12.9158 | 12.7368 | 12.2558 | 11.6779 | 11.1821 | 10.8737 | 10.6453 | 10.1968 | 10.06 | 5.4641 | 13.5179 | 13.3168 | 13.1011 | 13.0211 | 12.8442 | 12.3684 | 11.7979 | 11.3105 | 11.0042 | 10.7768 | 10.2463 | 10.1084
|  | CONON BRIDGE | FB |  |  |  |  | 6.5193 | 14.9711 | 14.8805 | 14.7879 | 14.7479 | 14.7068 | 14.5605 | 14.4226 | 14.2132 | 13.9963 | 13.5258 | 13.3532 | 13.2258 | 5.6711 | 13.6147 | 13.5021 | 13.3863 | 13.34 | 13.2905 | 13.1105 | 12.9389 | 12.6779 | 12.4221 | 11.8853 | 11.6895 | 11.5463 | 5.5462 | 13.7137 | 13.6032 | 13.4895 | 13.4432 | 13.3947 | 13.2158 | 13.0474 | 12.7895 | 12.5379 | 12.0063 | 11.8137 | 11.6716
| BEAULY | CONON FALLS | MINIMUM HEADROOM | NH 38745 57593 | YES | YES | 0.2551 | 0.49368 | 0.49053 | 0.48842 | 0.28842 | 0.28526 | 0.28105 | 0.27684 | 0.27368 | 0.27053 | 0.26737 | 0.25579 | 0.24421 | 0.23474 | 0.49158 | 0.48737 | 0.48316 | 0.31368 | 0.30947 | 0.30316 | 0.29684 | 0.29158 | 0.28632 | 0.28211 | 0.26526 | 0.24842 | 0.23474 | 0.49158 | 0.48632 | 0.48211 | 0.28526 | 0.28105 | 0.27579 | 0.27053 | 0.26737 | 0.26316 | 0.26 | 0.24632 | 0.23263 | 0.22105
|  | CONON FALLS | EE |  |  |  |  | 0.49368 | 0.49053 | 0.48842 | 0.28842 | 0.28526 | 0.28105 | 0.27684 | 0.27368 | 0.27053 | 0.26737 | 0.25579 | 0.24421 | 0.23474 | 0.49158 | 0.48737 | 0.48316 | 0.31368 | 0.30947 | 0.30316 | 0.29684 | 0.29158 | 0.28632 | 0.28211 | 0.26526 | 0.24842 | 0.23474 | 0.49158 | 0.48632 | 0.48211 | 0.28526 | 0.28105 | 0.27579 | 0.27053 | 0.26737 | 0.26316 | 0.26 | 0.24632 | 0.23263 | 0.22105
|  | CONON FALLS | HT |  |  |  |  | 0.49579 | 0.49474 | 0.49158 | 0.48842 | 0.48526 | 0.48211 | 0.47895 | 0.47684 | 0.47368 | 0.47158 | 0.45895 | 0.44842 | 0.43895 | 0.49368 | 0.49053 | 0.48632 | 0.48211 | 0.47789 | 0.47263 | 0.46737 | 0.46316 | 0.46 | 0.45579 | 0.44211 | 0.42737 | 0.41684 | 0.49263 | 0.49158 | 0.48737 | 0.48211 | 0.47684 | 0.47263 | 0.46737 | 0.46421 | 0.46105 | 0.45579 | 0.44316 | 0.42842 | 0.41579
|  | CONON FALLS | HE |  |  |  |  | 0.49684 | 0.49474 | 0.49368 | 0.49158 | 0.49053 | 0.48632 | 0.48421 | 0.48211 | 0.48105 | 0.48 | 0.47368 | 0.46737 | 0.46211 | 0.49579 | 0.49263 | 0.49053 | 0.48842 | 0.48632 | 0.48316 | 0.48 | 0.47684 | 0.47474 | 0.47368 | 0.46421 | 0.45474 | 0.44737 | 0.49579 | 0.49263 | 0.49158 | 0.48842 | 0.48526 | 0.48211 | 0.47895 | 0.47579 | 0.47474 | 0.47158 | 0.46211 | 0.45263 | 0.44421
|  | CONON FALLS | FB |  |  |  |  | 0.49789 | 0.49789 | 0.49684 | 0.49579 | 0.49474 | 0.49368 | 0.49263 | 0.49263 | 0.49158 | 0.49053 | 0.48632 | 0.48 | 0.47684 | 0.49684 | 0.49579 | 0.49474 | 0.49368 | 0.49158 | 0.48947 | 0.48842 | 0.48842 | 0.48526 | 0.48316 | 0.47368 | 0.46421 | 0.45579 | 0.49789 | 0.49684 | 0.49474 | 0.49263 | 0.49158 | 0.48947 | 0.48842 | 0.48842 | 0.48632 | 0.48421 | 0.47684 | 0.46632 | 0.45789
| DUDHOPE | CONSTABLE STREET | MINIMUM HEADROOM | NO 40903 30821 | NO | YES | 0 | 33.08 | 32.9958 | 32.9053 | 32.8211 | 32.7263 | 32.6 | 32.4958 | 32.3295 | 32.0853 | 31.9032 | 31.14 | 30.6305 | 30.2747 | 27.1884 | 27.0232 | 26.8253 | 26.6579 | 26.4768 | 26.2505 | 26.0095 | 25.6811 | 25.3621 | 25.1337 | 24.3305 | 23.6189 | 23.0474 | 31.3647 | 31.3195 | 31.2816 | 31.23 | 31.1732 | 31.1111 | 31.0511 | 30.9805 | 30.7237 | 30.5342 | 29.8763 | 29.2974 | 28.8016
|  | CONSTABLE STREET | EE |  |  |  |  | 33.08 | 32.9958 | 32.9053 | 32.8211 | 32.7263 | 32.6126 | 32.4989 | 32.3568 | 32.2126 | 32.0558 | 31.3474 | 30.8526 | 30.48 | 27.1884 | 27.0232 | 26.8253 | 26.6579 | 26.4768 | 26.2674 | 26.0716 | 25.7726 | 25.5347 | 25.3326 | 24.4189 | 23.7779 | 23.2947 | 31.3647 | 31.3195 | 31.2826 | 31.2405 | 31.1889 | 31.1226 | 31.0511 | 30.9868 | 30.8584 | 30.6942 | 29.9521 | 29.4321 | 29.0247
|  | CONSTABLE STREET | HT |  |  |  |  | 33.0958 | 33.0168 | 32.9232 | 32.8442 | 32.7411 | 32.6 | 32.4958 | 32.3295 | 32.0853 | 31.9032 | 31.14 | 30.6305 | 30.2747 | 27.2232 | 27.0705 | 26.8821 | 26.7453 | 26.5505 | 26.2505 | 26.0095 | 25.6811 | 25.3621 | 25.1337 | 24.3305 | 23.6189 | 23.0474 | 31.37 | 31.3279 | 31.2816 | 31.23 | 31.1732 | 31.1111 | 31.0837 | 30.9805 | 30.7237 | 30.5342 | 29.8763 | 29.2974 | 28.8016
|  | CONSTABLE STREET | HE |  |  |  |  | 33.1263 | 33.0558 | 32.9821 | 32.9263 | 32.8526 | 32.7589 | 32.6779 | 32.5821 | 32.4789 | 32.4168 | 31.9737 | 31.6684 | 31.4663 | 27.2958 | 27.1705 | 27.0221 | 26.94 | 26.8253 | 26.6821 | 26.5768 | 26.3853 | 26.1768 | 26.0442 | 25.2453 | 24.8474 | 24.5832 | 31.3805 | 31.3363 | 31.3005 | 31.2574 | 31.2047 | 31.1353 | 31.0658 | 31.0184 | 30.9679 | 30.9405 | 30.5911 | 30.2711 | 30.0584
|  | CONSTABLE STREET | FB |  |  |  |  | 33.1621 | 33.12 | 33.0726 | 33.0326 | 32.9895 | 32.9442 | 32.8937 | 32.8516 | 32.7853 | 32.7189 | 32.3884 | 32.1126 | 31.8495 | 27.3684 | 27.2874 | 27.1947 | 27.1263 | 27.0526 | 26.9716 | 26.88 | 26.8126 | 26.6779 | 26.5526 | 25.8474 | 25.4084 | 25.0589 | 31.3974 | 31.3742 | 31.35 | 31.3237 | 31.2974 | 31.2679 | 31.2384 | 31.21 | 31.1763 | 31.1405 | 30.9974 | 30.7342 | 30.4563
| ALNESS | CONTULLICH | MINIMUM HEADROOM | NN 59226 32752 | YES | YES | 0 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.1 | 0.10211 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.095789 | 0.095789 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947
|  | CONTULLICH | EE |  |  |  |  | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.10211 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.095789 | 0.095789 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.098947
|  | CONTULLICH | HT |  |  |  |  | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.1 | 0.10211 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.095789 | 0.095789 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947
|  | CONTULLICH | HE |  |  |  |  | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1
|  | CONTULLICH | FB |  |  |  |  | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105
| FORT WILLIAM | CORRAN | MINIMUM HEADROOM | NN 02545 63126 | YES | NO | 0 | 1.1621 | 1.1568 | 0.14211 | 0.13684 | 0.13053 | 0.12316 | 0.11474 | 0.10842 | 0.10211 | 0.097895 | 0.076842 | 0.055789 | 0.024211 | 1.08 | 1.0737 | 0.13474 | 0.12316 | 0.10947 | 0.095789 | 0.082105 | 0.066316 | 0.052632 | 0.041053 | 0.0010526 | -0.032632 | -0.054737 | 0.95684 | 0.94 | -0.11053 | -0.12632 | -0.14421 | -0.16211 | -0.17895 | -0.20105 | -0.22 | -0.23579 | -0.28947 | -0.34105 | -0.38737
|  | CORRAN | EE |  |  |  |  | 1.1621 | 1.1568 | 0.14211 | 0.13684 | 0.13053 | 0.12316 | 0.11474 | 0.10842 | 0.10211 | 0.097895 | 0.076842 | 0.055789 | 0.024211 | 1.08 | 1.0737 | 0.13474 | 0.12316 | 0.10947 | 0.095789 | 0.082105 | 0.066316 | 0.052632 | 0.041053 | 0.0010526 | -0.032632 | -0.054737 | 0.95684 | 0.94 | -0.11053 | -0.12632 | -0.14421 | -0.16211 | -0.17895 | -0.20105 | -0.22 | -0.23579 | -0.28947 | -0.34105 | -0.38737
|  | CORRAN | HT |  |  |  |  | 1.1632 | 1.1568 | 1.1516 | 1.1463 | 1.1389 | 1.1253 | 1.1021 | 1.0779 | 1.06 | 1.0421 | 0.95474 | 0.9 | 0.86316 | 1.0811 | 1.0737 | 1.0684 | 1.0621 | 1.0432 | 1.0126 | 0.98632 | 0.96105 | 0.94105 | 0.92211 | 0.84526 | 0.77684 | 0.72421 | 0.96316 | 0.94632 | 0.93158 | 0.91368 | 0.88947 | 0.85684 | 0.82947 | 0.80316 | 0.78211 | 0.76211 | 0.68105 | 0.61053 | 0.55684
|  | CORRAN | HE |  |  |  |  | 1.1642 | 1.16 | 1.1568 | 1.1516 | 1.1463 | 1.1389 | 1.1316 | 1.1263 | 1.1221 | 1.1147 | 1.0779 | 1.0421 | 1.0232 | 1.0821 | 1.0779 | 1.0747 | 1.0684 | 1.0632 | 1.0558 | 1.0484 | 1.0347 | 1.0158 | 1.0021 | 0.96105 | 0.92211 | 0.90105 | 0.97263 | 0.96211 | 0.95368 | 0.94421 | 0.93053 | 0.91895 | 0.90632 | 0.88105 | 0.86105 | 0.84632 | 0.80316 | 0.76211 | 0.74
|  | CORRAN | FB |  |  |  |  | 1.1674 | 1.1653 | 1.1632 | 1.1611 | 1.1589 | 1.1568 | 1.1547 | 1.1526 | 1.1505 | 1.1474 | 1.1147 | 1.0768 | 1.0495 | 1.0853 | 1.0832 | 1.0811 | 1.0789 | 1.0758 | 1.0737 | 1.0716 | 1.0695 | 1.0663 | 1.0484 | 1 | 0.95895 | 0.92842 | 0.98 | 0.97263 | 0.96526 | 0.95789 | 0.94947 | 0.94105 | 0.93474 | 0.92737 | 0.91263 | 0.89368 | 0.84316 | 0.79895 | 0.76632
| KILLIN | COSHIEVILLE | MINIMUM HEADROOM | NN 77193 48683 | YES | YES | 0 | 2.9495 | 2.9211 | 2.8874 | 2.8326 | 2.7853 | 2.7368 | 2.6832 | 2.6253 | 2.5537 | 2.5116 | 2.3063 | 2.1411 | 2.0126 | 2.9758 | 2.9516 | 2.9189 | 2.8611 | 2.8126 | 2.7621 | 2.7063 | 2.6442 | 2.5653 | 2.5232 | 2.3032 | 2.1305 | 2 | 2.9684 | 2.9368 | 2.9011 | 2.8389 | 2.7863 | 2.7337 | 2.6737 | 2.6074 | 2.5263 | 2.48 | 2.2442 | 2.0558 | 1.9084
|  | COSHIEVILLE | EE |  |  |  |  | 2.9495 | 2.9211 | 2.8874 | 2.8326 | 2.7853 | 2.7368 | 2.6832 | 2.6253 | 2.5537 | 2.5116 | 2.3063 | 2.1411 | 2.0126 | 2.9758 | 2.9516 | 2.9189 | 2.8611 | 2.8126 | 2.7621 | 2.7063 | 2.6442 | 2.5653 | 2.5232 | 2.3032 | 2.1305 | 2 | 2.9684 | 2.9368 | 2.9011 | 2.8389 | 2.7863 | 2.7337 | 2.6737 | 2.6074 | 2.5263 | 2.48 | 2.2442 | 2.0558 | 1.9084
|  | COSHIEVILLE | HT |  |  |  |  | 2.96 | 2.9379 | 2.9095 | 2.8653 | 2.8221 | 2.7747 | 2.7221 | 2.6674 | 2.6 | 2.56 | 2.3642 | 2.2253 | 2.1305 | 2.9842 | 2.9653 | 2.9347 | 2.8863 | 2.84 | 2.7874 | 2.7274 | 2.6653 | 2.5916 | 2.5484 | 2.3684 | 2.2095 | 2.0768 | 2.9811 | 2.9568 | 2.9263 | 2.8768 | 2.8295 | 2.7768 | 2.7179 | 2.6547 | 2.5811 | 2.5368 | 2.3516 | 2.1842 | 2.0463
|  | COSHIEVILLE | HE |  |  |  |  | 2.9768 | 2.96 | 2.9442 | 2.9232 | 2.9063 | 2.8863 | 2.8526 | 2.8168 | 2.7568 | 2.7347 | 2.6253 | 2.5421 | 2.4811 | 2.9947 | 2.9811 | 2.9695 | 2.9516 | 2.9358 | 2.9147 | 2.88 | 2.84 | 2.7726 | 2.7484 | 2.6274 | 2.54 | 2.4758 | 2.9916 | 2.9811 | 2.9632 | 2.9411 | 2.9232 | 2.9021 | 2.8653 | 2.8253 | 2.7579 | 2.7337 | 2.6095 | 2.5147 | 2.4442
|  | COSHIEVILLE | FB |  |  |  |  | 2.9853 | 2.9779 | 2.9684 | 2.9568 | 2.9474 | 2.9368 | 2.9274 | 2.9158 | 2.8874 | 2.8632 | 2.7537 | 2.6474 | 2.5768 | 3.0021 | 2.9968 | 2.9916 | 2.9832 | 2.9747 | 2.9621 | 2.9526 | 2.94 | 2.9074 | 2.8811 | 2.7547 | 2.6337 | 2.5537 | 2.9958 | 2.9937 | 2.9905 | 2.9779 | 2.9674 | 2.9547 | 2.9463 | 2.9326 | 2.9 | 2.8747 | 2.7495 | 2.6305 | 2.5484
| COUPAR ANGUS | COUPAR ANGUS | MINIMUM HEADROOM | NO 21784 39212 | NO | YES | 0 | 14.3374 | 14.2721 | 14.1858 | 13.5868 | 12.9047 | 12.7868 | 12.6584 | 12.5479 | 12.3553 | 12.1995 | 10.6889 | 10.4479 | 10.2763 | 14.4032 | 14.3337 | 14.2411 | 13.5516 | 12.76 | 12.6284 | 12.4842 | 12.3611 | 12.1421 | 11.9663 | 10.5874 | 10.3147 | 10.1211 | 13.9476 | 13.8782 | 13.7866 | 13.1382 | 12.4003 | 12.2761 | 12.1392 | 12.0234 | 11.8161 | 11.6508 | 10.1361 | 9.8803 | 9.6982
|  | COUPAR ANGUS | EE |  |  |  |  | 14.3374 | 14.2721 | 14.1858 | 13.5868 | 12.9047 | 12.7868 | 12.6584 | 12.5563 | 12.4363 | 12.3847 | 10.6889 | 10.4479 | 10.2763 | 14.4032 | 14.3337 | 14.2411 | 13.5516 | 12.76 | 12.6284 | 12.4842 | 12.3695 | 12.2337 | 12.1768 | 10.5874 | 10.3147 | 10.1211 | 13.9476 | 13.8782 | 13.7866 | 13.1382 | 12.4003 | 12.2761 | 12.1392 | 12.0308 | 11.9034 | 11.8497 | 10.1361 | 9.8803 | 9.6982
|  | COUPAR ANGUS | HT |  |  |  |  | 14.3532 | 14.2963 | 14.2079 | 13.5963 | 12.9089 | 12.8111 | 12.6847 | 12.5479 | 12.3553 | 12.1995 | 10.8142 | 10.5858 | 10.4279 | 14.4211 | 14.36 | 14.2663 | 13.5642 | 12.7674 | 12.6579 | 12.5158 | 12.3611 | 12.1421 | 11.9663 | 10.7232 | 10.4611 | 10.2368 | 13.9645 | 13.9045 | 13.8108 | 13.1497 | 12.4076 | 12.3024 | 12.1687 | 12.0234 | 11.8161 | 11.6508 | 10.3066 | 10.0571 | 9.8445
|  | COUPAR ANGUS | HE |  |  |  |  | 14.3963 | 14.3542 | 14.2911 | 13.7153 | 13.0563 | 12.9637 | 12.8142 | 12.7258 | 12.5995 | 12.5732 | 11.6447 | 11.5195 | 11.4205 | 14.4674 | 14.4221 | 14.3547 | 13.6989 | 12.9337 | 12.8305 | 12.6621 | 12.5621 | 12.4189 | 12.3895 | 11.4621 | 11.3211 | 11.2084 | 14.0097 | 13.9655 | 13.8992 | 13.2771 | 12.5645 | 12.4666 | 12.3066 | 12.2129 | 12.0782 | 12.0497 | 11.0929 | 10.9603 | 10.8539
|  | COUPAR ANGUS | FB |  |  |  |  | 14.4195 | 14.3921 | 14.3616 | 14.2689 | 14.0742 | 13.9279 | 13.8132 | 13.7111 | 13.6289 | 13.5953 | 13.2942 | 13.0047 | 12.8858 | 14.4916 | 14.4621 | 14.4295 | 14.3284 | 14.1116 | 13.9421 | 13.8105 | 13.6926 | 13.5989 | 13.5621 | 13.2168 | 12.8863 | 12.7495 | 14.0339 | 14.0055 | 13.9729 | 13.8729 | 13.6624 | 13.5045 | 13.3813 | 13.2718 | 13.1834 | 13.1476 | 12.8245 | 12.515 | 12.3866
| CRAIGIEBUCKLER | CRAIGIEBUCKLER | MINIMUM HEADROOM | NJ 90775 04519 | NO | YES | 0.20918 | 23.9442 | 23.8968 | 23.8558 | 23.8042 | 23.6937 | 23.5653 | 23.44 | 23.3211 | 23.2042 | 23.0611 | 22.5926 | 22.2021 | 21.9189 | 22.3505 | 22.2137 | 22.0905 | 21.9684 | 21.8263 | 21.6895 | 21.5568 | 21.4274 | 21.3011 | 21.1484 | 20.6853 | 20.2979 | 19.9053 | 21.7516 | 21.6116 | 21.4863 | 21.3611 | 21.2158 | 21.0768 | 20.9421 | 20.8095 | 20.6821 | 20.5263 | 20.0526 | 19.6589 | 19.2579
|  | CRAIGIEBUCKLER | EE |  |  |  |  | 23.9442 | 23.8968 | 23.8558 | 23.8126 | 23.6937 | 23.5653 | 23.44 | 23.3211 | 23.2042 | 23.0811 | 22.6379 | 22.32 | 22.0474 | 22.3505 | 22.2137 | 22.0905 | 21.9684 | 21.8263 | 21.6895 | 21.5568 | 21.4274 | 21.3011 | 21.1663 | 20.6853 | 20.3379 | 20.0368 | 21.7516 | 21.6116 | 21.4863 | 21.3611 | 21.2158 | 21.0768 | 20.9421 | 20.8095 | 20.6821 | 20.5432 | 20.0526 | 19.6979 | 19.3895
|  | CRAIGIEBUCKLER | HT |  |  |  |  | 23.9505 | 23.9053 | 23.8568 | 23.8042 | 23.7295 | 23.6179 | 23.4905 | 23.36 | 23.2211 | 23.0611 | 22.5926 | 22.2021 | 21.9189 | 22.3884 | 22.2642 | 22.1442 | 22.0221 | 21.8705 | 21.7505 | 21.6137 | 21.4726 | 21.3221 | 21.1484 | 20.7253 | 20.2979 | 19.9053 | 21.7905 | 21.6642 | 21.5411 | 21.4168 | 21.2621 | 21.14 | 21 | 20.8568 | 20.7032 | 20.5263 | 20.0958 | 19.6589 | 19.2579
|  | CRAIGIEBUCKLER | HE |  |  |  |  | 23.9758 | 23.9347 | 23.9053 | 23.8653 | 23.8158 | 23.7537 | 23.6895 | 23.6484 | 23.5768 | 23.4958 | 23.22 | 23.0568 | 22.9137 | 22.4821 | 22.3937 | 22.3179 | 22.2389 | 22.1263 | 22.0221 | 21.9053 | 21.8137 | 21.7158 | 21.6263 | 21.3232 | 21.1442 | 20.9863 | 21.8874 | 21.7968 | 21.7189 | 21.6389 | 21.5242 | 21.4189 | 21.3 | 21.2063 | 21.1063 | 21.0147 | 20.7042 | 20.5221 | 20.36
|  | CRAIGIEBUCKLER | FB |  |  |  |  | 23.9958 | 23.98 | 23.9621 | 23.9432 | 23.9232 | 23.9021 | 23.88 | 23.8579 | 23.8347 | 23.8105 | 23.5684 | 23.3432 | 23.1789 | 22.5284 | 22.4737 | 22.4179 | 22.3632 | 22.2958 | 22.2337 | 22.1747 | 22.1063 | 22.0421 | 21.9653 | 21.6884 | 21.4411 | 21.2589 | 21.9337 | 21.8779 | 21.8211 | 21.7642 | 21.6958 | 21.6326 | 21.5726 | 21.5021 | 21.4368 | 21.3579 | 21.0747 | 20.8211 | 20.6347
| REDMOSS | CRAIGINCHES | MINIMUM HEADROOM | NJ 94694 04089 | NO | YES | 0.55102 | 23.942 | 23.9231 | 23.9073 | 23.8852 | 23.7894 | 23.6936 | 23.5999 | 23.4925 | 23.3725 | 23.2588 | 22.8767 | 22.5125 | 22.2409 | 22.9136 | 22.8462 | 22.7746 | 22.6704 | 22.5515 | 22.4441 | 22.3399 | 22.2178 | 22.0809 | 21.9525 | 21.5188 | 21.1599 | 20.7967 | 22.4188 | 22.3525 | 22.2831 | 22.1809 | 22.0652 | 21.9599 | 21.8567 | 21.7367 | 21.6052 | 21.4788 | 21.0557 | 20.7052 | 20.3494
|  | CRAIGINCHES | EE |  |  |  |  | 23.942 | 23.9231 | 23.9083 | 23.8894 | 23.7894 | 23.6936 | 23.5999 | 23.4925 | 23.3725 | 23.2673 | 22.8767 | 22.562 | 22.2662 | 22.9136 | 22.8462 | 22.7746 | 22.6704 | 22.5515 | 22.4441 | 22.3399 | 22.2178 | 22.0809 | 21.9609 | 21.5188 | 21.1599 | 20.8199 | 22.4188 | 22.3525 | 22.2831 | 22.1809 | 22.0652 | 21.9599 | 21.8567 | 21.7367 | 21.6052 | 21.4883 | 21.0557 | 20.7052 | 20.3736
|  | CRAIGINCHES | HT |  |  |  |  | 23.9462 | 23.9273 | 23.9073 | 23.8852 | 23.8378 | 23.7557 | 23.6357 | 23.4946 | 23.3873 | 23.2588 | 22.8831 | 22.5125 | 22.2409 | 22.9346 | 22.8704 | 22.8083 | 22.7315 | 22.6094 | 22.5178 | 22.3809 | 22.2209 | 22.0988 | 21.9525 | 21.6052 | 21.1873 | 20.7967 | 22.4388 | 22.3767 | 22.3157 | 22.2399 | 22.1209 | 22.0304 | 21.8978 | 21.7409 | 21.622 | 21.4788 | 21.1399 | 20.7315 | 20.3494
|  | CRAIGINCHES | HE |  |  |  |  | 23.9494 | 23.9304 | 23.9157 | 23.8946 | 23.8683 | 23.8357 | 23.8031 | 23.782 | 23.7136 | 23.6462 | 23.3588 | 23.1925 | 23.0336 | 22.9725 | 22.9283 | 22.8894 | 22.8441 | 22.7736 | 22.7115 | 22.6388 | 22.5673 | 22.4809 | 22.4031 | 22.0736 | 21.8841 | 21.702 | 22.4767 | 22.4325 | 22.3936 | 22.3504 | 22.2799 | 22.2188 | 22.1473 | 22.0778 | 21.9936 | 21.9178 | 21.5967 | 21.4115 | 21.2336
|  | CRAIGINCHES | FB |  |  |  |  | 23.9578 | 23.9483 | 23.9388 | 23.9283 | 23.9157 | 23.9041 | 23.8915 | 23.8788 | 23.8652 | 23.8409 | 23.5936 | 23.3652 | 23.1946 | 22.9925 | 22.9609 | 22.9294 | 22.8967 | 22.8546 | 22.8178 | 22.7831 | 22.7378 | 22.6873 | 22.6146 | 22.3336 | 22.0725 | 21.8757 | 22.4957 | 22.4652 | 22.4336 | 22.402 | 22.3599 | 22.3252 | 22.2904 | 22.2462 | 22.1967 | 22.1262 | 21.8515 | 21.5967 | 21.4052
| CRAIGIEBUCKLER | CRAIGTON | MINIMUM HEADROOM | NJ 89195 03438 | NO | YES | 0.20408 | 12.7474 | 11.06 | 9.4232 | 8.6516 | 8.3537 | 7.24 | 6.8263 | 6.66 | 6.4989 | 6.1674 | 5.2653 | 4.9863 | 4.7411 | 11.9158 | 9.9126 | 7.9379 | 7.0116 | 6.6579 | 5.3221 | 4.8316 | 4.64 | 4.4526 | 4.0579 | 2.9958 | 2.6768 | 2.3916 | 9.9126 | 7.9158 | 5.9737 | 5.0621 | 4.7137 | 3.4 | 2.9168 | 2.7274 | 2.5432 | 2.1547 | 1.1095 | 0.79368 | 0.51263
|  | CRAIGTON | EE |  |  |  |  | 12.9684 | 11.06 | 9.4232 | 8.6516 | 8.3537 | 7.24 | 6.8263 | 6.66 | 6.4989 | 6.1674 | 5.2653 | 4.9863 | 4.7411 | 12.1811 | 9.9126 | 7.9379 | 7.0116 | 6.6579 | 5.3221 | 4.8316 | 4.64 | 4.4526 | 4.0579 | 2.9958 | 2.6768 | 2.3916 | 10.1779 | 7.9158 | 5.9737 | 5.0621 | 4.7137 | 3.4 | 2.9168 | 2.7274 | 2.5432 | 2.1547 | 1.1095 | 0.79368 | 0.51263
|  | CRAIGTON | HT |  |  |  |  | 12.8179 | 11.2453 | 9.5463 | 8.7789 | 8.4768 | 8.3263 | 8.1579 | 7.9789 | 7.6337 | 6.9874 | 6.0274 | 5.6779 | 5.4295 | 12.0021 | 10.1347 | 8.0874 | 7.1663 | 6.8095 | 6.6358 | 6.4411 | 6.2337 | 5.8253 | 5.0537 | 4.0042 | 3.6 | 3.2389 | 9.9979 | 8.1347 | 6.12 | 5.2147 | 4.8632 | 4.6916 | 4.4989 | 4.2947 | 3.8926 | 3.1326 | 2.0989 | 1.7011 | 1.3442
|  | CRAIGTON | HE |  |  |  |  | 12.7474 | 11.3568 | 9.7505 | 9.0158 | 8.7274 | 7.6274 | 7.22 | 7.0853 | 6.9463 | 6.6642 | 5.8842 | 5.7463 | 5.6158 | 11.9158 | 10.2674 | 8.3284 | 7.4463 | 7.1042 | 5.7842 | 5.3011 | 5.1453 | 4.9832 | 4.6442 | 3.7147 | 3.5568 | 3.4042 | 9.9126 | 8.2653 | 6.3589 | 5.4905 | 5.1537 | 3.8547 | 3.3789 | 3.2253 | 3.0653 | 2.7316 | 1.8168 | 1.66 | 1.5105
|  | CRAIGTON | FB |  |  |  |  | 14.5221 | 13.9463 | 13.2358 | 12.7989 | 11.3663 | 10.5495 | 10.2726 | 9.9842 | 9.8989 | 9.7011 | 9.3611 | 9.0021 | 8.8611 | 14.0158 | 13.3358 | 12.4968 | 11.9811 | 10.2789 | 9.2947 | 8.9632 | 8.6168 | 8.5168 | 8.2821 | 7.8832 | 7.46 | 7.2947 | 12.0189 | 11.3368 | 10.4947 | 9.9768 | 8.2768 | 7.3084 | 6.9821 | 6.6411 | 6.5432 | 6.3116 | 5.9189 | 5.5011 | 5.3389
| BRACO | CRIEFF | MINIMUM HEADROOM | NN 85626 22119 | NO | YES | 0.23469 | 14.0342 | 22.6505 | 22.5389 | 22.4116 | 22.2853 | 22.1684 | 22.0168 | 21.8947 | 21.7716 | 21.6653 | 21.0874 | 20.7947 | 20.5832 | 14.6284 | 22.6684 | 22.4116 | 22.1253 | 21.8547 | 21.6 | 21.3042 | 21.0547 | 20.8053 | 20.5789 | 19.6179 | 18.9411 | 18.4095 | 13.3203 | 21.5979 | 21.3589 | 21.0926 | 20.8389 | 20.6074 | 20.3295 | 20.0968 | 19.8611 | 19.6495 | 18.7621 | 18.1263 | 17.6295
|  | CRIEFF | EE |  |  |  |  | 14.0342 | 22.6505 | 22.5389 | 22.4116 | 22.2853 | 22.1684 | 22.0168 | 21.8947 | 21.7716 | 21.6653 | 21.2358 | 20.9284 | 20.7211 | 14.6284 | 22.6684 | 22.4116 | 22.1253 | 21.8547 | 21.6 | 21.3042 | 21.0547 | 20.8053 | 20.5789 | 19.6179 | 18.9705 | 18.5368 | 13.3203 | 21.5979 | 21.3589 | 21.0926 | 20.8389 | 20.6074 | 20.3295 | 20.0968 | 19.8611 | 19.6495 | 18.7621 | 18.1537 | 17.7442
|  | CRIEFF | HT |  |  |  |  | 14.05 | 22.6716 | 22.5547 | 22.4568 | 22.3179 | 22.1895 | 22.0589 | 21.9274 | 21.7884 | 21.6779 | 21.0874 | 20.7947 | 20.5832 | 14.6674 | 22.72 | 22.4716 | 22.2432 | 21.9526 | 21.6958 | 21.4347 | 21.1747 | 20.9 | 20.6558 | 19.6274 | 18.9411 | 18.4095 | 13.355 | 21.6474 | 21.4158 | 21.2095 | 20.9389 | 20.6979 | 20.4526 | 20.2095 | 19.9516 | 19.7326 | 18.7684 | 18.1263 | 17.6295
|  | CRIEFF | HE |  |  |  |  | 14.0974 | 22.7368 | 22.6505 | 22.5505 | 22.4463 | 22.3568 | 22.2295 | 22.1063 | 22.0116 | 21.9432 | 21.6189 | 21.4326 | 21.3179 | 14.7653 | 22.86 | 22.6642 | 22.46 | 22.2537 | 22.0674 | 21.8326 | 21.6042 | 21.4053 | 21.24 | 20.4642 | 20.0421 | 19.7905 | 13.4476 | 21.7779 | 21.5958 | 21.4042 | 21.2116 | 21.0432 | 20.8221 | 20.6 | 20.4147 | 20.26 | 19.5411 | 19.1484 | 18.9126
|  | CRIEFF | FB |  |  |  |  | 14.1521 | 22.8379 | 22.7895 | 22.7411 | 22.6926 | 22.6389 | 22.58 | 22.5211 | 22.4611 | 22.3937 | 22.1305 | 21.9253 | 21.7968 | 14.8779 | 23.0621 | 22.9537 | 22.8505 | 22.7495 | 22.6284 | 22.5011 | 22.3674 | 22.2337 | 22.0853 | 21.4863 | 21.0326 | 20.7295 | 13.555 | 21.9695 | 21.8674 | 21.7695 | 21.6747 | 21.5632 | 21.4432 | 21.32 | 21.1958 | 21.0579 | 20.5021 | 20.0789 | 19.7989
| PORT ANN | CRINAN | MINIMUM HEADROOM | NR 79620 92347 | YES | YES | 0 | 0.60316 | 0.58737 | 0.57368 | 0.55053 | 0.53158 | 0.50947 | 0.48737 | 0.46947 | 0.45158 | 0.43263 | 0.29474 | 0.23158 | 0.17895 | 0.55368 | 0.53789 | 0.52316 | 0.49895 | 0.47895 | 0.45684 | 0.43368 | 0.41579 | 0.39684 | 0.36421 | 0.22526 | 0.16 | 0.10737 | 0.56105 | 0.54421 | 0.52737 | 0.50211 | 0.48105 | 0.45684 | 0.43263 | 0.41263 | 0.39158 | 0.36947 | 0.21263 | 0.14211 | 0.081053
|  | CRINAN | EE |  |  |  |  | 0.60316 | 0.58737 | 0.57368 | 0.55053 | 0.53158 | 0.50947 | 0.48737 | 0.46947 | 0.45158 | 0.43263 | 0.29474 | 0.23158 | 0.17895 | 0.55368 | 0.53789 | 0.52316 | 0.49895 | 0.47895 | 0.45684 | 0.43368 | 0.41579 | 0.39684 | 0.37895 | 0.22526 | 0.16 | 0.10737 | 0.56105 | 0.54421 | 0.52737 | 0.50211 | 0.48105 | 0.45684 | 0.43263 | 0.41263 | 0.39158 | 0.37263 | 0.21263 | 0.14211 | 0.081053
|  | CRINAN | HT |  |  |  |  | 0.60947 | 0.59579 | 0.58421 | 0.56947 | 0.55158 | 0.53368 | 0.51579 | 0.49789 | 0.47263 | 0.43263 | 0.31789 | 0.26211 | 0.22526 | 0.55789 | 0.54526 | 0.53263 | 0.51579 | 0.49684 | 0.47684 | 0.45789 | 0.43789 | 0.40947 | 0.36421 | 0.25053 | 0.18737 | 0.13684 | 0.56842 | 0.55368 | 0.54105 | 0.52316 | 0.50316 | 0.48526 | 0.46526 | 0.44526 | 0.41579 | 0.36947 | 0.25474 | 0.18842 | 0.13579
|  | CRINAN | HE |  |  |  |  | 0.61789 | 0.60947 | 0.60105 | 0.59368 | 0.58421 | 0.57368 | 0.56526 | 0.55368 | 0.54421 | 0.53474 | 0.42632 | 0.39579 | 0.37053 | 0.56842 | 0.56105 | 0.55158 | 0.54316 | 0.53474 | 0.52316 | 0.51474 | 0.50316 | 0.49158 | 0.48211 | 0.35895 | 0.32737 | 0.3 | 0.57789 | 0.56947 | 0.56 | 0.55158 | 0.54105 | 0.53158 | 0.52 | 0.50842 | 0.49789 | 0.48632 | 0.36316 | 0.32842 | 0.29895
|  | CRINAN | FB |  |  |  |  | 0.62421 | 0.61684 | 0.61263 | 0.60632 | 0.60105 | 0.59579 | 0.58947 | 0.58421 | 0.57684 | 0.56737 | 0.51474 | 0.45263 | 0.42421 | 0.57579 | 0.56842 | 0.56316 | 0.55579 | 0.54947 | 0.54421 | 0.53789 | 0.53158 | 0.52316 | 0.51263 | 0.45263 | 0.38 | 0.34842 | 0.58526 | 0.57684 | 0.57158 | 0.56526 | 0.56 | 0.55368 | 0.54632 | 0.54105 | 0.53263 | 0.52211 | 0.46211 | 0.38947 | 0.35789
| PORT ANN | CROMALT | MINIMUM HEADROOM | NN 08395 07755 | YES | YES | 0 | 2.4716 | 2.4568 | 2.4484 | 2.9168 | 2.9084 | 2.8895 | 2.86 | 2.8221 | 2.7642 | 2.7263 | 2.6295 | 2.5968 | 2.5768 | -3.0547 | -3.0716 | -3.08 | -2.6137 | -2.6232 | -2.6442 | -2.6758 | -2.7168 | -2.78 | -2.82 | -2.9242 | -2.9611 | -2.9821 | 2.1274 | 2.1221 | 2.1179 | 2.6074 | 2.6032 | 2.5958 | 2.5863 | 2.5737 | 2.5547 | 2.5432 | 2.5105 | 2.4958 | 2.4863
|  | CROMALT | EE |  |  |  |  | 2.4716 | 2.4579 | 2.4505 | 2.9368 | 2.9295 | 2.92 | 2.9042 | 2.8768 | 2.8326 | 2.8263 | 2.6316 | 2.5968 | 2.5768 | -3.0547 | -3.0695 | -3.0779 | -2.5926 | -2.6 | -2.6105 | -2.6274 | -2.6558 | -2.7042 | -2.7116 | -2.9242 | -2.9611 | -2.9821 | 2.1274 | 2.1221 | 2.1189 | 2.6137 | 2.6095 | 2.6042 | 2.5968 | 2.5874 | 2.5737 | 2.5705 | 2.5105 | 2.4958 | 2.4874
|  | CROMALT | HT |  |  |  |  | 2.4747 | 2.4568 | 2.4484 | 2.9168 | 2.9084 | 2.8895 | 2.86 | 2.8221 | 2.7642 | 2.7263 | 2.6295 | 2.6053 | 2.5863 | -3.0516 | -3.0716 | -3.08 | -2.6137 | -2.6232 | -2.6442 | -2.6758 | -2.7168 | -2.78 | -2.82 | -2.9189 | -2.9474 | -2.9716 | 2.1295 | 2.1221 | 2.1179 | 2.6074 | 2.6032 | 2.5958 | 2.5863 | 2.5737 | 2.5547 | 2.5432 | 2.5105 | 2.4979 | 2.4863
|  | CROMALT | HE |  |  |  |  | 2.4789 | 2.4653 | 2.4621 | 2.9432 | 2.9389 | 2.9337 | 2.9032 | 2.8768 | 2.8284 | 2.8253 | 2.6747 | 2.6611 | 2.6505 | -3.0474 | -3.0621 | -3.0653 | -2.5853 | -2.5905 | -2.5947 | -2.6284 | -2.6568 | -2.7095 | -2.7126 | -2.8779 | -2.8926 | -2.9032 | 2.1305 | 2.1253 | 2.1232 | 2.6158 | 2.6126 | 2.6095 | 2.5979 | 2.5895 | 2.5758 | 2.5737 | 2.5295 | 2.5232 | 2.5189
|  | CROMALT | FB |  |  |  |  | 2.4863 | 2.4832 | 2.4811 | 2.9768 | 2.9716 | 2.9695 | 2.9663 | 2.9568 | 2.9347 | 2.9295 | 2.8453 | 2.7663 | 2.7537 | -3.0389 | -3.0432 | -3.0453 | -2.5495 | -2.5547 | -2.5568 | -2.5611 | -2.5705 | -2.5947 | -2.6 | -2.6916 | -2.7779 | -2.7916 | 2.1326 | 2.1305 | 2.1305 | 2.6284 | 2.6263 | 2.6242 | 2.6232 | 2.62 | 2.6126 | 2.6095 | 2.5842 | 2.56 | 2.5547
| ALNESS | CROSSHILLS | MINIMUM HEADROOM | NH 65470 70156 | NO | YES | 0 | 14.0932 | 13.9542 | 13.8037 | 13.4995 | 13.3826 | 11.1258 | 8.9521 | 6.6858 | 5.0511 | 4.5542 | 3.8268 | 3.4847 | 3.2426 | 15.0737 | 14.9084 | 14.7242 | 14.3432 | 14.2074 | 11.3158 | 8.5316 | 5.6274 | 3.5379 | 2.9137 | 2.0895 | 1.6863 | 1.3347 | 15.7876 | 15.6392 | 15.4761 | 15.1413 | 15.0118 | 12.1718 | 9.395 | 6.5003 | 4.4171 | 3.7929 | 2.9624 | 2.5561 | 2.215
|  | CROSSHILLS | EE |  |  |  |  | 14.0932 | 13.9542 | 13.8037 | 13.4995 | 13.3826 | 13.2521 | 12.5521 | 10.7384 | 8.7237 | 6.4026 | 3.8753 | 3.5384 | 3.29 | 15.0737 | 14.9084 | 14.7242 | 14.3432 | 14.2074 | 14.0558 | 13.1726 | 10.8526 | 8.2747 | 5.2968 | 2.0895 | 1.6863 | 1.3895 | 15.7876 | 15.6392 | 15.4761 | 15.1413 | 15.0118 | 14.8666 | 14.0192 | 11.7045 | 9.1329 | 6.1624 | 2.9624 | 2.5561 | 2.2561
|  | CROSSHILLS | HT |  |  |  |  | 14.1216 | 13.9974 | 13.8511 | 13.5553 | 13.4311 | 11.1258 | 8.9521 | 6.6858 | 5.0511 | 4.5542 | 3.8268 | 3.4847 | 3.2426 | 15.1095 | 14.9589 | 14.7821 | 14.4147 | 14.2684 | 11.3158 | 8.5316 | 5.6274 | 3.5379 | 2.9137 | 2.1358 | 1.6968 | 1.3347 | 15.8192 | 15.6866 | 15.5297 | 15.2087 | 15.0718 | 12.1718 | 9.395 | 6.5003 | 4.4171 | 3.7929 | 3.0161 | 2.5771 | 2.215
|  | CROSSHILLS | HE |  |  |  |  | 14.1837 | 14.0816 | 13.9689 | 13.7047 | 13.6195 | 13.3047 | 12.8268 | 10.9005 | 8.6963 | 6.1163 | 4.4605 | 4.2563 | 4.1142 | 15.1874 | 15.0642 | 14.9263 | 14.5979 | 14.5011 | 14.1126 | 13.5137 | 11.0442 | 8.2179 | 4.9021 | 2.7905 | 2.5432 | 2.3684 | 15.8866 | 15.7771 | 15.6561 | 15.3697 | 15.2803 | 14.9245 | 14.3624 | 11.9003 | 9.0824 | 5.7761 | 3.6697 | 3.4213 | 3.2466
|  | CROSSHILLS | FB |  |  |  |  | 14.2668 | 14.2121 | 14.1437 | 14.0142 | 13.9647 | 13.9142 | 13.6963 | 13.4911 | 12.6668 | 11.6668 | 8.2668 | 8.0416 | 7.8711 | 15.28 | 15.22 | 15.1358 | 14.9747 | 14.9147 | 14.8547 | 14.5789 | 14.32 | 13.2632 | 11.9821 | 7.6242 | 7.3537 | 7.1421 | 15.9624 | 15.9171 | 15.8424 | 15.7024 | 15.6487 | 15.595 | 15.3571 | 15.1266 | 14.1161 | 12.8382 | 8.4939 | 8.2224 | 8.0118
| KEITH 1 | CULLEN | MINIMUM HEADROOM | NJ 51590 65032 | YES | YES | 0 | 7.3305 | 7.2516 | 7.1653 | 7.0589 | 6.9874 | 6.8979 | 6.7768 | 6.6874 | 6.5905 | 6.4958 | 4.4011 | 4.2947 | 4.2253 | 7.1011 | 7.0358 | 6.9663 | 6.8789 | 6.8179 | 6.7442 | 6.6463 | 6.5716 | 6.4905 | 6.4074 | 4.7726 | 4.6526 | 4.5737 | 7.2747 | 7.2547 | 7.2358 | 7.1379 | 7.0589 | 6.9611 | 6.8263 | 6.7274 | 6.6211 | 6.5168 | 4.3989 | 4.2779 | 4.1989
|  | CULLEN | EE |  |  |  |  | 7.3305 | 7.2516 | 7.1926 | 7.0979 | 7.0274 | 6.9516 | 6.8537 | 6.7326 | 6.6232 | 6.5674 | 6.1526 | 5.9379 | 5.78 | 7.1011 | 7.0358 | 6.9863 | 6.9105 | 6.8505 | 6.7863 | 6.7042 | 6.6063 | 6.5168 | 6.4705 | 6.0263 | 5.7821 | 5.6021 | 7.2747 | 7.2547 | 7.2368 | 7.1789 | 7.1042 | 7.0221 | 6.9147 | 6.78 | 6.6579 | 6.5968 | 6.1337 | 5.8947 | 5.7189
|  | CULLEN | HT |  |  |  |  | 7.3453 | 7.2653 | 7.1653 | 7.0589 | 6.9874 | 6.8979 | 6.7768 | 6.6874 | 6.5905 | 6.4958 | 6.1389 | 5.9326 | 5.7895 | 7.1126 | 7.0463 | 6.9663 | 6.8789 | 6.8179 | 6.7442 | 6.6463 | 6.5716 | 6.4905 | 6.4074 | 6.0768 | 5.8263 | 5.6211 | 7.2768 | 7.2568 | 7.2358 | 7.1379 | 7.0589 | 6.9611 | 6.8263 | 6.7274 | 6.6211 | 6.5168 | 6.1832 | 5.9379 | 5.7358
|  | CULLEN | HE |  |  |  |  | 7.3884 | 7.3284 | 7.2695 | 7.2021 | 7.16 | 7.1137 | 7.0137 | 6.9253 | 6.8432 | 6.8126 | 4.4011 | 4.2947 | 4.2253 | 7.1474 | 7.0968 | 7.0495 | 6.9926 | 6.9558 | 6.9137 | 6.8305 | 6.7589 | 6.6926 | 6.6674 | 4.7726 | 4.6526 | 4.5737 | 7.2853 | 7.2674 | 7.2526 | 7.2337 | 7.2105 | 7.1821 | 7.0947 | 6.9958 | 6.9053 | 6.8716 | 4.3989 | 4.2779 | 4.1989
|  | CULLEN | FB |  |  |  |  | 7.4305 | 7.4063 | 7.3789 | 7.3505 | 7.3242 | 7.2989 | 7.2737 | 7.2284 | 7.1632 | 7.1284 | 6.8895 | 6.6589 | 6.5568 | 7.1811 | 7.1611 | 7.1389 | 7.1158 | 7.0926 | 7.0726 | 7.0505 | 7.0137 | 6.9621 | 6.9337 | 6.7432 | 6.5611 | 6.4663 | 7.2958 | 7.2895 | 7.2821 | 7.2737 | 7.2653 | 7.2568 | 7.2474 | 7.2379 | 7.2284 | 7.2095 | 6.9484 | 6.6895 | 6.5747
| INVERNESS | CULLODEN | MINIMUM HEADROOM | NH 71240 45502 | NO | YES | 0.059184 | 14.4284 | 28.3263 | 28.0537 | 27.7874 | 27.6379 | 27.0937 | 26.7253 | 26.2863 | 25.8979 | 25.5411 | 24.4453 | 24.0158 | 23.7116 | 16.2105 | 28.5968 | 28.3074 | 27.9474 | 27.7389 | 26.8358 | 26.2389 | 25.5158 | 24.8611 | 24.2453 | 22.5589 | 21.8526 | 21.2632 | 15.9421 | 28.9647 | 28.4711 | 28.0026 | 27.7795 | 26.79 | 26.1384 | 25.3479 | 24.6626 | 24.0416 | 22.3374 | 21.6258 | 21.03
|  | CULLODEN | EE |  |  |  |  | 14.4284 | 28.3263 | 28.0537 | 27.7874 | 27.6379 | 27.4611 | 26.8116 | 26.3105 | 25.8989 | 25.7316 | 24.5747 | 24.1642 | 23.8716 | 16.2105 | 28.5968 | 28.3074 | 27.9474 | 27.7389 | 27.5021 | 26.4105 | 25.5674 | 24.8611 | 24.5905 | 22.5589 | 21.92 | 21.4505 | 15.9421 | 28.9647 | 28.4711 | 28.0026 | 27.7795 | 27.5289 | 26.33 | 25.4058 | 24.6626 | 24.3889 | 22.3374 | 21.6932 | 21.2195
|  | CULLODEN | HT |  |  |  |  | 14.4642 | 28.3758 | 28.0958 | 27.8295 | 27.6653 | 27.0937 | 26.7253 | 26.2863 | 25.8979 | 25.5411 | 24.4453 | 24.0158 | 23.7116 | 16.2484 | 28.6505 | 28.3537 | 28.0326 | 27.8053 | 26.8358 | 26.2389 | 25.5158 | 24.8611 | 24.2453 | 22.5726 | 21.8526 | 21.2632 | 16.0011 | 29.0511 | 28.5584 | 28.0984 | 27.8553 | 26.79 | 26.1384 | 25.3479 | 24.6637 | 24.0416 | 22.3521 | 21.6258 | 21.03
|  | CULLODEN | HE |  |  |  |  | 14.5442 | 28.4832 | 28.2505 | 28.0179 | 27.8916 | 27.5463 | 27.0526 | 26.6232 | 26.2663 | 26.1505 | 25.2411 | 24.9937 | 24.8221 | 16.3337 | 28.7642 | 28.5168 | 28.2705 | 28.14 | 27.6126 | 26.8011 | 26.0737 | 25.4768 | 25.2916 | 23.6116 | 23.2084 | 22.9232 | 16.1305 | 29.2342 | 28.8205 | 28.4184 | 28.2405 | 27.6447 | 26.7574 | 25.9584 | 25.3047 | 25.1016 | 23.3995 | 22.9921 | 22.7047
|  | CULLODEN | FB |  |  |  |  | 14.6558 | 28.6726 | 28.5474 | 28.4347 | 28.3684 | 28.3 | 28.0179 | 27.7116 | 27.4958 | 27.42 | 26.7084 | 26.4432 | 26.2568 | 16.4505 | 28.9621 | 28.8284 | 28.7095 | 28.64 | 28.5684 | 28.2663 | 27.7547 | 27.3884 | 27.2779 | 26.0874 | 25.6905 | 25.3958 | 16.3053 | 29.5195 | 29.3058 | 29.1153 | 29.01 | 28.9016 | 28.3658 | 27.7816 | 27.3795 | 27.2605 | 25.9553 | 25.5268 | 25.2058
| CRAIGIEBUCKLER | CULTER | MINIMUM HEADROOM | NJ 84009 00884 | NO | YES | 0 | 12.1021 | 12 | 11.7958 | 11.5874 | 11.3642 | 11.12 | 10.9358 | 10.8021 | 10.6263 | 10.4758 | 7.7716 | 6.9537 | 6.6632 | 11.1305 | 10.9137 | 10.68 | 10.4421 | 10.1884 | 9.9126 | 9.7074 | 9.5579 | 9.3611 | 9.1937 | 7.3074 | 6.0937 | 5.7653 | 11.6021 | 11.4442 | 11.2568 | 11.0221 | 10.7716 | 10.5 | 10.2968 | 10.1484 | 9.9537 | 9.7884 | 7.5053 | 6.0442 | 5.72
|  | CULTER | EE |  |  |  |  | 12.1021 | 12 | 11.7958 | 11.5874 | 11.3642 | 11.12 | 10.9358 | 10.8105 | 10.6853 | 10.5663 | 8.3274 | 6.9537 | 6.6632 | 11.1305 | 10.9137 | 10.68 | 10.4421 | 10.1884 | 9.9126 | 9.7074 | 9.5674 | 9.4295 | 9.2947 | 7.3074 | 6.0937 | 5.7653 | 11.6021 | 11.4442 | 11.2568 | 11.0221 | 10.7716 | 10.5 | 10.2968 | 10.1579 | 10.02 | 9.8874 | 7.5053 | 6.0442 | 5.72
|  | CULTER | HT |  |  |  |  | 12.1084 | 12.0411 | 11.8368 | 11.6337 | 11.38 | 11.1568 | 10.9558 | 10.8021 | 10.6263 | 10.4758 | 7.7716 | 7.3758 | 7.0863 | 11.1642 | 10.96 | 10.7284 | 10.4968 | 10.2084 | 9.9558 | 9.7295 | 9.5579 | 9.3611 | 9.1937 | 7.5895 | 6.4895 | 6.0768 | 11.6253 | 11.4779 | 11.3053 | 11.0768 | 10.7916 | 10.5421 | 10.3179 | 10.1484 | 9.9537 | 9.7884 | 7.8684 | 6.5716 | 6.1632
|  | CULTER | HE |  |  |  |  | 12.1263 | 12.0853 | 11.9674 | 11.7968 | 11.6053 | 11.3905 | 11.2189 | 11.1242 | 11.0095 | 10.9326 | 9.8316 | 9.26 | 9.1021 | 11.24 | 11.0674 | 10.8758 | 10.6821 | 10.4642 | 10.2221 | 10.0316 | 9.9253 | 9.7979 | 9.7105 | 8.6768 | 8.1684 | 7.9884 | 11.6811 | 11.5547 | 11.4189 | 11.2589 | 11.0453 | 10.8053 | 10.6168 | 10.5116 | 10.3853 | 10.2989 | 9.1105 | 8.5032 | 8.3253
|  | CULTER | FB |  |  |  |  | 12.1432 | 12.1305 | 12.1126 | 12.0916 | 12.0463 | 11.9347 | 11.8495 | 11.7958 | 11.7337 | 11.6642 | 11.3389 | 11.0716 | 10.9074 | 11.3621 | 11.2684 | 11.1653 | 11.0642 | 10.9653 | 10.8379 | 10.7411 | 10.68 | 10.6116 | 10.5337 | 10.1663 | 9.8632 | 9.6768 | 11.7232 | 11.7011 | 11.6274 | 11.5558 | 11.4842 | 11.3937 | 11.3179 | 11.2579 | 11.1895 | 11.1126 | 10.7495 | 10.4505 | 10.2663
| ELGIN | CUMMING STREET | MINIMUM HEADROOM | NJ 21542 63007 | NO | YES | 0.11531 | 21.5058 | 21.3268 | 21.1658 | 20.6511 | 20.5458 | 20.0637 | 19.9532 | 19.8279 | 19.6984 | 19.6111 | 19.2089 | 18.9363 | 18.6774 | 23.6442 | 23.5821 | 23.4537 | 22.8526 | 22.7063 | 21.9558 | 21.8021 | 21.6316 | 21.4463 | 21.3232 | 20.7505 | 20.3463 | 19.9621 | 24.5087 | 24.4645 | 24.3887 | 23.6203 | 23.4761 | 22.7361 | 22.5845 | 22.4139 | 22.2308 | 22.1087 | 21.5434 | 21.1582 | 20.7792
|  | CUMMING STREET | EE |  |  |  |  | 21.5058 | 21.3268 | 21.1711 | 20.6837 | 20.5795 | 20.09 | 19.9637 | 19.8279 | 19.6984 | 19.6111 | 19.2089 | 18.9363 | 18.6774 | 23.6442 | 23.5821 | 23.4589 | 22.9021 | 22.7558 | 22 | 21.8263 | 21.6316 | 21.4463 | 21.3232 | 20.7505 | 20.3463 | 19.9621 | 24.5087 | 24.4645 | 24.3971 | 23.6687 | 23.5245 | 22.7792 | 22.6066 | 22.4139 | 22.2308 | 22.1087 | 21.5434 | 21.1582 | 20.7792
|  | CUMMING STREET | HT |  |  |  |  | 21.5268 | 21.3479 | 21.1658 | 20.6511 | 20.5458 | 20.0637 | 19.9532 | 19.8458 | 19.7363 | 19.6374 | 19.2721 | 18.9447 | 18.7016 | 23.6526 | 23.5916 | 23.4537 | 22.8526 | 22.7063 | 21.9558 | 21.8021 | 21.6547 | 21.5032 | 21.3695 | 20.9663 | 20.4747 | 20.0316 | 24.515 | 24.4718 | 24.3887 | 23.6203 | 23.4761 | 22.7361 | 22.5845 | 22.4382 | 22.2887 | 22.1561 | 21.7708 | 21.2845 | 20.8476
|  | CUMMING STREET | HE |  |  |  |  | 21.5658 | 21.4068 | 21.2679 | 20.8153 | 20.7574 | 20.3174 | 20.2258 | 20.1405 | 20.05 | 20.0047 | 19.79 | 19.6089 | 19.4784 | 23.6653 | 23.6084 | 23.5547 | 23.0779 | 23.0147 | 22.3568 | 22.2379 | 22.1189 | 21.9926 | 21.9263 | 21.6158 | 21.3495 | 21.1558 | 24.5234 | 24.4824 | 24.4497 | 23.8687 | 23.7992 | 23.1318 | 23.0129 | 22.8961 | 22.7708 | 22.7045 | 22.3982 | 22.1361 | 21.9445
|  | CUMMING STREET | FB |  |  |  |  | 21.6553 | 21.5837 | 21.5174 | 21.3584 | 21.3226 | 21.1416 | 21.1068 | 21.0595 | 20.9911 | 20.9353 | 20.67 | 20.4142 | 20.2405 | 23.6979 | 23.6737 | 23.6505 | 23.6063 | 23.5874 | 23.4295 | 23.3947 | 23.3484 | 23.2811 | 23.2242 | 22.92 | 22.5547 | 22.2926 | 24.5476 | 24.5308 | 24.5139 | 24.4876 | 24.4708 | 24.3434 | 24.2992 | 24.2361 | 24.1424 | 24.0666 | 23.6982 | 23.3255 | 23.0666
| ST FILLANS | DALCHONZIE | MINIMUM HEADROOM | NN 74079 21921 | YES | YES | 0 | 4.6232 | 4.5979 | 4.5716 | 4.5389 | 4.5116 | 4.4821 | 4.4526 | 4.4242 | 4.3968 | 4.3684 | 4.2674 | 4.2 | 4.1516 | 6.1389 | 6.0737 | 6.0063 | 5.9126 | 5.86 | 5.7926 | 5.7221 | 5.6621 | 5.6074 | 5.5579 | 5.3695 | 5.2074 | 5.0737 | 5.8095 | 5.7568 | 5.7021 | 5.6147 | 5.5621 | 5.4947 | 5.4263 | 5.3663 | 5.3116 | 5.2632 | 5.0758 | 4.9158 | 4.7832
|  | DALCHONZIE | EE |  |  |  |  | 4.6232 | 4.5979 | 4.5789 | 4.5516 | 4.5284 | 4.5011 | 4.4684 | 4.4389 | 4.4095 | 4.3916 | 4.3032 | 4.2389 | 4.1926 | 6.1389 | 6.0737 | 6.0211 | 5.9453 | 5.8958 | 5.8442 | 5.7768 | 5.6979 | 5.6232 | 5.5832 | 5.3695 | 5.2074 | 5.0789 | 5.8095 | 5.7568 | 5.7147 | 5.6474 | 5.5979 | 5.5463 | 5.48 | 5.4021 | 5.3274 | 5.2884 | 5.0758 | 4.9158 | 4.7895
|  | DALCHONZIE | HT |  |  |  |  | 4.6263 | 4.6011 | 4.5716 | 4.5389 | 4.5116 | 4.4821 | 4.4526 | 4.4242 | 4.3968 | 4.3684 | 4.2674 | 4.2 | 4.1516 | 6.1484 | 6.0821 | 6.0063 | 5.9126 | 5.86 | 5.7926 | 5.7221 | 5.6621 | 5.6074 | 5.5579 | 5.3916 | 5.22 | 5.0737 | 5.8168 | 5.7632 | 5.7021 | 5.6147 | 5.5621 | 5.4947 | 5.4263 | 5.3663 | 5.3116 | 5.2632 | 5.0979 | 4.9274 | 4.7832
|  | DALCHONZIE | HE |  |  |  |  | 4.6389 | 4.6179 | 4.6021 | 4.5779 | 4.5621 | 4.5389 | 4.5105 | 4.4884 | 4.4674 | 4.4579 | 4.4147 | 4.3821 | 4.3568 | 6.1811 | 6.1295 | 6.0842 | 6.0242 | 6 | 5.9695 | 5.9063 | 5.8505 | 5.7968 | 5.7737 | 5.6674 | 5.5789 | 5.5063 | 5.8442 | 5.8011 | 5.7653 | 5.7168 | 5.6947 | 5.6663 | 5.6074 | 5.5526 | 5.4989 | 5.4768 | 5.3705 | 5.2842 | 5.2126
|  | DALCHONZIE | FB |  |  |  |  | 4.6516 | 4.6442 | 4.6358 | 4.6263 | 4.6179 | 4.6095 | 4.6011 | 4.5895 | 4.5747 | 4.5642 | 4.5105 | 4.4632 | 4.4347 | 6.2168 | 6.1958 | 6.1726 | 6.1495 | 6.1316 | 6.1147 | 6.0968 | 6.0663 | 6.0221 | 5.9968 | 5.8463 | 5.7074 | 5.6168 | 5.8726 | 5.8558 | 5.8368 | 5.8179 | 5.8032 | 5.7884 | 5.7737 | 5.7484 | 5.7137 | 5.6926 | 5.5484 | 5.4116 | 5.3221
| NAIRN | DALCROSS | MINIMUM HEADROOM | NH 76333 51847 | NO | YES | 0 | 14.5037 | 14.2742 | 13.9889 | 13.6584 | 13.5542 | 12.2279 | 10.4353 | 8.7995 | 7.9616 | 7.4732 | 5.7984 | 5.5353 | 5.3363 | 13.56 | 13.2853 | 12.9558 | 12.5779 | 12.4663 | 10.8842 | 8.7653 | 6.8337 | 5.8432 | 5.2684 | 3.3768 | 3.0947 | 2.8789 | 13.8992 | 13.6255 | 13.2992 | 12.9255 | 12.8108 | 11.2466 | 9.1339 | 7.2076 | 6.2203 | 5.6466 | 3.7339 | 3.4434 | 3.2234
|  | DALCROSS | EE |  |  |  |  | 14.5037 | 14.2742 | 13.9889 | 13.6584 | 13.5542 | 13.4595 | 12.8258 | 11.4237 | 9.5216 | 8.0121 | 5.7984 | 5.5353 | 5.3363 | 13.56 | 13.2853 | 12.9558 | 12.5779 | 12.4663 | 12.3653 | 11.6284 | 9.9842 | 7.7421 | 5.9632 | 3.3768 | 3.0947 | 2.8789 | 13.8992 | 13.6255 | 13.2992 | 12.9255 | 12.8108 | 12.7097 | 11.9771 | 10.335 | 8.0961 | 6.3213 | 3.7339 | 3.4434 | 3.2234
|  | DALCROSS | HT |  |  |  |  | 14.5458 | 14.3268 | 14.0668 | 13.7553 | 13.6858 | 12.2279 | 10.4353 | 8.7995 | 7.9616 | 7.4732 | 6.3205 | 6.1595 | 6.0405 | 13.6032 | 13.3421 | 13.0379 | 12.68 | 12.6063 | 10.8842 | 8.7653 | 6.8337 | 5.8432 | 5.2684 | 3.9642 | 3.78 | 3.6158 | 13.9434 | 13.6845 | 13.3834 | 13.0318 | 12.9561 | 11.2466 | 9.1339 | 7.2076 | 6.2203 | 5.6466 | 4.3445 | 4.1561 | 3.9908
|  | DALCROSS | HE |  |  |  |  | 14.6363 | 14.4858 | 14.2932 | 14.0553 | 14.0342 | 13.7847 | 13.35 | 11.9742 | 9.9774 | 8.39 | 6.9111 | 6.8574 | 6.8153 | 13.7 | 13.5095 | 13.2758 | 12.9958 | 12.9726 | 12.68 | 12.1684 | 10.5411 | 8.1789 | 6.3 | 4.5526 | 4.4916 | 4.4421 | 14.0424 | 13.8571 | 13.6297 | 13.3561 | 13.3339 | 13.0487 | 12.5413 | 10.9182 | 8.5634 | 6.6908 | 4.9476 | 4.8876 | 4.8382
|  | DALCROSS | FB |  |  |  |  | 14.7016 | 14.6363 | 14.5521 | 14.4563 | 14.4458 | 14.4353 | 14.1711 | 13.93 | 13.2784 | 12.5658 | 10.1068 | 10.0468 | 10.0005 | 13.7811 | 13.6989 | 13.5916 | 13.4695 | 13.4579 | 13.4442 | 13.1316 | 12.8474 | 12.0779 | 11.2347 | 8.3263 | 8.2568 | 8.2042 | 14.1224 | 14.0424 | 13.9371 | 13.8192 | 13.8066 | 13.7939 | 13.4887 | 13.2118 | 12.4508 | 11.6108 | 8.7108 | 8.6424 | 8.5897
| TAYNUILT | DALMALLY | MINIMUM HEADROOM | NN 15538 26930 | YES | YES | 0 | 1.0168 | 1.0168 | 1.0147 | 1.0126 | 1.0095 | 1.0063 | 1.0032 | 0.99895 | 0.99684 | 0.99368 | 0.98526 | 0.97789 | 0.97368 | 1.0063 | 1.0042 | 1.0021 | 0.99789 | 0.99474 | 0.99053 | 0.98632 | 0.98316 | 0.98 | 0.97789 | 0.96737 | 0.96105 | 0.95579 | 1.0158 | 1.0137 | 1.0116 | 1.0074 | 1.0042 | 1 | 0.99579 | 0.99263 | 0.98947 | 0.98737 | 0.97789 | 0.97053 | 0.96526
|  | DALMALLY | EE |  |  |  |  | 1.0168 | 1.0168 | 1.0147 | 1.0126 | 1.0095 | 1.0063 | 1.0032 | 0.99895 | 0.99684 | 0.99368 | 0.98526 | 0.97895 | 0.97474 | 1.0063 | 1.0042 | 1.0021 | 0.99789 | 0.99474 | 0.99053 | 0.98632 | 0.98316 | 0.98 | 0.97789 | 0.96737 | 0.96105 | 0.95684 | 1.0158 | 1.0137 | 1.0116 | 1.0074 | 1.0042 | 1 | 0.99579 | 0.99263 | 0.98947 | 0.98737 | 0.97789 | 0.97053 | 0.96632
|  | DALMALLY | HT |  |  |  |  | 1.0179 | 1.0168 | 1.0147 | 1.0137 | 1.0105 | 1.0074 | 1.0053 | 1.0021 | 0.99789 | 0.99474 | 0.98526 | 0.97789 | 0.97368 | 1.0084 | 1.0053 | 1.0021 | 1 | 0.99579 | 0.99263 | 0.98947 | 0.98526 | 0.98211 | 0.97789 | 0.97053 | 0.96316 | 0.95579 | 1.0179 | 1.0147 | 1.0116 | 1.0095 | 1.0053 | 1.0021 | 0.99895 | 0.99474 | 0.99158 | 0.98737 | 0.98 | 0.97263 | 0.96526
|  | DALMALLY | HE |  |  |  |  | 1.0179 | 1.0179 | 1.0168 | 1.0158 | 1.0137 | 1.0126 | 1.0105 | 1.0095 | 1.0084 | 1.0084 | 1.0063 | 1.0011 | 0.99895 | 1.0095 | 1.0095 | 1.0074 | 1.0053 | 1.0021 | 1 | 0.99789 | 0.99684 | 0.99474 | 0.99368 | 0.99053 | 0.98632 | 0.98316 | 1.0179 | 1.0179 | 1.0168 | 1.0147 | 1.0116 | 1.0095 | 1.0074 | 1.0063 | 1.0042 | 1.0032 | 1 | 0.99579 | 0.99263
|  | DALMALLY | FB |  |  |  |  | 1.0179 | 1.0179 | 1.0179 | 1.0168 | 1.0168 | 1.0168 | 1.0158 | 1.0147 | 1.0137 | 1.0137 | 1.0095 | 1.0063 | 1.0032 | 1.0105 | 1.0095 | 1.0095 | 1.0074 | 1.0063 | 1.0053 | 1.0032 | 1.0021 | 1.0011 | 1 | 0.99368 | 0.99053 | 0.98632 | 1.0179 | 1.0179 | 1.0179 | 1.0168 | 1.0158 | 1.0147 | 1.0126 | 1.0116 | 1.0105 | 1.0095 | 1.0032 | 1 | 0.99579
| TAYNUILT | DALMALLY SCHOOL | MINIMUM HEADROOM | NN 17249 27128 | YES | YES | 0 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391
|  | DALMALLY SCHOOL | EE |  |  |  |  | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391
|  | DALMALLY SCHOOL | HT |  |  |  |  | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391
|  | DALMALLY SCHOOL | HE |  |  |  |  | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391
|  | DALMALLY SCHOOL | FB |  |  |  |  | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | -0.00078947 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.10929 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391 | 0.071391
| INVERNESS | DALNEIGH | MINIMUM HEADROOM | NH 65564 44955 | YES | YES | 0.28061 | 11.0305 | 10.7589 | 10.4042 | 10.1189 | 9.8979 | 8.1568 | 6.5768 | 5.3158 | 4.64 | 4.2863 | 2.9947 | 2.3126 | 1.8284 | 10.9095 | 10.6063 | 10.2063 | 9.8863 | 9.6432 | 7.6495 | 5.8389 | 4.3989 | 3.6326 | 3.24 | 1.9274 | 1.1874 | 0.50947 | 10.8937 | 10.5863 | 10.18 | 9.8558 | 9.6095 | 7.5821 | 5.7421 | 4.2779 | 3.5 | 3.1021 | 1.7716 | 1.0221 | 0.33579
|  | DALNEIGH | EE |  |  |  |  | 11.0305 | 10.7589 | 10.4042 | 10.1189 | 9.8979 | 9.6474 | 9.2842 | 7.5179 | 5.9021 | 4.7042 | 3.1137 | 2.4516 | 1.9547 | 10.9095 | 10.6063 | 10.2063 | 9.8863 | 9.6432 | 9.3716 | 8.9684 | 6.9432 | 5.0926 | 3.72 | 1.9274 | 1.1937 | 0.63895 | 10.8937 | 10.5863 | 10.18 | 9.8558 | 9.6095 | 9.3347 | 8.9263 | 6.8663 | 4.9863 | 3.5905 | 1.7716 | 1.0284 | 0.46632
|  | DALNEIGH | HT |  |  |  |  | 11.0905 | 10.8389 | 10.4916 | 10.2211 | 9.9832 | 8.1568 | 6.5768 | 5.3158 | 4.64 | 4.2863 | 2.9947 | 2.3126 | 1.8284 | 10.9768 | 10.6958 | 10.3063 | 10.0053 | 9.7442 | 7.6495 | 5.8389 | 4.3989 | 3.6326 | 3.24 | 2 | 1.1874 | 0.50947 | 10.9621 | 10.6768 | 10.2811 | 9.9768 | 9.7126 | 7.5821 | 5.7421 | 4.2779 | 3.5 | 3.1021 | 1.8453 | 1.0221 | 0.33579
|  | DALNEIGH | HE |  |  |  |  | 11.2126 | 11.0042 | 10.7179 | 10.5053 | 10.3411 | 10.1242 | 9.8358 | 7.9716 | 6.3011 | 5.1474 | 4.1895 | 3.7832 | 3.4916 | 11.1137 | 10.8832 | 10.56 | 10.3263 | 10.1484 | 9.9137 | 9.5979 | 7.4579 | 5.5389 | 4.2116 | 3.1274 | 2.6737 | 2.3463 | 11.1011 | 10.8674 | 10.54 | 10.3032 | 10.1242 | 9.8863 | 9.5663 | 7.3895 | 5.4389 | 4.0895 | 2.9884 | 2.5284 | 2.1958
|  | DALNEIGH | FB |  |  |  |  | 11.3389 | 11.2263 | 11.0589 | 10.94 | 10.8421 | 10.7421 | 10.5747 | 10.4147 | 9.5705 | 8.8042 | 6.8632 | 6.42 | 6.0842 | 11.2547 | 11.1274 | 10.9389 | 10.8063 | 10.6979 | 10.5863 | 10.3989 | 10.22 | 9.2505 | 8.3705 | 6.1516 | 5.6579 | 5.28 | 11.2432 | 11.1147 | 10.9232 | 10.7884 | 10.6789 | 10.5663 | 10.3758 | 10.1937 | 9.2084 | 8.3137 | 6.0579 | 5.5579 | 5.1737
| COUPAR ANGUS | DALRULZION | MINIMUM HEADROOM | NO 13498 58153 | NO | YES | 0 | 2.4842 | 2.4705 | 2.46 | 2.4474 | 2.4326 | 2.4158 | 2.3989 | 2.3821 | 2.3568 | 2.3305 | 2.2305 | 2.1337 | 2.0621 | 2.7063 | 2.6789 | 2.6505 | 2.6105 | 2.5737 | 2.5347 | 2.4947 | 2.4558 | 2.4232 | 2.3905 | 2.2695 | 2.1526 | 2.0663 | 2.7126 | 2.6905 | 2.6653 | 2.6284 | 2.5926 | 2.5579 | 2.5189 | 2.4842 | 2.4526 | 2.4211 | 2.2989 | 2.1789 | 2.0884
|  | DALRULZION | EE |  |  |  |  | 2.4842 | 2.4705 | 2.46 | 2.4474 | 2.4326 | 2.4158 | 2.3989 | 2.3821 | 2.3568 | 2.3305 | 2.2305 | 2.1337 | 2.0621 | 2.7063 | 2.6789 | 2.6505 | 2.6105 | 2.5737 | 2.5347 | 2.4947 | 2.4558 | 2.4232 | 2.3905 | 2.2695 | 2.1526 | 2.0663 | 2.7126 | 2.6905 | 2.6653 | 2.6284 | 2.5926 | 2.5579 | 2.5189 | 2.4842 | 2.4526 | 2.4211 | 2.2989 | 2.1789 | 2.0884
|  | DALRULZION | HT |  |  |  |  | 2.4874 | 2.4768 | 2.4642 | 2.4537 | 2.44 | 2.4263 | 2.4126 | 2.3979 | 2.3842 | 2.3589 | 2.2358 | 2.1453 | 2.0853 | 2.7084 | 2.6895 | 2.6663 | 2.6368 | 2.5989 | 2.5621 | 2.5274 | 2.4884 | 2.4558 | 2.4179 | 2.2958 | 2.1716 | 2.0779 | 2.7137 | 2.7032 | 2.68 | 2.6547 | 2.6189 | 2.5863 | 2.5537 | 2.52 | 2.4884 | 2.4547 | 2.3347 | 2.2126 | 2.1189
|  | DALRULZION | HE |  |  |  |  | 2.4916 | 2.4853 | 2.4768 | 2.4684 | 2.4589 | 2.4453 | 2.4316 | 2.4221 | 2.4126 | 2.4084 | 2.3884 | 2.3674 | 2.3389 | 2.7116 | 2.7063 | 2.7 | 2.6863 | 2.6716 | 2.6526 | 2.6347 | 2.6137 | 2.5926 | 2.5758 | 2.5126 | 2.4463 | 2.4011 | 2.7168 | 2.7116 | 2.7053 | 2.6968 | 2.6832 | 2.6653 | 2.6474 | 2.6295 | 2.6084 | 2.5947 | 2.5358 | 2.4758 | 2.4337
|  | DALRULZION | FB |  |  |  |  | 2.4979 | 2.4937 | 2.4895 | 2.4853 | 2.4832 | 2.4789 | 2.4747 | 2.4695 | 2.4653 | 2.4589 | 2.44 | 2.4211 | 2.38 | 2.7179 | 2.7137 | 2.7105 | 2.7074 | 2.7 | 2.6884 | 2.6779 | 2.6663 | 2.6516 | 2.6326 | 2.5632 | 2.4874 | 2.4305 | 2.7232 | 2.7189 | 2.7158 | 2.7126 | 2.7105 | 2.7021 | 2.6926 | 2.6821 | 2.6695 | 2.6516 | 2.5905 | 2.5232 | 2.4716
| BOAT OF GARTEN | DALWHINNIE | MINIMUM HEADROOM | NN 63711 84671 | YES | YES | 0 | 1.0168 | 1.0095 | 1.0042 | 0.99579 | 0.98737 | 0.97895 | 0.96947 | 0.96105 | 0.95368 | 0.94737 | 0.92 | 0.89579 | 0.87684 | 0.98632 | 0.97789 | 0.97053 | 0.95895 | 0.94947 | 0.93895 | 0.92737 | 0.91684 | 0.90737 | 0.9 | 0.86526 | 0.83368 | 0.80842 | 0.98632 | 0.97789 | 0.97053 | 0.95895 | 0.94947 | 0.93895 | 0.92737 | 0.91684 | 0.90737 | 0.9 | 0.86526 | 0.83368 | 0.80842
|  | DALWHINNIE | EE |  |  |  |  | 1.0168 | 1.0095 | 1.0042 | 0.99579 | 0.98737 | 0.97895 | 0.96947 | 0.96105 | 0.95368 | 0.94737 | 0.92 | 0.89579 | 0.87684 | 0.98632 | 0.97789 | 0.97053 | 0.95895 | 0.94947 | 0.93895 | 0.92737 | 0.91684 | 0.90737 | 0.9 | 0.86526 | 0.83368 | 0.80842 | 0.98632 | 0.97789 | 0.97053 | 0.95895 | 0.94947 | 0.93895 | 0.92737 | 0.91684 | 0.90737 | 0.9 | 0.86526 | 0.83368 | 0.80842
|  | DALWHINNIE | HT |  |  |  |  | 1.0179 | 1.0116 | 1.0074 | 1.0011 | 0.99368 | 0.98421 | 0.97684 | 0.96947 | 0.96105 | 0.95263 | 0.92105 | 0.89579 | 0.88 | 0.98842 | 0.98105 | 0.97474 | 0.96737 | 0.95684 | 0.94526 | 0.93684 | 0.92737 | 0.91684 | 0.90737 | 0.87474 | 0.84105 | 0.81368 | 0.98842 | 0.98105 | 0.97474 | 0.96737 | 0.95684 | 0.94632 | 0.93684 | 0.92737 | 0.91684 | 0.90737 | 0.87474 | 0.84211 | 0.81474
|  | DALWHINNIE | HE |  |  |  |  | 1.0211 | 1.0179 | 1.0147 | 1.0105 | 1.0074 | 1.0011 | 0.99579 | 0.99263 | 0.98737 | 0.98316 | 0.97053 | 0.95684 | 0.94632 | 0.99263 | 0.98842 | 0.98421 | 0.98 | 0.97579 | 0.96947 | 0.96421 | 0.95895 | 0.95263 | 0.94737 | 0.93053 | 0.91263 | 0.9 | 0.99263 | 0.98842 | 0.98421 | 0.98 | 0.97579 | 0.96947 | 0.96421 | 0.95895 | 0.95263 | 0.94737 | 0.93053 | 0.91263 | 0.9
|  | DALWHINNIE | FB |  |  |  |  | 1.0242 | 1.0211 | 1.0189 | 1.0168 | 1.0137 | 1.0126 | 1.0095 | 1.0074 | 1.0042 | 1 | 0.98421 | 0.96737 | 0.95474 | 0.99579 | 0.99263 | 0.98947 | 0.98632 | 0.98316 | 0.98105 | 0.97789 | 0.97474 | 0.97053 | 0.96526 | 0.94421 | 0.92316 | 0.90632 | 0.99579 | 0.99263 | 0.98947 | 0.98632 | 0.98316 | 0.98105 | 0.97789 | 0.97474 | 0.97053 | 0.96526 | 0.94421 | 0.92316 | 0.90632
| WILLOWDALE | DENBURN | MINIMUM HEADROOM | NJ 93484 06342 | NO | YES | 0 | 20.2279 | 20.1532 | 20.0689 | 19.9363 | 19.7942 | 19.6584 | 19.5258 | 19.3963 | 19.2784 | 19.1332 | 18.6574 | 18.1342 | 17.7405 | 19.1621 | 19.0789 | 18.9842 | 18.8337 | 18.6737 | 18.5221 | 18.3758 | 18.2305 | 18.1 | 17.9347 | 17.4032 | 16.8853 | 16.3758 | 19.6861 | 19.6029 | 19.5082 | 19.3555 | 19.1955 | 19.045 | 18.8976 | 18.7524 | 18.6208 | 18.4566 | 17.9229 | 17.4029 | 16.8924
|  | DENBURN | EE |  |  |  |  | 20.2279 | 20.1532 | 20.0689 | 19.9363 | 19.7942 | 19.6584 | 19.5258 | 19.3963 | 19.2784 | 19.1332 | 18.6574 | 18.1974 | 17.7774 | 19.1621 | 19.0789 | 18.9842 | 18.8337 | 18.6737 | 18.5221 | 18.3758 | 18.2305 | 18.1 | 17.9347 | 17.4032 | 16.8853 | 16.4084 | 19.6861 | 19.6029 | 19.5082 | 19.3555 | 19.1955 | 19.045 | 18.8976 | 18.7524 | 18.6208 | 18.4566 | 17.9229 | 17.4029 | 16.9239
|  | DENBURN | HT |  |  |  |  | 20.2479 | 20.1805 | 20.1111 | 20.0142 | 19.8658 | 19.7458 | 19.6268 | 19.5058 | 19.3847 | 19.2142 | 18.6616 | 18.1342 | 17.7405 | 19.1842 | 19.1095 | 19.0337 | 18.9253 | 18.7579 | 18.6242 | 18.4926 | 18.3579 | 18.2232 | 18.0326 | 17.5263 | 16.9326 | 16.3758 | 19.7082 | 19.6345 | 19.5576 | 19.4492 | 19.2818 | 19.1471 | 19.0155 | 18.8787 | 18.7439 | 18.5524 | 18.045 | 17.4503 | 16.8924
|  | DENBURN | HE |  |  |  |  | 20.2911 | 20.2342 | 20.1879 | 20.1363 | 20.0584 | 19.9868 | 19.9005 | 19.8289 | 19.7521 | 19.6584 | 19.3795 | 19.1311 | 18.9068 | 19.2326 | 19.1726 | 19.1211 | 19.0663 | 18.9811 | 18.9042 | 18.8116 | 18.7326 | 18.6474 | 18.5421 | 18.2295 | 17.9484 | 17.6937 | 19.7576 | 19.6976 | 19.6461 | 19.5903 | 19.505 | 19.4282 | 19.3355 | 19.2566 | 19.1713 | 19.0661 | 18.7513 | 18.4703 | 18.2145
|  | DENBURN | FB |  |  |  |  | 20.3079 | 20.2721 | 20.2353 | 20.1963 | 20.1489 | 20.1047 | 20.0626 | 20.0132 | 19.9563 | 19.8658 | 19.5732 | 19.2668 | 19.0079 | 19.2516 | 19.2126 | 19.1716 | 19.1295 | 19.0768 | 19.0274 | 18.9821 | 18.9274 | 18.8642 | 18.7632 | 18.4358 | 18.0895 | 17.7947 | 19.7766 | 19.7376 | 19.6966 | 19.6545 | 19.6018 | 19.5524 | 19.5061 | 19.4513 | 19.3882 | 19.2871 | 18.9587 | 18.6113 | 18.3155
| TAYNUILT | DERVAIG | MINIMUM HEADROOM | NM 42441 51227 | YES | YES | 0 | 3.7884 | 3.7316 | 3.6453 | 3.5726 | 3.5053 | 3.4316 | 3.3579 | 3.2926 | 3.2284 | 3.0832 | 1.0989 | -0.72421 | -0.86421 | 3.7832 | 3.7179 | 3.6221 | 3.5411 | 3.4663 | 3.3853 | 3.3053 | 3.2337 | 3.1632 | 2.9916 | 2.5147 | -0.096842 | -0.29579 | 3.8305 | 3.7674 | 3.6716 | 3.5916 | 3.5179 | 3.4368 | 3.3589 | 3.2884 | 3.2189 | 3.0568 | 2.5905 | -0.82842 | -1.0263
|  | DERVAIG | EE |  |  |  |  | 3.7884 | 3.7347 | 3.6453 | 3.5726 | 3.5053 | 3.4316 | 3.3579 | 3.2926 | 3.2284 | 5.0274 | 4.4547 | 0.33368 | 0.17684 | 3.7832 | 3.7232 | 3.6221 | 3.5411 | 3.4663 | 3.3853 | 3.3053 | 3.2337 | 3.1632 | 5.46 | 4.8116 | 1.5158 | 1.3484 | 3.8305 | 3.7716 | 3.6716 | 3.5916 | 3.5179 | 3.4368 | 3.3589 | 3.2884 | 3.2189 | 5.2316 | 4.5884 | 0.37895 | 0.2
|  | DERVAIG | HT |  |  |  |  | 3.8074 | 3.7316 | 3.6853 | 3.6274 | 3.56 | 3.4947 | 3.4284 | 3.3653 | 3.2505 | 3.0832 | 1.0989 | -0.72421 | -0.86421 | 3.8042 | 3.7179 | 3.6663 | 3.6042 | 3.5284 | 3.4558 | 3.3821 | 3.3116 | 3.1832 | 2.9916 | 2.5147 | -0.096842 | -0.29579 | 3.8505 | 3.7674 | 3.7168 | 3.6547 | 3.5811 | 3.5105 | 3.4379 | 3.3684 | 3.2432 | 3.0568 | 2.5905 | -0.82842 | -1.0263
|  | DERVAIG | HE |  |  |  |  | 3.8432 | 3.8074 | 3.7442 | 3.7116 | 3.6789 | 3.6379 | 3.5979 | 3.5632 | 3.5221 | 3.4895 | 3.0179 | 1.3453 | 1.2695 | 3.8442 | 3.8053 | 3.7326 | 3.6989 | 3.6632 | 3.62 | 3.5779 | 3.54 | 3.4958 | 3.4579 | 2.9147 | 1.6347 | 1.5484 | 3.8895 | 3.8516 | 3.7821 | 3.7474 | 3.7126 | 3.6695 | 3.6274 | 3.5895 | 3.5463 | 3.5095 | 2.9811 | 1.2695 | 1.1842
|  | DERVAIG | FB |  |  |  |  | 3.86 | 3.8389 | 3.8168 | 3.7789 | 3.7558 | 3.7326 | 3.7095 | 3.6874 | 3.6589 | 3.6221 | 3.3989 | 3.1305 | 3.0232 | 3.8632 | 3.8389 | 3.8147 | 3.7726 | 3.7463 | 3.7211 | 3.6958 | 3.6705 | 3.6379 | 3.5968 | 3.3421 | 3.0337 | 2.9105 | 3.9084 | 3.8863 | 3.8611 | 3.8189 | 3.7947 | 3.7695 | 3.7442 | 3.72 | 3.6884 | 3.6495 | 3.4011 | 3.1011 | 2.9811
| BEAULY | DINGWALL | MINIMUM HEADROOM | NH 53956 59680 | NO | YES | 0.73265 | 13.5216 | 13.4447 | 13.1932 | 12.8879 | 12.7363 | 11.8753 | 11.0153 | 10.1889 | 9.6668 | 9.5195 | 6.9026 | 6.4511 | 6.1058 | 11.7095 | 11.4916 | 11.2021 | 10.8526 | 10.6853 | 9.5137 | 8.52 | 7.5642 | 6.9663 | 6.8042 | 4.6105 | 4.1074 | 3.72 | 12.0613 | 11.8645 | 11.6087 | 11.3003 | 11.1487 | 10.3308 | 9.3792 | 8.4129 | 7.8087 | 7.6445 | 4.875 | 4.3645 | 3.9718
|  | DINGWALL | EE |  |  |  |  | 13.5216 | 13.4447 | 13.1932 | 12.8879 | 12.7363 | 12.57 | 12.0289 | 11.1742 | 10.3279 | 9.5374 | 6.9026 | 6.4511 | 6.1058 | 11.7095 | 11.4916 | 11.2021 | 10.8526 | 10.6853 | 10.5042 | 9.8884 | 8.9063 | 7.9326 | 7.0116 | 4.6105 | 4.1074 | 3.72 | 12.0613 | 11.8645 | 11.6087 | 11.3003 | 11.1487 | 10.9813 | 10.4392 | 9.5824 | 8.6097 | 7.6834 | 4.875 | 4.3645 | 3.9718
|  | DINGWALL | HT |  |  |  |  | 13.7374 | 13.6963 | 13.5311 | 13.2468 | 13.0921 | 11.8753 | 11.0153 | 10.1889 | 9.6668 | 9.5195 | 7.4784 | 7.0163 | 6.6932 | 11.9126 | 11.7084 | 11.4263 | 11.0979 | 10.9242 | 9.5137 | 8.52 | 7.5642 | 6.9663 | 6.8042 | 5.0958 | 4.5432 | 4.0842 | 12.4276 | 12.2476 | 11.9992 | 11.7087 | 11.5508 | 10.3308 | 9.3792 | 8.4129 | 7.8087 | 7.6445 | 5.6245 | 5.0655 | 4.6024
|  | DINGWALL | HE |  |  |  |  | 13.7479 | 13.7079 | 13.6732 | 13.4279 | 13.3258 | 13.0405 | 12.7289 | 11.8458 | 10.9742 | 10.1721 | 8.9879 | 8.7163 | 8.5163 | 11.9989 | 11.8295 | 11.5916 | 11.3084 | 11.1958 | 10.8705 | 10.5158 | 9.4916 | 8.4842 | 7.5505 | 6.4347 | 6.1295 | 5.9021 | 12.5034 | 12.3529 | 12.1445 | 11.8939 | 11.7887 | 11.5003 | 11.1866 | 10.2992 | 9.3434 | 8.3982 | 7.1224 | 6.8129 | 6.5834
|  | DINGWALL | FB |  |  |  |  | 13.7732 | 13.7574 | 13.7416 | 13.7247 | 13.7058 | 13.6626 | 13.4963 | 13.3205 | 12.9416 | 12.5153 | 11.3721 | 11.0711 | 10.8416 | 12.0821 | 11.9905 | 11.86 | 11.7179 | 11.6495 | 11.5779 | 11.3832 | 11.1779 | 10.7337 | 10.24 | 8.9211 | 8.5832 | 8.3211 | 12.5792 | 12.4992 | 12.3824 | 12.2582 | 12.1971 | 12.1329 | 11.9624 | 11.7834 | 11.3992 | 10.9718 | 9.7866 | 9.4445 | 9.1792
| CARRADALE 1 | DIPPEN | MINIMUM HEADROOM | NR 80026 37592 | YES | YES | 0 | 1.0189 | 1.0095 | 1.0011 | 0.98737 | 0.97789 | 0.96421 | 0.94842 | 0.93474 | 0.91684 | 0.90632 | 0.85684 | 0.82737 | 0.80737 | 0.80737 | 0.8 | 0.79368 | 0.78316 | 0.77684 | 0.76632 | 0.75474 | 0.74105 | 0.72316 | 0.71158 | 0.66526 | 0.62421 | 0.60211 | 0.76105 | 0.75053 | 0.74 | 0.72526 | 0.71474 | 0.69895 | 0.68 | 0.66211 | 0.64 | 0.62737 | 0.57263 | 0.53263 | 0.50947
|  | DIPPEN | EE |  |  |  |  | 1.0189 | 1.0095 | 1.0011 | 0.99158 | 0.98211 | 0.97053 | 0.95895 | 0.94842 | 0.93474 | 0.92737 | 0.86316 | 0.82737 | 0.80737 | 0.80737 | 0.8 | 0.79368 | 0.78737 | 0.78 | 0.77053 | 0.76105 | 0.75368 | 0.74105 | 0.73368 | 0.66526 | 0.62421 | 0.60211 | 0.76105 | 0.75053 | 0.74 | 0.72947 | 0.71895 | 0.70632 | 0.69368 | 0.68211 | 0.66421 | 0.65474 | 0.57263 | 0.53263 | 0.50947
|  | DIPPEN | HT |  |  |  |  | 1.0221 | 1.0126 | 1.0011 | 0.98737 | 0.97789 | 0.96421 | 0.94842 | 0.93474 | 0.91684 | 0.90632 | 0.85684 | 0.82842 | 0.80737 | 0.80947 | 0.80211 | 0.79368 | 0.78316 | 0.77684 | 0.76632 | 0.75474 | 0.74105 | 0.72316 | 0.71158 | 0.66947 | 0.63263 | 0.60421 | 0.76421 | 0.75368 | 0.74105 | 0.72526 | 0.71474 | 0.69895 | 0.68 | 0.66211 | 0.64 | 0.62737 | 0.57684 | 0.54 | 0.51158
|  | DIPPEN | HE |  |  |  |  | 1.0284 | 1.0221 | 1.0158 | 1.0084 | 1.0032 | 0.99579 | 0.98 | 0.97158 | 0.96105 | 0.95684 | 0.91789 | 0.90316 | 0.89263 | 0.81474 | 0.80947 | 0.80421 | 0.79789 | 0.79368 | 0.78737 | 0.77579 | 0.76947 | 0.76211 | 0.75789 | 0.72316 | 0.70842 | 0.69684 | 0.77263 | 0.76632 | 0.75895 | 0.75053 | 0.74421 | 0.73684 | 0.71895 | 0.70947 | 0.69684 | 0.69158 | 0.64211 | 0.62316 | 0.60842
|  | DIPPEN | FB |  |  |  |  | 1.0305 | 1.0274 | 1.0242 | 1.0189 | 1.0158 | 1.0116 | 1.0074 | 1.0021 | 0.99579 | 0.99158 | 0.95895 | 0.93263 | 0.91895 | 0.81579 | 0.81368 | 0.81053 | 0.80737 | 0.80526 | 0.80105 | 0.79895 | 0.79368 | 0.78947 | 0.78632 | 0.76421 | 0.73789 | 0.72421 | 0.77579 | 0.77158 | 0.76737 | 0.76211 | 0.75789 | 0.75263 | 0.74842 | 0.74211 | 0.73474 | 0.72947 | 0.69158 | 0.65684 | 0.63895
| BRORA | DORNOCH | MINIMUM HEADROOM | NH 79721 89953 | YES | YES | 0.05102 | 3.8937 | 3.8653 | 3.8421 | 3.82 | 3.7916 | 3.7147 | 3.6337 | 3.1758 | 2.9168 | 2.8579 | 2.5968 | 2.4095 | 2.2747 | 4.2832 | 4.1537 | 4.0526 | 3.9874 | 3.9232 | 3.3442 | 2.6832 | 2.0737 | 1.8011 | 1.7411 | 1.5053 | 1.3116 | 1.1326 | 4.4042 | 4.2811 | 4.1853 | 4.1232 | 4.0611 | 3.5147 | 2.8674 | 2.1958 | 1.8958 | 1.8326 | 1.5789 | 1.3716 | 1.1789
|  | DORNOCH | EE |  |  |  |  | 3.8937 | 3.8653 | 3.8421 | 3.82 | 3.7947 | 3.7621 | 3.7295 | 3.6558 | 3.5747 | 3.0368 | 2.6326 | 2.4526 | 2.3221 | 4.2832 | 4.1537 | 4.0526 | 3.9874 | 3.9232 | 3.8505 | 3.7842 | 3.2053 | 2.5432 | 1.9284 | 1.5053 | 1.3168 | 1.18 | 4.4042 | 4.2811 | 4.1853 | 4.1232 | 4.0611 | 3.9905 | 3.9274 | 3.3811 | 2.7179 | 2.0389 | 1.5789 | 1.3747 | 1.2274
|  | DORNOCH | HT |  |  |  |  | 3.8979 | 3.8695 | 3.8432 | 3.82 | 3.7916 | 3.7147 | 3.6337 | 3.1758 | 2.9168 | 2.8579 | 2.5968 | 2.4095 | 2.2747 | 4.3 | 4.1758 | 4.0768 | 4.0211 | 3.9516 | 3.3442 | 2.6832 | 2.0737 | 1.8011 | 1.7411 | 1.5189 | 1.3116 | 1.1326 | 4.42 | 4.3021 | 4.2084 | 4.1537 | 4.0874 | 3.5147 | 2.8674 | 2.1958 | 1.8958 | 1.8326 | 1.5947 | 1.3716 | 1.1789
|  | DORNOCH | HE |  |  |  |  | 3.9074 | 3.8811 | 3.8632 | 3.8432 | 3.8211 | 3.7926 | 3.7632 | 3.6916 | 3.6105 | 3.1053 | 2.9579 | 2.8526 | 2.78 | 4.3379 | 4.2274 | 4.1484 | 4.1105 | 4.0684 | 4.0253 | 3.9789 | 3.36 | 2.6442 | 2 | 1.8453 | 1.7347 | 1.6589 | 4.4558 | 4.3516 | 4.2758 | 4.24 | 4.1989 | 4.1558 | 4.1116 | 3.5274 | 2.8274 | 2.1137 | 1.9463 | 1.8263 | 1.7442
|  | DORNOCH | FB |  |  |  |  | 3.9211 | 3.9105 | 3.9 | 3.8916 | 3.8811 | 3.8726 | 3.8621 | 3.8526 | 3.8189 | 3.7811 | 3.6811 | 3.6421 | 3.62 | 4.3968 | 4.3432 | 4.2905 | 4.2653 | 4.2379 | 4.2105 | 4.1853 | 4.16 | 3.8884 | 3.5558 | 2.8021 | 2.6726 | 2.5758 | 4.5126 | 4.4611 | 4.4105 | 4.3874 | 4.3611 | 4.3347 | 4.3105 | 4.2863 | 4.0305 | 3.7168 | 2.9947 | 2.8547 | 2.7495
| CLACHAN | DOUGLAS PIER | MINIMUM HEADROOM | NS 19396 99616 | YES | YES | 0 | 1.0532 | 1.0437 | 1.0321 | 1.0153 | 0.99737 | 0.98263 | 0.96474 | 0.95105 | 0.93526 | 0.92158 | 0.87105 | 0.82053 | 0.78368 | 1.0511 | 1.0395 | 1.0258 | 1.0068 | 0.98684 | 0.97 | 0.95105 | 0.93526 | 0.91632 | 0.90158 | 0.84474 | 0.78684 | 0.74474 | 1.0447 | 1.0332 | 1.0205 | 1.0005 | 0.98053 | 0.96368 | 0.94474 | 0.92895 | 0.91105 | 0.89632 | 0.83842 | 0.78158 | 0.73947
|  | DOUGLAS PIER | EE |  |  |  |  | 1.0532 | 1.0437 | 1.0321 | 1.0153 | 0.99737 | 0.98263 | 0.96474 | 0.95105 | 0.93526 | 0.92158 | 0.87105 | 0.82053 | 0.78368 | 1.0511 | 1.0395 | 1.0258 | 1.0068 | 0.98684 | 0.97 | 0.95105 | 0.93526 | 0.91632 | 0.90158 | 0.84474 | 0.78684 | 0.74474 | 1.0447 | 1.0332 | 1.0205 | 1.0005 | 0.98053 | 0.96368 | 0.94474 | 0.92895 | 0.91105 | 0.89632 | 0.83842 | 0.78158 | 0.73947
|  | DOUGLAS PIER | HT |  |  |  |  | 1.0563 | 1.0468 | 1.0384 | 1.0247 | 1.0089 | 0.99421 | 0.97947 | 0.96368 | 0.94789 | 0.93421 | 0.87211 | 0.82368 | 0.79 | 1.0532 | 1.0426 | 1.0332 | 1.0195 | 1.0016 | 0.98474 | 0.96684 | 0.95 | 0.93211 | 0.91737 | 0.85842 | 0.80158 | 0.75316 | 1.0468 | 1.0374 | 1.0279 | 1.0132 | 0.99526 | 0.97842 | 0.96158 | 0.94474 | 0.92579 | 0.91105 | 0.85211 | 0.79526 | 0.74789
|  | DOUGLAS PIER | HE |  |  |  |  | 1.0637 | 1.0574 | 1.0511 | 1.0458 | 1.0384 | 1.0311 | 1.0237 | 1.0163 | 1.0068 | 0.99842 | 0.97105 | 0.94368 | 0.92579 | 1.0616 | 1.0553 | 1.0489 | 1.0426 | 1.0353 | 1.0268 | 1.0184 | 1.0111 | 1.0005 | 0.99105 | 0.95947 | 0.92895 | 0.90684 | 1.0563 | 1.0489 | 1.0426 | 1.0363 | 1.0289 | 1.0205 | 1.0132 | 1.0047 | 0.99421 | 0.98474 | 0.95316 | 0.92263 | 0.90158
|  | DOUGLAS PIER | FB |  |  |  |  | 1.0668 | 1.0626 | 1.0584 | 1.0542 | 1.05 | 1.0458 | 1.0405 | 1.0374 | 1.03 | 1.0216 | 0.99105 | 0.95737 | 0.93211 | 1.0658 | 1.0616 | 1.0563 | 1.0521 | 1.0468 | 1.0426 | 1.0363 | 1.0321 | 1.0247 | 1.0153 | 0.98053 | 0.94158 | 0.91105 | 1.0595 | 1.0553 | 1.05 | 1.0458 | 1.0405 | 1.0363 | 1.03 | 1.0268 | 1.0184 | 1.01 | 0.97421 | 0.93632 | 0.90579
| ARDMORE | DRIMORE | MINIMUM HEADROOM | NF 77377 40049 | YES | YES | 0 | 2.4642 | 2.4495 | 2.44 | 2.4263 | 2.4137 | 2.4011 | 2.3874 | 2.3758 | 2.3642 | 2.3547 | 2.3105 | 1.5768 | 1.5558 | 2.4589 | 2.4442 | 2.4326 | 2.4179 | 2.4032 | 2.3895 | 2.3747 | 2.3621 | 2.3484 | 2.3379 | 2.2947 | 1.6926 | 1.6684 | 2.4589 | 2.4442 | 2.4326 | 2.4179 | 2.4032 | 2.3895 | 2.3747 | 2.3621 | 2.3484 | 2.3379 | 2.2947 | 1.5474 | 1.5232
|  | DRIMORE | EE |  |  |  |  | 2.4642 | 2.4495 | 2.44 | 2.4263 | 2.4137 | 2.4011 | 2.3874 | 2.3758 | 2.3642 | 2.3547 | 2.3147 | 1.5768 | 1.5558 | 2.4589 | 2.4442 | 2.4326 | 2.4179 | 2.4032 | 2.3895 | 2.3747 | 2.3621 | 2.3484 | 2.3379 | 2.2947 | 1.6926 | 1.6684 | 2.4589 | 2.4442 | 2.4326 | 2.4179 | 2.4032 | 2.3895 | 2.3747 | 2.3621 | 2.3484 | 2.3379 | 2.2947 | 1.5474 | 1.5232
|  | DRIMORE | HT |  |  |  |  | 2.4663 | 2.4558 | 2.4442 | 2.4337 | 2.4221 | 2.4084 | 2.3968 | 2.3853 | 2.3747 | 2.3611 | 2.3105 | 1.7189 | 1.6968 | 2.4632 | 2.4505 | 2.4379 | 2.4253 | 2.4126 | 2.3989 | 2.3863 | 2.3737 | 2.3611 | 2.3463 | 2.3021 | 1.8126 | 1.7811 | 2.4632 | 2.4505 | 2.4379 | 2.4253 | 2.4126 | 2.3989 | 2.3863 | 2.3737 | 2.3611 | 2.3463 | 2.3021 | 1.6958 | 1.6632
|  | DRIMORE | HE |  |  |  |  | 2.4737 | 2.4663 | 2.4589 | 2.4516 | 2.4421 | 2.4326 | 2.4232 | 2.4158 | 2.4074 | 2.4032 | 2.3842 | 2.0895 | 2.0768 | 2.4716 | 2.4632 | 2.4547 | 2.4463 | 2.4368 | 2.4274 | 2.4158 | 2.4084 | 2.3989 | 2.3947 | 2.3726 | 2.1295 | 2.1147 | 2.4716 | 2.4632 | 2.4547 | 2.4474 | 2.4368 | 2.4274 | 2.4158 | 2.4084 | 2.4 | 2.3947 | 2.3726 | 2.0716 | 2.0558
|  | DRIMORE | FB |  |  |  |  | 2.48 | 2.4758 | 2.4705 | 2.4642 | 2.4589 | 2.4537 | 2.4484 | 2.4432 | 2.4368 | 2.4305 | 2.4074 | 2.3832 | 2.3653 | 2.4779 | 2.4726 | 2.4663 | 2.46 | 2.4547 | 2.4484 | 2.4421 | 2.4358 | 2.4295 | 2.4232 | 2.3958 | 2.3695 | 2.3495 | 2.4779 | 2.4726 | 2.4663 | 2.46 | 2.4547 | 2.4484 | 2.4421 | 2.4358 | 2.4295 | 2.4232 | 2.3968 | 2.3695 | 2.3495
| CEANNACROC | DRUMNADROCHIT | MINIMUM HEADROOM | NH 50306 29824 | YES | NO | 0 | 5.3821 | 5.2347 | 5.1747 | 5.1095 | 5.0389 | 4.6242 | 4.3084 | 4.0811 | 3.9642 | 3.8158 | 3.5168 | 3.3032 | 3.1168 | 5.3547 | 5.2011 | 5.1495 | 5.0905 | 5.0274 | 4.5137 | 4.1589 | 3.9074 | 3.7811 | 3.7137 | 3.4305 | 3.2453 | 3.0916 | 5.3758 | 5.2053 | 5.1379 | 5.0653 | 4.9842 | 4.5 | 4.1305 | 3.8684 | 3.7347 | 3.5684 | 3.2316 | 2.9884 | 2.7789
|  | DRUMNADROCHIT | EE |  |  |  |  | 5.3821 | 5.2347 | 5.1747 | 5.1095 | 5.0389 | 4.9684 | 4.9 | 4.3979 | 4.0589 | 3.8158 | 3.5168 | 3.3032 | 3.1168 | 5.3547 | 5.2011 | 5.1495 | 5.0905 | 5.0274 | 4.9621 | 4.9011 | 4.3463 | 3.9747 | 3.7137 | 3.4305 | 3.2453 | 3.0916 | 5.3758 | 5.2053 | 5.1379 | 5.0653 | 4.9842 | 4.9063 | 4.8316 | 4.2453 | 3.8516 | 3.5684 | 3.2316 | 2.9884 | 2.7789
|  | DRUMNADROCHIT | HT |  |  |  |  | 5.4084 | 5.2789 | 5.2368 | 5.1916 | 5.1379 | 4.6242 | 4.3084 | 4.0811 | 3.9642 | 3.9168 | 3.6958 | 3.5284 | 3.4095 | 5.3747 | 5.2326 | 5.1916 | 5.1463 | 5.0916 | 4.5137 | 4.1589 | 3.9074 | 3.7811 | 3.7316 | 3.5537 | 3.3779 | 3.2326 | 5.4042 | 5.2568 | 5.2095 | 5.1589 | 5.1 | 4.5 | 4.1305 | 3.8684 | 3.7347 | 3.6811 | 3.4832 | 3.2832 | 3.1147
|  | DRUMNADROCHIT | HE |  |  |  |  | 5.4347 | 5.3158 | 5.2874 | 5.2568 | 5.22 | 5.1832 | 5.1453 | 4.6211 | 4.2926 | 4.0863 | 3.9642 | 3.8558 | 3.7642 | 5.4042 | 5.2737 | 5.2474 | 5.2179 | 5.1821 | 5.1474 | 5.1095 | 4.5189 | 4.1516 | 3.92 | 3.8021 | 3.7011 | 3.62 | 5.4358 | 5.2979 | 5.2663 | 5.2326 | 5.1916 | 5.1537 | 5.1116 | 4.4989 | 4.1158 | 3.8737 | 3.7368 | 3.6137 | 3.5105
|  | DRUMNADROCHIT | FB |  |  |  |  | 5.4968 | 5.4411 | 5.4137 | 5.3968 | 5.3768 | 5.3568 | 5.3368 | 5.3179 | 5.0916 | 4.92 | 4.5895 | 4.4947 | 4.42 | 5.4716 | 5.4074 | 5.38 | 5.3621 | 5.34 | 5.3189 | 5.2989 | 5.2779 | 5.0221 | 4.8295 | 4.4589 | 4.3568 | 4.2768 | 5.5074 | 5.4411 | 5.4116 | 5.3916 | 5.3695 | 5.3463 | 5.3253 | 5.3032 | 5.0379 | 4.8389 | 4.4547 | 4.3474 | 4.2621
| GRUDIE BRIDGE | DRUMRUNIE | MINIMUM HEADROOM | NC 16664 05298 | YES | NO | 0 | 0.20947 | 0.20842 | 0.20737 | 0.20632 | 0.20526 | 0.20211 | 0.2 | 0.19789 | 0.19368 | 0.18947 | 0.17684 | 0.16632 | 0.15789 | 0.20632 | 0.20316 | 0.2 | 0.19474 | 0.19053 | 0.18526 | 0.18105 | 0.17579 | 0.17158 | 0.16737 | 0.15263 | 0.14105 | 0.13158 | 0.067368 | 0.066316 | 0.065263 | 0.063158 | 0.061053 | 0.057895 | 0.055789 | 0.053684 | 0.051579 | 0.049474 | 0.043158 | 0.037895 | 0.033684
|  | DRUMRUNIE | EE |  |  |  |  | 0.20947 | 0.20842 | 0.20737 | 0.20632 | 0.20526 | 0.20211 | 0.20105 | 0.19789 | 0.19368 | 0.18947 | 0.17684 | 0.16632 | 0.15789 | 0.20632 | 0.20316 | 0.2 | 0.19474 | 0.19053 | 0.18526 | 0.18105 | 0.17579 | 0.17158 | 0.16737 | 0.15263 | 0.14105 | 0.13158 | 0.067368 | 0.066316 | 0.065263 | 0.063158 | 0.061053 | 0.057895 | 0.056842 | 0.053684 | 0.051579 | 0.050526 | 0.043158 | 0.038947 | 0.034737
|  | DRUMRUNIE | HT |  |  |  |  | 0.21053 | 0.20947 | 0.20737 | 0.20632 | 0.20526 | 0.20211 | 0.2 | 0.19895 | 0.19684 | 0.19158 | 0.17684 | 0.16632 | 0.15895 | 0.20737 | 0.20421 | 0.20105 | 0.19895 | 0.19368 | 0.18737 | 0.18316 | 0.17895 | 0.17474 | 0.16947 | 0.15579 | 0.14316 | 0.13368 | 0.068421 | 0.067368 | 0.065263 | 0.064211 | 0.062105 | 0.057895 | 0.055789 | 0.054737 | 0.052632 | 0.049474 | 0.043158 | 0.037895 | 0.033684
|  | DRUMRUNIE | HE |  |  |  |  | 0.21053 | 0.21053 | 0.20842 | 0.20737 | 0.20632 | 0.20316 | 0.20316 | 0.20211 | 0.2 | 0.2 | 0.19789 | 0.19474 | 0.18737 | 0.20737 | 0.20737 | 0.20526 | 0.20316 | 0.20105 | 0.19789 | 0.19684 | 0.19474 | 0.19053 | 0.18947 | 0.18105 | 0.17263 | 0.16526 | 0.069474 | 0.068421 | 0.066316 | 0.065263 | 0.064211 | 0.061053 | 0.061053 | 0.06 | 0.056842 | 0.056842 | 0.053684 | 0.050526 | 0.048421
|  | DRUMRUNIE | FB |  |  |  |  | 0.21053 | 0.21053 | 0.21053 | 0.20947 | 0.20947 | 0.20947 | 0.20737 | 0.20737 | 0.20632 | 0.20632 | 0.20421 | 0.2 | 0.19368 | 0.20737 | 0.20737 | 0.20737 | 0.20632 | 0.20526 | 0.20421 | 0.20211 | 0.20105 | 0.19895 | 0.19789 | 0.18842 | 0.17895 | 0.17053 | 0.069474 | 0.068421 | 0.068421 | 0.067368 | 0.067368 | 0.067368 | 0.065263 | 0.065263 | 0.064211 | 0.064211 | 0.06 | 0.055789 | 0.053684
| STRATHLEVEN | DRYMEN | MINIMUM HEADROOM | NS 48494 88026 | YES | YES | 0 | 0.92947 | 0.88105 | 0.82632 | 0.76211 | 0.69158 | 0.62105 | 0.54737 | 0.48211 | 0.41368 | 0.34526 | -0.013684 | -0.32421 | -0.55789 | 0.92632 | 0.87579 | 0.81684 | 0.74842 | 0.67263 | 0.59684 | 0.51579 | 0.43263 | 0.37158 | 0.28421 | -0.050526 | -0.41895 | -0.75158 | 1.0116 | 0.95684 | 0.89579 | 0.82211 | 0.74211 | 0.66211 | 0.57895 | 0.50316 | 0.42526 | 0.34842 | 0.025263 | -0.34842 | -0.68737
|  | DRYMEN | EE |  |  |  |  | 0.92947 | 0.88105 | 0.82632 | 0.76211 | 0.69158 | 0.62105 | 0.54737 | 0.48211 | 0.41368 | 0.34526 | 0.092632 | -0.18947 | -0.44316 | 0.92632 | 0.87579 | 0.81684 | 0.74842 | 0.67263 | 0.59684 | 0.51684 | 0.44632 | 0.37158 | 0.29895 | 0.032632 | -0.27684 | -0.55368 | 1.0116 | 0.95684 | 0.89579 | 0.82211 | 0.74211 | 0.66211 | 0.57895 | 0.50316 | 0.42526 | 0.34842 | 0.067368 | -0.25789 | -0.55053
|  | DRYMEN | HT |  |  |  |  | 0.94316 | 0.90105 | 0.84632 | 0.78526 | 0.71158 | 0.64105 | 0.56737 | 0.49368 | 0.43158 | 0.35474 | -0.013684 | -0.32421 | -0.55789 | 0.93895 | 0.89158 | 0.83053 | 0.76211 | 0.68 | 0.6 | 0.51579 | 0.43263 | 0.37158 | 0.28421 | -0.050526 | -0.41895 | -0.75158 | 1.0263 | 0.97895 | 0.91789 | 0.84737 | 0.76421 | 0.68421 | 0.59895 | 0.51368 | 0.45474 | 0.36632 | 0.025263 | -0.34842 | -0.68737
|  | DRYMEN | HE |  |  |  |  | 0.96526 | 0.93474 | 0.89789 | 0.85368 | 0.80105 | 0.75158 | 0.69368 | 0.64421 | 0.59263 | 0.54105 | 0.35579 | 0.11474 | -0.087368 | 0.96316 | 0.92947 | 0.88947 | 0.84 | 0.78316 | 0.72737 | 0.66421 | 0.60842 | 0.55053 | 0.49158 | 0.29053 | 0.0094737 | -0.22 | 1.0516 | 1.0168 | 0.97579 | 0.92526 | 0.86842 | 0.81053 | 0.74632 | 0.68947 | 0.63053 | 0.57158 | 0.36526 | 0.076842 | -0.15789
|  | DRYMEN | FB |  |  |  |  | 0.98 | 0.96316 | 0.94421 | 0.92 | 0.89579 | 0.87158 | 0.84316 | 0.81579 | 0.78632 | 0.74947 | 0.61579 | 0.46 | 0.31895 | 0.98 | 0.95895 | 0.93895 | 0.91158 | 0.88421 | 0.85579 | 0.82526 | 0.79368 | 0.76 | 0.71789 | 0.56421 | 0.38526 | 0.22316 | 1.0674 | 1.0484 | 1.0274 | 1 | 0.97368 | 0.94421 | 0.91474 | 0.88316 | 0.84842 | 0.80737 | 0.65263 | 0.47263 | 0.30947
| DUNVEGAN | DRYNOCH | MINIMUM HEADROOM | NG 41080 31292 | YES | YES | 1.2245 | 2.4432 | 2.4137 | 2.3832 | 2.3432 | 2.3042 | 2.2642 | 2.2221 | 2.1874 | 2.1558 | 2.1263 | 0.58947 | 0.47789 | 0.38526 | 2.4232 | 2.3895 | 2.3568 | 2.3126 | 2.2695 | 2.2253 | 2.18 | 2.1421 | 2.1074 | 2.0758 | 0.82211 | 0.69684 | 0.6 | 2.4863 | 2.4747 | 2.4632 | 2.4232 | 2.3811 | 2.3368 | 2.2926 | 2.2558 | 2.2211 | 2.1884 | 0.66 | 0.52737 | 0.42105
|  | DRYNOCH | EE |  |  |  |  | 2.4432 | 2.4137 | 2.3832 | 2.3432 | 2.3042 | 2.2642 | 2.2221 | 2.1874 | 2.1558 | 2.1263 | 0.58947 | 0.47789 | 0.38526 | 2.4232 | 2.3895 | 2.3568 | 2.3126 | 2.2695 | 2.2253 | 2.18 | 2.1421 | 2.1074 | 2.0758 | 0.82211 | 0.69684 | 0.6 | 2.4863 | 2.4747 | 2.4632 | 2.4232 | 2.3811 | 2.3368 | 2.2926 | 2.2558 | 2.2211 | 2.1884 | 0.66 | 0.52737 | 0.42105
|  | DRYNOCH | HT |  |  |  |  | 2.4526 | 2.4274 | 2.3989 | 2.3674 | 2.3295 | 2.2926 | 2.2589 | 2.2253 | 2.1926 | 2.1568 | 0.88105 | 0.76842 | 0.68842 | 2.4326 | 2.4032 | 2.3726 | 2.3389 | 2.2958 | 2.2558 | 2.2179 | 2.1811 | 2.1453 | 2.1074 | 1.0789 | 0.94947 | 0.84105 | 2.4874 | 2.4779 | 2.4653 | 2.4516 | 2.4105 | 2.3705 | 2.3337 | 2.2968 | 2.2621 | 2.2242 | 0.98105 | 0.84737 | 0.73368
|  | DRYNOCH | HE |  |  |  |  | 2.4726 | 2.4537 | 2.4368 | 2.4189 | 2.3958 | 2.3737 | 2.3516 | 2.3316 | 2.3095 | 2.2937 | 1.6632 | 1.5947 | 1.5421 | 2.4568 | 2.4337 | 2.4158 | 2.3979 | 2.3716 | 2.3495 | 2.3253 | 2.3032 | 2.2811 | 2.2621 | 1.7411 | 1.6674 | 1.6116 | 2.4926 | 2.4832 | 2.4758 | 2.4653 | 2.4526 | 2.4368 | 2.4221 | 2.4105 | 2.3926 | 2.3737 | 1.7526 | 1.6832 | 1.6242
|  | DRYNOCH | FB |  |  |  |  | 2.4853 | 2.4737 | 2.46 | 2.4484 | 2.4347 | 2.4211 | 2.4084 | 2.3968 | 2.3821 | 2.3611 | 2.2895 | 2.2147 | 2.1547 | 2.4695 | 2.4558 | 2.4421 | 2.4284 | 2.4137 | 2.3979 | 2.3842 | 2.3705 | 2.3537 | 2.3295 | 2.2484 | 2.1642 | 2.0947 | 2.5011 | 2.4968 | 2.4916 | 2.4874 | 2.4821 | 2.4779 | 2.4716 | 2.4674 | 2.4621 | 2.4442 | 2.3653 | 2.2832 | 2.2158
| KEITH 2 | DUFFTOWN | MINIMUM HEADROOM | NJ 32060 39722 | NO | YES | 0 | 6.1926 | 6.1768 | 6.16 | 15.69 | 15.6395 | 15.5553 | 15.4405 | 15.3616 | 15.2995 | 15.2553 | 14.1816 | 13.7837 | 13.6647 | 5.7937 | 5.7779 | 5.76 | 19.5432 | 19.5095 | 19.4126 | 19.2789 | 19.1863 | 19.1168 | 19.0674 | 18.8211 | 17.7674 | 17.6305 | 6.1695 | 6.1284 | 6.0905 | 15.2074 | 15.1705 | 15.1147 | 14.9768 | 14.8832 | 14.8105 | 14.76 | 14.5042 | 13.2337 | 13.0926
|  | DUFFTOWN | EE |  |  |  |  | 6.1926 | 6.1768 | 6.16 | 15.6932 | 15.6742 | 15.6258 | 15.5479 | 15.4342 | 15.3321 | 15.2921 | 15.0363 | 13.7837 | 13.6647 | 5.7937 | 5.7779 | 5.76 | 19.5432 | 19.5253 | 19.4968 | 19.4095 | 19.2768 | 19.1589 | 19.1147 | 18.8211 | 17.7674 | 17.6305 | 6.1695 | 6.1284 | 6.0958 | 15.2305 | 15.1937 | 15.1516 | 15.0958 | 14.9768 | 14.8547 | 14.8084 | 14.5042 | 13.2337 | 13.0926
|  | DUFFTOWN | HT |  |  |  |  | 6.1979 | 6.1811 | 6.1632 | 15.69 | 15.6395 | 15.5553 | 15.4405 | 15.3616 | 15.2995 | 15.2553 | 14.1816 | 14.0384 | 13.9342 | 5.7989 | 5.7821 | 5.7642 | 19.5453 | 19.5095 | 19.4126 | 19.2789 | 19.1863 | 19.1168 | 19.0674 | 18.8811 | 18.0158 | 17.8653 | 6.18 | 6.1379 | 6.0905 | 15.2074 | 15.1705 | 15.1147 | 14.9768 | 14.8832 | 14.8105 | 14.76 | 14.5674 | 13.5295 | 13.3726
|  | DUFFTOWN | HE |  |  |  |  | 6.2053 | 6.1926 | 6.1821 | 15.7184 | 15.7016 | 15.6816 | 15.6489 | 15.5584 | 15.4784 | 15.4584 | 15.3342 | 14.8184 | 14.77 | 5.8063 | 5.7937 | 5.7832 | 19.5695 | 19.5526 | 19.5326 | 19.5105 | 19.4179 | 19.3263 | 19.3032 | 19.1589 | 18.7211 | 18.6653 | 6.1895 | 6.1695 | 6.1442 | 15.2884 | 15.2642 | 15.2368 | 15.1695 | 15.1126 | 15.0274 | 15.0042 | 14.8547 | 14.3295 | 14.2716
|  | DUFFTOWN | FB |  |  |  |  | 6.2126 | 6.2074 | 6.2021 | 15.7468 | 15.7405 | 15.7332 | 15.7268 | 15.7195 | 15.7132 | 15.7047 | 15.5668 | 15.4247 | 15.3542 | 5.8137 | 5.8084 | 5.8032 | 19.5979 | 19.5916 | 19.5842 | 19.5779 | 19.5705 | 19.5642 | 19.5558 | 19.4221 | 19.2558 | 19.1747 | 6.1968 | 6.1916 | 6.1863 | 15.3526 | 15.34 | 15.3263 | 15.3137 | 15.2895 | 15.2558 | 15.2379 | 15.1263 | 14.9537 | 14.8684
| BRACO | DUNBLANE | MINIMUM HEADROOM | NN 77907 01544 | NO | YES | 0.16327 | 14.8334 | 14.6376 | 14.3808 | 14.0797 | 13.7303 | 13.3861 | 13.0145 | 12.6471 | 12.2639 | 11.8587 | 9.3882 | 7.7439 | 6.3997 | 13.1032 | 12.8937 | 12.6147 | 12.2768 | 11.8947 | 11.5179 | 11.0821 | 10.6295 | 10.1558 | 9.6558 | 7.3558 | 5.2442 | 3.2832 | 13.8936 | 13.683 | 13.403 | 13.0799 | 12.6851 | 12.2609 | 11.803 | 11.3493 | 10.8767 | 10.3757 | 7.9283 | 5.8146 | 3.8514
|  | DUNBLANE | EE |  |  |  |  | 14.8334 | 14.6376 | 14.3808 | 14.1061 | 13.8113 | 13.4997 | 13.1629 | 12.8639 | 12.5576 | 12.2513 | 10.2787 | 8.9397 | 7.7324 | 13.1032 | 12.8937 | 12.6147 | 12.3158 | 11.9968 | 11.6589 | 11.2979 | 10.9368 | 10.5642 | 10.1884 | 8.1337 | 6.4663 | 4.9568 | 13.8936 | 13.683 | 13.403 | 13.1062 | 12.7841 | 12.4083 | 12.002 | 11.6346 | 11.2599 | 10.8799 | 8.6314 | 6.9514 | 5.4304
|  | DUNBLANE | HT |  |  |  |  | 14.8661 | 14.6724 | 14.3871 | 14.0797 | 13.7303 | 13.3861 | 13.0145 | 12.6471 | 12.2639 | 11.8587 | 9.3882 | 7.7439 | 6.3997 | 13.1368 | 12.9263 | 12.6147 | 12.2768 | 11.8947 | 11.5179 | 11.0821 | 10.6295 | 10.1558 | 9.6558 | 7.3558 | 5.2442 | 3.2832 | 13.9293 | 13.7209 | 13.4114 | 13.0799 | 12.6851 | 12.2609 | 11.803 | 11.3493 | 10.8767 | 10.3757 | 7.9283 | 5.8146 | 3.8514
|  | DUNBLANE | HE |  |  |  |  | 14.9629 | 14.8166 | 14.6113 | 14.3934 | 14.1418 | 13.8745 | 13.5892 | 13.3366 | 13.0724 | 12.8208 | 11.4776 | 10.3176 | 9.2566 | 13.2421 | 13.0853 | 12.8611 | 12.6221 | 12.3484 | 12.0589 | 11.7495 | 11.4726 | 11.1737 | 10.8568 | 9.3263 | 7.86 | 6.5147 | 14.0336 | 13.8778 | 13.6546 | 13.4188 | 13.1472 | 12.8609 | 12.5304 | 12.2188 | 11.8925 | 11.5736 | 9.9693 | 8.4999 | 7.1514
|  | DUNBLANE | FB |  |  |  |  | 15.0261 | 14.9492 | 14.8503 | 14.745 | 14.6282 | 14.5061 | 14.3692 | 14.2292 | 14.0808 | 13.9061 | 13.2239 | 12.4397 | 11.7492 | 13.3105 | 13.2263 | 13.1189 | 13.0021 | 12.8747 | 12.7411 | 12.5895 | 12.4368 | 12.2726 | 12.0811 | 11.3179 | 10.3326 | 9.4568 | 14.1009 | 14.0188 | 13.9114 | 13.7967 | 13.6714 | 13.5388 | 13.3904 | 13.2399 | 13.0778 | 12.8872 | 12.042 | 11.0578 | 10.183
| DUNOON | DUNOON | MINIMUM HEADROOM | NS 17135 77531 | NO | YES | 0 | 17.5789 | 17.2905 | 17.0747 | 16.8316 | 16.7263 | 16.5442 | 16.3789 | 16.2232 | 16.1168 | 15.9253 | 15.0905 | 14.7674 | 14.5253 | 19.0484 | 18.8211 | 18.5979 | 18.3232 | 18.2105 | 18.0095 | 17.8284 | 17.6558 | 17.5411 | 17.3284 | 16.3674 | 15.9895 | 15.6937 | 19.1947 | 19.1589 | 19.0926 | 18.7589 | 18.6274 | 18.3905 | 18.1811 | 17.9779 | 17.8453 | 17.5916 | 16.4663 | 16.0495 | 15.7337
|  | DUNOON | EE |  |  |  |  | 17.5789 | 17.4684 | 17.0747 | 16.8316 | 16.7263 | 16.5442 | 16.3789 | 16.2232 | 16.1168 | 16.0242 | 15.0905 | 14.7674 | 14.5253 | 19.0484 | 18.9558 | 18.5979 | 18.3232 | 18.2105 | 18.0095 | 17.8284 | 17.6558 | 17.5411 | 17.4411 | 16.3674 | 15.9895 | 15.6937 | 19.1947 | 19.1589 | 19.0926 | 18.7589 | 18.6274 | 18.3905 | 18.1811 | 17.9779 | 17.8453 | 17.7305 | 16.4663 | 16.0495 | 15.7337
|  | DUNOON | HT |  |  |  |  | 17.6084 | 17.2905 | 17.0947 | 16.9747 | 16.8684 | 16.7147 | 16.5558 | 16.3863 | 16.1989 | 15.9253 | 15.1684 | 14.8484 | 14.6211 | 19.0737 | 18.8211 | 18.62 | 18.4895 | 18.3737 | 18.2032 | 18.0284 | 17.8421 | 17.6337 | 17.3284 | 16.5611 | 16.1684 | 15.8379 | 19.2021 | 19.1684 | 19.1189 | 18.9663 | 18.8337 | 18.6316 | 18.4263 | 18.2053 | 17.9589 | 17.5916 | 16.6895 | 16.2568 | 15.8937
|  | DUNOON | HE |  |  |  |  | 17.6674 | 17.5863 | 17.2305 | 17.0337 | 16.9674 | 16.8379 | 16.7063 | 16.5779 | 16.5053 | 16.4547 | 15.6895 | 15.5158 | 15.3958 | 19.1211 | 19.0505 | 18.7726 | 18.5526 | 18.4821 | 18.3421 | 18.2 | 18.0579 | 17.98 | 17.9242 | 17.0589 | 16.8674 | 16.7305 | 19.2126 | 19.1779 | 19.1537 | 19.0379 | 18.9611 | 18.8011 | 18.6368 | 18.4695 | 18.38 | 18.3158 | 17.2568 | 17.0326 | 16.8747
|  | DUNOON | FB |  |  |  |  | 17.7021 | 17.6558 | 17.6053 | 17.4368 | 17.3453 | 17.2821 | 17.2116 | 17.1326 | 17.08 | 17.02 | 16.6484 | 16.2105 | 16.0389 | 19.1505 | 19.1126 | 19.0695 | 18.9368 | 18.8621 | 18.8095 | 18.7516 | 18.6674 | 18.6105 | 18.5442 | 18.1305 | 17.64 | 17.4484 | 19.2274 | 19.2137 | 19.1979 | 19.1821 | 19.1632 | 19.1453 | 19.1253 | 19.1063 | 19.0842 | 19.0421 | 18.5474 | 17.9526 | 17.7232
| DUNVEGAN | DUNVEGAN | MINIMUM HEADROOM | NG 27646 47150 | YES | YES | 0 | 3.6358 | 3.6221 | 3.6095 | 3.5832 | 3.5358 | 2.0474 | 0.82842 | -0.21789 | -0.69053 | -0.73789 | -0.94211 | -1.0958 | -1.2032 | 3.5863 | 3.5432 | 3.5011 | 3.4463 | 3.3937 | 1.6263 | 0.20526 | -1.0305 | -1.5863 | -1.6389 | -1.8505 | -2.0253 | -2.1642 | 3.1884 | 3.1484 | 3.1084 | 3.0579 | 3.0074 | 1.4211 | 0.19895 | -0.98526 | -1.54 | -1.5916 | -1.8032 | -1.9779 | -2.1158
|  | DUNVEGAN | EE |  |  |  |  | 3.6358 | 3.6221 | 3.6105 | 3.5832 | 3.5358 | 3.4853 | 3.4337 | 1.9937 | 0.75474 | -0.32105 | -0.92421 | -1.0768 | -1.1947 | 3.5863 | 3.5432 | 3.5011 | 3.4463 | 3.3937 | 3.3368 | 3.28 | 1.5705 | 0.12421 | -1.1463 | -1.8505 | -2.0253 | -2.1611 | 3.1884 | 3.1484 | 3.1084 | 3.0579 | 3.0074 | 2.9547 | 2.9011 | 1.3674 | 0.12526 | -1.1011 | -1.8032 | -1.9779 | -2.1137
|  | DUNVEGAN | HT |  |  |  |  | 3.6368 | 3.6232 | 3.6095 | 3.5937 | 3.5589 | 2.0474 | 0.82842 | -0.21789 | -0.69053 | -0.73789 | -0.94211 | -1.0958 | -1.2032 | 3.5968 | 3.5589 | 3.5232 | 3.4779 | 3.4211 | 1.6263 | 0.20526 | -1.0305 | -1.5863 | -1.6389 | -1.8263 | -2.0084 | -2.1642 | 3.1989 | 3.1621 | 3.1284 | 3.0853 | 3.0326 | 1.4211 | 0.19895 | -0.98526 | -1.54 | -1.5916 | -1.7789 | -1.9611 | -2.1158
|  | DUNVEGAN | HE |  |  |  |  | 3.6411 | 3.6284 | 3.6211 | 3.6074 | 3.5926 | 3.5747 | 3.5547 | 2.0063 | 0.67579 | -0.44 | -0.63263 | -0.72105 | -0.78842 | 3.6253 | 3.5968 | 3.5758 | 3.5505 | 3.5211 | 3.4926 | 3.4621 | 1.5821 | 0.027368 | -1.2926 | -1.5168 | -1.6189 | -1.6958 | 3.2242 | 3.1979 | 3.1779 | 3.1537 | 3.1253 | 3.0979 | 3.0684 | 1.38 | 0.046316 | -1.2463 | -1.4705 | -1.5716 | -1.6484
|  | DUNVEGAN | FB |  |  |  |  | 3.6484 | 3.6442 | 3.64 | 3.6347 | 3.6295 | 3.6242 | 3.6179 | 3.6126 | 2.9768 | 2.3863 | 1.0747 | 0.97263 | 0.88947 | 3.64 | 3.6242 | 3.6074 | 3.5895 | 3.5705 | 3.5526 | 3.5358 | 3.5189 | 2.7316 | 2.0232 | 0.49158 | 0.37368 | 0.27684 | 3.2389 | 3.2232 | 3.2084 | 3.1916 | 3.1737 | 3.1568 | 3.1411 | 3.1253 | 2.4063 | 1.7737 | 0.44632 | 0.34316 | 0.26
| DYCE | DYCE NORTH | MINIMUM HEADROOM | NJ 89092 12705 | NO | YES | 0 | 20.64 | 20.44 | 20.3358 | 20.2 | 20.0863 | 19.9453 | 19.8305 | 19.7221 | 19.6137 | 19.5042 | 19.1253 | 18.8253 | 18.5474 | 20.7853 | 20.5611 | 20.4453 | 20.2947 | 20.1684 | 20.0147 | 19.8895 | 19.7705 | 19.6516 | 19.5305 | 19.1147 | 18.7937 | 18.4884 | 21.1979 | 20.9726 | 20.8568 | 20.7063 | 20.58 | 20.4242 | 20.2968 | 20.1737 | 20.0516 | 19.9284 | 19.5032 | 19.1789 | 18.8674
|  | DYCE NORTH | EE |  |  |  |  | 20.64 | 20.44 | 20.3358 | 20.2 | 20.0863 | 19.9453 | 19.8305 | 19.7221 | 19.6137 | 19.5042 | 19.1253 | 18.8274 | 18.5547 | 20.7853 | 20.5611 | 20.4453 | 20.2947 | 20.1684 | 20.0147 | 19.8895 | 19.7705 | 19.6516 | 19.5305 | 19.1147 | 18.7937 | 18.4905 | 21.1979 | 20.9726 | 20.8568 | 20.7063 | 20.58 | 20.4242 | 20.2968 | 20.1737 | 20.0516 | 19.9284 | 19.5032 | 19.1789 | 18.8674
|  | DYCE NORTH | HT |  |  |  |  | 20.6474 | 20.5011 | 20.3989 | 20.28 | 20.1611 | 20.0674 | 19.9579 | 19.8326 | 19.7316 | 19.5958 | 19.2084 | 18.8253 | 18.5474 | 20.7926 | 20.6295 | 20.5179 | 20.3863 | 20.2547 | 20.1537 | 20.0326 | 19.8958 | 19.7853 | 19.6368 | 19.3 | 18.8789 | 18.4884 | 21.2063 | 21.0421 | 20.9305 | 20.7979 | 20.6663 | 20.5642 | 20.4432 | 20.3032 | 20.1916 | 20.0389 | 19.7 | 19.2674 | 18.8674
|  | DYCE NORTH | HE |  |  |  |  | 20.6926 | 20.6211 | 20.5589 | 20.4853 | 20.4105 | 20.2863 | 20.2063 | 20.1411 | 20.0684 | 19.9979 | 19.7547 | 19.5905 | 19.4411 | 20.8432 | 20.7653 | 20.6968 | 20.6158 | 20.5358 | 20.3989 | 20.3137 | 20.2432 | 20.1642 | 20.0842 | 19.8158 | 19.6337 | 19.4663 | 21.2558 | 21.1789 | 21.1095 | 21.0284 | 20.9484 | 20.8116 | 20.7253 | 20.6547 | 20.5758 | 20.4958 | 20.2232 | 20.0368 | 19.8653
|  | DYCE NORTH | FB |  |  |  |  | 21.2232 | 21.1337 | 21.0463 | 20.9821 | 20.9168 | 20.8505 | 20.7789 | 20.7295 | 20.6842 | 20.6211 | 20.3895 | 20.1716 | 20.0074 | 21.2695 | 21.2547 | 21.2411 | 21.1758 | 21.1032 | 21.0284 | 20.9484 | 20.8947 | 20.8453 | 20.7758 | 20.5189 | 20.2768 | 20.0937 | 21.7042 | 21.6737 | 21.6137 | 21.5684 | 21.5179 | 21.4432 | 21.3632 | 21.3084 | 21.2589 | 21.1884 | 20.9316 | 20.6884 | 20.5042
| THURSO | EDAY | MINIMUM HEADROOM | HY 56341 33422 | YES | YES | 0 | 0.99368 | 0.98947 | 0.98842 | 0.98421 | 0.97895 | -1.6526 | -4.2853 | -6.9147 | -9.5463 | -9.5484 | -12.1674 | -12.1747 | -12.1789 | 0.99263 | 0.98842 | 0.98632 | 0.98211 | 0.97684 | -1.6558 | -4.2884 | -6.9189 | -9.5505 | -9.5537 | -12.1705 | -12.1789 | -12.1832 | 0.99263 | 0.98842 | 0.98632 | 0.98211 | 0.97684 | -1.6558 | -4.2884 | -6.9189 | -9.5505 | -9.5526 | -12.1705 | -12.1789 | -12.1832
|  | EDAY | EE |  |  |  |  | 0.99368 | 0.98947 | 0.98842 | 0.98421 | 0.97895 | -1.6526 | -4.2853 | -6.9147 | -9.5463 | -9.5484 | -9.5611 | -9.5716 | -9.58 | 0.99263 | 0.98842 | 0.98632 | 0.98211 | 0.97684 | -1.6558 | -4.2884 | -6.9189 | -9.5505 | -9.5537 | -9.5663 | -9.5789 | -9.5895 | 0.99263 | 0.98842 | 0.98632 | 0.98211 | 0.97684 | -1.6558 | -4.2884 | -6.9189 | -9.5505 | -9.5526 | -9.5663 | -9.5789 | -9.5895
|  | EDAY | HT |  |  |  |  | 0.99474 | 0.99263 | 0.98947 | 0.98526 | 0.98105 | -1.6505 | -4.2811 | -6.9105 | -9.5432 | -9.5453 | -9.56 | -9.5705 | -9.5779 | 0.99474 | 0.99158 | 0.98737 | 0.98421 | 0.97895 | -1.6526 | -4.2842 | -6.9147 | -9.5463 | -9.5495 | -9.5632 | -9.5758 | -9.5863 | 0.99474 | 0.99158 | 0.98737 | 0.98421 | 0.97895 | -1.6526 | -4.2842 | -6.9147 | -9.5463 | -9.5495 | -9.5632 | -9.5758 | -9.5863
|  | EDAY | HE |  |  |  |  | 0.99684 | 0.99474 | 0.99368 | 0.99158 | 0.98842 | 0.98632 | 0.98421 | -1.6463 | -4.2758 | -6.9042 | -12.1674 | -12.1747 | -12.1789 | 0.99579 | 0.99474 | 0.99263 | 0.99053 | 0.98737 | 0.98526 | 0.98211 | -1.6474 | -4.2779 | -6.9063 | -12.1705 | -12.1789 | -12.1832 | 0.99579 | 0.99474 | 0.99263 | 0.99053 | 0.98737 | 0.98526 | 0.98211 | -1.6474 | -4.2779 | -6.9063 | -12.1705 | -12.1789 | -12.1832
|  | EDAY | FB |  |  |  |  | 0.99789 | 0.99684 | 0.99579 | 0.99368 | 0.99263 | 0.99053 | 0.98947 | 0.98842 | 0.98737 | 0.98421 | 0.97684 | 0.96842 | 0.96 | 0.99684 | 0.99579 | 0.99579 | 0.99263 | 0.99158 | 0.98947 | 0.98842 | 0.98632 | 0.98526 | 0.98316 | 0.97368 | 0.96421 | 0.95474 | 0.99684 | 0.99579 | 0.99579 | 0.99263 | 0.99158 | 0.98947 | 0.98842 | 0.98632 | 0.98526 | 0.98316 | 0.97368 | 0.96421 | 0.95474
| THURSO | EDAY TIDAL | MINIMUM HEADROOM | HY 54226 31320 | YES | YES | 0 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895
|  | EDAY TIDAL | EE |  |  |  |  | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895
|  | EDAY TIDAL | HT |  |  |  |  | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895
|  | EDAY TIDAL | HE |  |  |  |  | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895
|  | EDAY TIDAL | FB |  |  |  |  | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895 | 3.5895
| FIDDES | EDZELL | MINIMUM HEADROOM | NO 63500 70513 | YES | YES | 0.091837 | 3.8158 | 3.7389 | 3.6695 | 3.5916 | 3.2032 | 2.7905 | 2.2116 | 1.5547 | 0.79684 | 0.54842 | -0.075789 | -0.23368 | -0.34211 | 3.7726 | 3.6758 | 3.5905 | 3.4937 | 3.0158 | 2.5326 | 1.8547 | 1.0842 | 0.19474 | -0.087368 | -0.76421 | -0.95684 | -1.1116 | 3.7874 | 3.6916 | 3.6053 | 3.5095 | 3.0316 | 2.5495 | 1.8726 | 1.1042 | 0.21684 | -0.064211 | -0.74 | -0.93158 | -1.0863
|  | EDZELL | EE |  |  |  |  | 3.8158 | 3.7453 | 3.6779 | 3.5916 | 3.2032 | 2.7905 | 2.3768 | 1.8737 | 1.3347 | 1.0758 | 0.06 | -0.19263 | -0.3 | 3.7726 | 3.6842 | 3.6011 | 3.4937 | 3.0158 | 2.5326 | 2.0495 | 1.46 | 0.82842 | 0.52632 | -0.65263 | -0.94526 | -1.0674 | 3.7874 | 3.7 | 3.6168 | 3.5095 | 3.0316 | 2.5495 | 2.0674 | 1.4789 | 0.84842 | 0.54737 | -0.62842 | -0.92 | -1.0421
|  | EDZELL | HT |  |  |  |  | 3.8253 | 3.7389 | 3.6695 | 3.6179 | 3.2295 | 2.8189 | 2.2116 | 1.5547 | 0.79684 | 0.54842 | -0.075789 | -0.23368 | -0.34211 | 3.7842 | 3.6758 | 3.5905 | 3.5284 | 3.0474 | 2.5653 | 1.8547 | 1.0842 | 0.19474 | -0.087368 | -0.76421 | -0.95684 | -1.1116 | 3.7989 | 3.6916 | 3.6053 | 3.5432 | 3.0632 | 2.5832 | 1.8726 | 1.1042 | 0.21684 | -0.064211 | -0.74 | -0.93158 | -1.0863
|  | EDZELL | HE |  |  |  |  | 3.8505 | 3.7926 | 3.7453 | 3.6916 | 3.3295 | 2.9063 | 2.5095 | 2.0547 | 1.5621 | 1.32 | 0.77684 | 0.23368 | 0.041053 | 3.8147 | 3.7432 | 3.6853 | 3.6179 | 3.1611 | 2.6663 | 2.2021 | 1.6705 | 1.0926 | 0.80737 | 0.17368 | -0.46316 | -0.68632 | 3.8295 | 3.7589 | 3.7011 | 3.6337 | 3.1768 | 2.6832 | 2.22 | 1.6884 | 1.1126 | 0.82842 | 0.19579 | -0.44 | -0.66316
|  | EDZELL | FB |  |  |  |  | 3.8811 | 3.8505 | 3.8326 | 3.8032 | 3.6726 | 3.5116 | 3.3284 | 3.1253 | 2.8737 | 2.7116 | 2.4611 | 2.0021 | 1.7347 | 3.8526 | 3.8147 | 3.7916 | 3.7568 | 3.5895 | 3.3842 | 3.1568 | 2.9179 | 2.6232 | 2.4347 | 2.1442 | 1.6074 | 1.2947 | 3.8674 | 3.8295 | 3.8063 | 3.7716 | 3.6053 | 3.4 | 3.1737 | 2.9347 | 2.6411 | 2.4516 | 2.1621 | 1.6263 | 1.3147
| MILTON OF CRAIGIE | EDZELL STREET | MINIMUM HEADROOM | NO 47103 32070 | YES | YES | 0 | 9.8695 | 9.8021 | 9.7432 | 9.6842 | 9.6211 | 9.5495 | 9.4789 | 9.4242 | 9.3695 | 9.3137 | 9.0432 | 8.8589 | 8.7347 | 10.3032 | 10.2716 | 10.2463 | 10.2168 | 10.1811 | 10.1232 | 10.0463 | 9.9874 | 9.9284 | 9.8663 | 9.6274 | 9.4021 | 9.2295 | 10.4263 | 10.4 | 10.3716 | 10.3063 | 10.2379 | 10.1611 | 10.0853 | 10.0263 | 9.9674 | 9.9053 | 9.6663 | 9.4411 | 9.2674
|  | EDZELL STREET | EE |  |  |  |  | 9.8695 | 9.8021 | 9.7432 | 9.6842 | 9.6211 | 9.5495 | 9.4789 | 9.4242 | 9.3695 | 9.3137 | 9.1179 | 8.9421 | 8.8126 | 10.3032 | 10.2716 | 10.2463 | 10.2179 | 10.1842 | 10.1232 | 10.0463 | 9.9874 | 9.9284 | 9.8663 | 9.6526 | 9.4568 | 9.3116 | 10.4263 | 10.4 | 10.3716 | 10.3063 | 10.2379 | 10.1611 | 10.0853 | 10.0263 | 9.9674 | 9.9053 | 9.6905 | 9.4937 | 9.3495
|  | EDZELL STREET | HT |  |  |  |  | 9.8863 | 9.8274 | 9.7674 | 9.7095 | 9.6411 | 9.5821 | 9.5253 | 9.4663 | 9.4053 | 9.3337 | 9.0432 | 8.8589 | 8.7347 | 10.3084 | 10.28 | 10.2484 | 10.2168 | 10.1811 | 10.1484 | 10.1 | 10.0368 | 9.9705 | 9.8926 | 9.6274 | 9.4021 | 9.2295 | 10.4295 | 10.4053 | 10.3789 | 10.3358 | 10.2621 | 10.1989 | 10.1368 | 10.0747 | 10.0095 | 9.9316 | 9.6663 | 9.4411 | 9.2674
|  | EDZELL STREET | HE |  |  |  |  | 9.9337 | 9.8905 | 9.8558 | 9.8137 | 9.7663 | 9.7084 | 9.6579 | 9.6211 | 9.5842 | 9.5484 | 9.4379 | 9.3347 | 9.2642 | 10.3242 | 10.3 | 10.2821 | 10.2568 | 10.2284 | 10.1916 | 10.1537 | 10.1305 | 10.1063 | 10.0916 | 10.0116 | 9.8958 | 9.8158 | 10.4411 | 10.42 | 10.4042 | 10.3811 | 10.3558 | 10.3221 | 10.2863 | 10.2474 | 10.2084 | 10.1695 | 10.0495 | 9.9347 | 9.8547
|  | EDZELL STREET | FB |  |  |  |  | 9.9558 | 9.9284 | 9.9011 | 9.8716 | 9.84 | 9.8084 | 9.7758 | 9.7463 | 9.7179 | 9.6789 | 9.5632 | 9.4505 | 9.3695 | 10.3358 | 10.3253 | 10.3137 | 10.3 | 10.2863 | 10.2716 | 10.2568 | 10.2432 | 10.2284 | 10.2105 | 10.1379 | 10.0116 | 9.92 | 10.4516 | 10.4432 | 10.4337 | 10.4221 | 10.4116 | 10.3989 | 10.3874 | 10.3747 | 10.3442 | 10.3021 | 10.1758 | 10.0505 | 9.9589
| ELGIN | ELGIN | MINIMUM HEADROOM | NJ 21256 64664 | NO | YES | 0 | 10.5642 | 9.8484 | 9.5989 | 9.3526 | 9.0695 | 8.6926 | 8.0179 | 7.1053 | 5.9411 | 5.1316 | -10.4505 | -16.8474 | -20.9937 | 9.3558 | 8.5232 | 8.2432 | 7.9663 | 7.6474 | 7.2179 | 6.4095 | 5.34 | 3.9716 | 3.0253 | -12.2884 | -21.9779 | -27.7758 | 9.9221 | 9.1347 | 8.8516 | 8.5726 | 8.2516 | 7.8211 | 7.02 | 5.9516 | 4.5853 | 3.64 | -11.6453 | -21.3211 | -27.0895
|  | ELGIN | EE |  |  |  |  | 10.5642 | 9.8484 | 9.5989 | 9.3526 | 9.0695 | 8.6926 | 8.2842 | 7.6411 | 6.9611 | 6.6295 | -1.3621 | -6.8884 | -8.9537 | 9.3558 | 8.5232 | 8.2432 | 7.9663 | 7.6474 | 7.2179 | 6.7526 | 6.0105 | 5.2221 | 4.8389 | -4.5347 | -11.0042 | -13.4095 | 9.9221 | 9.1347 | 8.8516 | 8.5726 | 8.2516 | 7.8211 | 7.3537 | 6.6095 | 5.8189 | 5.4358 | -3.9274 | -10.3905 | -12.7958
|  | ELGIN | HT |  |  |  |  | 10.5895 | 9.9621 | 9.7116 | 9.4863 | 9.2042 | 8.8547 | 8.0179 | 7.1053 | 5.9411 | 5.1316 | -10.4505 | -16.8474 | -19.5811 | 9.3811 | 8.6516 | 8.3684 | 8.1158 | 7.7937 | 7.3895 | 6.4095 | 5.34 | 3.9716 | 3.0253 | -12.2884 | -21.9779 | -25.9811 | 9.9495 | 9.2642 | 8.9789 | 8.7263 | 8.4021 | 7.9979 | 7.02 | 5.9516 | 4.5853 | 3.64 | -11.6453 | -21.3211 | -25.3179
|  | ELGIN | HE |  |  |  |  | 10.6916 | 10.1558 | 10.0063 | 9.8632 | 9.6674 | 9.3726 | 9.0263 | 8.5316 | 7.9821 | 7.72 | 0.85895 | -3.1011 | -6.9411 | 9.4905 | 8.8632 | 8.6905 | 8.5263 | 8.3021 | 7.9632 | 7.5632 | 6.9832 | 6.3389 | 6.0316 | -2.0453 | -6.6979 | -11.2126 | 10.0568 | 9.4811 | 9.3084 | 9.1442 | 8.9211 | 8.5821 | 8.1821 | 7.6042 | 6.9611 | 6.6537 | -1.4084 | -6.0516 | -10.5568
|  | ELGIN | FB |  |  |  |  | 11.0653 | 10.9063 | 10.7674 | 10.6642 | 10.5463 | 10.3842 | 10.2232 | 10.0432 | 9.7968 | 9.6084 | -0.22421 | -12.9758 | -20.9937 | 9.9863 | 9.7642 | 9.5811 | 9.4621 | 9.3242 | 9.1358 | 8.9484 | 8.7389 | 8.4505 | 8.2305 | -3.3516 | -18.3463 | -27.7758 | 10.4832 | 10.2916 | 10.1337 | 10.0295 | 9.9105 | 9.7463 | 9.5653 | 9.3568 | 9.0684 | 8.8495 | -2.7116 | -17.6779 | -27.0895
| ARBROATH | ELLIOT DEPOT | MINIMUM HEADROOM | NO 62251 40381 | YES | YES | 0 | 1.6326 | 1.4189 | 1.2579 | 1.14 | 1.0768 | -0.53579 | -0.60632 | -0.67474 | -0.73053 | -0.78211 | -10.3642 | -18.9358 | -26.2505 | 0.68105 | 0.44105 | 0.26105 | 0.12737 | 0.058947 | -1.7968 | -1.8726 | -1.9463 | -2.0063 | -2.0621 | -10.9032 | -23.2147 | -31.8158 | 1.4053 | 1.16 | 0.97684 | 0.84 | 0.77158 | -1.1179 | -1.1947 | -1.2695 | -1.3295 | -1.3874 | -10.3811 | -22.74 | -31.3295
|  | ELLIOT DEPOT | EE |  |  |  |  | 1.6358 | 1.4189 | 1.2579 | 1.14 | 1.0768 | -0.53579 | -0.60632 | -0.67474 | -0.73053 | -0.78211 | -2.9295 | -4.5011 | -6.6232 | 0.68632 | 0.44105 | 0.26105 | 0.12737 | 0.058947 | -1.7968 | -1.8726 | -1.9463 | -2.0063 | -2.0621 | -4.5263 | -6.3263 | -8.7684 | 1.4095 | 1.16 | 0.97684 | 0.84 | 0.77158 | -1.1179 | -1.1947 | -1.2695 | -1.3295 | -1.3874 | -3.8947 | -5.7263 | -8.2126
|  | ELLIOT DEPOT | HT |  |  |  |  | 1.6326 | 1.4726 | 1.32 | 1.2116 | 1.1611 | -0.42737 | -0.46737 | -0.50526 | -0.54105 | -0.58421 | -10.3642 | -16.2537 | -19.1979 | 0.68105 | 0.50105 | 0.32947 | 0.20737 | 0.15368 | -1.6779 | -1.7211 | -1.7621 | -1.8011 | -1.8474 | -10.9032 | -19.1705 | -23.4674 | 1.4053 | 1.2211 | 1.0463 | 0.92211 | 0.86737 | -0.99474 | -1.0389 | -1.0811 | -1.12 | -1.1674 | -10.3811 | -18.6842 | -23
|  | ELLIOT DEPOT | HE |  |  |  |  | 1.6684 | 1.5705 | 1.4568 | 1.3821 | 1.3611 | -0.21474 | -0.24 | -0.26 | -0.28211 | -0.30105 | -2.3158 | -3.7684 | -5.8042 | 0.71895 | 0.60737 | 0.47684 | 0.39368 | 0.37053 | -1.4453 | -1.4716 | -1.4937 | -1.5168 | -1.5389 | -3.86 | -5.5347 | -7.8821 | 1.4432 | 1.3295 | 1.1979 | 1.1126 | 1.0895 | -0.75789 | -0.78526 | -0.80632 | -0.83053 | -0.85263 | -3.2147 | -4.9179 | -7.3063
|  | ELLIOT DEPOT | FB |  |  |  |  | 1.9789 | 1.8989 | 1.8126 | 1.7663 | 1.7389 | 1.7168 | 1.6979 | 1.68 | 1.6632 | 1.6421 | -7.8758 | -18.9358 | -26.2505 | 1.0768 | 0.98526 | 0.88632 | 0.83263 | 0.80316 | 0.77789 | 0.75684 | 0.73684 | 0.71895 | 0.69579 | -10.2863 | -23.2147 | -31.8158 | 1.8074 | 1.7137 | 1.6137 | 1.5589 | 1.5284 | 1.5032 | 1.4821 | 1.4621 | 1.4442 | 1.42 | -9.7547 | -22.74 | -31.3295
| DYCE | ELLON | MINIMUM HEADROOM | NJ 95510 30054 | NO | YES | 0.86327 | 13.2639 | 39.1442 | 39.06 | 38.5558 | 36.3821 | 34.2758 | 31.8989 | 31.4905 | 31.0747 | 30.8505 | 23.1758 | 20.5516 | 19.9116 | 11.4484 | 36.2747 | 35.7968 | 35.1463 | 32.4263 | 29.8053 | 26.9926 | 26.5316 | 26.0611 | 25.8137 | 16.9832 | 14.6042 | 13.8789 | 12.762 | 38.3263 | 37.9084 | 37.3347 | 34.7516 | 32.1253 | 29.3116 | 28.8484 | 28.3779 | 28.1284 | 19.2926 | 16.5274 | 15.7989
|  | ELLON | EE |  |  |  |  | 13.2639 | 39.1442 | 39.06 | 38.6663 | 36.4916 | 34.2758 | 31.8989 | 31.4905 | 31.0747 | 30.8505 | 23.28 | 20.5516 | 19.9116 | 11.4484 | 36.2747 | 35.8116 | 35.2842 | 32.5674 | 29.8053 | 26.9926 | 26.5316 | 26.0611 | 25.8137 | 16.9832 | 14.6042 | 13.8789 | 12.762 | 38.3263 | 37.9168 | 37.4505 | 34.8905 | 32.1253 | 29.3116 | 28.8484 | 28.3779 | 28.1284 | 19.2926 | 16.5274 | 15.7989
|  | ELLON | HT |  |  |  |  | 13.2839 | 39.1726 | 39.0768 | 38.5558 | 36.3821 | 36.0632 | 35.6484 | 35.2695 | 33.7779 | 31.1168 | 23.1758 | 20.8863 | 20.2758 | 11.5095 | 36.3568 | 35.7968 | 35.1463 | 32.4263 | 32.0495 | 31.5516 | 31.1 | 29.2442 | 26.1147 | 17.1653 | 15.0305 | 14.1589 | 12.8167 | 38.4032 | 37.9084 | 37.3347 | 34.7516 | 34.3747 | 33.8768 | 33.4232 | 31.5674 | 28.4368 | 19.5168 | 17.0474 | 16.1747
|  | ELLON | HE |  |  |  |  | 13.3387 | 39.2516 | 39.2053 | 39.14 | 37.08 | 34.9305 | 32.5505 | 32.2305 | 31.8716 | 31.74 | 24.5516 | 21.4368 | 21.0811 | 11.6979 | 36.6811 | 36.2979 | 35.8621 | 33.2621 | 30.5768 | 27.7189 | 27.3547 | 26.9442 | 26.7968 | 18.3811 | 15.8589 | 15.4505 | 12.9872 | 38.6937 | 38.36 | 37.9768 | 35.5916 | 32.9053 | 30.0463 | 29.6821 | 29.2716 | 29.1242 | 20.7063 | 17.5389 | 17.1305
|  | ELLON | FB |  |  |  |  | 13.3724 | 39.3242 | 39.2979 | 39.2705 | 39.24 | 38.8063 | 37.7853 | 36.4579 | 36.2621 | 36.1358 | 33.7589 | 31.4274 | 31.0568 | 12.0368 | 37.1947 | 37.0105 | 36.8505 | 36.3053 | 35.4032 | 34.1232 | 32.4568 | 32.2189 | 32.0695 | 29.1242 | 26.4063 | 25.9821 | 13.1314 | 39.0958 | 38.9832 | 38.8421 | 38.3705 | 37.5926 | 36.4526 | 34.7863 | 34.5474 | 34.3979 | 31.4516 | 28.7337 | 28.3084
| TAYNUILT | EREDINE | MINIMUM HEADROOM | NM 97142 09376 | YES | YES | 0 | 0.16421 | 0.11263 | 0.056842 | 0.0010526 | -0.056842 | -0.10842 | -0.16105 | -0.21263 | -0.26632 | -0.32316 | -0.68632 | -0.89789 | -1.1116 | 0.16421 | 0.11368 | 0.061053 | 0.0073684 | -0.048421 | -0.095789 | -0.14737 | -0.19684 | -0.24842 | -0.30211 | -0.61789 | -0.82 | -1.0232 | 0.16105 | 0.10842 | 0.052632 | -0.0031579 | -0.062105 | -0.11263 | -0.16632 | -0.21895 | -0.27263 | -0.32947 | -0.69789 | -0.91053 | -1.1263
|  | EREDINE | EE |  |  |  |  | 0.16421 | 0.11263 | 0.056842 | 0.0010526 | -0.056842 | -0.10842 | -0.16105 | -0.21263 | -0.26632 | -0.32316 | -0.68632 | -0.89789 | -1.1116 | 0.16421 | 0.11368 | 0.061053 | 0.0073684 | -0.048421 | -0.095789 | -0.14737 | -0.19684 | -0.24842 | -0.30211 | -0.61789 | -0.82 | -1.0232 | 0.16105 | 0.10842 | 0.052632 | -0.0031579 | -0.062105 | -0.11263 | -0.16632 | -0.21895 | -0.27263 | -0.32947 | -0.69789 | -0.91053 | -1.1263
|  | EREDINE | HT |  |  |  |  | 0.19579 | 0.18316 | 0.16842 | 0.15263 | 0.13579 | 0.12 | 0.10421 | 0.088421 | 0.071579 | 0.054737 | -0.16526 | -0.24737 | -0.31474 | 0.19474 | 0.18105 | 0.16632 | 0.15263 | 0.13684 | 0.12105 | 0.10632 | 0.090526 | 0.073684 | 0.057895 | -0.11158 | -0.19053 | -0.27053 | 0.19474 | 0.18 | 0.16421 | 0.14842 | 0.13158 | 0.11579 | 0.1 | 0.084211 | 0.066316 | 0.049474 | -0.15789 | -0.24105 | -0.32632
|  | EREDINE | HE |  |  |  |  | 0.19684 | 0.18421 | 0.16947 | 0.15263 | 0.13684 | 0.12211 | 0.10316 | 0.088421 | 0.072632 | 0.055789 | -0.076842 | -0.15789 | -0.24105 | 0.19474 | 0.18211 | 0.16842 | 0.15263 | 0.13789 | 0.12316 | 0.10526 | 0.091579 | 0.075789 | 0.06 | -0.054737 | -0.13368 | -0.21263 | 0.19474 | 0.18105 | 0.16632 | 0.14947 | 0.13263 | 0.11789 | 0.098947 | 0.084211 | 0.068421 | 0.051579 | -0.084211 | -0.16526 | -0.24947
|  | EREDINE | FB |  |  |  |  | 0.20526 | 0.20316 | 0.2 | 0.19579 | 0.19263 | 0.18947 | 0.18632 | 0.18316 | 0.18105 | 0.17789 | 0.16632 | 0.15158 | 0.14 | 0.20421 | 0.20105 | 0.19789 | 0.19474 | 0.19158 | 0.18737 | 0.18421 | 0.18105 | 0.17895 | 0.17474 | 0.16421 | 0.14947 | 0.13895 | 0.20421 | 0.20211 | 0.19895 | 0.19474 | 0.19263 | 0.18737 | 0.18316 | 0.18105 | 0.17789 | 0.17474 | 0.16211 | 0.14632 | 0.13474
| INVERNESS | ERROGIE | MINIMUM HEADROOM | NH 56674 22810 | YES | YES | 0 | 1.0316 | 1.0221 | 1.0095 | 0.99263 | 0.97474 | 0.95789 | 0.94316 | 0.92632 | 0.90737 | 0.89053 | 0.83158 | 0.76632 | 0.70105 | 1.0316 | 1.0179 | 1.0053 | 0.99053 | 0.97368 | 0.95789 | 0.94211 | 0.92632 | 0.90842 | 0.89053 | 0.83263 | 0.77053 | 0.70737 | 1.0221 | 1.0095 | 0.99789 | 0.98316 | 0.96526 | 0.94737 | 0.93368 | 0.91684 | 0.89789 | 0.88105 | 0.82316 | 0.75789 | 0.69263
|  | ERROGIE | EE |  |  |  |  | 1.0316 | 1.0221 | 1.0095 | 0.99263 | 0.97474 | 0.95789 | 0.94316 | 0.92632 | 0.90737 | 0.89053 | 0.83158 | 0.76632 | 0.70105 | 1.0316 | 1.0179 | 1.0053 | 0.99053 | 0.97368 | 0.95789 | 0.94211 | 0.92632 | 0.90842 | 0.89053 | 0.83263 | 0.77053 | 0.70737 | 1.0221 | 1.0095 | 0.99789 | 0.98316 | 0.96526 | 0.94737 | 0.93368 | 0.91684 | 0.89789 | 0.88105 | 0.82316 | 0.75789 | 0.69263
|  | ERROGIE | HT |  |  |  |  | 1.0368 | 1.0326 | 1.0305 | 1.0274 | 1.0232 | 1.0168 | 1.0116 | 1.0063 | 1.0011 | 0.99474 | 0.97053 | 0.94632 | 0.92632 | 1.0358 | 1.0337 | 1.0295 | 1.0253 | 1.0189 | 1.0137 | 1.0084 | 1.0032 | 0.99895 | 0.99368 | 0.97368 | 0.94947 | 0.92421 | 1.0295 | 1.0253 | 1.0211 | 1.0179 | 1.0116 | 1.0074 | 1.0032 | 0.99895 | 0.99263 | 0.98737 | 0.96526 | 0.94105 | 0.91368
|  | ERROGIE | HE |  |  |  |  | 1.0368 | 1.0337 | 1.0295 | 1.0274 | 1.0242 | 1.0221 | 1.0168 | 1.0116 | 1.0084 | 1.0021 | 0.98421 | 0.96 | 0.93474 | 1.0358 | 1.0347 | 1.0305 | 1.0263 | 1.0221 | 1.0189 | 1.0116 | 1.0074 | 1.0042 | 0.99895 | 0.98316 | 0.95895 | 0.93474 | 1.0295 | 1.0263 | 1.02 | 1.0168 | 1.0126 | 1.0095 | 1.0042 | 1 | 0.99579 | 0.99158 | 0.97579 | 0.95053 | 0.92632
|  | ERROGIE | FB |  |  |  |  | 1.0389 | 1.0379 | 1.0368 | 1.0368 | 1.0358 | 1.0347 | 1.0337 | 1.0337 | 1.0316 | 1.0316 | 1.0284 | 1.0242 | 1.0189 | 1.0379 | 1.0358 | 1.0358 | 1.0358 | 1.0358 | 1.0337 | 1.0337 | 1.0337 | 1.0316 | 1.0305 | 1.0263 | 1.0211 | 1.0168 | 1.0326 | 1.0305 | 1.0295 | 1.0295 | 1.0284 | 1.0263 | 1.0263 | 1.0253 | 1.0242 | 1.0221 | 1.0189 | 1.0158 | 1.0116
| ABERNETHY | ERROL | MINIMUM HEADROOM | NO 23206 23038 | NO | YES | 0.05102 | 5.2179 | 5.1347 | 5.0221 | 4.8874 | 4.8211 | 4.6453 | 4.5179 | 4.4032 | 4.2916 | 4.1821 | 1.0547 | -0.26 | -0.43158 | 5.1821 | 5.0642 | 4.9316 | 4.7747 | 4.7011 | 4.5063 | 4.3684 | 4.2442 | 4.1221 | 4.0032 | 0.72947 | -0.36421 | -0.55895 | 5.2926 | 5.1779 | 5.0495 | 4.8979 | 4.8242 | 4.6232 | 4.4811 | 4.3516 | 4.2253 | 4.1074 | 0.60947 | -0.74 | -0.93474
|  | ERROL | EE |  |  |  |  | 5.2179 | 5.1347 | 5.0221 | 4.8874 | 4.8211 | 4.6453 | 4.5179 | 4.4032 | 4.2916 | 4.2021 | 1.0547 | -0.26 | -0.43158 | 5.1821 | 5.0642 | 4.9316 | 4.7747 | 4.7011 | 4.5063 | 4.3684 | 4.2442 | 4.1221 | 4.02 | 0.72947 | -0.36421 | -0.55895 | 5.2926 | 5.1779 | 5.0495 | 4.8979 | 4.8242 | 4.6232 | 4.4811 | 4.3516 | 4.2253 | 4.1242 | 0.60947 | -0.74 | -0.93474
|  | ERROL | HT |  |  |  |  | 5.22 | 5.1589 | 5.0442 | 4.9042 | 4.8337 | 4.6621 | 4.5421 | 4.4126 | 4.2916 | 4.1821 | 2.1147 | 1.8716 | 1.7 | 5.2021 | 5.0926 | 4.96 | 4.7979 | 4.72 | 4.5263 | 4.3968 | 4.2558 | 4.1253 | 4.0032 | 3 | 2.0453 | 1.8 | 5.2968 | 5.2053 | 5.0768 | 4.9189 | 4.8421 | 4.6463 | 4.5116 | 4.3653 | 4.2295 | 4.1074 | 2.92 | 1.7621 | 1.5168
|  | ERROL | HE |  |  |  |  | 5.2358 | 5.2084 | 5.1337 | 5.0242 | 4.9789 | 4.8358 | 4.7326 | 4.64 | 4.5421 | 4.4737 | 1.9979 | 1.4168 | 1.3179 | 5.2568 | 5.1674 | 5.0632 | 4.9347 | 4.8863 | 4.7221 | 4.6053 | 4.5042 | 4.3968 | 4.3221 | 1.5811 | 1.0789 | 0.96632 | 5.3126 | 5.2779 | 5.1768 | 5.0526 | 5.0042 | 4.8442 | 4.7284 | 4.6232 | 4.5126 | 4.4337 | 1.6 | 0.99474 | 0.88211
|  | ERROL | FB |  |  |  |  | 5.2505 | 5.2389 | 5.2263 | 5.1832 | 5.1537 | 5.0958 | 5.0379 | 4.9874 | 4.9295 | 4.8832 | 4.64 | 4.4579 | 4.34 | 5.2768 | 5.2389 | 5.18 | 5.1168 | 5.0832 | 5.0168 | 4.9484 | 4.8895 | 4.8232 | 4.7705 | 4.4979 | 4.2989 | 4.1663 | 5.3274 | 5.3147 | 5.2916 | 5.2295 | 5.1968 | 5.1316 | 5.0663 | 5.0084 | 4.9442 | 4.8926 | 4.6137 | 4.4063 | 4.2705
| FASNAKYLE | FASNAKYLE | MINIMUM HEADROOM | NH 31948 29998 | YES | YES | 0 | 1.0032 | 0.99053 | 0.97579 | 0.96 | 0.94737 | 0.93053 | 0.91684 | 0.90105 | 0.88737 | 0.87474 | 0.82526 | 0.77579 | 0.73158 | 1.0011 | 0.98842 | 0.97579 | 0.96211 | 0.94737 | 0.93053 | 0.91684 | 0.9 | 0.88526 | 0.87158 | 0.82 | 0.76632 | 0.71789 | 0.99474 | 0.97789 | 0.96211 | 0.94421 | 0.92842 | 0.91158 | 0.89579 | 0.87684 | 0.86316 | 0.84737 | 0.79368 | 0.73789 | 0.68737
|  | FASNAKYLE | EE |  |  |  |  | 1.0032 | 0.99053 | 0.97579 | 0.96 | 0.94737 | 0.93053 | 0.91684 | 0.90105 | 0.88737 | 0.87474 | 0.82526 | 0.77579 | 0.73158 | 1.0011 | 0.98842 | 0.97579 | 0.96211 | 0.94737 | 0.93053 | 0.91684 | 0.9 | 0.88526 | 0.87158 | 0.82 | 0.76632 | 0.71789 | 0.99474 | 0.97789 | 0.96211 | 0.94421 | 0.92842 | 0.91158 | 0.89579 | 0.87684 | 0.86316 | 0.84737 | 0.79368 | 0.73789 | 0.68737
|  | FASNAKYLE | HT |  |  |  |  | 1.0063 | 1.0021 | 0.99263 | 0.98316 | 0.97474 | 0.96632 | 0.95789 | 0.94947 | 0.93789 | 0.92947 | 0.88947 | 0.86 | 0.83579 | 1.0063 | 0.99895 | 0.99053 | 0.98105 | 0.97053 | 0.96211 | 0.95474 | 0.94526 | 0.93474 | 0.92737 | 0.89579 | 0.86526 | 0.83474 | 1.0021 | 0.99263 | 0.98316 | 0.97158 | 0.96105 | 0.95158 | 0.94316 | 0.93263 | 0.92 | 0.91158 | 0.87474 | 0.83895 | 0.80632
|  | FASNAKYLE | HE |  |  |  |  | 1.0084 | 1.0042 | 1.0011 | 0.99684 | 0.98842 | 0.98105 | 0.97368 | 0.96632 | 0.96 | 0.95474 | 0.93368 | 0.91158 | 0.89368 | 1.0095 | 1.0042 | 1.0011 | 0.99474 | 0.98632 | 0.98 | 0.97263 | 0.96632 | 0.96 | 0.95474 | 0.93474 | 0.91158 | 0.89263 | 1.0074 | 1 | 0.99368 | 0.98632 | 0.97789 | 0.96947 | 0.96211 | 0.95368 | 0.94737 | 0.94105 | 0.91684 | 0.89053 | 0.87053
|  | FASNAKYLE | FB |  |  |  |  | 1.0116 | 1.0095 | 1.0084 | 1.0063 | 1.0053 | 1.0021 | 0.99895 | 0.99579 | 0.99263 | 0.98737 | 0.97263 | 0.95579 | 0.94211 | 1.0116 | 1.0105 | 1.0074 | 1.0063 | 1.0032 | 0.99895 | 0.99579 | 0.99158 | 0.98842 | 0.98211 | 0.96632 | 0.94737 | 0.93158 | 1.0116 | 1.0095 | 1.0053 | 1.0011 | 0.99684 | 0.99263 | 0.98947 | 0.98632 | 0.98211 | 0.97684 | 0.95895 | 0.93895 | 0.92316
| TUMMEL BRIDGE | FINCASTLE | MINIMUM HEADROOM | NN 87976 61147 | YES | YES | 0 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.098947 | 0.097895 | 0.096842 | 0.094737 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.095789 | 0.094737
|  | FINCASTLE | EE |  |  |  |  | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.096842 | 0.096842 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.096842
|  | FINCASTLE | HT |  |  |  |  | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.098947 | 0.097895 | 0.096842 | 0.094737 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.096842 | 0.095789 | 0.095789 | 0.094737
|  | FINCASTLE | HE |  |  |  |  | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.1 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.097895 | 0.098947 | 0.097895 | 0.097895 | 0.097895
|  | FINCASTLE | FB |  |  |  |  | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947
| SHETLAND | FIRTH | MINIMUM HEADROOM | HU4396874166 | YES | YES | 0 | 0.16526 | -0.58737 | -1.5611 | -2.7853 | -4.3053 | -5.8379 | -7.38 | -8.9305 | -8.9789 | -8.9905 | -9.0442 | -9.0779 | -9.1011 | -0.0021053 | -0.90526 | -2.0737 | -3.5295 | -5.2368 | -7.0389 | -8.8642 | -10.6989 | -10.7537 | -10.7663 | -10.82 | -10.8653 | -10.8905 | -0.052632 | -1.0011 | -2.2284 | -3.7579 | -5.5516 | -7.3579 | -9.1768 | -11.0063 | -11.0611 | -11.0737 | -11.1274 | -11.1726 | -11.1979
|  | FIRTH | EE |  |  |  |  | 0.16526 | -0.58737 | -1.5611 | -2.7768 | -4.2958 | -5.8168 | -7.3453 | -8.8789 | -8.9284 | -8.9379 | -9.0389 | -9.0779 | -9.1011 | -0.0021053 | -0.90526 | -2.0737 | -3.52 | -5.2263 | -7.0147 | -8.8221 | -10.6368 | -10.6937 | -10.7042 | -10.82 | -10.8653 | -10.8905 | -0.052632 | -1.0011 | -2.2284 | -3.7474 | -5.54 | -7.3337 | -9.1358 | -10.9453 | -11.0011 | -11.0116 | -11.1274 | -11.1726 | -11.1979
|  | FIRTH | HT |  |  |  |  | 0.16842 | -0.58316 | -1.5568 | -2.7853 | -4.3053 | -5.8379 | -7.38 | -8.9305 | -8.9789 | -8.9905 | -9.0442 | -9.0779 | -9.1011 | 0.0031579 | -0.9 | -2.0684 | -3.5295 | -5.2368 | -7.0389 | -8.8642 | -10.6989 | -10.7537 | -10.7663 | -10.8179 | -10.8568 | -10.8895 | -0.047368 | -0.99579 | -2.2232 | -3.7579 | -5.5516 | -7.3579 | -9.1768 | -11.0063 | -11.0611 | -11.0737 | -11.1253 | -11.1642 | -11.1968
|  | FIRTH | HE |  |  |  |  | 0.17684 | -0.57263 | -1.5432 | -2.7568 | -4.2737 | -5.7905 | -7.3305 | -8.8695 | -8.9189 | -8.9253 | -8.98 | -8.9968 | -9.0074 | 0.012632 | -0.88737 | -2.0526 | -3.4979 | -5.2011 | -6.9842 | -8.8063 | -10.6263 | -10.6842 | -10.6916 | -10.7547 | -10.7737 | -10.7853 | -0.036842 | -0.98211 | -2.2063 | -3.7242 | -5.5137 | -7.3032 | -9.1189 | -10.9337 | -10.9926 | -10.9989 | -11.0621 | -11.0811 | -11.0926
|  | FIRTH | FB |  |  |  |  | 0.75158 | 0.50737 | 0.18105 | -0.22316 | -0.70947 | -1.2747 | -1.9211 | -2.6537 | -2.6789 | -2.6842 | -2.7463 | -2.7905 | -2.8095 | 0.70211 | 0.40842 | 0.017895 | -0.46842 | -1.0526 | -1.7305 | -2.5063 | -3.3832 | -3.4105 | -3.4168 | -3.4842 | -3.5337 | -3.5547 | 0.68737 | 0.37895 | -0.031579 | -0.54211 | -1.1558 | -1.8684 | -2.6842 | -3.6042 | -3.6326 | -3.6389 | -3.7095 | -3.7611 | -3.7832
| FORT WILLIAM | FISHNISH | MINIMUM HEADROOM | NM 66623 42191 | YES | NO | 0 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105
|  | FISHNISH | EE |  |  |  |  | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105
|  | FISHNISH | HT |  |  |  |  | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105
|  | FISHNISH | HE |  |  |  |  | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105
|  | FISHNISH | FB |  |  |  |  | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105
| THURSO | FLOTTA | MINIMUM HEADROOM | NC 94318 95432 | YES | YES | 0 | -1.2768 | -1.2779 | -1.28 | -1.2821 | -1.2842 | -1.2863 | -1.2884 | -1.2905 | -1.28 | -1.2821 | 0.51158 | -1.1337 | -1.1337 | -1.2526 | -1.2537 | -1.2568 | -1.26 | -1.2621 | -1.2642 | -1.2674 | -1.2705 | -1.2568 | -1.2589 | 0.34526 | -0.49789 | -0.49789 | -1.2432 | -1.2442 | -1.2463 | -1.2484 | -1.2495 | -1.2516 | -1.2547 | -1.2568 | -1.2463 | -1.2484 | 0.85368 | -0.72947 | -0.72947
|  | FLOTTA | EE |  |  |  |  | -1.2768 | -1.2779 | -1.28 | -1.2821 | -1.2842 | -1.2863 | -1.2884 | -1.2905 | 0.51474 | 0.51474 | 0.51263 | 0.51053 | 0.50947 | -1.2526 | -1.2537 | -1.2568 | -1.26 | -1.2621 | -1.2642 | -1.2674 | -1.2705 | 0.34842 | 0.34842 | 0.34632 | 0.34421 | 0.34316 | -1.2432 | -1.2442 | -1.2463 | -1.2484 | -1.2495 | -1.2516 | -1.2547 | -1.2568 | 0.85684 | 0.85684 | 0.85474 | 0.85263 | 0.85158
|  | FLOTTA | HT |  |  |  |  | -1.2768 | -1.2779 | -1.28 | -1.2821 | 0.51895 | 0.51789 | 0.51684 | 0.51579 | 0.51579 | 0.51474 | 0.51158 | 0.50947 | 0.50842 | -1.2526 | -1.2537 | -1.2558 | -1.2589 | 0.35263 | 0.35158 | 0.35053 | 0.34947 | 0.34947 | 0.34842 | 0.34526 | 0.34316 | 0.34211 | -1.2432 | -1.2442 | -1.2453 | -1.2484 | 0.86105 | 0.86 | 0.85895 | 0.85789 | 0.85789 | 0.85684 | 0.85368 | 0.85158 | 0.85053
|  | FLOTTA | HE |  |  |  |  | -1.2758 | -1.2768 | -1.2768 | -1.2779 | -1.2789 | -1.2811 | -1.2821 | -1.2832 | 0.51684 | 0.51579 | 0.51474 | -1.1337 | -1.1337 | -1.2516 | -1.2526 | -1.2526 | -1.2537 | -1.2547 | -1.2568 | -1.2579 | -1.26 | 0.35053 | 0.34947 | 0.34842 | -0.49789 | -0.49789 | -1.2421 | -1.2432 | -1.2432 | -1.2442 | -1.2453 | -1.2474 | -1.2474 | -1.2495 | 0.85895 | 0.85789 | 0.85684 | -0.72947 | -0.72947
|  | FLOTTA | FB |  |  |  |  | -1.2747 | -1.2758 | -1.2768 | -1.2768 | -1.2768 | -1.2789 | -1.28 | -1.28 | -1.28 | -1.2821 | 0.51789 | 0.51684 | 0.51684 | -1.2495 | -1.2516 | -1.2526 | -1.2526 | -1.2526 | -1.2547 | -1.2558 | -1.2558 | -1.2568 | -1.2589 | 0.35158 | 0.35053 | 0.35053 | -1.2411 | -1.2421 | -1.2432 | -1.2432 | -1.2432 | -1.2453 | -1.2453 | -1.2453 | -1.2463 | -1.2484 | 0.86 | 0.85895 | 0.85895
| ELGIN | FOCHABERS | MINIMUM HEADROOM | NC 94318 95432 | NO | YES | 0 | 15.4911 | 15.3868 | 15.3153 | 15.1879 | 13.4889 | 11.8005 | 11.6911 | 11.4763 | 11.2079 | 10.6353 | 5.5774 | 5.3416 | 5.17 | 14.3916 | 14.2716 | 14.1895 | 14.0421 | 11.9958 | 9.98 | 9.8579 | 9.6095 | 9.2968 | 8.6274 | 2.7284 | 2.4032 | 2.2011 | 15.0624 | 14.9561 | 14.8824 | 14.7518 | 12.7118 | 10.6992 | 10.5782 | 10.3297 | 10.0182 | 9.3497 | 3.4697 | 3.1445 | 2.9434
|  | FOCHABERS | EE |  |  |  |  | 15.4911 | 15.3868 | 15.3153 | 15.2184 | 13.5205 | 11.8005 | 11.6911 | 11.4763 | 11.2079 | 11.1426 | 6.0574 | 5.3553 | 5.1837 | 14.3916 | 14.2716 | 14.1895 | 14.0779 | 12.0326 | 9.98 | 9.8579 | 9.6095 | 9.2968 | 9.2242 | 3.2221 | 2.4032 | 2.2084 | 15.0624 | 14.9561 | 14.8824 | 14.7834 | 12.7487 | 10.6992 | 10.5782 | 10.3297 | 10.0182 | 9.9445 | 3.9603 | 3.1445 | 2.9508
|  | FOCHABERS | HT |  |  |  |  | 15.5121 | 15.4142 | 15.3216 | 15.1879 | 13.4889 | 13.3689 | 13.0732 | 12.7479 | 11.8574 | 10.6353 | 5.5774 | 5.3416 | 5.17 | 14.4168 | 14.3032 | 14.1968 | 14.0421 | 11.9958 | 11.8589 | 11.5084 | 11.1221 | 10.0663 | 8.6274 | 2.7284 | 2.4484 | 2.2011 | 15.0845 | 14.9845 | 14.8897 | 14.7518 | 12.7118 | 12.5739 | 12.2245 | 11.8392 | 10.7845 | 9.3497 | 3.4697 | 3.1897 | 2.9434
|  | FOCHABERS | HE |  |  |  |  | 15.5605 | 15.4847 | 15.4321 | 15.3521 | 13.6816 | 11.9932 | 11.8637 | 11.7174 | 11.5247 | 11.4889 | 7.1363 | 6.2121 | 5.8268 | 14.4726 | 14.3863 | 14.3263 | 14.2347 | 12.2221 | 10.2032 | 10.0579 | 9.8884 | 9.6653 | 9.6253 | 4.4811 | 3.3926 | 2.9411 | 15.1339 | 15.0561 | 15.0024 | 14.9213 | 12.9382 | 10.9224 | 10.7771 | 10.6076 | 10.3855 | 10.3455 | 5.2171 | 4.1318 | 3.6813
|  | FOCHABERS | FB |  |  |  |  | 15.5974 | 15.5595 | 15.5268 | 15.4911 | 15.1963 | 14.6626 | 14.31 | 14.0837 | 13.9942 | 13.9542 | 12.7658 | 10.4111 | 9.9816 | 14.5158 | 14.4695 | 14.4326 | 14.3926 | 14.0379 | 13.3958 | 12.9726 | 12.7021 | 12.5958 | 12.5505 | 11.1253 | 8.34 | 7.8337 | 15.1729 | 15.1318 | 15.0992 | 15.0634 | 14.7497 | 14.1087 | 13.6866 | 13.4161 | 13.3108 | 13.2655 | 11.8434 | 9.0634 | 8.5603
| NAIRN | FORRES | MINIMUM HEADROOM | NJ 03362 59425 | NO | YES | 0.061224 | 16.9153 | 16.3174 | 15.6795 | 14.9226 | 14.1963 | 36.8347 | 36.0095 | 35.6916 | 35.1968 | 33.9558 | 26.6432 | 25.8442 | 25.4011 | 14.6705 | 13.9621 | 13.2042 | 12.3063 | 11.4474 | 33.3653 | 32.3916 | 32.0242 | 31.4421 | 29.9642 | 22.2432 | 20.8853 | 20.3726 | 15.2392 | 14.5782 | 13.8329 | 12.935 | 12.075 | 34.6179 | 33.6442 | 33.2768 | 32.6937 | 31.2158 | 23.2432 | 21.8221 | 21.3095
|  | FORRES | EE |  |  |  |  | 16.9153 | 16.3174 | 15.6795 | 14.9342 | 14.2195 | 36.8347 | 36.0095 | 35.6916 | 35.3305 | 35.1779 | 27.8032 | 25.8442 | 25.4011 | 14.6705 | 13.9621 | 13.2042 | 12.3168 | 11.4716 | 33.3653 | 32.3916 | 32.0242 | 31.6042 | 31.4316 | 23.2105 | 20.8853 | 20.3726 | 15.2392 | 14.5782 | 13.8329 | 12.9445 | 12.1003 | 34.6179 | 33.6442 | 33.2768 | 32.8568 | 32.6842 | 24.1474 | 21.8221 | 21.3095
|  | FORRES | HT |  |  |  |  | 16.9405 | 16.4195 | 15.7437 | 14.9226 | 14.1963 | 37.2642 | 36.7547 | 36.2505 | 35.1968 | 33.9558 | 26.6432 | 26.0705 | 25.6474 | 14.6979 | 14.0821 | 13.2821 | 12.3063 | 11.4474 | 33.8821 | 33.2842 | 32.6937 | 31.4421 | 29.9642 | 22.2432 | 21.18 | 20.5695 | 15.2655 | 14.6897 | 13.9108 | 12.935 | 12.075 | 35.1347 | 34.5358 | 33.9453 | 32.6937 | 31.2158 | 23.2432 | 22.1789 | 21.5684
|  | FORRES | HE |  |  |  |  | 17.03 | 16.5626 | 15.9784 | 15.2805 | 14.63 | 37.2737 | 36.4579 | 36.2495 | 35.9937 | 35.9137 | 30.1516 | 28.4326 | 27.7895 | 14.8032 | 14.2516 | 13.5568 | 12.7274 | 11.9579 | 33.8853 | 32.9221 | 32.6821 | 32.3863 | 32.2958 | 25.6211 | 23.5663 | 22.8011 | 15.3645 | 14.8487 | 14.1855 | 13.3561 | 12.5866 | 35.1389 | 34.1747 | 33.9358 | 33.64 | 33.5484 | 26.7463 | 24.6916 | 23.9263
|  | FORRES | FB |  |  |  |  | 17.2911 | 17.2321 | 16.9837 | 16.7721 | 16.5026 | 39.6821 | 39.2558 | 38.8221 | 38.6989 | 38.6021 | 37.1316 | 33.9853 | 33.3905 | 15.2516 | 15.0432 | 14.7474 | 14.4979 | 14.1789 | 36.7368 | 36.2295 | 35.7126 | 35.5695 | 35.46 | 33.7126 | 29.9411 | 29.2337 | 15.7824 | 15.5876 | 15.3129 | 15.0792 | 14.7813 | 37.9916 | 37.4842 | 36.9663 | 36.8242 | 36.7137 | 34.9653 | 31.1926 | 30.4853
| DOUNREAY | FORSS | MINIMUM HEADROOM | ND 02614 69148 | YES | YES | 0 | -2.7411 | -2.7526 | -2.7632 | -2.7779 | -2.7926 | -2.8084 | -2.8221 | -2.8337 | -2.8463 | -2.8568 | -2.9105 | -4.7905 | -5.7516 | -2.5905 | -2.6042 | -2.6147 | -2.6316 | -2.6463 | -2.6642 | -2.6789 | -2.6916 | -2.7063 | -2.7179 | -2.7663 | -4.2916 | -5.0379 | -2.6926 | -2.7042 | -2.7147 | -2.7295 | -2.7432 | -2.7589 | -2.7737 | -2.7842 | -2.7979 | -2.8074 | -2.8505 | -4.7537 | -5.7232
|  | FORSS | EE |  |  |  |  | -2.7411 | -2.7526 | -2.7632 | -2.7779 | -2.7926 | -2.8084 | -2.8221 | -2.8337 | -2.8463 | -2.8568 | -2.9 | -4.7905 | -4.8189 | -2.5905 | -2.6042 | -2.6147 | -2.6316 | -2.6463 | -2.6642 | -2.6789 | -2.6916 | -2.7063 | -2.7179 | -2.7663 | -4.2916 | -4.3221 | -2.6926 | -2.7042 | -2.7147 | -2.7295 | -2.7432 | -2.7589 | -2.7737 | -2.7842 | -2.7979 | -2.8074 | -2.8505 | -4.7537 | -4.7821
|  | FORSS | HT |  |  |  |  | -2.7389 | -2.7484 | -2.7579 | -2.7705 | -2.7863 | -2.7989 | -2.8126 | -2.8253 | -2.8389 | -2.8516 | -2.9105 | -4.4326 | -4.4568 | -2.5884 | -2.5989 | -2.6095 | -2.6232 | -2.64 | -2.6537 | -2.6684 | -2.6811 | -2.6968 | -2.7105 | -2.7642 | -3.9989 | -4.0326 | -2.6905 | -2.7 | -2.7105 | -2.7221 | -2.7379 | -2.7505 | -2.7632 | -2.7758 | -2.7895 | -2.8021 | -2.8495 | -4.3853 | -4.4168
|  | FORSS | HE |  |  |  |  | -2.7316 | -2.7389 | -2.7453 | -2.7505 | -2.7579 | -2.7674 | -2.7747 | -2.7832 | -2.7905 | -2.7958 | -2.82 | -3.5811 | -5.7516 | -2.5811 | -2.5884 | -2.5958 | -2.6011 | -2.6095 | -2.6189 | -2.6263 | -2.6358 | -2.6432 | -2.6495 | -2.6747 | -3.2905 | -5.0379 | -2.6842 | -2.6905 | -2.6968 | -2.7021 | -2.7105 | -2.7189 | -2.7263 | -2.7347 | -2.7421 | -2.7474 | -2.7716 | -3.5368 | -5.7232
|  | FORSS | FB |  |  |  |  | -2.7263 | -2.7316 | -2.7358 | -2.74 | -2.7453 | -2.7484 | -2.7537 | -2.7589 | -2.7642 | -2.7705 | -2.7958 | -2.8221 | -2.8411 | -2.5758 | -2.5811 | -2.5853 | -2.5905 | -2.5958 | -2.6 | -2.6053 | -2.6105 | -2.6168 | -2.6232 | -2.6505 | -2.68 | -2.7021 | -2.6789 | -2.6832 | -2.6874 | -2.6916 | -2.6968 | -2.7011 | -2.7053 | -2.7105 | -2.7158 | -2.7221 | -2.7463 | -2.7737 | -2.7916
| BRACO | FORTEVIOT | MINIMUM HEADROOM | NO 04539 18092 | YES | YES | 1.8327 | 3.1747 | 3.1326 | 3.0926 | 3.0263 | 2.9558 | 2.8411 | 2.7263 | 2.6947 | 2.6632 | 2.64 | 2.4211 | 2.3168 | 2.2453 | 2.7137 | 2.6663 | 2.6211 | 2.5442 | 2.4642 | 2.3326 | 2.2021 | 2.1663 | 2.1316 | 2.1063 | 1.8874 | 1.7684 | 1.6653 | 2.78 | 2.7326 | 2.6874 | 2.6105 | 2.5295 | 2.3979 | 2.2663 | 2.2305 | 2.1958 | 2.1705 | 1.9516 | 1.8316 | 1.7274
|  | FORTEVIOT | EE |  |  |  |  | 3.1747 | 3.1326 | 3.0926 | 3.0263 | 2.9558 | 2.8411 | 2.7263 | 2.6947 | 2.6632 | 2.64 | 2.4495 | 2.3495 | 2.2695 | 2.7137 | 2.6663 | 2.6211 | 2.5442 | 2.4642 | 2.3326 | 2.2021 | 2.1663 | 2.1316 | 2.1063 | 1.8905 | 1.7779 | 1.6874 | 2.78 | 2.7326 | 2.6874 | 2.6105 | 2.5295 | 2.3979 | 2.2663 | 2.2305 | 2.1958 | 2.1705 | 1.9537 | 1.8411 | 1.7495
|  | FORTEVIOT | HT |  |  |  |  | 3.1779 | 3.1411 | 3.0979 | 3.0347 | 2.9611 | 2.9284 | 2.8926 | 2.86 | 2.7916 | 2.6863 | 2.4211 | 2.3168 | 2.2453 | 2.7168 | 2.6758 | 2.6284 | 2.5558 | 2.4716 | 2.4358 | 2.3968 | 2.3611 | 2.2832 | 2.1632 | 1.8874 | 1.7684 | 1.6653 | 2.7832 | 2.7421 | 2.6937 | 2.6211 | 2.5379 | 2.5011 | 2.4621 | 2.4263 | 2.3474 | 2.2274 | 1.9516 | 1.8316 | 1.7274
|  | FORTEVIOT | HE |  |  |  |  | 3.2021 | 3.1705 | 3.1411 | 3.0895 | 3.0305 | 2.9284 | 2.8221 | 2.8021 | 2.7758 | 2.7642 | 2.6242 | 2.5684 | 2.5211 | 2.7442 | 2.7095 | 2.6768 | 2.6179 | 2.5505 | 2.4337 | 2.3116 | 2.2895 | 2.2611 | 2.2474 | 2.0874 | 2.0253 | 1.9705 | 2.8105 | 2.7758 | 2.7432 | 2.6832 | 2.6158 | 2.4989 | 2.3768 | 2.3547 | 2.3253 | 2.3116 | 2.1516 | 2.0884 | 2.0337
|  | FORTEVIOT | FB |  |  |  |  | 3.2411 | 3.2284 | 3.2105 | 3.1937 | 3.1695 | 3.1316 | 3.0832 | 3.0189 | 2.9979 | 2.9821 | 2.8947 | 2.8021 | 2.7463 | 2.7895 | 2.7747 | 2.7558 | 2.7358 | 2.7084 | 2.6653 | 2.6084 | 2.5347 | 2.5105 | 2.4937 | 2.3947 | 2.2884 | 2.2242 | 2.8558 | 2.8411 | 2.8221 | 2.8021 | 2.7747 | 2.7316 | 2.6747 | 2.6 | 2.5768 | 2.5589 | 2.4589 | 2.3537 | 2.2884
| INVERNESS | FOYERS | MINIMUM HEADROOM | NH 49740 21044 | YES | YES | 0 | 0.99368 | 0.99053 | 0.98632 | 0.98211 | 0.97789 | 0.97263 | 0.96737 | 0.96316 | 0.95789 | 0.95368 | 0.94 | 0.92737 | 0.91895 | 0.99789 | 0.99579 | 0.99368 | 0.99263 | 0.99053 | 0.98842 | 0.98632 | 0.98526 | 0.98211 | 0.98 | 0.97474 | 0.96947 | 0.96526 | 0.99158 | 0.98737 | 0.98421 | 0.97895 | 0.97368 | 0.96737 | 0.96211 | 0.95684 | 0.95158 | 0.94632 | 0.93263 | 0.91895 | 0.90842
|  | FOYERS | EE |  |  |  |  | 0.99368 | 0.99053 | 0.98632 | 0.98211 | 0.97789 | 0.97263 | 0.96737 | 0.96316 | 0.95789 | 0.95368 | 0.94 | 0.92842 | 0.92 | 0.99789 | 0.99579 | 0.99474 | 0.99368 | 0.99158 | 0.98842 | 0.98632 | 0.98526 | 0.98211 | 0.98 | 0.97474 | 0.97158 | 0.96842 | 0.99158 | 0.98737 | 0.98421 | 0.97895 | 0.97368 | 0.96737 | 0.96211 | 0.95684 | 0.95158 | 0.94632 | 0.93263 | 0.91895 | 0.90947
|  | FOYERS | HT |  |  |  |  | 0.99474 | 0.99053 | 0.98737 | 0.98421 | 0.97895 | 0.97474 | 0.96947 | 0.96526 | 0.96 | 0.95579 | 0.94 | 0.92737 | 0.91895 | 0.99789 | 0.99579 | 0.99368 | 0.99263 | 0.99053 | 0.98842 | 0.98632 | 0.98526 | 0.98211 | 0.98 | 0.97474 | 0.96947 | 0.96526 | 0.99263 | 0.98842 | 0.98421 | 0.98105 | 0.97474 | 0.97053 | 0.96526 | 0.96 | 0.95368 | 0.94947 | 0.93474 | 0.92105 | 0.90842
|  | FOYERS | HE |  |  |  |  | 0.99789 | 0.99368 | 0.99263 | 0.98947 | 0.98737 | 0.98526 | 0.98211 | 0.97895 | 0.97789 | 0.97474 | 0.96632 | 0.95789 | 0.95158 | 0.99895 | 0.99684 | 0.99579 | 0.99368 | 0.99263 | 0.99053 | 0.98842 | 0.98737 | 0.98737 | 0.98632 | 0.98211 | 0.98 | 0.97789 | 0.99579 | 0.99263 | 0.99053 | 0.98737 | 0.98526 | 0.98211 | 0.97895 | 0.97684 | 0.97474 | 0.97158 | 0.96105 | 0.95158 | 0.94526
|  | FOYERS | FB |  |  |  |  | 0.99789 | 0.99684 | 0.99579 | 0.99474 | 0.99263 | 0.99053 | 0.99053 | 0.98737 | 0.98526 | 0.98421 | 0.97579 | 0.96632 | 0.95789 | 0.99895 | 0.99895 | 0.99895 | 0.99789 | 0.99684 | 0.99579 | 0.99579 | 0.99474 | 0.99368 | 0.99368 | 0.99053 | 0.98842 | 0.98632 | 0.99684 | 0.99579 | 0.99474 | 0.99263 | 0.99053 | 0.98842 | 0.98737 | 0.98526 | 0.98316 | 0.98105 | 0.97158 | 0.96 | 0.95158
| FRASERBURGH | FRASERBURGH | MINIMUM HEADROOM | NH 51502 69028 | NO | YES | 1.7255 | 37.6684 | 36.5137 | 35.4663 | 34.2232 | 32.46 | 30.6758 | 28.8968 | 28.4063 | 27.8589 | 26.3211 | 16.3863 | 14.3758 | 13.5284 | 33.5905 | 32.2832 | 31.0958 | 29.6874 | 27.6853 | 25.6474 | 23.5726 | 23.0158 | 22.3905 | 20.6011 | 12.5053 | 9.0484 | 8.0853 | 35.4011 | 34.1463 | 33.0074 | 31.6295 | 29.6189 | 27.5895 | 25.5653 | 25.0179 | 24.4063 | 22.6611 | 13.8905 | 9.7537 | 8.8095
|  | FRASERBURGH | EE |  |  |  |  | 37.6684 | 36.5137 | 35.4663 | 34.2232 | 32.46 | 30.6758 | 28.8968 | 28.4063 | 27.8589 | 26.6442 | 18.3116 | 14.3758 | 13.5284 | 33.5905 | 32.2832 | 31.0958 | 29.6874 | 27.6853 | 25.6474 | 23.5726 | 23.0158 | 22.3905 | 20.9747 | 12.5053 | 9.0484 | 8.0853 | 35.4011 | 34.1463 | 33.0074 | 31.6295 | 29.6189 | 27.5895 | 25.5653 | 25.0179 | 24.4063 | 23.0253 | 13.8905 | 9.7537 | 8.8095
|  | FRASERBURGH | HT |  |  |  |  | 37.6916 | 36.6779 | 35.6074 | 34.4011 | 32.6053 | 32.2432 | 31.5947 | 30.8895 | 29.2179 | 26.3211 | 16.3863 | 15.2284 | 14.4053 | 33.6147 | 32.4674 | 31.2568 | 29.8905 | 27.8537 | 27.4558 | 26.7316 | 25.9432 | 23.9937 | 20.6011 | 12.9011 | 9.8347 | 8.6589 | 35.4253 | 34.3242 | 33.1621 | 31.8337 | 29.7895 | 29.3895 | 28.6632 | 27.8716 | 25.9684 | 22.6611 | 14.4505 | 10.8442 | 9.6937
|  | FRASERBURGH | HE |  |  |  |  | 37.8221 | 36.9263 | 35.9842 | 34.8421 | 33.1916 | 31.5211 | 29.8232 | 29.4263 | 28.9558 | 27.8474 | 22.1179 | 20.0968 | 19.6011 | 33.7611 | 32.7463 | 31.6789 | 30.3842 | 28.5105 | 26.6179 | 24.6505 | 24.2 | 23.6611 | 22.3632 | 16.1379 | 14.2337 | 13.6653 | 35.5653 | 34.5916 | 33.5684 | 32.3263 | 30.4484 | 28.5484 | 26.6179 | 26.1758 | 25.6484 | 24.3821 | 17.9642 | 15.8011 | 15.2453
|  | FRASERBURGH | FB |  |  |  |  | 38.5337 | 38.1874 | 37.7937 | 37.4411 | 36.8695 | 36.16 | 35.2853 | 34.2274 | 34.0126 | 33.2674 | 31.7168 | 29.6189 | 29.1116 | 34.5684 | 34.1758 | 33.7305 | 33.3316 | 32.6842 | 31.8779 | 30.8832 | 29.6789 | 29.4389 | 28.5937 | 26.8442 | 24.4126 | 23.8274 | 36.3389 | 35.9621 | 35.5358 | 35.1526 | 34.5316 | 33.7589 | 32.8074 | 31.6221 | 31.3811 | 30.5316 | 28.7747 | 26.3853 | 25.8126
| LUNANHEAD | FRIOCKHEIM | MINIMUM HEADROOM | NO 58834 49317 | YES | YES | 0 | 5.3347 | 5.2853 | 5.2432 | 5.1958 | 5.1516 | 5.1 | 5.0484 | 4.9895 | 4.9347 | 4.8853 | 2.6968 | 2.5632 | 2.4632 | 4.7621 | 4.7063 | 4.6579 | 4.6063 | 4.5579 | 4.5011 | 4.4453 | 4.3789 | 4.3189 | 4.2642 | 1.8137 | 1.6537 | 1.5116 | 5.1211 | 5.0747 | 5.0347 | 4.9874 | 4.9411 | 4.8863 | 4.8326 | 4.7674 | 4.7084 | 4.6547 | 2.2168 | 2.0568 | 1.9147
|  | FRIOCKHEIM | EE |  |  |  |  | 5.3347 | 5.2853 | 5.2432 | 5.1958 | 5.1516 | 5.1 | 5.0484 | 4.9989 | 4.9368 | 4.8958 | 3.6053 | 3.4768 | 3.3853 | 4.7621 | 4.7063 | 4.6579 | 4.6063 | 4.5579 | 4.5011 | 4.4453 | 4.3895 | 4.3211 | 4.2758 | 2.8484 | 2.7053 | 2.6021 | 5.1211 | 5.0747 | 5.0347 | 4.9874 | 4.9411 | 4.8863 | 4.8326 | 4.7779 | 4.7105 | 4.6663 | 3.2221 | 3.0811 | 2.98
|  | FRIOCKHEIM | HT |  |  |  |  | 5.3484 | 5.3063 | 5.2632 | 5.2189 | 5.1737 | 5.1284 | 5.0653 | 4.9895 | 4.9347 | 4.8853 | 2.6968 | 2.5632 | 2.4632 | 4.7779 | 4.7295 | 4.6821 | 4.6337 | 4.5842 | 4.5347 | 4.4632 | 4.3789 | 4.3189 | 4.2642 | 1.8137 | 1.6537 | 1.5116 | 5.1337 | 5.0937 | 5.0526 | 5.0126 | 4.9642 | 4.9179 | 4.8505 | 4.7674 | 4.7084 | 4.6547 | 2.2168 | 2.0568 | 1.9147
|  | FRIOCKHEIM | HE |  |  |  |  | 5.3811 | 5.3495 | 5.3232 | 5.2958 | 5.2653 | 5.2305 | 5.1958 | 5.1579 | 5.1189 | 5.0947 | 3.9747 | 3.9084 | 3.8632 | 4.8137 | 4.78 | 4.7516 | 4.7211 | 4.6884 | 4.6505 | 4.6137 | 4.5726 | 4.5295 | 4.5021 | 3.2242 | 3.1495 | 3.0989 | 5.1632 | 5.1337 | 5.1084 | 5.0832 | 5.0537 | 5.0189 | 4.9853 | 4.9505 | 4.9095 | 4.8842 | 3.62 | 3.5474 | 3.4979
|  | FRIOCKHEIM | FB |  |  |  |  | 5.3979 | 5.3779 | 5.3579 | 5.3379 | 5.3168 | 5.2979 | 5.2768 | 5.2558 | 5.2326 | 5.2074 | 5.0947 | 4.9937 | 4.9274 | 4.8316 | 4.8105 | 4.7874 | 4.7663 | 4.7421 | 4.72 | 4.6979 | 4.6737 | 4.6484 | 4.62 | 4.4937 | 4.3789 | 4.3042 | 5.1779 | 5.1611 | 5.1421 | 5.1232 | 5.1042 | 5.0853 | 5.0663 | 5.0463 | 5.0253 | 4.9989 | 4.88 | 4.7684 | 4.6947
| KINTORE | FYVIE | MINIMUM HEADROOM | NJ 76759 37635 | NO | YES | 0.17857 | -4.9284 | -5.0526 | -5.1705 | -5.3242 | -5.3832 | -5.4526 | -5.5211 | -5.5832 | -5.6537 | -5.7021 | -7.6358 | -9.26 | -9.4147 | -1.5758 | -1.7021 | -1.8221 | -1.9789 | -2.04 | -2.1095 | -2.1789 | -2.2432 | -2.3137 | -2.3632 | -2.5926 | -5.3989 | -5.5611 | -1.2116 | -1.2853 | -1.4105 | -1.5747 | -1.6368 | -1.7095 | -1.7811 | -1.8474 | -1.92 | -1.9726 | -2.2 | -5.4863 | -5.6526
|  | FYVIE | EE |  |  |  |  | -4.9284 | -5.0526 | -5.1705 | -5.3189 | -5.3758 | -5.4379 | -5.5084 | -5.5832 | -5.6537 | -5.7021 | -5.9179 | -9.26 | -9.4147 | -1.5758 | -1.7021 | -1.8221 | -1.9747 | -2.0326 | -2.0947 | -2.1653 | -2.2432 | -2.3137 | -2.3632 | -2.5926 | -5.3989 | -5.5611 | -1.2116 | -1.2853 | -1.4105 | -1.5695 | -1.6295 | -1.6937 | -1.7674 | -1.8474 | -1.92 | -1.9726 | -2.2 | -5.4863 | -5.6526
|  | FYVIE | HT |  |  |  |  | -4.9189 | -5.0305 | -5.1695 | -5.3242 | -5.3832 | -5.4526 | -5.5211 | -5.5811 | -5.64 | -5.6968 | -7.6358 | -8.6768 | -8.8147 | -1.5653 | -1.6789 | -1.8211 | -1.9789 | -2.04 | -2.1095 | -2.1789 | -2.24 | -2.3 | -2.3568 | -2.5726 | -4.8842 | -5.0716 | -1.2084 | -1.2611 | -1.4095 | -1.5747 | -1.6368 | -1.7095 | -1.7811 | -1.8442 | -1.9053 | -1.9653 | -2.18 | -4.8453 | -5.0316
|  | FYVIE | HE |  |  |  |  | -4.8895 | -4.9832 | -5.0916 | -5.2211 | -5.2579 | -5.3 | -5.36 | -5.4095 | -5.4642 | -5.4958 | -5.6063 | -6.9568 | -7.0474 | -1.5358 | -1.6305 | -1.7421 | -1.8737 | -1.9116 | -1.9537 | -2.0137 | -2.0653 | -2.1211 | -2.1526 | -2.2653 | -3.4063 | -3.4989 | -1.2032 | -1.22 | -1.3263 | -1.4642 | -1.5032 | -1.5453 | -1.6084 | -1.6611 | -1.7189 | -1.7516 | -1.8684 | -3.1568 | -3.2537
|  | FYVIE | FB |  |  |  |  | -4.82 | -4.8558 | -4.9 | -4.94 | -4.9811 | -5.0158 | -5.0453 | -5.0779 | -5.1137 | -5.1453 | -5.2695 | -5.3895 | -5.4779 | -1.4642 | -1.5011 | -1.5474 | -1.5874 | -1.6295 | -1.6642 | -1.6947 | -1.7274 | -1.7642 | -1.7958 | -1.9221 | -2.0453 | -2.1358 | -1.1905 | -1.1968 | -1.2021 | -1.2084 | -1.2147 | -1.2453 | -1.2768 | -1.3116 | -1.3495 | -1.3821 | -1.5137 | -1.6421 | -1.7368
| GRUDIE BRIDGE | GARBAT FOREST | MINIMUM HEADROOM | NH 41255 67993 | YES | NO | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | GARBAT FOREST | EE |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | GARBAT FOREST | HT |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | GARBAT FOREST | HE |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | GARBAT FOREST | FB |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| STORNOWAY | GISLA | MINIMUM HEADROOM | NB 12846 25823 | YES | YES | 0 | 0.97789 | 2.46 | 2.4421 | 2.4284 | 2.4179 | 2.4074 | 2.3947 | 2.3842 | 2.3758 | 2.3663 | 2.3305 | 2.2979 | 2.2758 | 0.97579 | 2.4537 | 2.4337 | 2.4189 | 2.4063 | 2.3958 | 2.3821 | 2.3705 | 2.3611 | 2.3505 | 2.3105 | 2.2747 | 2.2495 | 0.97579 | 2.4558 | 2.4358 | 2.4221 | 2.4095 | 2.3989 | 2.3853 | 2.3747 | 2.3653 | 2.3547 | 2.3158 | 2.2811 | 2.2558
|  | GISLA | EE |  |  |  |  | 0.97789 | 2.4674 | 2.4421 | 2.4284 | 2.4179 | 2.4074 | 2.3947 | 2.3842 | 2.3758 | 2.3663 | 2.3305 | 2.2979 | 2.2758 | 0.97579 | 2.4632 | 2.4337 | 2.4189 | 2.4063 | 2.3958 | 2.3821 | 2.3705 | 2.3611 | 2.3505 | 2.3105 | 2.2747 | 2.2495 | 0.97579 | 2.4642 | 2.4358 | 2.4221 | 2.4095 | 2.3989 | 2.3853 | 2.3747 | 2.3653 | 2.3547 | 2.3158 | 2.2811 | 2.2558
|  | GISLA | HT |  |  |  |  | 0.98105 | 2.46 | 2.4495 | 2.4389 | 2.4295 | 2.4189 | 2.4095 | 2.3968 | 2.3863 | 2.3747 | 2.3316 | 2.2989 | 2.2789 | 0.97895 | 2.4537 | 2.4421 | 2.4316 | 2.42 | 2.4084 | 2.3979 | 2.3842 | 2.3737 | 2.3611 | 2.3232 | 2.2832 | 2.2537 | 0.98 | 2.4558 | 2.4442 | 2.4337 | 2.4221 | 2.4116 | 2.4011 | 2.3874 | 2.3768 | 2.3653 | 2.3274 | 2.2895 | 2.26
|  | GISLA | HE |  |  |  |  | 0.98737 | 2.4811 | 2.4579 | 2.4516 | 2.4463 | 2.4358 | 2.4284 | 2.4211 | 2.4147 | 2.4105 | 2.3926 | 2.3758 | 2.3642 | 0.98632 | 2.4789 | 2.4526 | 2.4463 | 2.44 | 2.4295 | 2.4211 | 2.4137 | 2.4063 | 2.4021 | 2.3821 | 2.3632 | 2.3495 | 0.98632 | 2.4789 | 2.4537 | 2.4474 | 2.4421 | 2.4305 | 2.4232 | 2.4158 | 2.4084 | 2.4042 | 2.3842 | 2.3663 | 2.3537
|  | GISLA | FB |  |  |  |  | 0.99158 | 2.4874 | 2.4832 | 2.4716 | 2.4674 | 2.4621 | 2.4579 | 2.4537 | 2.4474 | 2.4421 | 2.4211 | 2.4011 | 2.3853 | 0.99053 | 2.4853 | 2.4811 | 2.4684 | 2.4632 | 2.4579 | 2.4526 | 2.4484 | 2.4411 | 2.4347 | 2.4116 | 2.3895 | 2.3705 | 0.99053 | 2.4863 | 2.4811 | 2.4684 | 2.4642 | 2.4589 | 2.4537 | 2.4495 | 2.4432 | 2.4368 | 2.4137 | 2.3926 | 2.3737
| ALNESS | GLASTULLICH | MINIMUM HEADROOM | NH 78509 76508 | YES | YES | 0 | 1.4879 | 1.4542 | 1.4237 | 1.3921 | 1.3595 | 1.2121 | 0.96895 | 0.60263 | 0.17526 | -0.12579 | -0.83211 | -1.0437 | -1.1205 | 1.4763 | 1.4395 | 1.4047 | 1.37 | 1.3332 | 1.1626 | 0.87842 | 0.45105 | -0.05 | -0.40263 | -0.54263 | -1.1784 | -1.2658 | 1.4626 | 1.4268 | 1.3953 | 1.3626 | 1.3279 | 1.1574 | 0.87421 | 0.44789 | -0.052105 | -0.40263 | -0.54368 | -1.3479 | -1.4353
|  | GLASTULLICH | EE |  |  |  |  | 1.4879 | 1.4542 | 1.4237 | 1.3921 | 1.3595 | 1.3226 | 1.2858 | 1.1353 | 0.89421 | 0.53105 | -0.25105 | -1.0437 | -1.1205 | 1.4763 | 1.4395 | 1.4047 | 1.37 | 1.3332 | 1.2932 | 1.2532 | 1.0784 | 0.79632 | 0.37 | -0.54263 | -1.1784 | -1.2658 | 1.4626 | 1.4268 | 1.3953 | 1.3626 | 1.3279 | 1.2868 | 1.2468 | 1.0732 | 0.79211 | 0.36789 | -0.54368 | -1.3479 | -1.4353
|  | GLASTULLICH | HT |  |  |  |  | 1.4974 | 1.4689 | 1.4384 | 1.4079 | 1.3711 | 1.2121 | 0.96895 | 0.60263 | 0.17526 | -0.12579 | -0.83211 | -0.93316 | -1.0058 | 1.4879 | 1.4553 | 1.4216 | 1.3889 | 1.3479 | 1.1626 | 0.87842 | 0.45105 | -0.05 | -0.40263 | -0.54053 | -1.0816 | -1.1847 | 1.4732 | 1.4426 | 1.41 | 1.3795 | 1.3405 | 1.1574 | 0.87421 | 0.44789 | -0.052105 | -0.40263 | -0.54158 | -1.2174 | -1.3205
|  | GLASTULLICH | HE |  |  |  |  | 1.5195 | 1.4963 | 1.4795 | 1.4584 | 1.4332 | 1.4089 | 1.3795 | 1.2258 | 0.96579 | 0.54789 | -0.076316 | -0.41421 | -0.45947 | 1.5132 | 1.4879 | 1.4679 | 1.4458 | 1.4184 | 1.3921 | 1.3616 | 1.1816 | 0.87737 | 0.38684 | -0.34474 | -0.62368 | -0.67526 | 1.4963 | 1.4721 | 1.4542 | 1.4321 | 1.4058 | 1.3805 | 1.3511 | 1.1763 | 0.87316 | 0.38368 | -0.34579 | -0.69211 | -0.74368
|  | GLASTULLICH | FB |  |  |  |  | 1.5311 | 1.5184 | 1.5047 | 1.4911 | 1.4753 | 1.4605 | 1.4447 | 1.43 | 1.3574 | 1.2384 | 0.49737 | 0.42895 | 0.37421 | 1.5258 | 1.5111 | 1.4963 | 1.4795 | 1.4616 | 1.4458 | 1.4289 | 1.4111 | 1.3279 | 1.1879 | 0.31842 | 0.24158 | 0.17947 | 1.5079 | 1.4953 | 1.4805 | 1.4658 | 1.4489 | 1.4332 | 1.4174 | 1.4016 | 1.3216 | 1.1826 | 0.31632 | 0.23947 | 0.17737
| SHIN | GLEDFIELD | MINIMUM HEADROOM | NH 58876 90837 | YES | NO | 0 | 2.7484 | 2.7263 | 2.7063 | 2.6811 | 2.6568 | 2.2653 | 2.0147 | 1.8453 | 1.7653 | 1.7211 | 1.5632 | 1.4895 | 1.4326 | 2.4547 | 2.4316 | 2.4074 | 2.38 | 2.3516 | 1.8874 | 1.5968 | 1.4 | 1.3063 | 1.2568 | 1.0863 | 1.0074 | 0.93474 | 2.5663 | 2.5421 | 2.5189 | 2.4905 | 2.4632 | 2.0358 | 1.7674 | 1.5747 | 1.4811 | 1.4326 | 1.2526 | 1.1695 | 1.1074
|  | GLEDFIELD | EE |  |  |  |  | 2.7484 | 2.7263 | 2.7063 | 2.6811 | 2.6568 | 2.6295 | 2.5853 | 2.2032 | 1.9537 | 1.7716 | 1.5632 | 1.4905 | 1.4411 | 2.4547 | 2.4316 | 2.4074 | 2.38 | 2.3516 | 2.3211 | 2.2705 | 1.8242 | 1.5326 | 1.3232 | 1.0863 | 1.0074 | 0.95474 | 2.5663 | 2.5421 | 2.5189 | 2.4905 | 2.4632 | 2.4337 | 2.3842 | 1.9695 | 1.7 | 1.4916 | 1.2526 | 1.1695 | 1.1147
|  | GLEDFIELD | HT |  |  |  |  | 2.7547 | 2.7347 | 2.7168 | 2.6958 | 2.6716 | 2.2653 | 2.0147 | 1.8453 | 1.7653 | 1.7211 | 1.5684 | 1.4895 | 1.4326 | 2.4632 | 2.44 | 2.4189 | 2.3958 | 2.3674 | 1.8874 | 1.5968 | 1.4 | 1.3063 | 1.2568 | 1.1053 | 1.0137 | 0.93474 | 2.5737 | 2.5516 | 2.5326 | 2.5084 | 2.4811 | 2.0358 | 1.7674 | 1.5747 | 1.4811 | 1.4326 | 1.28 | 1.1863 | 1.1074
|  | GLEDFIELD | HE |  |  |  |  | 2.7674 | 2.7547 | 2.7432 | 2.7284 | 2.7126 | 2.6916 | 2.6653 | 2.2516 | 1.9968 | 1.8295 | 1.7074 | 1.6674 | 1.6432 | 2.4789 | 2.4642 | 2.4505 | 2.4358 | 2.4168 | 2.3926 | 2.3642 | 1.8747 | 1.5758 | 1.3811 | 1.2411 | 1.1979 | 1.1705 | 2.5884 | 2.5737 | 2.5611 | 2.5463 | 2.5284 | 2.5053 | 2.4768 | 2.0221 | 1.7463 | 1.5568 | 1.4147 | 1.3695 | 1.3421
|  | GLEDFIELD | FB |  |  |  |  | 2.7789 | 2.7695 | 2.7611 | 2.7516 | 2.7421 | 2.7326 | 2.72 | 2.7074 | 2.5358 | 2.4042 | 2.1158 | 2.0684 | 2.0368 | 2.4905 | 2.48 | 2.4705 | 2.46 | 2.4495 | 2.4368 | 2.4221 | 2.4074 | 2.2 | 2.0463 | 1.7095 | 1.6568 | 1.6211 | 2.6 | 2.5905 | 2.58 | 2.5705 | 2.56 | 2.5484 | 2.5347 | 2.52 | 2.3274 | 2.1853 | 1.8737 | 1.8242 | 1.7895
| FORT AUGUSTUS | GLEN LAOGH | MINIMUM HEADROOM | NH 27430 00910 | YES | YES | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | GLEN LAOGH | EE |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | GLEN LAOGH | HT |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | GLEN LAOGH | HE |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
|  | GLEN LAOGH | FB |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
| KINLOCHLEVEN | GLENCOE | MINIMUM HEADROOM | NN 10658 58797 | YES | YES | 0 | 3.1963 | 3.17 | 3.1447 | 3.1153 | 3.0858 | 2.9321 | 2.8079 | 2.7184 | 2.6479 | 2.5753 | 2.3995 | 2.2742 | 2.1626 | 2.8932 | 2.8626 | 2.8311 | 2.7974 | 2.7616 | 2.4995 | 2.2574 | 2.0879 | 2.0047 | 1.9542 | 1.7711 | 1.6479 | 1.5395 | 3.1563 | 3.1195 | 3.0826 | 3.0395 | 2.9963 | 2.6416 | 2.3879 | 2.2089 | 2.1195 | 2.0405 | 1.8363 | 1.6921 | 1.5637
|  | GLENCOE | EE |  |  |  |  | 3.1963 | 3.17 | 3.1447 | 3.1153 | 3.0858 | 3.0532 | 3.0226 | 2.8258 | 2.6911 | 2.5753 | 2.3995 | 2.2742 | 2.1626 | 2.8932 | 2.8626 | 2.8311 | 2.7974 | 2.7616 | 2.7226 | 2.6858 | 2.3868 | 2.1342 | 1.9542 | 1.7711 | 1.6479 | 1.5395 | 3.1563 | 3.1195 | 3.0826 | 3.0395 | 2.9963 | 2.9521 | 2.9079 | 2.5016 | 2.2321 | 2.0405 | 1.8363 | 1.6921 | 1.5637
|  | GLENCOE | HT |  |  |  |  | 3.2047 | 3.1889 | 3.1732 | 3.1532 | 3.13 | 2.9321 | 2.8079 | 2.7184 | 2.6479 | 2.6205 | 2.4932 | 2.39 | 2.3153 | 2.9058 | 2.8858 | 2.8668 | 2.8437 | 2.8163 | 2.4995 | 2.2574 | 2.0879 | 2.0047 | 1.9763 | 1.8658 | 1.7532 | 1.6553 | 3.1668 | 3.1447 | 3.1216 | 3.0932 | 3.0574 | 2.6416 | 2.3879 | 2.2089 | 2.1195 | 2.09 | 1.97 | 1.8479 | 1.7395
|  | GLENCOE | HE |  |  |  |  | 3.2142 | 3.2016 | 3.1889 | 3.1763 | 3.1605 | 3.1447 | 3.1268 | 2.9216 | 2.7932 | 2.7121 | 2.6489 | 2.5837 | 2.5247 | 2.9163 | 2.9016 | 2.8868 | 2.8732 | 2.8542 | 2.8374 | 2.8174 | 2.4995 | 2.2479 | 2.0879 | 2.0132 | 1.9468 | 1.8858 | 3.1711 | 3.1616 | 3.1511 | 3.1342 | 3.1132 | 3.0921 | 3.0711 | 2.6405 | 2.3742 | 2.2058 | 2.1237 | 2.0479 | 1.9795
|  | GLENCOE | FB |  |  |  |  | 3.2226 | 3.2153 | 3.21 | 3.2026 | 3.1942 | 3.1868 | 3.1805 | 3.1721 | 3.0847 | 3.0174 | 2.8868 | 2.8511 | 2.8237 | 2.9268 | 2.9184 | 2.9121 | 2.9016 | 2.8921 | 2.8826 | 2.8753 | 2.8658 | 2.7447 | 2.6416 | 2.3911 | 2.3311 | 2.2858 | 3.1774 | 3.1732 | 3.1711 | 3.1647 | 3.1521 | 3.1405 | 3.1311 | 3.1184 | 2.9332 | 2.7942 | 2.5321 | 2.4679 | 2.4195
| DUNOON | GLENDARUEL | MINIMUM HEADROOM | NN 03067 59147 | YES | YES | 0 | 0.17447 | 0.17079 | 0.16816 | 0.16553 | 0.16289 | 0.15921 | 0.15658 | 0.15395 | 0.15026 | 0.14763 | 0.13289 | 0.11868 | 0.10763 | 0.16868 | 0.16553 | 0.16289 | 0.16026 | 0.15711 | 0.15289 | 0.14974 | 0.14658 | 0.14289 | 0.13974 | 0.12658 | 0.11079 | 0.096053 | 0.165 | 0.16079 | 0.15868 | 0.155 | 0.15184 | 0.14816 | 0.145 | 0.14184 | 0.13763 | 0.13447 | 0.12079 | 0.105 | 0.089211
|  | GLENDARUEL | EE |  |  |  |  | 0.33237 | 0.32763 | 0.32237 | 0.31395 | 0.305 | 0.29711 | 0.28816 | 0.28026 | 0.27184 | 0.26289 | 0.23237 | 0.19868 | 0.16395 | 0.32289 | 0.31763 | 0.30974 | 0.30132 | 0.29237 | 0.285 | 0.27553 | 0.26763 | 0.25816 | 0.24921 | 0.21816 | 0.18395 | 0.14868 | 0.325 | 0.31816 | 0.31079 | 0.30237 | 0.29237 | 0.28395 | 0.27447 | 0.26553 | 0.25605 | 0.24711 | 0.21395 | 0.17816 | 0.14237
|  | GLENDARUEL | HT |  |  |  |  | 0.17447 | 0.17079 | 0.16868 | 0.16553 | 0.16289 | 0.15974 | 0.15658 | 0.15395 | 0.15026 | 0.14763 | 0.13289 | 0.11868 | 0.10763 | 0.16868 | 0.16553 | 0.16342 | 0.16026 | 0.15711 | 0.15289 | 0.14974 | 0.14658 | 0.14289 | 0.13974 | 0.12658 | 0.11079 | 0.096053 | 0.165 | 0.16079 | 0.15868 | 0.155 | 0.15184 | 0.14816 | 0.145 | 0.14184 | 0.13763 | 0.13447 | 0.12079 | 0.105 | 0.089211
|  | GLENDARUEL | HE |  |  |  |  | 0.17447 | 0.17079 | 0.16816 | 0.16553 | 0.16289 | 0.15921 | 0.15658 | 0.15395 | 0.15079 | 0.14816 | 0.13763 | 0.12447 | 0.11079 | 0.16921 | 0.16605 | 0.16289 | 0.16079 | 0.15816 | 0.15395 | 0.15184 | 0.14868 | 0.14605 | 0.14289 | 0.13184 | 0.11763 | 0.10447 | 0.165 | 0.16132 | 0.15868 | 0.15553 | 0.15289 | 0.14921 | 0.14658 | 0.14342 | 0.14026 | 0.13711 | 0.12553 | 0.11184 | 0.097105
|  | GLENDARUEL | FB |  |  |  |  | 0.33658 | 0.33605 | 0.33553 | 0.33553 | 0.33447 | 0.33447 | 0.33395 | 0.33289 | 0.33289 | 0.33289 | 0.32974 | 0.32237 | 0.31816 | 0.32605 | 0.32447 | 0.32447 | 0.32447 | 0.32342 | 0.32342 | 0.32342 | 0.32289 | 0.32237 | 0.32237 | 0.31816 | 0.31079 | 0.30658 | 0.33132 | 0.33026 | 0.32974 | 0.32974 | 0.32868 | 0.32816 | 0.32763 | 0.32658 | 0.32658 | 0.32605 | 0.31921 | 0.31079 | 0.30605
| ABERNETHY | GLENDEVON | MINIMUM HEADROOM | NO 00101 02760 | YES | YES | 0.14286 | 4.0632 | 4.0021 | 3.9337 | 3.8411 | 3.8011 | 3.7526 | 3.7021 | 3.6368 | 3.5768 | 3.5484 | 3.0253 | 2.9179 | 2.84 | 3.8442 | 3.7768 | 3.6926 | 3.5863 | 3.5432 | 3.4895 | 3.4379 | 3.3789 | 3.3137 | 3.2842 | 2.8368 | 2.7284 | 2.6547 | 3.8789 | 3.8095 | 3.7295 | 3.6211 | 3.5768 | 3.5221 | 3.4653 | 3.3905 | 3.3221 | 3.2905 | 2.7379 | 2.6168 | 2.5284
|  | GLENDEVON | EE |  |  |  |  | 4.0632 | 4.0021 | 3.9453 | 3.8716 | 3.8295 | 3.7737 | 3.7021 | 3.6368 | 3.5768 | 3.5484 | 3.0253 | 2.9179 | 2.84 | 3.8442 | 3.7768 | 3.7158 | 3.6337 | 3.5895 | 3.5274 | 3.4495 | 3.3789 | 3.3137 | 3.2842 | 2.8368 | 2.7284 | 2.6547 | 3.8789 | 3.8095 | 3.7432 | 3.6589 | 3.6105 | 3.5463 | 3.4653 | 3.3905 | 3.3221 | 3.2905 | 2.7379 | 2.6168 | 2.5284
|  | GLENDEVON | HT |  |  |  |  | 4.0674 | 4.0116 | 3.9337 | 3.8411 | 3.8011 | 3.7526 | 3.7074 | 3.6695 | 3.6305 | 3.5905 | 3.1547 | 3.0589 | 2.9895 | 3.8474 | 3.7832 | 3.6926 | 3.5863 | 3.5432 | 3.4895 | 3.4379 | 3.3958 | 3.3537 | 3.3105 | 2.9516 | 2.8453 | 2.7505 | 3.8842 | 3.8189 | 3.7295 | 3.6211 | 3.5768 | 3.5221 | 3.4705 | 3.4274 | 3.3842 | 3.34 | 2.9032 | 2.7916 | 2.6905
|  | GLENDEVON | HE |  |  |  |  | 4.0842 | 4.0389 | 3.9863 | 3.9211 | 3.8947 | 3.8537 | 3.7811 | 3.7326 | 3.6937 | 3.6811 | 3.4674 | 3.4147 | 3.3768 | 3.8663 | 3.8147 | 3.7547 | 3.68 | 3.6505 | 3.6063 | 3.5221 | 3.4684 | 3.4253 | 3.4116 | 3.2253 | 3.1695 | 3.1337 | 3.9032 | 3.8505 | 3.7905 | 3.7137 | 3.6842 | 3.6389 | 3.5547 | 3.5 | 3.4547 | 3.4421 | 3.2126 | 3.1537 | 3.1116
|  | GLENDEVON | FB |  |  |  |  | 4.1253 | 4.1116 | 4.0926 | 4.0747 | 4.0568 | 4.0379 | 4.0158 | 3.9863 | 3.9526 | 3.9379 | 3.8316 | 3.7505 | 3.7095 | 3.9147 | 3.8979 | 3.8747 | 3.8558 | 3.8347 | 3.8126 | 3.7884 | 3.7547 | 3.7147 | 3.6979 | 3.5758 | 3.4832 | 3.4368 | 3.9516 | 3.9358 | 3.9137 | 3.8926 | 3.8726 | 3.8495 | 3.8253 | 3.7916 | 3.7505 | 3.7347 | 3.6126 | 3.5189 | 3.4726
| FORT AUGUSTUS | GLENDOE | MINIMUM HEADROOM | NH 40060 08894 | YES | YES | 0 | 6.7442 | 6.7316 | 6.7189 | 6.7053 | 6.6916 | 6.5284 | 6.3663 | 6.2537 | 6.1989 | 6.1158 | 5.9863 | 5.8926 | 5.8063 | 6.6768 | 6.6642 | 6.6516 | 6.6379 | 6.6232 | 6.4547 | 6.2674 | 6.1379 | 6.0768 | 6.0474 | 5.9316 | 5.8579 | 5.7926 | 6.7358 | 6.7168 | 6.6958 | 6.6737 | 6.6516 | 6.5084 | 6.3189 | 6.1874 | 6.1242 | 6.0305 | 5.8832 | 5.7768 | 5.6779
|  | GLENDOE | EE |  |  |  |  | 6.7442 | 6.7316 | 6.7189 | 6.7053 | 6.6916 | 6.6747 | 6.6505 | 6.42 | 6.2432 | 6.1158 | 5.9863 | 5.8926 | 5.8063 | 6.6768 | 6.6642 | 6.6516 | 6.6379 | 6.6232 | 6.6074 | 6.5937 | 6.3863 | 6.1884 | 6.0474 | 5.9316 | 5.8579 | 5.7926 | 6.7358 | 6.7168 | 6.6958 | 6.6737 | 6.6516 | 6.6284 | 6.6074 | 6.3863 | 6.1789 | 6.0305 | 5.8832 | 5.7768 | 5.6779
|  | GLENDOE | HT |  |  |  |  | 6.7526 | 6.7474 | 6.74 | 6.7347 | 6.7284 | 6.5284 | 6.3663 | 6.2537 | 6.1989 | 6.1832 | 6.1158 | 6.0568 | 6.0137 | 6.6842 | 6.6779 | 6.6705 | 6.6642 | 6.6568 | 6.4547 | 6.2674 | 6.1379 | 6.0768 | 6.0632 | 6.0116 | 5.9558 | 5.9074 | 6.7495 | 6.7421 | 6.7326 | 6.7242 | 6.7147 | 6.5084 | 6.3189 | 6.1874 | 6.1242 | 6.1074 | 6.0453 | 5.9768 | 5.9147
|  | GLENDOE | HE |  |  |  |  | 6.7537 | 6.7474 | 6.7432 | 6.7379 | 6.7316 | 6.7253 | 6.7179 | 6.5179 | 6.3463 | 6.2368 | 6.1926 | 6.1505 | 6.1126 | 6.6863 | 6.6789 | 6.6758 | 6.6695 | 6.6642 | 6.6579 | 6.6505 | 6.4495 | 6.2505 | 6.1253 | 6.0842 | 6.0484 | 6.02 | 6.7516 | 6.7421 | 6.7358 | 6.7284 | 6.72 | 6.7116 | 6.7032 | 6.4979 | 6.2968 | 6.1684 | 6.1179 | 6.0695 | 6.0284
|  | GLENDOE | FB |  |  |  |  | 6.7558 | 6.7537 | 6.7537 | 6.7516 | 6.7495 | 6.7474 | 6.7453 | 6.7432 | 6.7084 | 6.6221 | 6.4642 | 6.4358 | 6.4105 | 6.6874 | 6.6863 | 6.6842 | 6.6821 | 6.68 | 6.6768 | 6.6747 | 6.6726 | 6.6432 | 6.5547 | 6.3716 | 6.34 | 6.3137 | 6.7558 | 6.7526 | 6.7505 | 6.7484 | 6.7463 | 6.7432 | 6.74 | 6.7379 | 6.7168 | 6.6179 | 6.4326 | 6.3989 | 6.3716
| BRACO | GLENEAGLES | MINIMUM HEADROOM | NN 91540 11582 | NO | YES | 2.102 | 24.2442 | 24.0558 | 23.8221 | 23.6221 | 23.4958 | 23.3368 | 23.1095 | 22.8242 | 22.4811 | 22.34 | 21.5916 | 21.2874 | 20.9737 | 22.2568 | 22.0253 | 21.7821 | 21.5347 | 21.3842 | 21.1958 | 20.8779 | 20.5263 | 20.1011 | 19.9368 | 19.0926 | 18.9147 | 18.4737 | 19.6726 | 19.4421 | 19.1589 | 18.9116 | 18.7621 | 18.5737 | 18.2979 | 17.9474 | 17.5221 | 17.3589 | 16.4758 | 16.3337 | 15.9326
|  | GLENEAGLES | EE |  |  |  |  | 24.2442 | 24.0558 | 23.8221 | 23.6221 | 23.4958 | 23.3368 | 23.1589 | 22.9516 | 22.7095 | 22.5937 | 21.5916 | 21.3389 | 21.0032 | 22.2568 | 22.0253 | 21.7821 | 21.5347 | 21.3842 | 21.1958 | 20.9853 | 20.7316 | 20.4326 | 20.2937 | 19.0926 | 18.9147 | 18.5211 | 19.6726 | 19.4421 | 19.1589 | 18.9116 | 18.7621 | 18.5737 | 18.3632 | 18.1116 | 17.8137 | 17.6747 | 16.4758 | 16.3337 | 15.9411
|  | GLENEAGLES | HT |  |  |  |  | 24.2716 | 24.0916 | 23.9274 | 23.7084 | 23.5726 | 23.3684 | 23.1095 | 22.8242 | 22.4811 | 22.34 | 21.7347 | 21.2874 | 20.9737 | 22.2916 | 22.0716 | 21.8716 | 21.6042 | 21.4442 | 21.1958 | 20.8779 | 20.5263 | 20.1011 | 19.9368 | 19.4779 | 18.9347 | 18.4737 | 19.7074 | 19.4884 | 19.2884 | 19.0211 | 18.8621 | 18.6147 | 18.2979 | 17.9474 | 17.5221 | 17.3589 | 16.9347 | 16.3926 | 15.9326
|  | GLENEAGLES | HE |  |  |  |  | 24.3326 | 24.1905 | 24.0653 | 23.9168 | 23.8411 | 23.74 | 23.5263 | 23.3379 | 23.0758 | 23.0063 | 22.3295 | 22.0684 | 21.8737 | 22.3779 | 22.1926 | 22.0379 | 21.8568 | 21.7716 | 21.6568 | 21.3989 | 21.1663 | 20.84 | 20.7547 | 19.9063 | 19.6021 | 19.3716 | 19.7937 | 19.6084 | 19.4537 | 19.2737 | 19.1884 | 19.0747 | 18.8168 | 18.5853 | 18.2589 | 18.1737 | 17.3284 | 17.0242 | 16.7958
|  | GLENEAGLES | FB |  |  |  |  | 24.3516 | 24.3368 | 24.2653 | 24.1937 | 24.1463 | 24.0916 | 24.0368 | 23.9589 | 23.7916 | 23.7221 | 23.2158 | 22.8116 | 22.6021 | 22.4663 | 22.3684 | 22.28 | 22.1916 | 22.1358 | 22.0705 | 22.0053 | 21.9095 | 21.7 | 21.6158 | 20.9853 | 20.4832 | 20.2211 | 19.8821 | 19.7842 | 19.6958 | 19.6084 | 19.5526 | 19.4874 | 19.4221 | 19.3263 | 19.1179 | 19.0337 | 18.4042 | 17.9032 | 17.6421
| RANNOCH | GLENETIVE | MINIMUM HEADROOM | NN 25850 54886 | YES | YES | 0 | 0.26 | 0.24421 | 0.22421 | 0.20211 | 0.18 | 0.10737 | 0.017895 | -0.044211 | -0.085263 | -0.16 | -0.24 | -0.30105 | -0.36211 | 0.25684 | 0.23684 | 0.21579 | 0.19579 | 0.17368 | 0.086316 | -0.015789 | -0.085263 | -0.11474 | -0.16737 | -0.24632 | -0.30842 | -0.37684 | 0.27053 | 0.24947 | 0.22842 | 0.20632 | 0.18421 | 0.087368 | -0.016842 | -0.089474 | -0.13158 | -0.22 | -0.30947 | -0.37895 | -0.44526
|  | GLENETIVE | EE |  |  |  |  | 0.26 | 0.24421 | 0.22421 | 0.20211 | 0.18 | 0.16 | 0.14 | 0.017895 | -0.085263 | -0.16 | -0.24 | -0.30105 | -0.36211 | 0.25684 | 0.23684 | 0.21579 | 0.19579 | 0.17368 | 0.15368 | 0.13579 | 0.010526 | -0.090526 | -0.16737 | -0.24632 | -0.30842 | -0.37684 | 0.27053 | 0.24947 | 0.22842 | 0.20632 | 0.18421 | 0.16421 | 0.14316 | -0.011579 | -0.13158 | -0.22 | -0.30947 | -0.37895 | -0.44526
|  | GLENETIVE | HT |  |  |  |  | 0.26737 | 0.26421 | 0.26 | 0.25684 | 0.25263 | 0.10737 | 0.017895 | -0.044211 | -0.070526 | -0.075789 | -0.10211 | -0.12632 | -0.14526 | 0.26737 | 0.26316 | 0.25789 | 0.25263 | 0.24737 | 0.086316 | -0.015789 | -0.085263 | -0.11474 | -0.11789 | -0.13263 | -0.14842 | -0.16421 | 0.28316 | 0.27789 | 0.27263 | 0.26632 | 0.26 | 0.087368 | -0.016842 | -0.089474 | -0.12 | -0.12632 | -0.14947 | -0.17789 | -0.20421
|  | GLENETIVE | HE |  |  |  |  | 0.26737 | 0.26421 | 0.26 | 0.25684 | 0.25263 | 0.24737 | 0.24316 | 0.089474 | -0.0063158 | -0.068421 | -0.089474 | -0.11158 | -0.13474 | 0.26737 | 0.26316 | 0.25789 | 0.25263 | 0.24737 | 0.24105 | 0.23474 | 0.071579 | -0.038947 | -0.10947 | -0.12316 | -0.13684 | -0.15263 | 0.28316 | 0.27789 | 0.27263 | 0.26632 | 0.26 | 0.25368 | 0.24737 | 0.068421 | -0.044211 | -0.11684 | -0.14105 | -0.16632 | -0.19368
|  | GLENETIVE | FB |  |  |  |  | 0.26947 | 0.26842 | 0.26737 | 0.26737 | 0.26632 | 0.26526 | 0.26526 | 0.26421 | 0.20526 | 0.15895 | 0.08 | 0.076842 | 0.073684 | 0.27158 | 0.27053 | 0.26842 | 0.26737 | 0.26632 | 0.26526 | 0.26421 | 0.26316 | 0.19263 | 0.13895 | 0.047368 | 0.045263 | 0.043158 | 0.28842 | 0.28632 | 0.28526 | 0.28316 | 0.28211 | 0.28105 | 0.28 | 0.27789 | 0.20211 | 0.14842 | 0.055789 | 0.051579 | 0.047368
| FORT WILLIAM | GLENUIG | MINIMUM HEADROOM | NM 67224 77119 | YES | NO | 0 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.094737 | 0.094737 | 0.092632 | 0.084211 | 0.083158 | 0.083158 | 0.083158 | 0.083158 | 0.082105 | 0.082105 | 0.081053 | 0.081053 | 0.08 | 0.078947 | 0.077895 | 0.076842 | 0.081053 | 0.08 | 0.078947 | 0.078947 | 0.077895 | 0.077895 | 0.076842 | 0.075789 | 0.075789 | 0.074737 | 0.073684 | 0.072632 | 0.070526
|  | GLENUIG | EE |  |  |  |  | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.095789 | 0.094737 | 0.093684 | 0.084211 | 0.083158 | 0.083158 | 0.083158 | 0.083158 | 0.083158 | 0.082105 | 0.081053 | 0.081053 | 0.081053 | 0.08 | 0.077895 | 0.077895 | 0.081053 | 0.08 | 0.078947 | 0.078947 | 0.077895 | 0.077895 | 0.076842 | 0.075789 | 0.075789 | 0.075789 | 0.074737 | 0.072632 | 0.071579
|  | GLENUIG | HT |  |  |  |  | 0.10211 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.096842 | 0.094737 | 0.094737 | 0.092632 | 0.085263 | 0.083158 | 0.083158 | 0.083158 | 0.083158 | 0.082105 | 0.082105 | 0.082105 | 0.082105 | 0.08 | 0.078947 | 0.077895 | 0.076842 | 0.081053 | 0.08 | 0.08 | 0.078947 | 0.078947 | 0.077895 | 0.076842 | 0.076842 | 0.076842 | 0.074737 | 0.073684 | 0.072632 | 0.070526
|  | GLENUIG | HE |  |  |  |  | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.097895 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.085263 | 0.085263 | 0.085263 | 0.083158 | 0.083158 | 0.083158 | 0.083158 | 0.083158 | 0.081053 | 0.082105 | 0.082105 | 0.081053 | 0.08 | 0.081053 | 0.081053 | 0.081053 | 0.08 | 0.08 | 0.08 | 0.08 | 0.078947 | 0.076842 | 0.077895 | 0.076842 | 0.075789 | 0.074737
|  | GLENUIG | FB |  |  |  |  | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.097895 | 0.097895 | 0.085263 | 0.085263 | 0.085263 | 0.085263 | 0.084211 | 0.083158 | 0.083158 | 0.083158 | 0.083158 | 0.083158 | 0.083158 | 0.081053 | 0.081053 | 0.081053 | 0.081053 | 0.081053 | 0.081053 | 0.081053 | 0.08 | 0.08 | 0.08 | 0.078947 | 0.078947 | 0.077895 | 0.075789 | 0.075789
| BRORA | GOLSPIE | MINIMUM HEADROOM | NC 82996 00240 | YES | YES | 0 | 3.4579 | 3.4274 | 3.3979 | 3.3684 | 3.3358 | 2.7695 | 2.1432 | 1.6558 | 1.4295 | 1.3589 | 1.14 | 1.0432 | 0.97474 | 3.1263 | 3.0916 | 3.06 | 3.0274 | 2.9926 | 2.3242 | 1.5874 | 1.0126 | 0.75053 | 0.66947 | 0.44105 | 0.33474 | 0.24 | 3.1126 | 3.0779 | 3.0463 | 3.0137 | 2.98 | 2.3295 | 1.5926 | 1.0179 | 0.75579 | 0.67368 | 0.43579 | 0.32526 | 0.23579
|  | GOLSPIE | EE |  |  |  |  | 3.4579 | 3.4274 | 3.3979 | 3.3684 | 3.3358 | 3.3032 | 3.2337 | 2.6726 | 2.0358 | 1.5505 | 1.1505 | 1.0526 | 0.97474 | 3.1263 | 3.0916 | 3.06 | 3.0274 | 2.9926 | 2.9568 | 2.8779 | 2.22 | 1.4716 | 0.90211 | 0.44105 | 0.33474 | 0.24947 | 3.1126 | 3.0779 | 3.0463 | 3.0137 | 2.98 | 2.9432 | 2.8663 | 2.2211 | 1.4716 | 0.90105 | 0.43579 | 0.32526 | 0.23579
|  | GOLSPIE | HT |  |  |  |  | 3.4674 | 3.44 | 3.4137 | 3.3874 | 3.3537 | 2.7695 | 2.1432 | 1.6558 | 1.4295 | 1.3589 | 1.14 | 1.0432 | 0.97684 | 3.1358 | 3.1053 | 3.0747 | 3.0474 | 3.0095 | 2.3242 | 1.5874 | 1.0126 | 0.75053 | 0.66947 | 0.44842 | 0.33474 | 0.24 | 3.1221 | 3.0926 | 3.0642 | 3.0358 | 2.9989 | 2.3295 | 1.5926 | 1.0179 | 0.75579 | 0.67368 | 0.45158 | 0.33684 | 0.24105
|  | GOLSPIE | HE |  |  |  |  | 3.4863 | 3.4663 | 3.4474 | 3.4295 | 3.4095 | 3.3737 | 3.32 | 2.7126 | 2.0221 | 1.5263 | 1.3221 | 1.2653 | 1.2189 | 3.1579 | 3.1347 | 3.1147 | 3.0958 | 3.0737 | 3.0358 | 2.9726 | 2.2589 | 1.4463 | 0.86316 | 0.62632 | 0.56211 | 0.51158 | 3.1432 | 3.1221 | 3.1021 | 3.0832 | 3.0611 | 3.0232 | 2.9621 | 2.2642 | 1.4516 | 0.86737 | 0.62947 | 0.56526 | 0.51263
|  | GOLSPIE | FB |  |  |  |  | 3.4979 | 3.4863 | 3.4726 | 3.4611 | 3.4474 | 3.4347 | 3.3895 | 3.3621 | 3.1 | 2.8021 | 2.1442 | 2.0789 | 2.0305 | 3.1695 | 3.1558 | 3.1421 | 3.1284 | 3.1137 | 3.0989 | 3.0463 | 3.0147 | 2.7063 | 2.3558 | 1.5821 | 1.5095 | 1.4537 | 3.1558 | 3.1432 | 3.1284 | 3.1147 | 3.1 | 3.0863 | 3.0358 | 3.0053 | 2.7084 | 2.3632 | 1.5905 | 1.5158 | 1.46
| BURGHMUIR | GOODLYBURN | MINIMUM HEADROOM | NO 10084 24586 | NO | YES | 0.071429 | 14.1639 | 14.1061 | 13.7576 | 13.5587 | 13.3903 | 13.1966 | 12.9282 | 12.725 | 12.5439 | 12.3924 | 11.7471 | 11.1934 | 10.8029 | 12.4842 | 12.3042 | 11.8653 | 11.6432 | 11.4558 | 11.2389 | 10.9347 | 10.7074 | 10.5074 | 10.3421 | 9.72 | 9.1284 | 8.5674 | 12.8304 | 12.6693 | 12.2904 | 12.0914 | 11.9209 | 11.7262 | 11.4567 | 11.2525 | 11.0714 | 10.9188 | 10.3641 | 9.8241 | 9.3241
|  | GOODLYBURN | EE |  |  |  |  | 14.1639 | 14.1061 | 13.7576 | 13.5713 | 13.4082 | 13.2418 | 13.0376 | 12.8082 | 12.5903 | 12.4692 | 11.8408 | 11.3218 | 10.9039 | 12.4842 | 12.3042 | 11.8653 | 11.6537 | 11.4716 | 11.2905 | 11.0642 | 10.8042 | 10.5579 | 10.4232 | 9.72 | 9.1347 | 8.6579 | 12.8304 | 12.6693 | 12.2904 | 12.102 | 11.9388 | 11.7725 | 11.5672 | 11.3378 | 11.1178 | 10.9957 | 10.3641 | 9.8441 | 9.423
|  | GOODLYBURN | HT |  |  |  |  | 14.1724 | 14.1187 | 13.7787 | 13.5587 | 13.3903 | 13.1966 | 12.9282 | 12.725 | 12.5439 | 12.3924 | 11.7471 | 11.1934 | 10.8029 | 12.5274 | 12.3674 | 11.8916 | 11.6432 | 11.4558 | 11.2389 | 10.9347 | 10.7074 | 10.5074 | 10.3421 | 9.7579 | 9.1284 | 8.5674 | 12.8683 | 12.7262 | 12.3114 | 12.0914 | 11.9209 | 11.7262 | 11.4567 | 11.2525 | 11.0714 | 10.9188 | 10.3872 | 9.8241 | 9.3241
|  | GOODLYBURN | HE |  |  |  |  | 14.1966 | 14.145 | 13.9713 | 13.825 | 13.7061 | 13.5882 | 13.3755 | 13.1976 | 13.0271 | 12.9618 | 12.6261 | 12.325 | 12.0713 | 12.6326 | 12.5105 | 12.1116 | 11.9484 | 11.8179 | 11.6937 | 11.4558 | 11.2558 | 11.0632 | 10.9895 | 10.6116 | 10.2695 | 9.9789 | 12.962 | 12.8504 | 12.5051 | 12.3588 | 12.2388 | 12.1209 | 11.9072 | 11.7283 | 11.5578 | 11.4914 | 11.1546 | 10.8525 | 10.5978
|  | GOODLYBURN | FB |  |  |  |  | 14.2229 | 14.2008 | 14.1187 | 14.0482 | 13.9745 | 13.9039 | 13.8324 | 13.7408 | 13.625 | 13.5439 | 13.1387 | 12.7429 | 12.4608 | 12.6968 | 12.6242 | 12.2737 | 12.1947 | 12.1126 | 12.0337 | 11.9547 | 11.8505 | 11.7189 | 11.6284 | 11.1705 | 10.72 | 10.3958 | 13.0188 | 12.9546 | 12.6525 | 12.582 | 12.5083 | 12.4367 | 12.3662 | 12.2736 | 12.1567 | 12.0757 | 11.6693 | 11.2714 | 10.9883
| CHARLESTON | GOURDIE | MINIMUM HEADROOM | NO 34573 32203 | YES | YES | 0.092857 | 5.4958 | 5.0611 | 4.7463 | 4.2042 | 3.5295 | 2.9747 | 2.8811 | 2.66 | 2.44 | 2.4137 | 1.9105 | 1.7432 | 1.6295 | 5.6516 | 5.1326 | 4.7547 | 4.1053 | 3.2968 | 2.6284 | 2.5211 | 2.2537 | 1.9905 | 1.9621 | 1.3968 | 1.1895 | 1.0579 | 5.8589 | 5.3389 | 4.9611 | 4.3126 | 3.5032 | 2.8358 | 2.7284 | 2.4611 | 2.1989 | 2.1705 | 1.6095 | 1.4021 | 1.2705
|  | GOURDIE | EE |  |  |  |  | 5.5337 | 5.0611 | 4.7463 | 4.3158 | 3.6495 | 2.9747 | 2.8811 | 2.7084 | 2.4537 | 2.4137 | 1.9211 | 1.7432 | 1.6295 | 5.6989 | 5.1326 | 4.7547 | 4.2389 | 3.4389 | 2.6284 | 2.5211 | 2.3158 | 2.0126 | 1.9663 | 1.3968 | 1.1895 | 1.0579 | 5.9063 | 5.3389 | 4.9611 | 4.4463 | 3.6453 | 2.8358 | 2.7284 | 2.5232 | 2.22 | 2.1747 | 1.6095 | 1.4021 | 1.2705
|  | GOURDIE | HT |  |  |  |  | 5.4989 | 5.1274 | 4.7611 | 4.2042 | 3.5295 | 3.4126 | 3.2242 | 2.9242 | 2.6863 | 2.4821 | 1.9105 | 1.7642 | 1.6611 | 5.6568 | 5.2105 | 4.7737 | 4.1053 | 3.2968 | 3.1589 | 2.9368 | 2.5768 | 2.2947 | 2.0642 | 1.4316 | 1.2568 | 1.1053 | 5.8642 | 5.4179 | 4.98 | 4.3126 | 3.5032 | 3.3653 | 3.1432 | 2.7842 | 2.5021 | 2.2768 | 1.6432 | 1.4695 | 1.3179
|  | GOURDIE | HE |  |  |  |  | 5.4958 | 5.1789 | 4.8653 | 4.4126 | 3.7653 | 3.1063 | 2.9232 | 2.66 | 2.44 | 2.4158 | 2.1905 | 2.1116 | 2.0516 | 5.6516 | 5.2726 | 4.8958 | 4.3537 | 3.5758 | 2.7863 | 2.5684 | 2.2537 | 1.9905 | 1.9621 | 1.6958 | 1.6053 | 1.5337 | 5.8589 | 5.48 | 5.1021 | 4.56 | 3.7821 | 2.9937 | 2.7758 | 2.4611 | 2.1989 | 2.1705 | 1.9042 | 1.8137 | 1.7432
|  | GOURDIE | FB |  |  |  |  | 6.0253 | 5.8821 | 5.7347 | 5.62 | 5.4095 | 5.1358 | 4.9537 | 4.7874 | 4.6695 | 4.6421 | 4.3168 | 4.0695 | 4 | 6.2884 | 6.1158 | 5.9411 | 5.8032 | 5.5505 | 5.2221 | 5.0042 | 4.8053 | 4.6632 | 4.6326 | 4.2463 | 3.9526 | 3.8716 | 6.3989 | 6.2695 | 6.1379 | 6.0105 | 5.7568 | 5.4295 | 5.2105 | 5.0126 | 4.8705 | 4.8389 | 4.4526 | 4.1589 | 4.0779
| BOAT OF GARTEN | GRANTOWN | MINIMUM HEADROOM | NJ 03670 26311 | NO | YES | 0 | 12.88 | 12.7863 | 12.6853 | 12.58 | 12.4747 | 12.3589 | 12.2158 | 12.0579 | 11.9242 | 11.8463 | 11.5116 | 11.2042 | 10.9758 | 11.4853 | 11.3779 | 11.2579 | 11.1368 | 11.0158 | 10.8832 | 10.7179 | 10.5316 | 10.3747 | 10.2863 | 9.9021 | 9.5411 | 9.2705 | 11.5358 | 11.4326 | 11.3179 | 11.2 | 11.0832 | 10.9547 | 10.7958 | 10.6168 | 10.4653 | 10.38 | 10.0095 | 9.6621 | 9.3958
|  | GRANTOWN | EE |  |  |  |  | 12.88 | 12.7863 | 12.6853 | 12.58 | 12.4747 | 12.3589 | 12.2158 | 12.0579 | 11.9242 | 11.8463 | 11.5116 | 11.2042 | 10.9758 | 11.4853 | 11.3779 | 11.2579 | 11.1368 | 11.0158 | 10.8832 | 10.7179 | 10.5316 | 10.3747 | 10.2863 | 9.9021 | 9.5411 | 9.2705 | 11.5358 | 11.4326 | 11.3179 | 11.2 | 11.0832 | 10.9547 | 10.7958 | 10.6168 | 10.4653 | 10.38 | 10.0095 | 9.6621 | 9.3958
|  | GRANTOWN | HT |  |  |  |  | 12.9095 | 12.8263 | 12.7305 | 12.6389 | 12.5337 | 12.4442 | 12.3274 | 12.1832 | 12.0558 | 11.9674 | 11.5663 | 11.2779 | 11.08 | 11.52 | 11.4242 | 11.3147 | 11.2105 | 11.0884 | 10.9842 | 10.8463 | 10.6747 | 10.5253 | 10.4242 | 10.0421 | 9.6789 | 9.3832 | 11.5695 | 11.4779 | 11.3716 | 11.2705 | 11.1526 | 11.0537 | 10.92 | 10.7579 | 10.6147 | 10.5179 | 10.1505 | 9.8042 | 9.5158
|  | GRANTOWN | HE |  |  |  |  | 12.9453 | 12.9189 | 12.8642 | 12.8137 | 12.7537 | 12.6916 | 12.5989 | 12.4895 | 12.3947 | 12.3568 | 12.1874 | 12.0284 | 11.9137 | 11.5947 | 11.5347 | 11.4684 | 11.4116 | 11.3432 | 11.2768 | 11.1705 | 11.0389 | 10.9253 | 10.8811 | 10.6811 | 10.4895 | 10.3495 | 11.6432 | 11.5853 | 11.5211 | 11.4663 | 11.4 | 11.3347 | 11.2326 | 11.1084 | 11 | 10.9579 | 10.7663 | 10.5842 | 10.4526
|  | GRANTOWN | FB |  |  |  |  | 12.9611 | 12.9516 | 12.9358 | 12.9032 | 12.8674 | 12.8305 | 12.7905 | 12.72 | 12.6547 | 12.6053 | 12.4284 | 12.2484 | 12.1084 | 11.6284 | 11.5916 | 11.5474 | 11.5084 | 11.4663 | 11.4232 | 11.3747 | 11.2905 | 11.2105 | 11.1516 | 10.9411 | 10.7253 | 10.5537 | 11.6758 | 11.6411 | 11.5979 | 11.5611 | 11.5211 | 11.48 | 11.4337 | 11.3526 | 11.2768 | 11.2221 | 11.0211 | 10.8158 | 10.6537
| SHETLAND | GREMISTA | MINIMUM HEADROOM | HU4646842756 | NO | YES | 229.402 | 37.2779 | 36.2737 | 35.0758 | 33.7832 | 32.3326 | 30.8621 | 29.3663 | 28.0568 | 27.76 | 70.5253 | 68.1126 | 66.6979 | 66.5095 | 33.4074 | 32.3105 | 30.96 | 29.4632 | 27.7747 | 26.0579 | 24.3168 | 22.7926 | 22.4579 | 75.5568 | 73.2716 | 72.2442 | 72.0421 | 34.3789 | 33.2463 | 31.8905 | 30.4042 | 28.7284 | 27.0326 | 25.2916 | 23.7663 | 23.4326 | 71.3674 | 68.9011 | 67.3684 | 67.1589
|  | GREMISTA | EE |  |  |  |  | 37.2779 | 36.2737 | 35.0758 | 33.7832 | 32.3326 | 30.8621 | 29.3663 | 28.0568 | 27.76 | 73.9537 | 71.8884 | 71.2695 | 70.8821 | 33.4074 | 32.3105 | 30.96 | 29.4632 | 27.7747 | 26.0579 | 24.3168 | 22.7926 | 22.4579 | 80.4926 | 77.8758 | 77.1842 | 76.7526 | 34.3789 | 33.2463 | 31.8905 | 30.4042 | 28.7284 | 27.0326 | 25.2916 | 23.7663 | 23.4326 | 75.8368 | 72.9821 | 72.3 | 71.8716
|  | GREMISTA | HT |  |  |  |  | 37.3232 | 36.36 | 35.1642 | 33.8158 | 32.3558 | 31.0526 | 29.6937 | 28.3095 | 27.84 | 70.5253 | 68.1126 | 67.5821 | 67.2147 | 33.4568 | 32.4042 | 31.0632 | 29.5021 | 27.8053 | 26.2821 | 24.6968 | 23.0874 | 22.5505 | 75.5568 | 73.2716 | 72.6463 | 72.1326 | 34.4284 | 33.3421 | 31.9916 | 30.4442 | 28.7568 | 27.2537 | 25.6705 | 24.0611 | 23.5242 | 71.3674 | 68.9011 | 68.2821 | 67.7737
|  | GREMISTA | HE |  |  |  |  | 37.4389 | 36.52 | 35.3905 | 34.1537 | 32.7663 | 31.3621 | 29.8474 | 28.5695 | 28.2884 | 71.0884 | 69.6316 | 66.6979 | 66.5095 | 33.5821 | 32.5779 | 31.32 | 29.8884 | 28.2789 | 26.6389 | 24.8716 | 23.3832 | 23.0632 | 76.3884 | 74.6726 | 72.2442 | 72.0421 | 34.5579 | 33.5211 | 32.2421 | 30.8295 | 29.2263 | 27.6074 | 25.8463 | 24.3568 | 24.0379 | 72.1905 | 70.3916 | 67.3684 | 67.1589
|  | GREMISTA | FB |  |  |  |  | 39.9632 | 37.7968 | 37.3747 | 36.9579 | 36.4484 | 35.8589 | 35.1884 | 34.4158 | 34.2726 | 71.4589 | 71.3368 | 71.2358 | 71.1842 | 35.7358 | 33.9726 | 33.5126 | 33.0558 | 32.4989 | 31.8537 | 31.0863 | 30.1905 | 30.0284 | 79.3484 | 79.2263 | 79.1253 | 79.0737 | 36.8579 | 34.9579 | 34.4863 | 34.0147 | 33.44 | 32.7737 | 32.0147 | 31.1305 | 30.9695 | 75.2768 | 75.1547 | 75.0537 | 75.0021
| WILLOWDALE | GREYFRIARS | MINIMUM HEADROOM | NJ 94327 07070 | NO | YES | 0.16327 | 24.6621 | 24.62 | 24.5642 | 24.5011 | 24.4074 | 23.9821 | 23.7568 | 23.6105 | 23.4642 | 23.3221 | 22.9147 | 22.4737 | 22.0905 | 23.2495 | 23.2063 | 23.1474 | 23.0368 | 22.9642 | 22.7737 | 22.5063 | 22.3347 | 22.1621 | 21.9947 | 21.5779 | 21.0611 | 20.6032 | 23.88 | 23.7105 | 23.4263 | 23.0842 | 22.9063 | 22.3811 | 22.1105 | 21.9379 | 21.7642 | 21.5958 | 21.2421 | 20.72 | 20.2568
|  | GREYFRIARS | EE |  |  |  |  | 24.6621 | 24.6232 | 24.5779 | 24.5211 | 24.4726 | 23.9821 | 23.7568 | 23.6105 | 23.4642 | 23.3221 | 22.9147 | 22.4768 | 22.0937 | 23.2495 | 23.2116 | 23.1621 | 23.0705 | 23.0063 | 22.7737 | 22.5063 | 22.3347 | 22.1621 | 21.9947 | 21.5779 | 21.0611 | 20.6032 | 23.88 | 23.8063 | 23.5379 | 23.1916 | 23.0411 | 22.3811 | 22.1105 | 21.9379 | 21.7642 | 21.5958 | 21.2421 | 20.72 | 20.2568
|  | GREYFRIARS | HT |  |  |  |  | 24.6674 | 24.62 | 24.5642 | 24.5011 | 24.4074 | 24.0463 | 23.8842 | 23.7063 | 23.5 | 23.3232 | 22.9789 | 22.4737 | 22.0905 | 23.2537 | 23.2063 | 23.1474 | 23.0368 | 22.9642 | 22.8368 | 22.6653 | 22.4558 | 22.2116 | 22.0032 | 21.7726 | 21.1895 | 20.62 | 23.8958 | 23.7105 | 23.4263 | 23.0842 | 22.9063 | 22.4632 | 22.2705 | 22.0589 | 21.8126 | 21.6032 | 21.4389 | 20.8505 | 20.2758
|  | GREYFRIARS | HE |  |  |  |  | 24.6789 | 24.6411 | 24.6074 | 24.5632 | 24.5147 | 24.4474 | 24.3789 | 24.3284 | 24.28 | 24.1463 | 23.2821 | 22.8411 | 22.6295 | 23.2642 | 23.2274 | 23.1947 | 23.1505 | 23.1011 | 23.0326 | 22.96 | 22.8853 | 22.8105 | 22.7547 | 21.9621 | 21.4274 | 21.1737 | 23.9326 | 23.8768 | 23.8 | 23.6958 | 23.5884 | 23.4137 | 23.2221 | 23.0368 | 22.8326 | 22.6305 | 21.5621 | 21.0221 | 20.7663
|  | GREYFRIARS | FB |  |  |  |  | 24.6926 | 24.6737 | 24.6526 | 24.6284 | 24.6042 | 24.5758 | 24.5474 | 24.5168 | 24.4853 | 24.4516 | 24.1537 | 23.5747 | 23.3463 | 23.2768 | 23.2589 | 23.2389 | 23.2158 | 23.1916 | 23.1632 | 23.1337 | 23.1021 | 23.0695 | 23.0284 | 22.8084 | 22.3063 | 22.0326 | 23.9526 | 23.9179 | 23.8821 | 23.8295 | 23.7832 | 23.7053 | 23.6147 | 23.5074 | 23.3916 | 23.2705 | 22.62 | 21.9105 | 21.6337
| SHETLAND | GUTCHER | MINIMUM HEADROOM | HU5453899599 | YES | YES | 0 | 0.98737 | 0.98105 | 0.97474 | 0.96842 | 0.96 | 0.95368 | 0.94737 | 0.94105 | 0.93368 | 0.92737 | 0.90421 | 0.88526 | 0.87053 | 0.98526 | 0.97789 | 0.97053 | 0.96316 | 0.95474 | 0.94737 | 0.94 | 0.93368 | 0.92526 | 0.91895 | 0.89579 | 0.87474 | 0.85684 | 0.98526 | 0.97789 | 0.97158 | 0.96421 | 0.95579 | 0.94737 | 0.94105 | 0.93368 | 0.92632 | 0.92 | 0.89684 | 0.87579 | 0.85684
|  | GUTCHER | EE |  |  |  |  | 0.98737 | 0.98105 | 0.97474 | 0.96842 | 0.96 | 0.95368 | 0.94737 | 0.94105 | 0.93368 | 0.92737 | 0.90632 | 0.88737 | 0.87368 | 0.98526 | 0.97789 | 0.97053 | 0.96316 | 0.95474 | 0.94737 | 0.94 | 0.93368 | 0.92526 | 0.91895 | 0.89579 | 0.87474 | 0.85895 | 0.98526 | 0.97789 | 0.97158 | 0.96421 | 0.95579 | 0.94737 | 0.94105 | 0.93368 | 0.92632 | 0.92 | 0.89684 | 0.87579 | 0.86
|  | GUTCHER | HT |  |  |  |  | 0.98947 | 0.98316 | 0.97684 | 0.97053 | 0.96316 | 0.95789 | 0.95158 | 0.94421 | 0.93684 | 0.93053 | 0.90421 | 0.88526 | 0.87053 | 0.98737 | 0.98 | 0.97263 | 0.96632 | 0.95789 | 0.95263 | 0.94526 | 0.93684 | 0.92947 | 0.92211 | 0.89789 | 0.87684 | 0.85684 | 0.98737 | 0.98105 | 0.97263 | 0.96632 | 0.95895 | 0.95368 | 0.94526 | 0.93789 | 0.93053 | 0.92316 | 0.89895 | 0.87684 | 0.85684
|  | GUTCHER | HE |  |  |  |  | 0.99474 | 0.98947 | 0.98526 | 0.98105 | 0.97684 | 0.97158 | 0.96737 | 0.96316 | 0.95789 | 0.95474 | 0.94211 | 0.93474 | 0.92842 | 0.99263 | 0.98737 | 0.98316 | 0.97789 | 0.97368 | 0.96842 | 0.96316 | 0.95895 | 0.95368 | 0.94947 | 0.93579 | 0.92737 | 0.92105 | 0.99263 | 0.98737 | 0.98316 | 0.97789 | 0.97474 | 0.96842 | 0.96316 | 0.96 | 0.95368 | 0.95053 | 0.93684 | 0.92842 | 0.92211
|  | GUTCHER | FB |  |  |  |  | 0.99684 | 0.99368 | 0.99158 | 0.98842 | 0.98526 | 0.98211 | 0.97895 | 0.97684 | 0.97263 | 0.96842 | 0.95579 | 0.94211 | 0.93368 | 0.99579 | 0.99158 | 0.98842 | 0.98632 | 0.98211 | 0.97895 | 0.97579 | 0.97263 | 0.96842 | 0.96421 | 0.94947 | 0.93368 | 0.92421 | 0.99579 | 0.99158 | 0.98947 | 0.98632 | 0.98211 | 0.98 | 0.97579 | 0.97368 | 0.96947 | 0.96526 | 0.94947 | 0.93474 | 0.92526
| THURSO | HALKIRK | MINIMUM HEADROOM | ND 13246 58223 | YES | YES | 0 | 6.1874 | 6.1537 | 6.1253 | 6.0937 | 6.0579 | 5.9116 | 5.8053 | 5.7263 | 5.6779 | 5.5968 | 5.3495 | 5.2453 | 5.1747 | 6.2442 | 6.2253 | 6.2095 | 6.1916 | 6.1705 | 6.1042 | 6.0558 | 6.0179 | 5.9726 | 5.8832 | 5.6263 | 5.5105 | 5.4126 | 6.44 | 6.4126 | 6.3895 | 6.3632 | 6.3347 | 6.2232 | 6.1421 | 6.0811 | 6.0411 | 5.9789 | 5.7274 | 5.6116 | 5.5137
|  | HALKIRK | EE |  |  |  |  | 6.1874 | 6.1537 | 6.1253 | 6.0937 | 6.0579 | 6.0168 | 5.9789 | 5.8305 | 5.7253 | 5.6358 | 5.3705 | 5.2705 | 5.1947 | 6.2442 | 6.2253 | 6.2095 | 6.1916 | 6.1705 | 6.1442 | 6.1189 | 6.0568 | 6.0084 | 5.9263 | 5.6263 | 5.5158 | 5.4305 | 6.44 | 6.4126 | 6.3895 | 6.3632 | 6.3347 | 6.3 | 6.2674 | 6.1568 | 6.0758 | 6.0084 | 5.7274 | 5.6168 | 5.5326
|  | HALKIRK | HT |  |  |  |  | 6.1979 | 6.1663 | 6.1379 | 6.1084 | 6.0705 | 5.9116 | 5.8053 | 5.7263 | 5.6779 | 5.5968 | 5.3495 | 5.2453 | 5.1747 | 6.2495 | 6.2305 | 6.2137 | 6.1947 | 6.1716 | 6.1042 | 6.0558 | 6.0179 | 5.9726 | 5.8832 | 5.6368 | 5.5105 | 5.4126 | 6.4474 | 6.4221 | 6.3979 | 6.3737 | 6.3421 | 6.2232 | 6.1421 | 6.0811 | 6.0411 | 5.9789 | 5.7368 | 5.6116 | 5.5137
|  | HALKIRK | HE |  |  |  |  | 6.2189 | 6.1979 | 6.1811 | 6.1611 | 6.1347 | 6.1105 | 6.0811 | 5.9295 | 5.8305 | 5.7547 | 5.5516 | 5.4916 | 5.4463 | 6.26 | 6.2453 | 6.2358 | 6.2211 | 6.2042 | 6.1853 | 6.1632 | 6.1021 | 6.06 | 6.0295 | 5.8284 | 5.7621 | 5.7105 | 6.4642 | 6.4463 | 6.4326 | 6.4147 | 6.3926 | 6.3705 | 6.3442 | 6.2316 | 6.1579 | 6.1021 | 5.9274 | 5.8611 | 5.8105
|  | HALKIRK | FB |  |  |  |  | 6.2316 | 6.2189 | 6.2053 | 6.1916 | 6.1747 | 6.16 | 6.1442 | 6.1284 | 6.0568 | 6 | 5.7747 | 5.7074 | 5.6547 | 6.2684 | 6.2611 | 6.2537 | 6.2463 | 6.2368 | 6.2284 | 6.2189 | 6.2105 | 6.1811 | 6.1568 | 6.06 | 6.0021 | 5.9421 | 6.4747 | 6.4653 | 6.4537 | 6.4432 | 6.4295 | 6.4168 | 6.4042 | 6.3916 | 6.3379 | 6.2958 | 6.1263 | 6.0737 | 6.0326
| ABERNETHY | HARBOUR | MINIMUM HEADROOM | NO 11948 22049 | NO | YES | 0 | 22.8926 | 22.8568 | 22.6705 | 22.3568 | 22.1926 | 21.9305 | 21.6253 | 21.3653 | 21.0432 | 20.9189 | 20.2021 | 19.7789 | 19.4779 | 22.1211 | 21.9147 | 21.7011 | 21.3411 | 21.1568 | 20.8568 | 20.5063 | 20.2105 | 19.8411 | 19.7053 | 18.9937 | 18.4968 | 18.0811 | 22.0242 | 21.9779 | 21.9295 | 21.7442 | 21.56 | 21.2611 | 20.9095 | 20.6147 | 20.2442 | 20.1084 | 19.3958 | 18.8989 | 18.4832
|  | HARBOUR | EE |  |  |  |  | 22.8926 | 22.8568 | 22.6926 | 22.4211 | 22.2705 | 22.0211 | 21.8074 | 21.5937 | 21.2284 | 21.1316 | 20.3032 | 19.8621 | 19.5442 | 22.1211 | 21.9147 | 21.7253 | 21.4126 | 21.2421 | 20.9589 | 20.7179 | 20.4747 | 20.0537 | 19.9453 | 18.9979 | 18.4968 | 18.1347 | 22.0242 | 21.9779 | 21.9389 | 21.8168 | 21.6453 | 21.3621 | 21.12 | 20.8789 | 20.4568 | 20.3484 | 19.4011 | 18.8989 | 18.5368
|  | HARBOUR | HT |  |  |  |  | 22.8958 | 22.86 | 22.6705 | 22.3568 | 22.1926 | 21.9305 | 21.6253 | 21.3653 | 21.0432 | 20.9189 | 20.2021 | 19.7789 | 19.4779 | 22.1253 | 21.9389 | 21.7011 | 21.3411 | 21.1568 | 20.8568 | 20.5063 | 20.2105 | 19.8411 | 19.7053 | 18.9937 | 18.5116 | 18.0811 | 22.0295 | 21.9811 | 21.9295 | 21.7442 | 21.56 | 21.2611 | 20.9095 | 20.6147 | 20.2442 | 20.1084 | 19.3958 | 18.9137 | 18.4832
|  | HARBOUR | HE |  |  |  |  | 22.9116 | 22.8779 | 22.8326 | 22.5895 | 22.4811 | 22.2916 | 22.0116 | 21.82 | 21.42 | 21.3684 | 20.9042 | 20.6737 | 20.4832 | 22.1442 | 22.0547 | 21.8863 | 21.6063 | 21.4863 | 21.2726 | 20.9537 | 20.7337 | 20.2705 | 20.2116 | 19.6789 | 19.4168 | 19.1989 | 22.0495 | 22.0053 | 21.9726 | 21.9242 | 21.8789 | 21.6768 | 21.3568 | 21.1379 | 20.6737 | 20.6147 | 20.0832 | 19.82 | 19.6021
|  | HARBOUR | FB |  |  |  |  | 22.9274 | 22.9147 | 22.9011 | 22.8863 | 22.8695 | 22.8368 | 22.7432 | 22.66 | 22.5179 | 22.4537 | 21.9 | 21.46 | 21.2484 | 22.1632 | 22.1474 | 22.1295 | 22.0505 | 21.9905 | 21.8916 | 21.7842 | 21.6905 | 21.5253 | 21.4547 | 20.8168 | 20.3105 | 20.0674 | 22.0695 | 22.0516 | 22.0337 | 22.0126 | 21.9926 | 21.9716 | 21.9484 | 21.9253 | 21.8979 | 21.8589 | 21.22 | 20.7137 | 20.4716
| ARDMORE | HARRIS GRID | MINIMUM HEADROOM | NG 13500 94249 | YES | YES | 0 | 29.9916 | 29.8505 | 29.8032 | 29.7979 | 29.7937 | 28.4305 | 28.4253 | 28.4221 | 28.4189 | 28.4147 | 25.1347 | 25.1211 | 25.1126 | 29.9905 | 29.8242 | 29.7695 | 29.7621 | 29.7589 | 28.6758 | 28.6705 | 28.6663 | 28.6632 | 28.6589 | 26.0263 | 26.0126 | 26.0021 | 29.9905 | 29.8242 | 29.7695 | 29.7632 | 29.7589 | 28.3989 | 28.3937 | 28.3895 | 28.3863 | 28.3821 | 25.1042 | 25.0905 | 25.08
|  | HARRIS GRID | EE |  |  |  |  | 29.9916 | 29.9884 | 29.8032 | 29.7979 | 29.7937 | 28.4305 | 28.4253 | 28.4221 | 28.4189 | 28.4147 | 25.1347 | 25.1211 | 25.1126 | 29.9905 | 29.9863 | 29.7695 | 29.7621 | 29.7589 | 28.6758 | 28.6705 | 28.6663 | 28.6632 | 28.6589 | 26.0263 | 26.0126 | 26.0021 | 29.9905 | 29.9863 | 29.7695 | 29.7632 | 29.7589 | 28.3989 | 28.3937 | 28.3895 | 28.3863 | 28.3821 | 25.1042 | 25.0905 | 25.08
|  | HARRIS GRID | HT |  |  |  |  | 29.9937 | 29.8505 | 29.8474 | 29.8421 | 29.8379 | 28.4716 | 28.4674 | 28.4632 | 28.4589 | 28.4547 | 25.8242 | 25.8126 | 25.8032 | 29.9926 | 29.8242 | 29.82 | 29.8147 | 29.8105 | 28.7242 | 28.72 | 28.7147 | 28.7105 | 28.7063 | 26.5947 | 26.5811 | 26.5695 | 29.9926 | 29.8242 | 29.8211 | 29.8147 | 29.8116 | 28.4474 | 28.4432 | 28.4379 | 28.4337 | 28.4295 | 25.8021 | 25.7884 | 25.7768
|  | HARRIS GRID | HE |  |  |  |  | 29.9968 | 29.9926 | 29.8084 | 29.8074 | 29.8042 | 28.4421 | 28.4389 | 28.4368 | 28.4326 | 28.4305 | 27.1168 | 27.1105 | 27.1063 | 29.9958 | 29.9926 | 29.7758 | 29.7737 | 29.7705 | 28.6895 | 28.6863 | 28.6832 | 28.68 | 28.6768 | 27.6232 | 27.6158 | 27.6116 | 29.9958 | 29.9926 | 29.7758 | 29.7747 | 29.7716 | 28.4126 | 28.4095 | 28.4063 | 28.4032 | 28.4 | 27.0874 | 27.0811 | 27.0758
|  | HARRIS GRID | FB |  |  |  |  | 29.9979 | 29.9958 | 29.9937 | 29.9168 | 29.9158 | 29.9137 | 29.9116 | 29.9095 | 29.9084 | 29.9063 | 29.8968 | 29.8853 | 29.8779 | 29.9968 | 29.9958 | 29.9937 | 29.9032 | 29.9011 | 29.8989 | 29.8968 | 29.8947 | 29.8937 | 29.8905 | 29.88 | 29.8674 | 29.8589 | 29.9968 | 29.9958 | 29.9937 | 29.9032 | 29.9011 | 29.8989 | 29.8979 | 29.8947 | 29.8937 | 29.8905 | 29.88 | 29.8674 | 29.8589
| DYCE | HARVEST AVENUE | MINIMUM HEADROOM | NJ 86978 11769 | NO | YES | 0 | 23.9147 | 23.9116 | 23.9084 | 23.9021 | 23.8989 | 23.8926 | 23.8863 | 23.8821 | 23.8758 | 23.8716 | 23.8537 | 23.8379 | 23.8274 | 22.5158 | 22.5095 | 22.5032 | 22.4895 | 22.4811 | 22.4684 | 22.4579 | 22.4474 | 22.4368 | 22.4274 | 22.3916 | 22.3568 | 22.3295 | 23.0916 | 23.0863 | 23.08 | 23.0684 | 23.06 | 23.0484 | 23.0389 | 23.0295 | 23.02 | 23.0116 | 22.9789 | 22.9474 | 22.9232
|  | HARVEST AVENUE | EE |  |  |  |  | 23.9147 | 23.9116 | 23.9084 | 23.9021 | 23.8989 | 23.8926 | 23.8863 | 23.8821 | 23.8758 | 23.8716 | 23.8547 | 23.84 | 23.8274 | 22.5158 | 22.5095 | 22.5032 | 22.4895 | 22.4811 | 22.4684 | 22.4579 | 22.4474 | 22.4368 | 22.4274 | 22.3916 | 22.3568 | 22.3295 | 23.0916 | 23.0863 | 23.08 | 23.0684 | 23.06 | 23.0484 | 23.0389 | 23.0295 | 23.02 | 23.0116 | 22.9789 | 22.9474 | 22.9232
|  | HARVEST AVENUE | HT |  |  |  |  | 23.9158 | 23.9137 | 23.9095 | 23.9053 | 23.9 | 23.8968 | 23.8916 | 23.8842 | 23.8789 | 23.8737 | 23.8537 | 23.8379 | 23.8274 | 22.5168 | 22.5137 | 22.5074 | 22.4989 | 22.4874 | 22.4789 | 22.4674 | 22.4568 | 22.4463 | 22.4358 | 22.4011 | 22.3663 | 22.3358 | 23.0926 | 23.0895 | 23.0832 | 23.0758 | 23.0663 | 23.0579 | 23.0474 | 23.0379 | 23.0284 | 23.0189 | 22.9863 | 22.9558 | 22.9284
|  | HARVEST AVENUE | HE |  |  |  |  | 23.9179 | 23.9158 | 23.9137 | 23.9105 | 23.9084 | 23.9063 | 23.9021 | 23.9 | 23.8979 | 23.8937 | 23.8853 | 23.8758 | 23.8705 | 22.5221 | 22.5179 | 22.5147 | 22.5116 | 22.5084 | 22.5042 | 22.5 | 22.4947 | 22.4895 | 22.4832 | 22.4642 | 22.4432 | 22.4305 | 23.0968 | 23.0937 | 23.0905 | 23.0874 | 23.0842 | 23.0811 | 23.0758 | 23.0716 | 23.0663 | 23.0611 | 23.0432 | 23.0253 | 23.0137
|  | HARVEST AVENUE | FB |  |  |  |  | 23.9179 | 23.9179 | 23.9158 | 23.9147 | 23.9137 | 23.9116 | 23.9105 | 23.9095 | 23.9074 | 23.9042 | 23.8947 | 23.8853 | 23.8768 | 22.5221 | 22.5211 | 22.5179 | 22.5158 | 22.5147 | 22.5116 | 22.5084 | 22.5063 | 22.5021 | 22.4958 | 22.4737 | 22.4516 | 22.4316 | 23.0979 | 23.0958 | 23.0937 | 23.0916 | 23.0905 | 23.0874 | 23.0853 | 23.0821 | 23.0789 | 23.0737 | 23.0526 | 23.0337 | 23.0158
| THURSO | HASTIGROW | MINIMUM HEADROOM | ND 26576 60773 | YES | YES | 0 | 3.1869 | 3.1354 | 3.0901 | 3.0375 | 2.9859 | 0.58589 | -1.8078 | -4.192 | -6.5762 | -8.9531 | -10.2152 | -10.3646 | -10.4731 | 2.8364 | 2.7775 | 2.7238 | 2.6617 | 2.6027 | 0.19432 | -2.2057 | -4.5973 | -6.9867 | -9.3709 | -10.4057 | -10.5815 | -10.7078 | 2.8691 | 2.8101 | 2.7564 | 2.6943 | 2.6343 | 0.22589 | -2.1741 | -4.5657 | -6.9552 | -9.3383 | -10.6131 | -10.7888 | -10.9162
|  | HASTIGROW | EE |  |  |  |  | 3.1869 | 3.1354 | 3.0901 | 3.0375 | 2.9859 | 0.58589 | -1.8078 | -4.192 | -6.5762 | -8.9531 | -10.2152 | -10.3646 | -10.4731 | 2.8364 | 2.7775 | 2.7238 | 2.6617 | 2.6027 | 0.19432 | -2.2057 | -4.5973 | -6.9867 | -9.3709 | -10.4057 | -10.5815 | -10.7078 | 2.8691 | 2.8101 | 2.7564 | 2.6943 | 2.6343 | 0.22589 | -2.1741 | -4.5657 | -6.9552 | -9.3383 | -10.6131 | -10.7888 | -10.9162
|  | HASTIGROW | HT |  |  |  |  | 3.1943 | 3.1543 | 3.1091 | 3.0596 | 3.0017 | 0.61432 | -1.7741 | -4.1615 | -6.5478 | -8.9373 | -10.0362 | -10.1994 | -10.3131 | 2.8533 | 2.7996 | 2.748 | 2.6912 | 2.6259 | 0.23116 | -2.1646 | -4.5583 | -6.9499 | -9.3457 | -10.2288 | -10.4331 | -10.6004 | 2.8869 | 2.8322 | 2.7806 | 2.7238 | 2.6575 | 0.26379 | -2.132 | -4.5257 | -6.9183 | -9.3141 | -10.3878 | -10.5931 | -10.7615
|  | HASTIGROW | HE |  |  |  |  | 3.2017 | 3.1869 | 3.1733 | 3.1417 | 3.1038 | 3.0638 | 3.0227 | 0.65537 | -1.7131 | -4.0699 | -9.2825 | -9.3709 | -9.4309 | 2.8922 | 2.8564 | 2.8238 | 2.788 | 2.7459 | 2.7027 | 2.6575 | 0.28589 | -2.0846 | -4.4457 | -9.5741 | -9.6794 | -9.7499 | 2.9259 | 2.8891 | 2.8575 | 2.8206 | 2.7785 | 2.7354 | 2.6901 | 0.31853 | -2.052 | -4.4131 | -9.6373 | -9.7425 | -9.8141
|  | HASTIGROW | FB |  |  |  |  | 3.2101 | 3.2048 | 3.1985 | 3.1912 | 3.1669 | 3.1448 | 3.1227 | 3.1006 | 3.0785 | 3.0491 | 2.9501 | 2.8459 | 2.7712 | 2.9069 | 2.8901 | 2.8669 | 2.8417 | 2.8143 | 2.788 | 2.7617 | 2.7375 | 2.7122 | 2.6775 | 2.5617 | 2.4385 | 2.3469 | 2.9469 | 2.9238 | 2.8996 | 2.8743 | 2.8469 | 2.8206 | 2.7954 | 2.7701 | 2.7448 | 2.7101 | 2.5933 | 2.4701 | 2.3806
| STRICHEN | HATTON | MINIMUM HEADROOM | NK 06441 37348 | NO | YES | 0.36735 | 5.6379 | 5.4221 | 5.2316 | 5.0032 | 4.8516 | 4.6705 | 4.5716 | 4.4253 | 4.2347 | 4.1021 | 2.8411 | 2.4663 | 2.2958 | 4.7211 | 4.4526 | 4.2137 | 3.9284 | 3.7421 | 3.5211 | 3.4042 | 3.2284 | 3.0105 | 2.86 | 2.3905 | 1.4368 | 1.2337 | 5.4832 | 5.2221 | 4.9905 | 4.7137 | 4.5337 | 4.3179 | 4.2032 | 4.0316 | 3.82 | 3.6737 | 3.1811 | 1.9726 | 1.7705
|  | HATTON | EE |  |  |  |  | 5.6379 | 5.4221 | 5.2316 | 5.0032 | 4.8516 | 4.6705 | 4.5716 | 4.4695 | 4.34 | 4.2463 | 3.6421 | 2.4663 | 2.2958 | 4.7211 | 4.4526 | 4.2137 | 3.9284 | 3.7421 | 3.5211 | 3.4042 | 3.2821 | 3.1326 | 3.0274 | 2.3905 | 1.4368 | 1.2337 | 5.4832 | 5.2221 | 4.9905 | 4.7137 | 4.5337 | 4.3179 | 4.2032 | 4.0853 | 3.9389 | 3.8358 | 3.1811 | 1.9726 | 1.7705
|  | HATTON | HT |  |  |  |  | 5.6495 | 5.4579 | 5.2621 | 5.0411 | 4.8716 | 4.7295 | 4.5905 | 4.4253 | 4.2347 | 4.1021 | 2.8411 | 2.5947 | 2.4179 | 4.7347 | 4.4958 | 4.2537 | 3.9768 | 3.7695 | 3.5968 | 3.4284 | 3.2284 | 3.0105 | 2.86 | 2.3947 | 1.5442 | 1.2947 | 5.4968 | 5.2642 | 5.0295 | 4.7611 | 4.5589 | 4.3905 | 4.2263 | 4.0316 | 3.82 | 3.6737 | 3.1916 | 2.1432 | 1.8916
|  | HATTON | HE |  |  |  |  | 5.6853 | 5.5158 | 5.3463 | 5.1453 | 5.0158 | 4.8558 | 4.7758 | 4.6958 | 4.5853 | 4.5211 | 4.0853 | 3.5979 | 3.4905 | 4.7779 | 4.5663 | 4.3547 | 4.1032 | 3.9453 | 3.7495 | 3.6579 | 3.5611 | 3.4263 | 3.3484 | 2.86 | 2.4558 | 2.3326 | 5.5379 | 5.3337 | 5.1274 | 4.8842 | 4.7305 | 4.54 | 4.4495 | 4.3558 | 4.2242 | 4.1484 | 3.66 | 3.1663 | 3.0474
|  | HATTON | FB |  |  |  |  | 5.7958 | 5.7274 | 5.6537 | 5.5853 | 5.5053 | 5.4084 | 5.3558 | 5.3053 | 5.2632 | 5.2105 | 4.9726 | 4.7789 | 4.6768 | 4.9158 | 4.8305 | 4.7389 | 4.6537 | 4.5537 | 4.4326 | 4.3684 | 4.3063 | 4.2558 | 4.1905 | 3.8989 | 3.66 | 3.5337 | 5.6474 | 5.5874 | 5.5011 | 5.4179 | 5.3211 | 5.2032 | 5.1411 | 5.0811 | 5.0305 | 4.9674 | 4.6842 | 4.4516 | 4.3295
| PERSLEY | HAUDAGAIN | MINIMUM HEADROOM | NJ 91425 09066 | NO | NO | 0.13265 | 20.6853 | 20.5758 | 20.5095 | 20.4358 | 20.3442 | 20.2484 | 20.1526 | 20.0579 | 19.9463 | 19.7979 | 19.34 | 18.8411 | 18.4642 | 19.8747 | 19.82 | 19.7516 | 19.6147 | 19.4474 | 19.2937 | 19.1463 | 19 | 18.8716 | 18.6947 | 18.1674 | 17.6895 | 17.12 | 20.2526 | 20.12 | 20.0432 | 19.9568 | 19.8505 | 19.7432 | 19.6379 | 19.54 | 19.4516 | 19.3432 | 18.9916 | 18.5589 | 17.9884
|  | HAUDAGAIN | EE |  |  |  |  | 20.6853 | 20.5758 | 20.5095 | 20.4358 | 20.3442 | 20.2484 | 20.1526 | 20.0579 | 19.9463 | 19.7979 | 19.3453 | 18.9442 | 18.5705 | 19.8747 | 19.82 | 19.7516 | 19.6147 | 19.4474 | 19.2937 | 19.1463 | 19 | 18.8716 | 18.6947 | 18.1674 | 17.6895 | 17.2347 | 20.2526 | 20.12 | 20.0432 | 19.9568 | 19.8505 | 19.7432 | 19.6379 | 19.54 | 19.4516 | 19.3432 | 18.9916 | 18.5589 | 18.1021
|  | HAUDAGAIN | HT |  |  |  |  | 20.7032 | 20.5989 | 20.5295 | 20.4547 | 20.3558 | 20.2758 | 20.1958 | 20.1137 | 20.0295 | 19.8495 | 19.34 | 18.8411 | 18.4642 | 19.8821 | 19.8326 | 19.7811 | 19.6789 | 19.4979 | 19.3695 | 19.2421 | 19.1147 | 18.9832 | 18.7653 | 18.2747 | 17.6905 | 17.12 | 20.2726 | 20.1484 | 20.0695 | 19.9842 | 19.8695 | 19.78 | 19.6916 | 19.6011 | 19.5074 | 19.3674 | 19.0326 | 18.56 | 17.9884
|  | HAUDAGAIN | HE |  |  |  |  | 20.7389 | 20.6432 | 20.5979 | 20.5421 | 20.4642 | 20.3811 | 20.2884 | 20.2295 | 20.1726 | 20.1158 | 19.9368 | 19.7326 | 19.5305 | 19.8958 | 19.8484 | 19.8179 | 19.7737 | 19.7158 | 19.6242 | 19.4905 | 19.3979 | 19.3126 | 19.1947 | 18.8821 | 18.6411 | 18.3937 | 20.3168 | 20.2042 | 20.1526 | 20.0916 | 20.0042 | 19.9147 | 19.8137 | 19.7484 | 19.6863 | 19.6179 | 19.4158 | 19.2632 | 19.1211
|  | HAUDAGAIN | FB |  |  |  |  | 20.7874 | 20.7368 | 20.7032 | 20.6674 | 20.6242 | 20.5842 | 20.5453 | 20.5011 | 20.4579 | 20.4032 | 20.2253 | 20.06 | 19.8516 | 19.9168 | 19.8947 | 19.8747 | 19.8526 | 19.8274 | 19.8021 | 19.7737 | 19.7432 | 19.7074 | 19.6263 | 19.3158 | 19.0147 | 18.7558 | 20.3747 | 20.3147 | 20.2758 | 20.2358 | 20.1853 | 20.14 | 20.0968 | 20.0453 | 19.9958 | 19.9326 | 19.7295 | 19.5379 | 19.3884
| WILLOWDALE | HAYTON | MINIMUM HEADROOM | NJ 92753 08909 | NO | YES | 0 | 22.3395 | 22.3111 | 22.3363 | 22.3216 | 22.3068 | 22.1984 | 22.1532 | 22.1247 | 22.0963 | 21.9879 | 21.3984 | 20.9816 | 20.6605 | 21.2274 | 21.1968 | 21.2242 | 21.2084 | 21.1905 | 21.0789 | 21.0305 | 20.9989 | 20.9653 | 20.9463 | 20.4453 | 20.2611 | 19.8221 | 21.6655 | 21.6361 | 21.6634 | 21.6487 | 21.6329 | 21.5203 | 21.4697 | 21.4371 | 21.3466 | 21.2708 | 20.5929 | 20.4066 | 20.0276
|  | HAYTON | EE |  |  |  |  | 22.3395 | 22.3111 | 22.5574 | 22.53 | 22.4974 | 22.4542 | 22.4068 | 22.3711 | 22.2921 | 22.1668 | 21.4058 | 21.0395 | 20.7153 | 21.2274 | 21.1968 | 21.5379 | 21.5074 | 21.4695 | 21.4253 | 21.3768 | 21.3347 | 21.2916 | 21.2547 | 20.68 | 20.2747 | 19.9168 | 21.6655 | 21.6361 | 21.9245 | 21.895 | 21.8603 | 21.8161 | 21.7687 | 21.7308 | 21.6918 | 21.6582 | 20.8676 | 20.4529 | 20.0845
|  | HAYTON | HT |  |  |  |  | 22.3458 | 22.59 | 22.5626 | 22.5321 | 22.4984 | 22.4626 | 22.4268 | 22.3689 | 22.1426 | 21.9879 | 21.3984 | 20.9816 | 20.6605 | 21.2337 | 21.5716 | 21.5421 | 21.5074 | 21.4695 | 21.4305 | 21.3863 | 21.3379 | 21.2863 | 21.2368 | 20.7274 | 20.2737 | 19.8221 | 21.6729 | 21.9603 | 21.9318 | 21.9003 | 21.8666 | 21.8308 | 21.7939 | 21.7561 | 21.6961 | 21.5318 | 20.9371 | 20.4813 | 20.0276
|  | HAYTON | HE |  |  |  |  | 22.3511 | 22.3237 | 22.5732 | 22.5458 | 22.5121 | 22.1984 | 22.1532 | 22.1247 | 22.0963 | 22.0816 | 21.4026 | 21.2353 | 21.0584 | 21.2421 | 21.2126 | 21.5579 | 21.5274 | 21.4916 | 21.0789 | 21.0305 | 20.9989 | 20.9653 | 20.9463 | 20.4453 | 20.2611 | 20.0611 | 21.6782 | 21.6508 | 21.9424 | 21.9139 | 21.8803 | 21.5203 | 21.4697 | 21.4371 | 21.3466 | 21.2708 | 20.5929 | 20.4066 | 20.2034
|  | HAYTON | FB |  |  |  |  | 22.3626 | 22.35 | 22.3363 | 22.3216 | 22.3068 | 22.29 | 22.2732 | 22.2563 | 22.2384 | 22.2195 | 22.0805 | 21.6532 | 21.4805 | 21.2537 | 21.2389 | 21.2242 | 21.2084 | 21.1905 | 21.1716 | 21.1537 | 21.1347 | 21.1137 | 21.0916 | 21.0074 | 20.7189 | 20.5221 | 21.6887 | 21.6761 | 21.6634 | 21.6487 | 21.6329 | 21.6161 | 21.5982 | 21.5792 | 21.5571 | 21.535 | 21.2718 | 20.8445 | 20.6729
| BRORA | HELMSDALE | MINIMUM HEADROOM | ND 02372 15376 | YES | YES | 0 | 1.2511 | 1.2237 | 1.1995 | 1.17 | 1.1384 | 1.0174 | 0.91421 | 0.83947 | 0.79632 | 0.73 | 0.61211 | 0.52053 | 0.44789 | 1.2595 | 1.2332 | 1.2089 | 1.1805 | 1.1489 | 1.0489 | 0.95632 | 0.88895 | 0.84895 | 0.77632 | 0.66053 | 0.57 | 0.49632 | 1.2353 | 1.2047 | 1.1784 | 1.1447 | 1.11 | 0.96895 | 0.84895 | 0.76158 | 0.71316 | 0.63947 | 0.50579 | 0.40263 | 0.32053
|  | HELMSDALE | EE |  |  |  |  | 1.2511 | 1.2237 | 1.1995 | 1.17 | 1.1384 | 1.1079 | 1.0795 | 0.92053 | 0.81211 | 0.73 | 0.61211 | 0.52053 | 0.44789 | 1.2595 | 1.2332 | 1.2089 | 1.1805 | 1.1489 | 1.1195 | 1.0911 | 0.94789 | 0.84895 | 0.77632 | 0.66053 | 0.57 | 0.49632 | 1.2353 | 1.2047 | 1.1784 | 1.1447 | 1.11 | 1.0753 | 1.0447 | 0.85842 | 0.73211 | 0.63947 | 0.50579 | 0.40263 | 0.32053
|  | HELMSDALE | HT |  |  |  |  | 1.2605 | 1.2416 | 1.2226 | 1.2026 | 1.1774 | 1.0174 | 0.91421 | 0.83947 | 0.79632 | 0.77526 | 0.66895 | 0.59211 | 0.53316 | 1.27 | 1.2511 | 1.2342 | 1.2142 | 1.1921 | 1.0489 | 0.95632 | 0.88895 | 0.85 | 0.83 | 0.74895 | 0.67105 | 0.59947 | 1.2468 | 1.2247 | 1.2047 | 1.1816 | 1.1553 | 0.96895 | 0.84895 | 0.76158 | 0.71316 | 0.69 | 0.59421 | 0.50263 | 0.41737
|  | HELMSDALE | HE |  |  |  |  | 1.2732 | 1.2584 | 1.2468 | 1.2321 | 1.2163 | 1.2005 | 1.1826 | 1.0216 | 0.91632 | 0.85105 | 0.79632 | 0.75105 | 0.71842 | 1.2816 | 1.2668 | 1.2553 | 1.2416 | 1.2258 | 1.2111 | 1.1932 | 1.05 | 0.95632 | 0.89842 | 0.84579 | 0.80158 | 0.76895 | 1.2616 | 1.2447 | 1.2321 | 1.2163 | 1.1984 | 1.1816 | 1.1626 | 0.97421 | 0.85316 | 0.77737 | 0.71421 | 0.66158 | 0.62579
|  | HELMSDALE | FB |  |  |  |  | 1.2805 | 1.2732 | 1.2647 | 1.2574 | 1.2458 | 1.2384 | 1.2289 | 1.2205 | 1.15 | 1.0932 | 0.97842 | 0.93421 | 0.90474 | 1.2879 | 1.2816 | 1.2732 | 1.2668 | 1.2574 | 1.2479 | 1.2416 | 1.2332 | 1.17 | 1.1195 | 1.0163 | 0.97737 | 0.95 | 1.2689 | 1.2605 | 1.2511 | 1.2437 | 1.2311 | 1.2205 | 1.2121 | 1.2026 | 1.1195 | 1.0542 | 0.92053 | 0.87105 | 0.83737
| INVERNESS | HILTON | MINIMUM HEADROOM | NH 67326 43262 | NO | YES | 0.5449 | 25.2126 | 24.6379 | 24.0305 | 23.36 | 23.0779 | 21.6263 | 20.4211 | 19.48 | 18.9947 | 18.74 | 17.5263 | 16.6716 | 16.0684 | 23.6895 | 23.04 | 22.3505 | 21.5905 | 21.2811 | 19.6263 | 18.2432 | 17.1642 | 16.6168 | 16.3411 | 15.1779 | 14.2189 | 13.3695 | 24.6221 | 24.18 | 23.4968 | 22.7421 | 22.4337 | 20.7937 | 19.4263 | 18.3432 | 17.7947 | 17.5179 | 16.3516 | 15.3884 | 14.5379
|  | HILTON | EE |  |  |  |  | 25.2126 | 24.6379 | 24.0305 | 23.36 | 23.0779 | 22.76 | 21.9916 | 20.7684 | 19.6347 | 18.8326 | 17.6968 | 16.8789 | 16.2716 | 23.6895 | 23.04 | 22.3505 | 21.5905 | 21.2811 | 20.9347 | 20.0705 | 18.6747 | 17.3674 | 16.4453 | 15.1779 | 14.2632 | 13.5811 | 24.6221 | 24.18 | 23.4968 | 22.7421 | 22.4337 | 22.0895 | 21.2337 | 19.8505 | 18.5484 | 17.6232 | 16.3516 | 15.4347 | 14.7484
|  | HILTON | HT |  |  |  |  | 25.2884 | 24.7432 | 24.14 | 23.48 | 23.1758 | 21.6263 | 20.4211 | 19.48 | 18.9947 | 18.74 | 17.5263 | 16.6716 | 16.0684 | 23.7747 | 23.1579 | 22.4758 | 21.7295 | 21.3968 | 19.6263 | 18.2432 | 17.1642 | 16.6168 | 16.3411 | 15.2484 | 14.2189 | 13.3695 | 24.6368 | 24.2979 | 23.6211 | 22.88 | 22.5495 | 20.7937 | 19.4263 | 18.3432 | 17.7947 | 17.5179 | 16.4211 | 15.3884 | 14.5379
|  | HILTON | HE |  |  |  |  | 25.4516 | 24.9632 | 24.4421 | 23.8537 | 23.6347 | 23.2274 | 22.7116 | 21.4705 | 20.3274 | 19.6126 | 19.0284 | 18.5232 | 18.1611 | 23.9305 | 23.4084 | 22.8158 | 22.1516 | 21.9137 | 21.4642 | 20.8905 | 19.4716 | 18.1579 | 17.3284 | 16.6758 | 16.1042 | 15.6947 | 24.6653 | 24.54 | 23.9579 | 23.2989 | 23.0621 | 22.6158 | 22.0463 | 20.64 | 19.3421 | 18.5084 | 17.8537 | 17.2811 | 16.8695
|  | HILTON | FB |  |  |  |  | 25.6084 | 25.3937 | 25.1126 | 24.8137 | 24.6853 | 24.5526 | 24.2737 | 23.9558 | 23.4368 | 22.8653 | 21.6011 | 21.0526 | 20.6411 | 23.9884 | 23.8895 | 23.5695 | 23.2295 | 23.0884 | 22.94 | 22.6253 | 22.2653 | 21.6726 | 21.02 | 19.5874 | 18.9779 | 18.5095 | 24.7147 | 24.6842 | 24.6505 | 24.3695 | 24.2284 | 24.0821 | 23.7695 | 23.4126 | 22.8242 | 22.1779 | 20.7568 | 20.1516 | 19.6905
| ARBROATH | HUME STREET | MINIMUM HEADROOM | NO 64067 41180 | NO | YES | 0 | 24.9242 | 24.8874 | 24.86 | 24.82 | 24.7737 | 24.7242 | 24.6642 | 24.6179 | 24.5705 | 24.52 | 22.3937 | 21.9442 | 21.6116 | 23.9695 | 23.7937 | 23.6126 | 23.3758 | 23.2305 | 23.0032 | 22.8295 | 22.6853 | 22.5421 | 22.4021 | 19.8726 | 19.3453 | 18.8768 | 24.8105 | 24.7737 | 24.7463 | 24.5642 | 24.42 | 24.1947 | 24.0232 | 23.8789 | 23.7379 | 23.5989 | 21.1042 | 20.5842 | 20.1116
|  | HUME STREET | EE |  |  |  |  | 24.9242 | 24.8874 | 24.86 | 24.8253 | 24.7821 | 24.7242 | 24.6642 | 24.6179 | 24.5705 | 24.5316 | 23.3095 | 22.8642 | 22.4989 | 23.9695 | 23.7958 | 23.6126 | 23.3758 | 23.2305 | 23.0032 | 22.8295 | 22.6853 | 22.5421 | 22.4021 | 20.8063 | 20.3084 | 19.8968 | 24.8105 | 24.7737 | 24.7463 | 24.5642 | 24.42 | 24.1947 | 24.0232 | 23.8789 | 23.7379 | 23.5989 | 22.0253 | 21.5326 | 21.1263
|  | HUME STREET | HT |  |  |  |  | 24.9316 | 24.8968 | 24.8611 | 24.82 | 24.7737 | 24.7284 | 24.68 | 24.6295 | 24.5779 | 24.52 | 22.3937 | 21.9442 | 21.6116 | 24.0084 | 23.7937 | 23.6242 | 23.4179 | 23.2737 | 23.1337 | 22.9874 | 22.8411 | 22.6968 | 22.5389 | 19.8726 | 19.3453 | 18.8768 | 24.8179 | 24.7832 | 24.7474 | 24.6053 | 24.4621 | 24.3232 | 24.1789 | 24.0347 | 23.8905 | 23.7347 | 21.1042 | 20.5842 | 20.1116
|  | HUME STREET | HE |  |  |  |  | 24.9389 | 24.9032 | 24.8779 | 24.84 | 24.7947 | 24.7368 | 24.6747 | 24.6389 | 24.6021 | 24.5832 | 24.0674 | 23.8326 | 23.6389 | 24.0821 | 23.9505 | 23.8358 | 23.7021 | 23.6221 | 23.3905 | 23.2926 | 23.2074 | 23.1126 | 23.0295 | 21.6632 | 21.4011 | 21.1821 | 24.8253 | 24.7895 | 24.7642 | 24.7263 | 24.6811 | 24.5779 | 24.48 | 24.3947 | 24.3011 | 24.2189 | 22.8716 | 22.6116 | 22.3968
|  | HUME STREET | FB |  |  |  |  | 24.9537 | 24.9379 | 24.9211 | 24.9021 | 24.8811 | 24.86 | 24.8389 | 24.8158 | 24.7937 | 24.7684 | 24.6779 | 24.6 | 24.56 | 24.1284 | 24.06 | 24.0032 | 23.9221 | 23.8642 | 23.7737 | 23.6505 | 23.5905 | 23.52 | 23.4295 | 23.0989 | 22.7537 | 22.4747 | 24.84 | 24.8242 | 24.8074 | 24.7884 | 24.7674 | 24.7463 | 24.7253 | 24.7021 | 24.68 | 24.6158 | 24.2884 | 23.9474 | 23.6726
| KEITH 2 | HUNTLY | MINIMUM HEADROOM | NJ 52762 39217 | NO | YES | 0 | 15.15 | 14.6216 | 14.13 | 13.5079 | 13.4037 | 13.2974 | 13.1763 | 13.0479 | 12.9205 | 12.8289 | 8.2605 | 4.2174 | 2.99 | 12.8484 | 12.2168 | 11.6305 | 10.8853 | 10.7684 | 10.6474 | 10.5116 | 10.3632 | 10.2168 | 10.1116 | 6.6137 | 1.3821 | -0.45684 | 13.7392 | 13.1939 | 12.6887 | 12.0097 | 11.895 | 11.7771 | 11.6424 | 11.495 | 11.3487 | 11.2434 | 7.7371 | 1.9097 | 0.070789
|  | HUNTLY | EE |  |  |  |  | 15.1584 | 14.6216 | 14.13 | 13.5079 | 13.4037 | 13.2974 | 13.1763 | 13.0479 | 12.9205 | 12.8289 | 11.6595 | 7.6763 | 6.71 | 12.8589 | 12.2168 | 11.6305 | 10.8853 | 10.7684 | 10.6474 | 10.5116 | 10.3632 | 10.2168 | 10.1116 | 8.7779 | 5.4747 | 4.32 | 13.7487 | 13.1939 | 12.6887 | 12.0097 | 11.895 | 11.7771 | 11.6424 | 11.495 | 11.3487 | 11.2434 | 9.8834 | 5.8308 | 4.695
|  | HUNTLY | HT |  |  |  |  | 15.15 | 14.7005 | 14.1732 | 13.5437 | 13.4363 | 13.3121 | 13.1889 | 13.0784 | 12.9753 | 12.8679 | 8.2605 | 4.2174 | 2.99 | 12.8484 | 12.3116 | 11.6821 | 10.9295 | 10.8084 | 10.6653 | 10.5253 | 10.3989 | 10.2821 | 10.1611 | 6.6137 | 1.3821 | -0.45684 | 13.7392 | 13.2761 | 12.7329 | 12.0529 | 11.9339 | 11.7939 | 11.6561 | 11.5318 | 11.415 | 11.2939 | 7.7371 | 1.9097 | 0.070789
|  | HUNTLY | HE |  |  |  |  | 15.1805 | 14.7826 | 14.3153 | 13.7332 | 13.6742 | 13.6111 | 13.5068 | 13.4174 | 13.3258 | 13.2679 | 12.35 | 10.41 | 9.5647 | 12.8832 | 12.4095 | 11.8495 | 11.1537 | 11.0895 | 11.0211 | 10.9053 | 10.8032 | 10.6979 | 10.6316 | 9.5558 | 7.8105 | 6.7958 | 13.7708 | 13.3613 | 12.8782 | 12.2718 | 12.2087 | 12.1413 | 12.0266 | 11.9266 | 11.8234 | 11.7582 | 10.6782 | 8.6339 | 7.6203
|  | HUNTLY | FB |  |  |  |  | 15.3542 | 15.3447 | 15.3079 | 15.1479 | 14.9847 | 14.8658 | 14.7753 | 14.7005 | 14.6374 | 14.5795 | 11.1279 | 7.1658 | 4.5268 | 13.4432 | 13.2684 | 13.0379 | 12.8474 | 12.6537 | 12.5126 | 12.4074 | 12.3189 | 12.2463 | 12.18 | 8.0316 | 3.2663 | 0.090526 | 14.2529 | 14.1013 | 13.9024 | 13.7382 | 13.5697 | 13.4466 | 13.355 | 13.2771 | 13.2129 | 13.1539 | 9.1634 | 4.3971 | 1.2203
| BRIDGE OF DUN | INCHBARE | MINIMUM HEADROOM | NO 60684 65379 | YES | YES | 0 | 2.1811 | 2.1768 | 2.1737 | 2.1684 | 2.1642 | 2.1568 | 2.1516 | 2.14 | 2.1284 | 2.1179 | 2.0768 | 2.0347 | 2.0021 | 2.2337 | 2.2242 | 2.2147 | 2.2 | 2.1863 | 2.1705 | 2.1579 | 2.1442 | 2.1326 | 2.1211 | 2.0789 | 2.0368 | 2.0042 | 2.1842 | 2.1737 | 2.1621 | 2.1463 | 2.1316 | 2.1137 | 2.1011 | 2.0842 | 2.0716 | 2.0589 | 2.0126 | 1.9663 | 1.9274
|  | INCHBARE | EE |  |  |  |  | 2.1811 | 2.1768 | 2.1737 | 2.1684 | 2.1642 | 2.1568 | 2.1516 | 2.14 | 2.1284 | 2.1179 | 2.0768 | 2.0347 | 2.0021 | 2.2337 | 2.2242 | 2.2147 | 2.2 | 2.1863 | 2.1705 | 2.1579 | 2.1442 | 2.1326 | 2.1211 | 2.0789 | 2.0368 | 2.0042 | 2.1842 | 2.1737 | 2.1621 | 2.1463 | 2.1316 | 2.1137 | 2.1011 | 2.0842 | 2.0716 | 2.0589 | 2.0126 | 1.9663 | 1.9274
|  | INCHBARE | HT |  |  |  |  | 2.1842 | 2.18 | 2.1779 | 2.1726 | 2.1695 | 2.1642 | 2.1611 | 2.1568 | 2.1526 | 2.1411 | 2.0968 | 2.0611 | 2.0368 | 2.24 | 2.2295 | 2.2232 | 2.2105 | 2.1989 | 2.1863 | 2.1737 | 2.1632 | 2.1516 | 2.1389 | 2.0989 | 2.06 | 2.0263 | 2.1905 | 2.18 | 2.1737 | 2.1611 | 2.1484 | 2.1347 | 2.1232 | 2.1116 | 2.1 | 2.0863 | 2.0453 | 2.0042 | 1.9684
|  | INCHBARE | HE |  |  |  |  | 2.1853 | 2.18 | 2.18 | 2.1758 | 2.1737 | 2.1674 | 2.1621 | 2.1579 | 2.1558 | 2.1547 | 2.1474 | 2.1421 | 2.1263 | 2.2463 | 2.2368 | 2.2337 | 2.2263 | 2.2221 | 2.2137 | 2.2074 | 2.1989 | 2.1916 | 2.1863 | 2.1642 | 2.1453 | 2.1274 | 2.1958 | 2.1874 | 2.1842 | 2.1768 | 2.1716 | 2.1632 | 2.1568 | 2.1474 | 2.1389 | 2.1337 | 2.1095 | 2.0895 | 2.0684
|  | INCHBARE | FB |  |  |  |  | 2.1874 | 2.1863 | 2.1853 | 2.1832 | 2.1811 | 2.18 | 2.1789 | 2.1779 | 2.1768 | 2.1747 | 2.1695 | 2.1642 | 2.1474 | 2.2495 | 2.2463 | 2.2421 | 2.2368 | 2.2326 | 2.2284 | 2.2253 | 2.2221 | 2.2168 | 2.2105 | 2.1842 | 2.1611 | 2.1421 | 2.2011 | 2.1979 | 2.1926 | 2.1874 | 2.1842 | 2.18 | 2.1768 | 2.1737 | 2.1674 | 2.16 | 2.1337 | 2.1116 | 2.0905
| DUNOON | INNELLAN | MINIMUM HEADROOM | NS 15129 70875 | YES | YES | 0 | 2.4537 | 1.54 | 1.2189 | 1.1916 | 1.1663 | 1.1379 | 1.1084 | 1.0779 | 1.0453 | 1.0253 | 0.88842 | 0.80737 | 0.74947 | 2.6779 | 1.3811 | 0.95474 | 0.92526 | 0.89789 | 0.86842 | 0.83684 | 0.80526 | 0.76737 | 0.74526 | 0.59579 | 0.50737 | 0.44632 | 2.6463 | 1.3853 | 0.95684 | 0.92632 | 0.89895 | 0.86737 | 0.83684 | 0.80316 | 0.76632 | 0.74316 | 0.58947 | 0.49789 | 0.43263
|  | INNELLAN | EE |  |  |  |  | 2.4537 | 2.4295 | 1.2189 | 1.1916 | 1.1663 | 1.1379 | 1.1084 | 1.0779 | 1.0453 | 1.0253 | 0.88842 | 0.80737 | 0.74947 | 2.6779 | 2.6505 | 0.95474 | 0.92526 | 0.89789 | 0.86842 | 0.83684 | 0.80526 | 0.76737 | 0.74526 | 0.59579 | 0.50737 | 0.44632 | 2.6463 | 2.6179 | 0.95684 | 0.92632 | 0.89895 | 0.86737 | 0.83684 | 0.80316 | 0.76632 | 0.74316 | 0.58947 | 0.49789 | 0.43263
|  | INNELLAN | HT |  |  |  |  | 2.46 | 1.54 | 1.5168 | 1.4926 | 1.4684 | 1.4368 | 1.4084 | 1.38 | 1.3442 | 1.3221 | 1.2189 | 1.1516 | 1.1011 | 2.6863 | 1.3811 | 1.3516 | 1.3211 | 1.2926 | 1.2526 | 1.2168 | 1.18 | 1.1347 | 1.1074 | 1.0011 | 0.91895 | 0.84842 | 2.6547 | 1.3853 | 1.3558 | 1.3242 | 1.2958 | 1.2547 | 1.2189 | 1.1821 | 1.1379 | 1.1095 | 1.0011 | 0.91789 | 0.84737
|  | INNELLAN | HE |  |  |  |  | 2.4747 | 2.46 | 1.2642 | 1.2474 | 1.2316 | 1.2126 | 1.1779 | 1.1579 | 1.1316 | 1.1211 | 1.0337 | 0.99474 | 0.96737 | 2.7053 | 2.6874 | 1.0042 | 0.98737 | 0.97053 | 0.95158 | 0.91158 | 0.88947 | 0.86105 | 0.84947 | 0.75053 | 0.70842 | 0.67895 | 2.6737 | 2.6568 | 1.0095 | 0.99158 | 0.97474 | 0.95474 | 0.91474 | 0.89263 | 0.86421 | 0.85158 | 0.75263 | 0.70842 | 0.67789
|  | INNELLAN | FB |  |  |  |  | 2.4821 | 2.4737 | 2.4632 | 1.9674 | 1.9579 | 1.9484 | 1.9379 | 1.9274 | 1.9137 | 1.9021 | 1.8389 | 1.7832 | 1.7526 | 2.7137 | 2.7032 | 2.6905 | 1.9905 | 1.9789 | 1.9663 | 1.9537 | 1.94 | 1.9221 | 1.9074 | 1.8242 | 1.7516 | 1.7105 | 2.6832 | 2.6726 | 2.6589 | 1.98 | 1.9684 | 1.9568 | 1.9442 | 1.9305 | 1.9137 | 1.9 | 1.8189 | 1.7484 | 1.7084
| KEITH 2 | INSCH | MINIMUM HEADROOM | NJ 63100 28651 | NO | YES | 0 | 14.3174 | 13.6826 | 13.0311 | 12.2363 | 12.1026 | 11.9311 | 11.7847 | 11.6732 | 11.5553 | 11.4595 | 9.17 | 7.8742 | 7.5974 | 13.0589 | 12.3147 | 11.5526 | 10.6211 | 10.4705 | 10.2789 | 10.1158 | 9.9905 | 9.8589 | 9.7516 | 7.8705 | 6.7432 | 6.4295 | 13.4876 | 12.7645 | 12.0224 | 11.1182 | 10.9708 | 10.7834 | 10.6234 | 10.4992 | 10.3708 | 10.2655 | 7.8992 | 6.5424 | 6.2318
|  | INSCH | EE |  |  |  |  | 14.3268 | 13.6826 | 13.0311 | 12.2363 | 12.1026 | 11.9311 | 11.7847 | 11.6732 | 11.5553 | 11.4595 | 9.17 | 7.8742 | 7.5974 | 13.0705 | 12.3147 | 11.5526 | 10.6211 | 10.4705 | 10.2789 | 10.1158 | 9.9905 | 9.8589 | 9.7516 | 7.8705 | 6.7432 | 6.4295 | 13.4982 | 12.7645 | 12.0224 | 11.1182 | 10.9708 | 10.7834 | 10.6234 | 10.4992 | 10.3708 | 10.2655 | 7.8992 | 6.5424 | 6.2318
|  | INSCH | HT |  |  |  |  | 14.3174 | 13.7458 | 13.0658 | 12.2732 | 12.1342 | 12.0237 | 11.9079 | 11.7868 | 11.6647 | 11.5258 | 9.4795 | 8.3311 | 8.0574 | 13.0589 | 12.3884 | 11.5937 | 10.6663 | 10.5105 | 10.3874 | 10.2589 | 10.1253 | 9.9958 | 9.84 | 8.2032 | 7.1484 | 6.7558 | 13.4876 | 12.8361 | 12.0634 | 11.1613 | 11.0087 | 10.8887 | 10.7624 | 10.6308 | 10.5066 | 10.3539 | 8.3276 | 7.0866 | 6.7013
|  | INSCH | HE |  |  |  |  | 14.3563 | 13.8511 | 13.2363 | 12.4837 | 12.3889 | 12.2489 | 12.1353 | 12.0447 | 11.9584 | 11.9005 | 10.8953 | 10.3353 | 10.1679 | 13.1032 | 12.5105 | 11.7895 | 10.9084 | 10.8042 | 10.6474 | 10.5232 | 10.4221 | 10.3242 | 10.2589 | 9.4 | 8.9074 | 8.7147 | 13.5308 | 12.9539 | 12.2539 | 11.3982 | 11.295 | 11.1413 | 11.0192 | 10.9203 | 10.8255 | 10.7613 | 9.7097 | 9.1192 | 8.9308
|  | INSCH | FB |  |  |  |  | 14.7637 | 14.6037 | 14.3816 | 14.1774 | 13.9784 | 13.8142 | 13.6816 | 13.5868 | 13.5258 | 13.4637 | 13.2184 | 12.9753 | 12.7995 | 13.5916 | 13.4 | 13.1337 | 12.8926 | 12.66 | 12.4695 | 12.3158 | 12.2063 | 12.1368 | 12.0674 | 11.7884 | 11.5116 | 11.3084 | 14.0055 | 13.8192 | 13.5603 | 13.3255 | 13.1003 | 12.9139 | 12.7645 | 12.6582 | 12.5897 | 12.5213 | 12.2497 | 11.9792 | 11.7813
| BURGHMUIR | INVERALMOND | MINIMUM HEADROOM | NO 08721 25807 | NO | YES | 0 | 24.3747 | 24.3747 | 24.3747 | 24.3747 | 24.3705 | 24.2789 | 24.1032 | 24.0937 | 24.0853 | 24.0768 | 23.8768 | 23.9 | 23.8705 | 23.0968 | 23.0547 | 22.9926 | 22.8547 | 22.7337 | 22.6242 | 22.4179 | 22.4074 | 22.3968 | 22.3874 | 22.1516 | 22.2084 | 22.1737 | 24.0421 | 24.0232 | 23.9895 | 23.8716 | 23.7684 | 23.6747 | 23.4884 | 23.4779 | 23.4684 | 23.4589 | 23.2389 | 23.2989 | 23.2653
|  | INVERALMOND | EE |  |  |  |  | 24.3747 | 24.3747 | 24.3747 | 24.3747 | 24.3705 | 24.2789 | 24.1032 | 24.0937 | 24.0853 | 24.0768 | 23.8768 | 23.9 | 23.8705 | 23.0968 | 23.0547 | 22.9926 | 22.8547 | 22.7337 | 22.6242 | 22.4179 | 22.4074 | 22.3968 | 22.3874 | 22.1516 | 22.2084 | 22.1737 | 24.0421 | 24.0232 | 23.9895 | 23.8716 | 23.7684 | 23.6747 | 23.4884 | 23.4779 | 23.4684 | 23.4589 | 23.2389 | 23.2989 | 23.2653
|  | INVERALMOND | HT |  |  |  |  | 24.3747 | 24.3747 | 24.3747 | 24.3747 | 24.3747 | 24.3737 | 24.3642 | 24.3558 | 24.2884 | 24.1579 | 23.9421 | 23.9063 | 23.8832 | 23.0968 | 23.0568 | 22.9968 | 22.8674 | 22.7474 | 22.7358 | 22.7263 | 22.7158 | 22.6368 | 22.4832 | 22.2684 | 22.2232 | 22.1884 | 24.0421 | 24.0253 | 23.9937 | 23.8832 | 23.78 | 23.7705 | 23.7621 | 23.7537 | 23.6853 | 23.5484 | 23.3568 | 23.3126 | 23.2789
|  | INVERALMOND | HE |  |  |  |  | 24.3747 | 24.3747 | 24.3747 | 24.3747 | 24.3747 | 24.3147 | 24.1495 | 24.1463 | 24.14 | 24.1347 | 23.9505 | 23.9316 | 23.9168 | 23.0968 | 23.0568 | 22.9989 | 22.8747 | 22.7653 | 22.6674 | 22.4726 | 22.4684 | 22.4621 | 22.4558 | 22.2389 | 22.2158 | 22.1979 | 24.0421 | 24.0253 | 23.9947 | 23.8895 | 23.7958 | 23.7116 | 23.5379 | 23.5347 | 23.5284 | 23.5232 | 23.3221 | 23.3011 | 23.2842
|  | INVERALMOND | FB |  |  |  |  | 24.3747 | 24.3747 | 24.3747 | 24.3747 | 24.3747 | 24.3747 | 24.3747 | 24.3747 | 24.3747 | 24.3747 | 24.3611 | 24.3063 | 24.2874 | 23.1074 | 23.0989 | 23.0832 | 23.0621 | 23.0221 | 22.9758 | 22.8958 | 22.7811 | 22.7789 | 22.7726 | 22.7221 | 22.6579 | 22.6347 | 24.0474 | 24.0432 | 24.0358 | 24.0263 | 24.0095 | 23.9758 | 23.9074 | 23.8095 | 23.8074 | 23.8021 | 23.7589 | 23.7032 | 23.6842
| CLACHAN | INVERARAY | MINIMUM HEADROOM | NN 09172 09746 | YES | YES | 0 | 2.3474 | 2.2179 | 2.0958 | 2.4442 | 2.3453 | 2.3137 | 2.3105 | 2.3063 | 2.2926 | 2.1137 | 1.7 | 1.6842 | 1.6726 | -3.0684 | -3.2621 | -3.4042 | -3.0811 | -3.1958 | -3.2316 | -3.2347 | -3.2389 | -3.2558 | -3.4621 | -3.9537 | -3.9874 | -4.0147 | 2.3453 | 2.1758 | 2.0316 | 2.3526 | 2.2368 | 2.2011 | 2.1968 | 2.1937 | 2.1768 | 1.9674 | 1.4811 | 1.4632 | 1.4495
|  | INVERARAY | EE |  |  |  |  | 2.4905 | 2.4874 | 2.2684 | 2.6116 | 2.4305 | 2.3947 | 2.3853 | 2.3779 | 2.3684 | 2.3611 | 1.7505 | 1.7211 | 1.6968 | -3.0179 | -3.0211 | -3.2758 | -2.9568 | -3.1674 | -3.2084 | -3.2189 | -3.2263 | -3.2379 | -3.2463 | -3.9537 | -3.9874 | -4.0147 | 2.4895 | 2.4863 | 2.2284 | 2.5453 | 2.3316 | 2.2905 | 2.28 | 2.2726 | 2.2611 | 2.2526 | 1.5368 | 1.5032 | 1.4758
|  | INVERARAY | HT |  |  |  |  | 2.3474 | 2.2179 | 2.0958 | 2.4442 | 2.4074 | 2.4 | 2.3916 | 2.3832 | 2.2926 | 2.1137 | 1.7495 | 1.7211 | 1.7 | -3.0684 | -3.2621 | -3.4042 | -3.0811 | -3.1232 | -3.1316 | -3.14 | -3.1505 | -3.2558 | -3.4621 | -3.8758 | -3.9105 | -3.94 | 2.3453 | 2.1758 | 2.0316 | 2.3526 | 2.3105 | 2.3021 | 2.2926 | 2.2821 | 2.1768 | 1.9674 | 1.5484 | 1.5147 | 1.4842
|  | INVERARAY | HE |  |  |  |  | 2.3484 | 2.3474 | 2.1695 | 2.52 | 2.3453 | 2.3137 | 2.3105 | 2.3063 | 2.3021 | 2.2979 | 1.7 | 1.6842 | 1.6726 | -3.0642 | -3.0674 | -3.3179 | -2.9926 | -3.1958 | -3.2316 | -3.2347 | -3.2389 | -3.2442 | -3.2495 | -3.9432 | -3.96 | -3.9737 | 2.3474 | 2.3463 | 2.1189 | 2.4432 | 2.2368 | 2.2011 | 2.1968 | 2.1937 | 2.1874 | 2.1832 | 1.4811 | 1.4632 | 1.4495
|  | INVERARAY | FB |  |  |  |  | 2.4968 | 2.4937 | 2.4926 | 2.9021 | 2.8411 | 2.7705 | 2.7558 | 2.7537 | 2.7495 | 2.7442 | 2.5768 | 2.3432 | 2.3263 | -3.0116 | -3.0137 | -3.0158 | -2.62 | -2.6916 | -2.7737 | -2.7895 | -2.7926 | -2.7968 | -2.8032 | -2.9968 | -3.2674 | -3.2863 | 2.4958 | 2.4937 | 2.4916 | 2.8853 | 2.8137 | 2.7305 | 2.7137 | 2.7116 | 2.7074 | 2.7011 | 2.5042 | 2.2305 | 2.2116
| LUNANHEAD | INVERARITY | MINIMUM HEADROOM | NO 44549 44200 | YES | YES | 0 | 0.35368 | 0.34632 | 0.34 | 0.32947 | 0.32211 | 0.31263 | 0.30421 | 0.29474 | 0.28737 | 0.28 | -1.2716 | -1.2968 | -1.3158 | 0.47895 | 0.47053 | 0.46316 | 0.45158 | 0.44316 | 0.43263 | 0.42316 | 0.41368 | 0.40526 | 0.39579 | -0.84947 | -0.87474 | -0.89368 | 0.31158 | 0.30316 | 0.29579 | 0.28526 | 0.27789 | 0.26737 | 0.25789 | 0.24947 | 0.24105 | 0.23263 | -1.3716 | -1.3958 | -1.4126
|  | INVERARITY | EE |  |  |  |  | 0.35368 | 0.34632 | 0.34 | 0.32947 | 0.32211 | 0.31263 | 0.30421 | 0.29474 | 0.28737 | 0.28 | -1.2716 | -1.2968 | -1.3158 | 0.47895 | 0.47053 | 0.46316 | 0.45158 | 0.44316 | 0.43263 | 0.42316 | 0.41368 | 0.40526 | 0.39579 | -0.84947 | -0.87474 | -0.89368 | 0.31158 | 0.30316 | 0.29579 | 0.28526 | 0.27789 | 0.26737 | 0.25789 | 0.24947 | 0.24105 | 0.23263 | -1.3716 | -1.3958 | -1.4126
|  | INVERARITY | HT |  |  |  |  | 0.35579 | 0.34842 | 0.34316 | 0.33474 | 0.32632 | 0.31895 | 0.30947 | 0.30105 | 0.29263 | 0.28421 | -0.96947 | -0.99368 | -1.0105 | 0.48105 | 0.47263 | 0.46632 | 0.45789 | 0.44842 | 0.44 | 0.42947 | 0.42105 | 0.41158 | 0.40105 | -0.59263 | -0.61789 | -0.64 | 0.31263 | 0.30526 | 0.3 | 0.29158 | 0.28211 | 0.27474 | 0.26421 | 0.25579 | 0.24737 | 0.23789 | -1.0526 | -1.0747 | -1.0958
|  | INVERARITY | HE |  |  |  |  | 0.36105 | 0.35579 | 0.35158 | 0.34737 | 0.34211 | 0.33684 | 0.33263 | 0.32737 | 0.32211 | 0.31789 | -0.30737 | -0.31895 | -0.32842 | 0.48632 | 0.48105 | 0.47684 | 0.47158 | 0.46526 | 0.46105 | 0.45579 | 0.44947 | 0.44421 | 0.44 | -0.036842 | -0.050526 | -0.058947 | 0.31789 | 0.31368 | 0.30842 | 0.30421 | 0.29895 | 0.29368 | 0.28947 | 0.28316 | 0.27789 | 0.27368 | -0.37263 | -0.38421 | -0.39263
|  | INVERARITY | FB |  |  |  |  | 0.36316 | 0.36 | 0.35789 | 0.35474 | 0.35158 | 0.34842 | 0.34421 | 0.34105 | 0.33789 | 0.33263 | 0.31474 | 0.29684 | 0.28526 | 0.48947 | 0.48526 | 0.48211 | 0.48 | 0.47579 | 0.47158 | 0.46842 | 0.46421 | 0.46105 | 0.45474 | 0.43579 | 0.41474 | 0.40105 | 0.32105 | 0.31684 | 0.31474 | 0.31158 | 0.30842 | 0.30526 | 0.30105 | 0.29789 | 0.29368 | 0.28842 | 0.27053 | 0.25158 | 0.23789
| INVERNESS | INVERARNIE | MINIMUM HEADROOM | NH 68830 34971 | YES | YES | 0 | 2.4432 | 2.4232 | 2.4032 | 2.3811 | 2.3568 | 2.3305 | 2.3095 | 2.2895 | 2.2695 | 2.2516 | 2.1758 | 2.1084 | 2.0526 | 2.4389 | 2.42 | 2.4011 | 2.3789 | 2.3558 | 2.3295 | 2.3084 | 2.2884 | 2.2695 | 2.2505 | 2.1758 | 2.1084 | 2.0495 | 2.4347 | 2.4126 | 2.3905 | 2.3663 | 2.3389 | 2.3095 | 2.2863 | 2.2642 | 2.2421 | 2.2221 | 2.1379 | 2.0632 | 2
|  | INVERARNIE | EE |  |  |  |  | 2.4432 | 2.4232 | 2.4032 | 2.3811 | 2.3568 | 2.3305 | 2.3095 | 2.2895 | 2.2695 | 2.2516 | 2.1758 | 2.1084 | 2.0526 | 2.4389 | 2.42 | 2.4011 | 2.3789 | 2.3558 | 2.3295 | 2.3084 | 2.2884 | 2.2695 | 2.2505 | 2.1758 | 2.1084 | 2.0495 | 2.4347 | 2.4126 | 2.3905 | 2.3663 | 2.3389 | 2.3095 | 2.2863 | 2.2642 | 2.2421 | 2.2221 | 2.1379 | 2.0632 | 2
|  | INVERARNIE | HT |  |  |  |  | 2.4516 | 2.4379 | 2.4242 | 2.4074 | 2.3895 | 2.3726 | 2.3589 | 2.3432 | 2.3295 | 2.3126 | 2.2379 | 2.1884 | 2.1547 | 2.4453 | 2.4316 | 2.4168 | 2.4011 | 2.3821 | 2.3653 | 2.3505 | 2.3347 | 2.3211 | 2.3042 | 2.2411 | 2.1863 | 2.1432 | 2.4453 | 2.4295 | 2.4137 | 2.3958 | 2.3758 | 2.3579 | 2.3432 | 2.3253 | 2.3105 | 2.2926 | 2.2253 | 2.1632 | 2.1158
|  | INVERARNIE | HE |  |  |  |  | 2.4589 | 2.4474 | 2.44 | 2.4274 | 2.4147 | 2.4042 | 2.3895 | 2.3811 | 2.3695 | 2.3632 | 2.3263 | 2.2937 | 2.2716 | 2.4547 | 2.4421 | 2.4358 | 2.4232 | 2.4105 | 2.4 | 2.3863 | 2.3779 | 2.3674 | 2.36 | 2.3232 | 2.2905 | 2.2684 | 2.4537 | 2.44 | 2.4326 | 2.4179 | 2.4053 | 2.3926 | 2.3779 | 2.3684 | 2.3568 | 2.3495 | 2.3063 | 2.2705 | 2.2442
|  | INVERARNIE | FB |  |  |  |  | 2.4674 | 2.4621 | 2.4558 | 2.4505 | 2.4432 | 2.4368 | 2.4316 | 2.4263 | 2.42 | 2.4116 | 2.3832 | 2.3568 | 2.3368 | 2.4632 | 2.4558 | 2.4505 | 2.4453 | 2.4368 | 2.4295 | 2.4242 | 2.4179 | 2.4105 | 2.4032 | 2.3705 | 2.3411 | 2.3221 | 2.4621 | 2.4568 | 2.4495 | 2.4442 | 2.4358 | 2.4274 | 2.4221 | 2.4158 | 2.4084 | 2.4011 | 2.3674 | 2.3379 | 2.3158
| FIDDES | INVERBERVIE | MINIMUM HEADROOM | NO 82850 72935 | NO | YES | 0.15 | 4 | 3.7421 | 3.5179 | 3.2432 | 3.1737 | 3.0989 | 2.8789 | 2.6011 | 2.2968 | 2.2221 | -3.2547 | -5.2347 | -5.4253 | 3.2063 | 2.9 | 2.6326 | 2.3063 | 2.2274 | 2.1432 | 1.8832 | 1.5547 | 1.1937 | 1.1105 | -1.8853 | -4.7874 | -5.0611 | 3.4905 | 3.1842 | 2.9168 | 2.5895 | 2.5105 | 2.4274 | 2.1674 | 1.8379 | 1.4768 | 1.3937 | -2.3358 | -6.0747 | -6.3484
|  | INVERBERVIE | EE |  |  |  |  | 4 | 3.7421 | 3.5179 | 3.2432 | 3.1737 | 3.0989 | 3.0053 | 2.84 | 2.6589 | 2.5958 | 1.7474 | -2.8474 | -3.0305 | 3.2063 | 2.9 | 2.6326 | 2.3063 | 2.2274 | 2.1432 | 2.0368 | 1.8432 | 1.6316 | 1.5579 | 0.55474 | -3.0221 | -3.2347 | 3.4905 | 3.1842 | 2.9168 | 2.5895 | 2.5105 | 2.4274 | 2.3211 | 2.1263 | 1.9147 | 1.8421 | 0.83684 | -3.7316 | -3.9453
|  | INVERBERVIE | HT |  |  |  |  | 4.0053 | 3.7947 | 3.5621 | 3.2958 | 3.2221 | 3.1263 | 2.8789 | 2.6011 | 2.2968 | 2.2221 | -3.2547 | -5.2347 | -5.4253 | 3.2116 | 2.9621 | 2.6853 | 2.3705 | 2.2863 | 2.1768 | 1.8832 | 1.5547 | 1.1937 | 1.1105 | -1.8853 | -4.7874 | -5.0611 | 3.4947 | 3.2463 | 2.9695 | 2.6537 | 2.5705 | 2.46 | 2.1674 | 1.8379 | 1.4768 | 1.3937 | -2.3358 | -6.0747 | -6.3484
|  | INVERBERVIE | HE |  |  |  |  | 4.0368 | 3.8568 | 3.6547 | 3.4105 | 3.3663 | 3.3158 | 3.2147 | 3.0779 | 2.9326 | 2.8937 | 0.76737 | -1.3358 | -1.4474 | 3.2484 | 3.0347 | 2.7947 | 2.5042 | 2.4558 | 2.4011 | 2.2863 | 2.1253 | 1.9526 | 1.9084 | 0.074737 | -1.6726 | -1.8042 | 3.5316 | 3.3189 | 3.0789 | 2.7884 | 2.7389 | 2.6853 | 2.5695 | 2.4084 | 2.2368 | 2.1916 | -0.0084211 | -2.1537 | -2.2853
|  | INVERBERVIE | FB |  |  |  |  | 4.2916 | 4.2147 | 4.12 | 4.0421 | 3.9611 | 3.8979 | 3.8474 | 3.7947 | 3.7284 | 3.6884 | 3.3832 | 2.8863 | 2.7684 | 3.5537 | 3.4621 | 3.3505 | 3.2568 | 3.1611 | 3.0863 | 3.0295 | 2.9674 | 2.8895 | 2.8432 | 2.4842 | 1.8926 | 1.7547 | 3.8347 | 3.7463 | 3.6337 | 3.5411 | 3.4453 | 3.3705 | 3.3126 | 3.2516 | 3.1737 | 3.1274 | 2.7684 | 2.1758 | 2.0379
| GRUDIE BRIDGE | INVERBROOM | MINIMUM HEADROOM | NH 17885 84667 | YES | NO | 0 | 0.21474 | 0.21368 | 0.21158 | 0.20737 | 0.20421 | 0.2 | 0.19789 | 0.19368 | 0.19053 | 0.18737 | 0.17684 | 0.16947 | 0.16526 | 0.20211 | 0.19895 | 0.19579 | 0.19263 | 0.18842 | 0.18421 | 0.18105 | 0.17684 | 0.17368 | 0.17053 | 0.15895 | 0.15053 | 0.14526 | 0.20737 | 0.20421 | 0.20211 | 0.19789 | 0.19474 | 0.18947 | 0.18632 | 0.18316 | 0.17895 | 0.17579 | 0.16526 | 0.15684 | 0.15158
|  | INVERBROOM | EE |  |  |  |  | 0.21474 | 0.21368 | 0.21158 | 0.20737 | 0.20421 | 0.2 | 0.19789 | 0.19368 | 0.19053 | 0.18737 | 0.17789 | 0.16947 | 0.16526 | 0.20211 | 0.19895 | 0.19579 | 0.19263 | 0.18842 | 0.18421 | 0.18105 | 0.17684 | 0.17368 | 0.17053 | 0.15895 | 0.15053 | 0.14526 | 0.20737 | 0.20421 | 0.20211 | 0.19789 | 0.19474 | 0.18947 | 0.18632 | 0.18316 | 0.17895 | 0.17579 | 0.16526 | 0.15684 | 0.15158
|  | INVERBROOM | HT |  |  |  |  | 0.21474 | 0.21368 | 0.21158 | 0.20947 | 0.20632 | 0.20105 | 0.19895 | 0.19579 | 0.19263 | 0.18947 | 0.17684 | 0.17053 | 0.16526 | 0.20316 | 0.2 | 0.19684 | 0.19474 | 0.19158 | 0.18526 | 0.18211 | 0.17895 | 0.17579 | 0.17158 | 0.16 | 0.15158 | 0.14632 | 0.20842 | 0.20526 | 0.20211 | 0.2 | 0.19684 | 0.19158 | 0.18842 | 0.18421 | 0.18211 | 0.17789 | 0.16526 | 0.15789 | 0.15263
|  | INVERBROOM | HE |  |  |  |  | 0.21474 | 0.21474 | 0.21263 | 0.21158 | 0.21053 | 0.21053 | 0.20737 | 0.20632 | 0.20316 | 0.20211 | 0.2 | 0.19579 | 0.19368 | 0.20421 | 0.20421 | 0.20105 | 0.19895 | 0.19684 | 0.19579 | 0.19263 | 0.19053 | 0.18842 | 0.18737 | 0.18421 | 0.17895 | 0.17789 | 0.20947 | 0.20947 | 0.20632 | 0.20421 | 0.20211 | 0.20105 | 0.19789 | 0.19684 | 0.19368 | 0.19263 | 0.18947 | 0.18526 | 0.18316
|  | INVERBROOM | FB |  |  |  |  | 0.21579 | 0.21474 | 0.21474 | 0.21474 | 0.21368 | 0.21368 | 0.21263 | 0.21158 | 0.21053 | 0.20947 | 0.20421 | 0.20105 | 0.19789 | 0.20632 | 0.20421 | 0.20421 | 0.20316 | 0.20105 | 0.2 | 0.19789 | 0.19684 | 0.19474 | 0.19474 | 0.18842 | 0.18421 | 0.18105 | 0.21053 | 0.20947 | 0.20947 | 0.20842 | 0.20632 | 0.20526 | 0.20316 | 0.20211 | 0.20105 | 0.2 | 0.19368 | 0.19053 | 0.18632
| FORT AUGUSTUS | INVERGARRY | MINIMUM HEADROOM | NH 29862 01000 | YES | YES | 0 | 0.98526 | 0.97474 | 0.96316 | 0.95158 | 0.94 | 0.92947 | 0.91684 | 0.90526 | 0.89579 | 0.88316 | 0.84211 | 0.80105 | 0.76105 | 1.0095 | 1.0021 | 0.99158 | 0.98105 | 0.96737 | 0.95579 | 0.94211 | 0.93053 | 0.92 | 0.90632 | 0.86316 | 0.81684 | 0.77579 | 1.0147 | 1.0042 | 0.98947 | 0.97579 | 0.96105 | 0.94842 | 0.93368 | 0.92105 | 0.90947 | 0.89474 | 0.84842 | 0.80105 | 0.75789
|  | INVERGARRY | EE |  |  |  |  | 0.98526 | 0.97474 | 0.96316 | 0.95158 | 0.94 | 0.92947 | 0.91684 | 0.90526 | 0.89579 | 0.88316 | 0.84211 | 0.80105 | 0.76105 | 1.0095 | 1.0021 | 0.99158 | 0.98105 | 0.96737 | 0.95579 | 0.94211 | 0.93053 | 0.92 | 0.90632 | 0.86316 | 0.81684 | 0.77579 | 1.0147 | 1.0042 | 0.98947 | 0.97579 | 0.96105 | 0.94842 | 0.93368 | 0.92105 | 0.90947 | 0.89474 | 0.84842 | 0.80105 | 0.75789
|  | INVERGARRY | HT |  |  |  |  | 0.99053 | 0.98632 | 0.98 | 0.97684 | 0.96947 | 0.96421 | 0.95895 | 0.95263 | 0.94632 | 0.94 | 0.91263 | 0.88947 | 0.87263 | 1.0137 | 1.0084 | 1.0032 | 0.99684 | 0.98947 | 0.98211 | 0.97579 | 0.96947 | 0.96211 | 0.95579 | 0.93158 | 0.90632 | 0.88737 | 1.0221 | 1.0168 | 1.0084 | 1.0032 | 0.99263 | 0.98526 | 0.97789 | 0.96947 | 0.96211 | 0.95368 | 0.92526 | 0.89368 | 0.86842
|  | INVERGARRY | HE |  |  |  |  | 0.99263 | 0.98737 | 0.98316 | 0.98 | 0.97474 | 0.97053 | 0.96526 | 0.96105 | 0.95789 | 0.95263 | 0.93789 | 0.92105 | 0.90316 | 1.0179 | 1.0126 | 1.0084 | 1.0042 | 1.0011 | 0.99684 | 0.99158 | 0.98737 | 0.98316 | 0.98 | 0.96421 | 0.94632 | 0.92737 | 1.0263 | 1.02 | 1.0137 | 1.0105 | 1.0042 | 0.99895 | 0.99263 | 0.98842 | 0.98316 | 0.97684 | 0.95684 | 0.93684 | 0.91684
|  | INVERGARRY | FB |  |  |  |  | 0.99368 | 0.99368 | 0.99053 | 0.99053 | 0.98842 | 0.98632 | 0.98421 | 0.98316 | 0.98105 | 0.97895 | 0.97053 | 0.96316 | 0.95579 | 1.0189 | 1.0168 | 1.0147 | 1.0126 | 1.0095 | 1.0084 | 1.0053 | 1.0032 | 0.99895 | 0.99789 | 0.98526 | 0.97158 | 0.96105 | 1.0284 | 1.0263 | 1.0232 | 1.0211 | 1.0189 | 1.0158 | 1.0126 | 1.0105 | 1.0074 | 1.0042 | 0.99053 | 0.97789 | 0.96526
| ALNESS | INVERGORDON | MINIMUM HEADROOM | NH 70756 69177 | NO | YES | 0.05102 | 14.5963 | 14.3574 | 14.2826 | 14.2153 | 14.1458 | 13.2816 | 12.0037 | 10.2247 | 8.9447 | 7.9489 | 5.7037 | 5.4816 | 5.3216 | 13.8442 | 13.6147 | 13.5316 | 13.4558 | 13.3789 | 12.3579 | 10.8505 | 8.7516 | 7.2421 | 6.0716 | 3.5105 | 3.2295 | 3.0137 | 14.1003 | 13.8876 | 13.8034 | 13.7297 | 13.655 | 12.675 | 11.2024 | 9.1066 | 7.6013 | 6.4329 | 3.8782 | 3.5866 | 3.3813
|  | INVERGORDON | EE |  |  |  |  | 14.5963 | 14.3574 | 14.2826 | 14.2153 | 14.1458 | 14.0668 | 13.8816 | 12.7995 | 11.5837 | 9.9637 | 6.0858 | 5.5047 | 5.3384 | 13.8442 | 13.6147 | 13.5316 | 13.4558 | 13.3789 | 13.2905 | 13.0779 | 11.8032 | 10.3716 | 8.4589 | 3.9021 | 3.2295 | 3.0432 | 14.1003 | 13.8876 | 13.8034 | 13.7297 | 13.655 | 13.5676 | 13.3613 | 12.1339 | 10.7182 | 8.8087 | 4.2603 | 3.5866 | 3.3961
|  | INVERGORDON | HT |  |  |  |  | 14.6121 | 14.3805 | 14.3121 | 14.2574 | 14.1837 | 13.2816 | 12.0037 | 10.2247 | 8.9447 | 7.9489 | 5.7037 | 5.4816 | 5.3216 | 13.8568 | 13.6411 | 13.5621 | 13.5021 | 13.42 | 12.3579 | 10.8505 | 8.7516 | 7.2421 | 6.0716 | 3.5105 | 3.2389 | 3.0137 | 14.1055 | 13.9129 | 13.8371 | 13.7771 | 13.6971 | 12.675 | 11.2024 | 9.1066 | 7.6013 | 6.4329 | 3.8782 | 3.6076 | 3.3813
|  | INVERGORDON | HE |  |  |  |  | 14.6426 | 14.4237 | 14.37 | 14.3342 | 14.2868 | 14.1921 | 14.0332 | 12.9437 | 11.5889 | 9.7395 | 6.4405 | 5.9447 | 5.8479 | 13.8779 | 13.6916 | 13.6295 | 13.5926 | 13.5389 | 13.4326 | 13.2505 | 11.9653 | 10.3674 | 8.1821 | 4.2979 | 3.7189 | 3.6084 | 14.1118 | 13.9624 | 13.9013 | 13.8645 | 13.8129 | 13.7097 | 13.5318 | 12.295 | 10.7192 | 8.5371 | 4.6634 | 4.0855 | 3.975
|  | INVERGORDON | FB |  |  |  |  | 14.6721 | 14.5784 | 14.5332 | 14.5111 | 14.4847 | 14.4574 | 14.3668 | 14.1974 | 13.8005 | 13.2237 | 9.8237 | 9.2279 | 9.1163 | 13.9011 | 13.8358 | 13.8021 | 13.7853 | 13.7653 | 13.7347 | 13.6284 | 13.4295 | 12.9611 | 12.2811 | 8.2663 | 7.5684 | 7.4389 | 14.1234 | 14.1108 | 14.0887 | 14.0634 | 14.0339 | 14.0024 | 13.9003 | 13.7076 | 13.2582 | 12.6045 | 8.6255 | 7.9276 | 7.7992
| FORT WILLIAM | INVERLOCHY | MINIMUM HEADROOM | NN 11653 74987 | NO | NO | 0.20306 | 16.0026 | 15.9647 | 30.4842 | 30.4516 | 30.4084 | 29.4674 | 28.4379 | 27.4674 | 26.6979 | 26.5853 | 26.0611 | 25.6747 | 25.3958 | 13.9084 | 13.8726 | 27.6432 | 27.5084 | 27.3726 | 26.1484 | 24.9832 | 23.8779 | 22.9842 | 22.8621 | 22.3158 | 21.8895 | 21.5411 | 14.8792 | 14.8403 | 28.9837 | 28.8479 | 28.7068 | 27.4532 | 26.2521 | 25.1195 | 24.2247 | 24.1016 | 23.53 | 23.0921 | 22.7542
|  | INVERLOCHY | EE |  |  |  |  | 16.0026 | 15.9647 | 30.4842 | 30.4516 | 30.4084 | 30.3537 | 30.0053 | 29.0547 | 28.1358 | 27.1558 | 26.0789 | 25.6926 | 25.3958 | 13.9084 | 13.8726 | 27.6432 | 27.5084 | 27.3726 | 27.2221 | 26.7821 | 25.7084 | 24.6684 | 23.5474 | 22.3158 | 21.8895 | 21.56 | 14.8792 | 14.8403 | 28.9837 | 28.8479 | 28.7068 | 28.5511 | 28.0963 | 26.9889 | 25.9142 | 24.77 | 23.53 | 23.0921 | 22.7542
|  | INVERLOCHY | HT |  |  |  |  | 16.0089 | 15.9763 | 30.4926 | 30.4526 | 30.4095 | 29.4674 | 28.4379 | 27.4674 | 26.6979 | 26.5853 | 26.0611 | 25.6747 | 25.4021 | 13.9147 | 13.8821 | 27.6484 | 27.5842 | 27.4432 | 26.1484 | 24.9832 | 23.8779 | 22.9842 | 22.8621 | 22.3853 | 21.9274 | 21.5411 | 14.8866 | 14.8539 | 28.9942 | 28.9342 | 28.7879 | 27.4532 | 26.2521 | 25.1195 | 24.2247 | 24.1016 | 23.6216 | 23.1605 | 22.7711
|  | INVERLOCHY | HE |  |  |  |  | 16.0184 | 15.9858 | 30.5126 | 30.48 | 30.44 | 30.3895 | 30.3368 | 29.4189 | 28.4853 | 27.4347 | 26.7537 | 26.5242 | 26.3547 | 13.9242 | 13.8916 | 27.6684 | 27.6368 | 27.5968 | 27.5011 | 27.1979 | 26.1032 | 25.0463 | 23.8453 | 23.06 | 22.8021 | 22.6116 | 14.8961 | 14.8634 | 29.0142 | 28.9816 | 28.9416 | 28.8479 | 28.5363 | 27.4068 | 26.3174 | 25.0858 | 24.2963 | 24.0353 | 23.8416
|  | INVERLOCHY | FB |  |  |  |  | 16.0384 | 16.0268 | 30.5621 | 30.5495 | 30.5337 | 30.5189 | 30.5032 | 30.4853 | 30.3095 | 29.8695 | 28.42 | 28.1737 | 27.9853 | 13.9432 | 13.9316 | 27.7179 | 27.7053 | 27.6895 | 27.6737 | 27.6579 | 27.5821 | 27.0916 | 26.5937 | 24.9516 | 24.68 | 24.4705 | 14.915 | 14.9034 | 29.0647 | 29.0521 | 29.0363 | 29.0205 | 29.0047 | 28.9321 | 28.4258 | 27.9121 | 26.2205 | 25.9405 | 25.7258
| PORT ANN | INVERNEIL | MINIMUM HEADROOM | NR 84790 80580 | YES | YES | 0 | 2.6332 | 2.6195 | 2.6058 | 2.5879 | 2.57 | 2.5532 | 2.5321 | 2.5047 | 2.4732 | 2.4532 | 2.3584 | 2.2858 | 2.2247 | 2.5174 | 2.5016 | 2.4868 | 2.4679 | 2.4479 | 2.4279 | 2.39 | 2.3637 | 2.3342 | 2.3153 | 2.2195 | 2.1479 | 2.0868 | 2.5658 | 2.5458 | 2.5268 | 2.5026 | 2.4805 | 2.4563 | 2.4268 | 2.3858 | 2.3489 | 2.3279 | 2.2205 | 2.1395 | 2.0711
|  | INVERNEIL | EE |  |  |  |  | 2.6332 | 2.6195 | 2.6058 | 2.5879 | 2.57 | 2.5532 | 2.5321 | 2.5047 | 2.4732 | 2.4532 | 2.3584 | 2.2858 | 2.2247 | 2.5174 | 2.5016 | 2.4868 | 2.4679 | 2.4479 | 2.4279 | 2.4005 | 2.3658 | 2.3342 | 2.3153 | 2.2195 | 2.1479 | 2.0868 | 2.5658 | 2.5458 | 2.5268 | 2.5026 | 2.4805 | 2.4563 | 2.4268 | 2.3858 | 2.3489 | 2.3279 | 2.2205 | 2.1395 | 2.0711
|  | INVERNEIL | HT |  |  |  |  | 2.6416 | 2.6332 | 2.6247 | 2.6142 | 2.6047 | 2.5826 | 2.5479 | 2.5237 | 2.5016 | 2.4858 | 2.4226 | 2.3721 | 2.3363 | 2.5237 | 2.5121 | 2.4995 | 2.4858 | 2.4721 | 2.4321 | 2.39 | 2.3637 | 2.3416 | 2.3258 | 2.2753 | 2.2247 | 2.1795 | 2.5742 | 2.5626 | 2.5489 | 2.5353 | 2.5195 | 2.4774 | 2.4332 | 2.4047 | 2.3805 | 2.3647 | 2.3068 | 2.2468 | 2.1953
|  | INVERNEIL | HE |  |  |  |  | 2.6458 | 2.6374 | 2.6311 | 2.6237 | 2.6174 | 2.6089 | 2.5889 | 2.5742 | 2.5542 | 2.5447 | 2.5026 | 2.47 | 2.4447 | 2.5332 | 2.5226 | 2.5153 | 2.5068 | 2.4995 | 2.4889 | 2.4574 | 2.4268 | 2.4005 | 2.3921 | 2.3511 | 2.3216 | 2.3005 | 2.5826 | 2.5721 | 2.5626 | 2.5532 | 2.5437 | 2.5342 | 2.5016 | 2.47 | 2.4416 | 2.4321 | 2.3837 | 2.3458 | 2.3184
|  | INVERNEIL | FB |  |  |  |  | 2.6479 | 2.6458 | 2.6426 | 2.6395 | 2.6363 | 2.6321 | 2.6279 | 2.6226 | 2.6142 | 2.61 | 2.5816 | 2.5416 | 2.5184 | 2.5374 | 2.5311 | 2.5258 | 2.5195 | 2.5153 | 2.5079 | 2.5016 | 2.4911 | 2.4753 | 2.4679 | 2.4216 | 2.3784 | 2.3542 | 2.5879 | 2.5826 | 2.5763 | 2.57 | 2.5658 | 2.5595 | 2.5542 | 2.5437 | 2.5279 | 2.5205 | 2.4711 | 2.4268 | 2.4005
| INVERNESS | INVERNESS | MINIMUM HEADROOM | NH 65302 42625 | NO | YES | 0 | 14.6058 | 14.2658 | 13.89 | 13.3689 | 13.2089 | 12.4037 | 11.9426 | 11.4805 | 11.1205 | 10.7195 | 9.47 | 8.9847 | 8.6384 | 12.8505 | 12.4653 | 12.0621 | 11.4674 | 11.2926 | 10.3663 | 9.8411 | 9.3168 | 8.9116 | 8.4558 | 7.1505 | 6.6126 | 6.1316 | 13.1971 | 12.8055 | 12.4108 | 11.8087 | 11.6297 | 10.7003 | 10.1687 | 9.6371 | 9.2255 | 8.7676 | 7.4276 | 6.9013 | 6.4139
|  | INVERNESS | EE |  |  |  |  | 14.6058 | 14.2658 | 13.89 | 13.3689 | 13.2089 | 13.0258 | 12.2279 | 11.5637 | 11.1205 | 10.8668 | 9.5511 | 9.0816 | 8.7321 | 12.8505 | 12.4653 | 12.0621 | 11.4674 | 11.2926 | 11.0947 | 10.1832 | 9.4253 | 8.9211 | 8.6379 | 7.1505 | 6.6337 | 6.2505 | 13.1971 | 12.8055 | 12.4108 | 11.8087 | 11.6297 | 11.4297 | 10.5055 | 9.7371 | 9.2255 | 8.9371 | 7.4276 | 6.9013 | 6.5055
|  | INVERNESS | HT |  |  |  |  | 14.6489 | 14.3932 | 13.9532 | 13.4447 | 13.2732 | 12.4037 | 11.9426 | 11.4805 | 11.1226 | 10.7195 | 9.47 | 8.9847 | 8.6384 | 12.8968 | 12.6337 | 12.1326 | 11.5505 | 11.3621 | 10.3663 | 9.8411 | 9.3168 | 8.9116 | 8.4558 | 7.1926 | 6.6126 | 6.1316 | 13.2455 | 12.9939 | 12.4866 | 11.8982 | 11.7076 | 10.7003 | 10.1687 | 9.6371 | 9.2297 | 8.7676 | 7.4908 | 6.9024 | 6.4139
|  | INVERNESS | HE |  |  |  |  | 14.7405 | 14.4511 | 14.1258 | 13.6605 | 13.5416 | 13.1447 | 12.5984 | 12.0226 | 11.6279 | 11.4311 | 10.3595 | 10.0753 | 9.8058 | 13.0011 | 12.6726 | 12.3274 | 11.7937 | 11.6663 | 11.2179 | 10.5979 | 9.9368 | 9.4863 | 9.2621 | 8.0368 | 7.7211 | 7.3937 | 13.3508 | 13.0182 | 12.6824 | 12.1445 | 12.0139 | 11.5613 | 10.9339 | 10.2645 | 9.8097 | 9.5824 | 8.3424 | 8.0192 | 7.6708
|  | INVERNESS | FB |  |  |  |  | 14.9342 | 14.7921 | 14.5826 | 14.3647 | 14.2953 | 14.2237 | 13.9111 | 13.5511 | 13.2942 | 13.1616 | 12.2532 | 11.9416 | 11.7058 | 13.2211 | 13.06 | 12.82 | 12.5684 | 12.4916 | 12.4116 | 12.0537 | 11.6389 | 11.3453 | 11.1958 | 10.1568 | 9.8074 | 9.5411 | 13.5739 | 13.4097 | 13.1666 | 12.9139 | 12.8361 | 12.7561 | 12.3929 | 11.9739 | 11.6761 | 11.5255 | 10.4739 | 10.1213 | 9.8529
| KINTORE | INVERURIE | MINIMUM HEADROOM | NJ 75665 21688 | NO | YES | 0.16122 | 29.7926 | 29.3947 | 28.4179 | 27.3063 | 25.2611 | 22.6137 | 20.0632 | 19.2211 | 18.8347 | 18.5989 | 12.1621 | 11.0726 | 10.3653 | 26.8895 | 25.9042 | 24.7063 | 23.3484 | 20.8568 | 17.8032 | 14.8442 | 13.8737 | 13.44 | 13.1768 | 6.5653 | 5.2242 | 4.4158 | 28.1989 | 27.4032 | 26.2789 | 24.9126 | 22.4537 | 19.4442 | 16.5463 | 15.5989 | 15.1726 | 14.9137 | 7.9811 | 6.5379 | 5.7326
|  | INVERURIE | EE |  |  |  |  | 29.7926 | 29.3947 | 28.4411 | 27.32 | 25.3211 | 22.6137 | 20.0632 | 19.2211 | 18.8347 | 18.5989 | 12.4242 | 11.0726 | 10.3653 | 26.8895 | 25.9042 | 24.7347 | 23.3611 | 20.9242 | 17.8032 | 14.8442 | 13.8737 | 13.44 | 13.1768 | 6.5653 | 5.2242 | 4.4211 | 28.1989 | 27.4032 | 26.3063 | 24.9274 | 22.5211 | 19.4442 | 16.5463 | 15.5989 | 15.1726 | 14.9137 | 7.9811 | 6.5379 | 5.7326
|  | INVERURIE | HT |  |  |  |  | 29.8032 | 29.4316 | 28.4179 | 27.3063 | 25.2611 | 24.4474 | 23.5516 | 22.6168 | 21.1768 | 18.86 | 12.1621 | 11.1726 | 10.4705 | 26.9516 | 25.9453 | 24.7063 | 23.3484 | 20.8568 | 19.9316 | 18.9095 | 17.8432 | 16.1895 | 13.4895 | 6.9021 | 5.4158 | 4.4158 | 28.2495 | 27.4389 | 26.2789 | 24.9126 | 22.4537 | 21.54 | 20.5326 | 19.48 | 17.8505 | 15.2179 | 8.3947 | 6.8189 | 5.8189
|  | INVERURIE | HE |  |  |  |  | 29.8274 | 29.6695 | 28.7758 | 27.7484 | 25.8705 | 23.3011 | 20.7695 | 19.9358 | 19.6116 | 19.4705 | 12.5905 | 11.9484 | 11.5274 | 27.1179 | 26.2347 | 25.1389 | 23.8821 | 21.5526 | 18.5916 | 15.6632 | 14.6989 | 14.3337 | 14.1737 | 7.1811 | 6.5232 | 6.04 | 28.3863 | 27.6726 | 26.7126 | 25.4505 | 23.1411 | 20.2221 | 17.3453 | 16.4053 | 16.0463 | 15.8895 | 8.3221 | 7.6189 | 7.1358
|  | INVERURIE | FB |  |  |  |  | 29.8842 | 29.8579 | 29.8284 | 29.7663 | 29.3653 | 28.5463 | 27.4232 | 26.0274 | 25.8368 | 25.6874 | 24.2474 | 22.6126 | 22.1842 | 27.6611 | 27.2863 | 26.8432 | 26.3432 | 25.8526 | 24.8421 | 23.4547 | 21.7095 | 21.4947 | 21.3284 | 19.6811 | 17.8042 | 17.3168 | 28.8263 | 28.5253 | 28.1705 | 27.7695 | 27.3747 | 26.4147 | 25.0211 | 23.2979 | 23.0853 | 22.9211 | 21.2958 | 19.4453 | 18.9642
| BROADFORD | KALNAKIL | MINIMUM HEADROOM | NG 69146 53941 | YES | YES | 0 | 2.4863 | 2.48 | 2.4737 | 2.4632 | 2.4558 | 2.4474 | 2.4389 | 2.4295 | 2.4232 | 2.4158 | 2.3853 | 2.3621 | 2.3453 | 2.4884 | 2.4821 | 2.4768 | 2.4674 | 2.4611 | 2.4526 | 2.4463 | 2.4368 | 2.4316 | 2.4253 | 2.4011 | 2.3789 | 2.3621 | 2.6274 | 2.62 | 2.6116 | 2.6011 | 2.5926 | 2.5821 | 2.5737 | 2.5632 | 2.5558 | 2.5484 | 2.5179 | 2.4905 | 2.4695
|  | KALNAKIL | EE |  |  |  |  | 2.4863 | 2.48 | 2.4737 | 2.4632 | 2.4558 | 2.4474 | 2.4389 | 2.4295 | 2.4232 | 2.4158 | 2.3884 | 2.3642 | 2.3453 | 2.4884 | 2.4821 | 2.4768 | 2.4674 | 2.4611 | 2.4526 | 2.4463 | 2.4368 | 2.4316 | 2.4253 | 2.4011 | 2.3789 | 2.3632 | 2.6274 | 2.62 | 2.6116 | 2.6011 | 2.5926 | 2.5821 | 2.5737 | 2.5632 | 2.5558 | 2.5484 | 2.5179 | 2.4905 | 2.4695
|  | KALNAKIL | HT |  |  |  |  | 2.4884 | 2.4821 | 2.4768 | 2.4674 | 2.4611 | 2.4526 | 2.4442 | 2.4358 | 2.4295 | 2.42 | 2.3853 | 2.3621 | 2.3453 | 2.4895 | 2.4842 | 2.4789 | 2.4705 | 2.4653 | 2.4568 | 2.4505 | 2.4421 | 2.4368 | 2.4284 | 2.4032 | 2.38 | 2.3621 | 2.6284 | 2.6221 | 2.6158 | 2.6063 | 2.5979 | 2.5884 | 2.58 | 2.5705 | 2.5632 | 2.5537 | 2.5221 | 2.4926 | 2.4705
|  | KALNAKIL | HE |  |  |  |  | 2.4937 | 2.4884 | 2.4842 | 2.4789 | 2.4747 | 2.4716 | 2.4663 | 2.4611 | 2.4558 | 2.4516 | 2.4368 | 2.4242 | 2.4168 | 2.4937 | 2.4895 | 2.4863 | 2.4811 | 2.4768 | 2.4737 | 2.4684 | 2.4642 | 2.46 | 2.4558 | 2.4432 | 2.4316 | 2.4253 | 2.6347 | 2.6295 | 2.6253 | 2.6189 | 2.6147 | 2.6116 | 2.6053 | 2.6 | 2.5947 | 2.5895 | 2.5726 | 2.5589 | 2.5495
|  | KALNAKIL | FB |  |  |  |  | 2.4958 | 2.4926 | 2.4895 | 2.4863 | 2.4842 | 2.4811 | 2.4789 | 2.4758 | 2.4726 | 2.4674 | 2.4505 | 2.4326 | 2.42 | 2.4968 | 2.4937 | 2.4905 | 2.4884 | 2.4853 | 2.4832 | 2.4811 | 2.4779 | 2.4758 | 2.4705 | 2.4558 | 2.44 | 2.4295 | 2.6379 | 2.6337 | 2.6305 | 2.6274 | 2.6242 | 2.6211 | 2.6189 | 2.6147 | 2.6105 | 2.6053 | 2.5863 | 2.5663 | 2.5516
| DUNOON | KAMES | MINIMUM HEADROOM | NR 96305 71237 | YES | YES | 0 | 2.3779 | 2.3579 | 2.3389 | 2.3126 | 2.2874 | 2.26 | 2.2316 | 2.1989 | 2.1684 | 2.1442 | 2.0253 | 1.9432 | 1.8863 | 2.3589 | 2.3368 | 2.3158 | 2.2874 | 2.26 | 2.2274 | 2.1958 | 2.1589 | 2.1232 | 2.0979 | 1.9684 | 1.8789 | 1.8168 | 2.3589 | 2.3358 | 2.3137 | 2.2842 | 2.2568 | 2.2263 | 2.1947 | 2.1579 | 2.1232 | 2.0958 | 1.9611 | 1.8695 | 1.8042
|  | KAMES | EE |  |  |  |  | 2.3779 | 2.3579 | 2.3389 | 2.3126 | 2.2874 | 2.2621 | 2.2326 | 2.2032 | 2.1726 | 2.1516 | 2.0253 | 1.9432 | 1.8863 | 2.3589 | 2.3368 | 2.3158 | 2.2874 | 2.26 | 2.2316 | 2.2 | 2.1663 | 2.1347 | 2.1105 | 1.9684 | 1.8789 | 1.8168 | 2.3589 | 2.3358 | 2.3137 | 2.2842 | 2.2568 | 2.2284 | 2.1968 | 2.1611 | 2.1295 | 2.1053 | 1.9611 | 1.8695 | 1.8042
|  | KAMES | HT |  |  |  |  | 2.3853 | 2.3653 | 2.3463 | 2.3211 | 2.2968 | 2.26 | 2.2316 | 2.1989 | 2.1684 | 2.1442 | 2.0305 | 1.96 | 1.9095 | 2.3674 | 2.3453 | 2.3232 | 2.2947 | 2.2684 | 2.2274 | 2.1958 | 2.1589 | 2.1232 | 2.0979 | 1.9905 | 1.9074 | 1.8358 | 2.3663 | 2.3453 | 2.3242 | 2.2947 | 2.2684 | 2.2263 | 2.1947 | 2.1579 | 2.1232 | 2.0958 | 1.9884 | 1.9032 | 1.8326
|  | KAMES | HE |  |  |  |  | 2.3968 | 2.3842 | 2.3747 | 2.3611 | 2.3463 | 2.3337 | 2.3053 | 2.2863 | 2.2632 | 2.2516 | 2.1716 | 2.1326 | 2.1021 | 2.3811 | 2.3674 | 2.3547 | 2.3411 | 2.3263 | 2.3126 | 2.2811 | 2.26 | 2.2337 | 2.22 | 2.1295 | 2.0863 | 2.0526 | 2.38 | 2.3674 | 2.3558 | 2.3411 | 2.3253 | 2.3116 | 2.28 | 2.2589 | 2.2326 | 2.2189 | 2.1274 | 2.0832 | 2.0495
|  | KAMES | FB |  |  |  |  | 2.4042 | 2.3968 | 2.3895 | 2.38 | 2.3705 | 2.3632 | 2.3537 | 2.3442 | 2.3295 | 2.3179 | 2.2484 | 2.1863 | 2.1474 | 2.3884 | 2.38 | 2.3716 | 2.3611 | 2.3516 | 2.3421 | 2.3326 | 2.3221 | 2.3053 | 2.2926 | 2.2116 | 2.14 | 2.0968 | 2.3884 | 2.38 | 2.3716 | 2.3611 | 2.3505 | 2.3421 | 2.3326 | 2.3221 | 2.3053 | 2.2916 | 2.2116 | 2.1411 | 2.0958
| KEITH 2 | KEITH | MINIMUM HEADROOM | NJ 43925 50405 | NO | YES | 0 | 15.7753 | 15.6174 | 15.3068 | 15.1574 | 15.0616 | 14.9574 | 14.79 | 14.6395 | 14.4711 | 14.3068 | 12.7721 | 12.2658 | 12.0321 | 14.5758 | 14.4105 | 14.0853 | 13.9305 | 13.8316 | 13.7242 | 13.5495 | 13.3947 | 13.2179 | 13.0484 | 12.4337 | 11.1632 | 10.92 | 15.0497 | 15.0182 | 14.9939 | 14.9624 | 14.8561 | 14.7392 | 14.5445 | 14.3729 | 14.1771 | 13.9876 | 13.3003 | 11.8055 | 11.5329
|  | KEITH | EE |  |  |  |  | 15.7753 | 15.6174 | 15.3068 | 15.1574 | 15.0616 | 14.9574 | 14.8332 | 14.6921 | 14.5532 | 14.4732 | 13.73 | 12.2658 | 12.0321 | 14.5758 | 14.4105 | 14.0853 | 13.9305 | 13.8316 | 13.7242 | 13.5958 | 13.4495 | 13.3053 | 13.2221 | 12.4474 | 11.1632 | 10.92 | 15.0497 | 15.0182 | 14.9939 | 14.9634 | 14.8561 | 14.7392 | 14.5992 | 14.4361 | 14.275 | 14.1845 | 13.3139 | 11.8055 | 11.5329
|  | KEITH | HT |  |  |  |  | 15.7879 | 15.6595 | 15.3532 | 15.1984 | 15.0963 | 14.9658 | 14.79 | 14.6395 | 14.4711 | 14.3068 | 12.7721 | 12.4658 | 12.2532 | 14.5884 | 14.4547 | 14.1337 | 13.9737 | 13.8684 | 13.7326 | 13.5495 | 13.3947 | 13.2179 | 13.0484 | 12.4337 | 11.3842 | 11.1042 | 15.0539 | 15.0255 | 14.9939 | 14.9624 | 14.8992 | 14.7487 | 14.5445 | 14.3729 | 14.1771 | 13.9876 | 13.3003 | 12.0708 | 11.7624
|  | KEITH | HE |  |  |  |  | 15.8311 | 15.7374 | 15.4605 | 15.3542 | 15.2942 | 15.2268 | 15.0974 | 14.9826 | 14.8647 | 14.8205 | 14.2426 | 13.6068 | 13.4974 | 14.6337 | 14.5368 | 14.2463 | 14.1358 | 14.0747 | 14.0063 | 13.8726 | 13.7526 | 13.6305 | 13.5853 | 12.98 | 12.4137 | 12.3 | 15.0624 | 15.0361 | 15.015 | 14.9866 | 14.9518 | 14.9087 | 14.8634 | 14.7792 | 14.6434 | 14.5929 | 13.9066 | 13.2434 | 13.1171
|  | KEITH | FB |  |  |  |  | 15.97 | 15.9079 | 15.8174 | 15.7426 | 15.6826 | 15.63 | 15.5847 | 15.5279 | 15.4605 | 15.4089 | 15.0521 | 14.6553 | 14.4963 | 14.7789 | 14.7137 | 14.62 | 14.5411 | 14.4789 | 14.4253 | 14.3768 | 14.3189 | 14.2484 | 14.1947 | 13.8221 | 13.4074 | 13.2421 | 15.0782 | 15.0676 | 15.0561 | 15.0445 | 15.0308 | 15.0171 | 15.0034 | 14.9887 | 14.9739 | 14.9582 | 14.8497 | 14.3813 | 14.1961
| KINTORE | KEMNAY | MINIMUM HEADROOM | NJ 73180 16804 | NO | YES | 0 | 15.1279 | 15.0468 | 14.9763 | 14.8605 | 14.3595 | 13.8953 | 13.3816 | 13.29 | 13.2037 | 13.1458 | 11.9826 | 11.7289 | 11.5468 | 13.7611 | 13.6621 | 13.5821 | 13.4484 | 12.8505 | 12.2979 | 11.6853 | 11.5811 | 11.4842 | 11.4179 | 10.0811 | 9.7979 | 9.5326 | 14.2739 | 14.1897 | 14.1192 | 13.9908 | 13.4097 | 12.8708 | 12.2729 | 12.1708 | 12.0761 | 12.0108 | 10.7087 | 10.4318 | 10.1729
|  | KEMNAY | EE |  |  |  |  | 15.1279 | 15.0468 | 14.9858 | 14.8974 | 14.3984 | 13.8953 | 13.3816 | 13.29 | 13.2037 | 13.1458 | 12.0247 | 11.7984 | 11.6121 | 13.7611 | 13.6621 | 13.5937 | 13.4916 | 12.8958 | 12.2979 | 11.6853 | 11.5811 | 11.4842 | 11.4179 | 10.0811 | 9.82 | 9.6021 | 14.2739 | 14.1897 | 14.1276 | 14.0318 | 13.455 | 12.8708 | 12.2729 | 12.1708 | 12.0761 | 12.0108 | 10.7087 | 10.4539 | 10.2424
|  | KEMNAY | HT |  |  |  |  | 15.1384 | 15.0647 | 14.9763 | 14.8605 | 14.3595 | 14.2911 | 14.2184 | 14.1458 | 13.8353 | 13.2647 | 11.9826 | 11.7289 | 11.5468 | 13.7779 | 13.6832 | 13.5821 | 13.4484 | 12.8505 | 12.7737 | 12.6926 | 12.6116 | 12.2442 | 11.5632 | 10.1116 | 9.7979 | 9.5326 | 14.2876 | 14.2087 | 14.1192 | 13.9908 | 13.4097 | 13.335 | 13.2539 | 13.175 | 12.8171 | 12.1518 | 10.7392 | 10.4318 | 10.1729
|  | KEMNAY | HE |  |  |  |  | 15.17 | 15.1163 | 15.0711 | 14.9911 | 14.5121 | 14.03 | 13.5289 | 13.4679 | 13.4068 | 13.37 | 12.3805 | 12.2647 | 12.1532 | 13.8253 | 13.7505 | 13.6937 | 13.6011 | 13.0305 | 12.4568 | 11.86 | 11.7916 | 11.7221 | 11.6789 | 10.4926 | 10.3589 | 10.2274 | 14.3266 | 14.2634 | 14.2161 | 14.1339 | 13.5855 | 13.0255 | 12.4434 | 12.3761 | 12.3087 | 12.2666 | 11.1118 | 10.9813 | 10.8529
|  | KEMNAY | FB |  |  |  |  | 15.2068 | 15.1858 | 15.1647 | 15.1416 | 15.0532 | 14.8921 | 14.6668 | 14.3647 | 14.3142 | 14.2763 | 13.9342 | 13.5405 | 13.4321 | 13.8758 | 13.8474 | 13.8147 | 13.7821 | 13.6663 | 13.4747 | 13.2042 | 12.8421 | 12.7842 | 12.7411 | 12.3368 | 11.8695 | 11.7432 | 14.3687 | 14.3445 | 14.3192 | 14.2918 | 14.1961 | 14.0182 | 13.7571 | 13.4034 | 13.3466 | 13.3045 | 12.9097 | 12.4539 | 12.3297
| TAYNUILT | KENMORE | MINIMUM HEADROOM | NN 00325 34042 | YES | YES | 0 | 1.0063 | 1.0021 | 0.99789 | 0.99579 | 0.99263 | 0.98947 | 0.98526 | 0.98105 | 0.97684 | 0.97474 | 0.96421 | 0.95263 | 0.94105 | 1.0095 | 1.0053 | 1.0021 | 0.99895 | 0.99474 | 0.99158 | 0.98632 | 0.98211 | 0.97895 | 0.97579 | 0.96526 | 0.95579 | 0.94632 | 0.88947 | 0.88526 | 0.88105 | 0.87895 | 0.87474 | 0.87053 | 0.86526 | 0.86211 | 0.85789 | 0.85474 | 0.84316 | 0.83053 | 0.81895
|  | KENMORE | EE |  |  |  |  | 1.0063 | 1.0021 | 0.99789 | 0.99579 | 0.99263 | 0.98947 | 0.98526 | 0.98105 | 0.97684 | 0.97474 | 0.96421 | 0.95263 | 0.94105 | 1.0095 | 1.0053 | 1.0021 | 0.99895 | 0.99474 | 0.99158 | 0.98632 | 0.98211 | 0.97895 | 0.97579 | 0.96526 | 0.95579 | 0.94632 | 0.88947 | 0.88526 | 0.88105 | 0.87895 | 0.87474 | 0.87053 | 0.86526 | 0.86211 | 0.85789 | 0.85474 | 0.84316 | 0.83053 | 0.81895
|  | KENMORE | HT |  |  |  |  | 1.0074 | 1.0053 | 1.0032 | 1.0032 | 1.0011 | 0.99895 | 0.99789 | 0.99579 | 0.99368 | 0.99158 | 0.98421 | 0.97474 | 0.97053 | 1.0116 | 1.0074 | 1.0042 | 1.0032 | 1.0011 | 0.99684 | 0.99368 | 0.99053 | 0.98737 | 0.98526 | 0.97684 | 0.96947 | 0.96211 | 0.89053 | 0.88842 | 0.88632 | 0.88632 | 0.88421 | 0.88105 | 0.87895 | 0.87684 | 0.87474 | 0.87263 | 0.86526 | 0.85789 | 0.85158
|  | KENMORE | HE |  |  |  |  | 1.0074 | 1.0063 | 1.0053 | 1.0053 | 1.0032 | 1 | 0.99895 | 0.99684 | 0.99474 | 0.99368 | 0.98947 | 0.98526 | 0.98105 | 1.0126 | 1.0105 | 1.0084 | 1.0084 | 1.0063 | 1.0032 | 1.0011 | 0.99895 | 0.99789 | 0.99789 | 0.99263 | 0.98737 | 0.98421 | 0.89158 | 0.88947 | 0.88842 | 0.88842 | 0.88632 | 0.88316 | 0.88105 | 0.88 | 0.87789 | 0.87684 | 0.87263 | 0.86632 | 0.86211
|  | KENMORE | FB |  |  |  |  | 1.0095 | 1.0084 | 1.0074 | 1.0074 | 1.0063 | 1.0063 | 1.0063 | 1.0042 | 1.0042 | 1.0042 | 1.0011 | 1 | 0.99789 | 1.0137 | 1.0116 | 1.0116 | 1.0105 | 1.0095 | 1.0084 | 1.0074 | 1.0042 | 1.0032 | 1.0032 | 0.99789 | 0.99474 | 0.99158 | 0.89368 | 0.89158 | 0.89053 | 0.89053 | 0.88947 | 0.88947 | 0.88947 | 0.88632 | 0.88632 | 0.88632 | 0.88316 | 0.88211 | 0.87895
| STRATHLEVEN | KEPCULLOCH | MINIMUM HEADROOM | NS 53864 91598 | NO | YES | 0.015306 | 5.9787 | 5.8808 | 5.7629 | 13.8721 | 13.7342 | 13.5921 | 13.4353 | 13.2858 | 13.1479 | 13.0142 | 12.3079 | 11.6553 | 11.1521 | 5.6958 | 5.5874 | 5.4558 | 13.1221 | 12.9674 | 12.8084 | 12.6326 | 12.4663 | 12.3105 | 12.1579 | 11.5074 | 10.7295 | 10.0032 | 5.852 | 5.7425 | 5.6099 | 13.4937 | 13.3358 | 13.1768 | 13.0021 | 12.8316 | 12.6768 | 12.5242 | 11.8832 | 11.1074 | 10.3811
|  | KEPCULLOCH | EE |  |  |  |  | 5.9787 | 5.8808 | 5.7629 | 13.8721 | 13.7342 | 13.5921 | 13.4353 | 13.2858 | 13.1479 | 13.0142 | 12.4995 | 11.9216 | 11.4111 | 5.6958 | 5.5874 | 5.4558 | 13.1221 | 12.9674 | 12.8084 | 12.6326 | 12.4663 | 12.3105 | 12.1579 | 11.5874 | 10.9253 | 10.3389 | 5.852 | 5.7425 | 5.6099 | 13.4937 | 13.3358 | 13.1768 | 13.0021 | 12.8316 | 12.6768 | 12.5242 | 11.9537 | 11.2905 | 10.7042
|  | KEPCULLOCH | HT |  |  |  |  | 6.0039 | 5.9071 | 5.7861 | 13.8879 | 13.7426 | 13.6089 | 13.4637 | 13.3205 | 13.1774 | 13.0479 | 12.3079 | 11.6553 | 11.1521 | 5.7232 | 5.6137 | 5.4789 | 13.1379 | 12.9726 | 12.8189 | 12.6526 | 12.4884 | 12.3253 | 12.1905 | 11.5074 | 10.7295 | 10.0032 | 5.8793 | 5.7699 | 5.6341 | 13.5095 | 13.3442 | 13.1916 | 13.0253 | 12.8611 | 12.6968 | 12.5663 | 11.8832 | 11.1074 | 10.3811
|  | KEPCULLOCH | HE |  |  |  |  | 6.0734 | 6.0197 | 5.9545 | 14.1195 | 14.0247 | 13.9279 | 13.8237 | 13.7289 | 13.63 | 13.5332 | 13.1521 | 12.7142 | 12.3195 | 5.7989 | 5.7389 | 5.6632 | 13.3916 | 13.2842 | 13.1737 | 13.0558 | 12.9463 | 12.8326 | 12.7211 | 12.2779 | 11.7663 | 11.3053 | 5.9562 | 5.8972 | 5.8214 | 13.7674 | 13.66 | 13.5505 | 13.4326 | 13.3242 | 13.2105 | 13.0979 | 12.6568 | 12.1474 | 11.6863
|  | KEPCULLOCH | FB |  |  |  |  | 6.0882 | 6.0587 | 6.0218 | 14.2247 | 14.1795 | 14.1321 | 14.0784 | 14.0247 | 13.9658 | 13.8963 | 13.6289 | 13.3258 | 13.0563 | 5.8158 | 5.7821 | 5.74 | 13.5116 | 13.4611 | 13.4074 | 13.3453 | 13.2842 | 13.2168 | 13.1368 | 12.8295 | 12.4789 | 12.1674 | 5.9741 | 5.9404 | 5.8983 | 13.8874 | 13.8368 | 13.7832 | 13.7211 | 13.66 | 13.5937 | 13.5126 | 13.2063 | 12.8579 | 12.5463
| TAYNUILT | KERRERA | MINIMUM HEADROOM | NM 82340 27997 | YES | YES | 0 | 0.29789 | 0.29789 | 0.29684 | 0.29579 | 0.29474 | 0.29474 | 0.29368 | 0.29263 | 0.29158 | 0.29053 | 0.28737 | 0.28526 | 0.28421 | 0.28947 | 0.28842 | 0.28842 | 0.28737 | 0.28632 | 0.28526 | 0.28421 | 0.28316 | 0.28211 | 0.28105 | 0.27789 | 0.27474 | 0.27474 | 0.29263 | 0.29158 | 0.29158 | 0.29053 | 0.28947 | 0.28842 | 0.28737 | 0.28632 | 0.28526 | 0.28421 | 0.28105 | 0.27895 | 0.27789
|  | KERRERA | EE |  |  |  |  | 0.29789 | 0.29789 | 0.29684 | 0.29579 | 0.29474 | 0.29474 | 0.29368 | 0.29263 | 0.29263 | 0.29053 | 0.28842 | 0.28632 | 0.28421 | 0.28947 | 0.28842 | 0.28842 | 0.28737 | 0.28632 | 0.28526 | 0.28421 | 0.28316 | 0.28316 | 0.28105 | 0.27895 | 0.27579 | 0.27474 | 0.29263 | 0.29158 | 0.29158 | 0.29053 | 0.28947 | 0.28842 | 0.28737 | 0.28632 | 0.28632 | 0.28421 | 0.28211 | 0.28 | 0.27789
|  | KERRERA | HT |  |  |  |  | 0.29895 | 0.29789 | 0.29789 | 0.29684 | 0.29474 | 0.29474 | 0.29368 | 0.29368 | 0.29158 | 0.29158 | 0.28737 | 0.28526 | 0.28421 | 0.29053 | 0.28842 | 0.28842 | 0.28842 | 0.28632 | 0.28632 | 0.28421 | 0.28421 | 0.28211 | 0.28211 | 0.27789 | 0.27474 | 0.27474 | 0.29368 | 0.29158 | 0.29158 | 0.29158 | 0.28947 | 0.28947 | 0.28737 | 0.28737 | 0.28526 | 0.28526 | 0.28105 | 0.27895 | 0.27789
|  | KERRERA | HE |  |  |  |  | 0.3 | 0.29789 | 0.29789 | 0.29789 | 0.29789 | 0.29684 | 0.29579 | 0.29474 | 0.29579 | 0.29368 | 0.29263 | 0.29263 | 0.29158 | 0.29158 | 0.28947 | 0.28947 | 0.28947 | 0.28842 | 0.28737 | 0.28632 | 0.28632 | 0.28737 | 0.28526 | 0.28421 | 0.28316 | 0.28211 | 0.29474 | 0.29263 | 0.29263 | 0.29263 | 0.29158 | 0.29053 | 0.28947 | 0.28947 | 0.29053 | 0.28842 | 0.28737 | 0.28632 | 0.28526
|  | KERRERA | FB |  |  |  |  | 0.3 | 0.3 | 0.29895 | 0.29789 | 0.29789 | 0.29789 | 0.29789 | 0.29789 | 0.29684 | 0.29684 | 0.29474 | 0.29263 | 0.29158 | 0.29158 | 0.29158 | 0.29053 | 0.28947 | 0.28947 | 0.28842 | 0.28842 | 0.28842 | 0.28842 | 0.28842 | 0.28632 | 0.28316 | 0.28211 | 0.29474 | 0.29474 | 0.29368 | 0.29263 | 0.29263 | 0.29158 | 0.29158 | 0.29158 | 0.29158 | 0.29158 | 0.28947 | 0.28632 | 0.28526
| GRUDIE BRIDGE | KERRY FALLS | MINIMUM HEADROOM | NG 82909 71978 | YES | NO | 2.0408 | 2.0968 | 2.08 | 2.0611 | 2.0432 | 2.0221 | 1.7863 | 1.2284 | 0.81158 | 0.62632 | 0.58947 | 0.41895 | 0.28105 | 0.18105 | 2.1337 | 2.1126 | 2.0905 | 2.0663 | 2.0389 | 1.7011 | 1.2042 | 0.81895 | 0.63684 | 0.6 | 0.46211 | 0.31895 | 0.19158 | 2.0642 | 2.0421 | 2.02 | 1.9968 | 1.9695 | 1.5389 | 0.88 | 0.39263 | 0.17684 | 0.13684 | -0.02 | -0.18105 | -0.32316
|  | KERRY FALLS | EE |  |  |  |  | 3.5421 | 3.4958 | 3.4484 | 3.3937 | 3.3379 | 3.2811 | 3.2232 | 2.7295 | 2.1516 | 1.7116 | 1.3758 | 1.2021 | 1.0547 | 3.5284 | 3.4863 | 3.4432 | 3.3895 | 3.3347 | 3.2789 | 3.2221 | 2.6705 | 2.0032 | 1.4989 | 1.1526 | 1 | 0.87789 | 3.5179 | 3.4663 | 3.4137 | 3.3505 | 3.2884 | 3.2253 | 3.1621 | 2.5842 | 1.9074 | 1.3916 | 1.0074 | 0.81263 | 0.64526
|  | KERRY FALLS | HT |  |  |  |  | 2.0968 | 2.08 | 2.0611 | 2.0432 | 2.0221 | 1.7863 | 1.2284 | 0.81158 | 0.62632 | 0.58947 | 0.41895 | 0.28105 | 0.18105 | 2.1337 | 2.1126 | 2.0905 | 2.0663 | 2.0389 | 1.7011 | 1.2042 | 0.81895 | 0.63684 | 0.6 | 0.46211 | 0.31895 | 0.19158 | 2.0642 | 2.0421 | 2.02 | 1.9968 | 1.9695 | 1.5389 | 0.88 | 0.39263 | 0.17684 | 0.13684 | -0.02 | -0.18105 | -0.32316
|  | KERRY FALLS | HE |  |  |  |  | 2.1 | 2.0842 | 2.0684 | 2.0516 | 2.0326 | 2.0116 | 1.9884 | 1.7726 | 1.1642 | 0.73789 | 0.62526 | 0.54 | 0.47579 | 2.1421 | 2.1232 | 2.1053 | 2.0863 | 2.0653 | 2.0421 | 2.0179 | 1.6874 | 1.1432 | 0.74526 | 0.63474 | 0.54947 | 0.48526 | 2.0716 | 2.0516 | 2.0347 | 2.0158 | 1.9937 | 1.9705 | 1.9463 | 1.5305 | 0.80842 | 0.30526 | 0.17895 | 0.082105 | 0.010526
|  | KERRY FALLS | FB |  |  |  |  | 3.5958 | 3.5842 | 3.5716 | 3.5589 | 3.5442 | 3.5316 | 3.5179 | 3.5063 | 3.2821 | 3.0011 | 2.4716 | 2.3979 | 2.3463 | 3.58 | 3.5663 | 3.5537 | 3.5389 | 3.5242 | 3.5105 | 3.4968 | 3.4832 | 3.2211 | 2.8926 | 2.2737 | 2.1937 | 2.1368 | 3.5789 | 3.5653 | 3.5516 | 3.5368 | 3.52 | 3.5063 | 3.4916 | 3.4779 | 3.2147 | 2.8874 | 2.2674 | 2.1853 | 2.1253
| TAYNUILT | KILCHRENAN | MINIMUM HEADROOM | NN 03495 23835 | YES | YES | 0 | 0.98421 | 0.88947 | 0.77895 | 0.69158 | 0.67579 | 0.65895 | 0.64105 | 0.62526 | 0.60947 | 0.59474 | 0.54 | 0.48421 | 0.43684 | 0.99263 | 0.88421 | 0.75579 | 0.66421 | 0.64842 | 0.63263 | 0.61579 | 0.60105 | 0.58632 | 0.57263 | 0.52105 | 0.47053 | 0.42842 | 0.98 | 0.89368 | 0.76211 | 0.66211 | 0.64316 | 0.62421 | 0.60526 | 0.58842 | 0.56947 | 0.55263 | 0.49158 | 0.42842 | 0.37474
|  | KILCHRENAN | EE |  |  |  |  | 0.98421 | 0.97053 | 0.83684 | 0.69158 | 0.67579 | 0.65895 | 0.64105 | 0.62526 | 0.60947 | 0.59474 | 0.54 | 0.48421 | 0.43684 | 0.99263 | 0.98 | 0.83158 | 0.66421 | 0.64842 | 0.63263 | 0.61579 | 0.60105 | 0.58632 | 0.57263 | 0.52105 | 0.47053 | 0.42842 | 0.98 | 0.96737 | 0.83158 | 0.66211 | 0.64316 | 0.62421 | 0.60526 | 0.58842 | 0.56947 | 0.55263 | 0.49158 | 0.42842 | 0.37474
|  | KILCHRENAN | HT |  |  |  |  | 0.99053 | 0.88947 | 0.77895 | 0.76632 | 0.75368 | 0.74211 | 0.72842 | 0.71684 | 0.70316 | 0.68947 | 0.63684 | 0.59368 | 0.56421 | 0.99789 | 0.88421 | 0.75579 | 0.74316 | 0.72947 | 0.71579 | 0.70316 | 0.69053 | 0.67579 | 0.66316 | 0.61684 | 0.57158 | 0.53368 | 0.98737 | 0.89368 | 0.76211 | 0.74842 | 0.73579 | 0.72105 | 0.70737 | 0.69368 | 0.67895 | 0.66421 | 0.61579 | 0.56526 | 0.52316
|  | KILCHRENAN | HE |  |  |  |  | 0.99684 | 0.98947 | 0.86421 | 0.73158 | 0.72632 | 0.71684 | 0.70842 | 0.70105 | 0.69263 | 0.68526 | 0.65789 | 0.63263 | 0.61053 | 1.0053 | 0.99789 | 0.85579 | 0.70105 | 0.69579 | 0.68632 | 0.67895 | 0.67158 | 0.66211 | 0.65684 | 0.62842 | 0.60421 | 0.58316 | 0.99158 | 0.98421 | 0.86316 | 0.70737 | 0.70105 | 0.69158 | 0.68316 | 0.67579 | 0.66526 | 0.65684 | 0.62737 | 0.59684 | 0.57158
|  | KILCHRENAN | FB |  |  |  |  | 1 | 0.99684 | 0.99263 | 0.93895 | 0.88421 | 0.88105 | 0.87684 | 0.87158 | 0.86737 | 0.86211 | 0.83789 | 0.81158 | 0.79368 | 1.0095 | 1.0053 | 1 | 0.94105 | 0.87789 | 0.87368 | 0.86842 | 0.86421 | 0.85895 | 0.85263 | 0.82632 | 0.79789 | 0.77684 | 0.99474 | 0.99263 | 0.98947 | 0.94947 | 0.88632 | 0.88211 | 0.87789 | 0.87263 | 0.86737 | 0.86 | 0.83263 | 0.80316 | 0.78316
| STRATHLEVEN | KILLEARN | MINIMUM HEADROOM | NS 51313 86758 | YES | YES | 0 | 0.89895 | 0.83474 | 0.73474 | 0.6 | 0.46947 | 0.31895 | 0.15368 | 0.0052632 | -0.14316 | -0.29684 | -1.0389 | -1.6968 | -2.2063 | 1.1968 | 1.12 | 1.0021 | 0.84632 | 0.69368 | 0.52105 | 0.32947 | 0.15684 | -0.013684 | -0.19053 | -0.87474 | -1.6684 | -2.4116 | 1.1853 | 1.1147 | 1.0053 | 0.85053 | 0.7 | 0.52842 | 0.34 | 0.16842 | 0 | -0.17579 | -0.85158 | -1.6368 | -2.3716
|  | KILLEARN | EE |  |  |  |  | 0.89895 | 0.83579 | 0.76 | 0.65789 | 0.54947 | 0.43895 | 0.30842 | 0.17263 | 0.042105 | -0.075789 | -0.57895 | -1.1126 | -1.6032 | 1.1968 | 1.1253 | 1.0358 | 0.91579 | 0.79053 | 0.66526 | 0.51684 | 0.36105 | 0.20947 | 0.073684 | -0.50526 | -1.1221 | -1.6916 | 1.1853 | 1.1168 | 1.0326 | 0.91579 | 0.79263 | 0.66632 | 0.51895 | 0.36421 | 0.21474 | 0.078947 | -0.49579 | -1.1095 | -1.6758
|  | KILLEARN | HT |  |  |  |  | 0.90316 | 0.83474 | 0.73474 | 0.6 | 0.46947 | 0.31895 | 0.15368 | 0.0052632 | -0.14316 | -0.29684 | -1.0389 | -1.6968 | -2.2063 | 1.2011 | 1.12 | 1.0021 | 0.84632 | 0.69368 | 0.52105 | 0.32947 | 0.15684 | -0.013684 | -0.19053 | -0.87474 | -1.6684 | -2.4116 | 1.1895 | 1.1147 | 1.0053 | 0.85053 | 0.7 | 0.52842 | 0.34 | 0.16842 | 0 | -0.17579 | -0.85158 | -1.6368 | -2.3716
|  | KILLEARN | HE |  |  |  |  | 0.93053 | 0.88 | 0.81158 | 0.72316 | 0.62947 | 0.53158 | 0.39895 | 0.27789 | 0.15895 | 0.054737 | -0.37263 | -0.85684 | -1.3105 | 1.2337 | 1.1737 | 1.0926 | 0.98842 | 0.88 | 0.76842 | 0.61474 | 0.47474 | 0.33789 | 0.21579 | -0.28 | -0.84526 | -1.3758 | 1.22 | 1.1653 | 1.0905 | 0.99158 | 0.88421 | 0.77263 | 0.62105 | 0.48211 | 0.34737 | 0.22632 | -0.26526 | -0.82316 | -1.3484
|  | KILLEARN | FB |  |  |  |  | 0.95789 | 0.93474 | 0.90211 | 0.86632 | 0.82737 | 0.78737 | 0.73789 | 0.68 | 0.61158 | 0.54421 | 0.25579 | -0.061053 | -0.33053 | 1.2642 | 1.2379 | 1.2 | 1.1579 | 1.1116 | 1.0642 | 1.0063 | 0.93789 | 0.85579 | 0.77895 | 0.44421 | 0.075789 | -0.23895 | 1.2495 | 1.2242 | 1.1884 | 1.1495 | 1.1074 | 1.0621 | 1.0084 | 0.94105 | 0.86105 | 0.78526 | 0.45474 | 0.089474 | -0.22105
| KILLIN | KILLIN TOWN | MINIMUM HEADROOM | NN 56931 32662 | YES | YES | 0 | 2.6621 | 2.6505 | 2.6379 | 2.6211 | 2.6042 | 2.5863 | 2.5663 | 2.5474 | 2.5116 | 2.4747 | 2.3011 | 2.5295 | 2.4674 | 2.5021 | 2.4789 | 2.4537 | 2.42 | 2.3832 | 2.3432 | 2.3 | 2.2611 | 2.2168 | 2.1737 | 2.0147 | 2.2337 | 2.1611 | 2.4611 | 2.4379 | 2.4105 | 2.3758 | 2.34 | 2.2989 | 2.2547 | 2.2147 | 2.1705 | 2.1263 | 1.9642 | 2.1884 | 2.1147
|  | KILLIN TOWN | EE |  |  |  |  | 2.6621 | 2.6505 | 2.6379 | 2.6211 | 2.6042 | 2.5863 | 2.5663 | 2.5474 | 2.5295 | 2.5 | 2.3821 | 6.9653 | 6.8495 | 2.5021 | 2.4789 | 2.4537 | 2.42 | 2.3874 | 2.3526 | 2.3147 | 2.2779 | 2.2411 | 2.2074 | 2.0758 | 6.64 | 6.5074 | 2.4611 | 2.4379 | 2.4105 | 2.3758 | 2.3421 | 2.3063 | 2.2674 | 2.2284 | 2.1926 | 2.1568 | 2.02 | 6.5789 | 6.4411
|  | KILLIN TOWN | HT |  |  |  |  | 2.6653 | 2.6547 | 2.6421 | 2.6242 | 2.6074 | 2.5884 | 2.5684 | 2.5516 | 2.5116 | 2.4747 | 2.3011 | 6.8632 | 6.7432 | 2.5074 | 2.4842 | 2.4579 | 2.4221 | 2.3832 | 2.3432 | 2.3 | 2.2611 | 2.2168 | 2.1737 | 2.0147 | 6.5474 | 6.3705 | 2.4663 | 2.4432 | 2.4168 | 2.3789 | 2.34 | 2.2989 | 2.2547 | 2.2147 | 2.1705 | 2.1263 | 1.9642 | 6.4937 | 6.3158
|  | KILLIN TOWN | HE |  |  |  |  | 2.6705 | 2.6621 | 2.6537 | 2.6421 | 2.6295 | 2.6147 | 2.5979 | 2.5842 | 2.5716 | 2.56 | 2.4874 | 7.0989 | 7.0021 | 2.5116 | 2.5021 | 2.4842 | 2.4621 | 2.4379 | 2.4105 | 2.3789 | 2.3505 | 2.3232 | 2.2947 | 2.1895 | 6.7842 | 6.6705 | 2.4789 | 2.4621 | 2.4432 | 2.42 | 2.3958 | 2.3674 | 2.3347 | 2.3053 | 2.2779 | 2.2495 | 2.1421 | 6.7337 | 6.6179
|  | KILLIN TOWN | FB |  |  |  |  | 2.6737 | 2.6716 | 2.6653 | 2.66 | 2.6547 | 2.6484 | 2.6421 | 2.6347 | 2.6284 | 2.6189 | 2.5842 | 2.5295 | 2.4674 | 2.5147 | 2.5126 | 2.5063 | 2.4958 | 2.4821 | 2.4695 | 2.4558 | 2.44 | 2.4242 | 2.4021 | 2.3211 | 2.2337 | 2.1611 | 2.4863 | 2.4779 | 2.4653 | 2.4537 | 2.44 | 2.4274 | 2.4126 | 2.3979 | 2.3821 | 2.36 | 2.2779 | 2.1884 | 2.1147
| TAYNUILT | KILMELFORD | MINIMUM HEADROOM | NM 84056 14437 | YES | YES | 0 | 0.93789 | 0.89053 | 0.83684 | 0.8 | 0.77158 | 0.72632 | 0.68526 | 4.7453 | 4.7137 | 4.6884 | 4.5968 | 4.5063 | 4.4368 | 0.93053 | 0.87474 | 0.82105 | 0.78 | 0.75053 | 0.70105 | 0.65684 | 4.7137 | 4.68 | 4.6547 | 4.56 | 4.4674 | 4.3979 | 0.92842 | 0.87368 | 0.81368 | 0.77053 | 0.73895 | 0.68632 | 0.64 | 4.6947 | 4.6579 | 4.6305 | 4.5274 | 4.4253 | 4.3453
|  | KILMELFORD | EE |  |  |  |  | 0.93789 | 0.91263 | 0.83684 | 0.8 | 0.77158 | 0.72632 | 0.68526 | 4.7453 | 4.7137 | 4.6884 | 4.5968 | 4.5063 | 4.4368 | 0.93053 | 0.90526 | 0.82105 | 0.78 | 0.75053 | 0.70105 | 0.65684 | 4.7137 | 4.68 | 4.6547 | 4.56 | 4.4674 | 4.3979 | 0.92842 | 0.9 | 0.81368 | 0.77053 | 0.73895 | 0.68632 | 0.64 | 4.6947 | 4.6579 | 4.6305 | 4.5274 | 4.4253 | 4.3453
|  | KILMELFORD | HT |  |  |  |  | 0.94526 | 0.89053 | 0.86632 | 0.83789 | 0.81263 | 0.77579 | 0.73789 | 4.8021 | 4.7674 | 4.7432 | 4.6421 | 4.5642 | 4.5084 | 0.93789 | 0.87474 | 0.84842 | 0.81789 | 0.78947 | 0.74842 | 0.70632 | 4.7653 | 4.7284 | 4.7021 | 4.6126 | 4.5221 | 4.4463 | 0.93789 | 0.87368 | 0.84632 | 0.81474 | 0.78632 | 0.74421 | 0.70211 | 4.7589 | 4.7221 | 4.6947 | 4.6021 | 4.5084 | 4.4295
|  | KILMELFORD | HE |  |  |  |  | 0.95684 | 0.94105 | 0.87789 | 0.85895 | 0.84737 | 0.82105 | 0.79368 | 4.8674 | 4.8432 | 4.8295 | 4.7832 | 4.7368 | 4.7021 | 0.95053 | 0.93474 | 0.86105 | 0.84105 | 0.82842 | 0.8 | 0.77053 | 4.8411 | 4.8147 | 4.8011 | 4.7516 | 4.7011 | 4.6653 | 0.95053 | 0.93368 | 0.85895 | 0.83789 | 0.82526 | 0.79579 | 0.76632 | 4.8347 | 4.8084 | 4.7937 | 4.7411 | 4.6874 | 4.6484
|  | KILMELFORD | FB |  |  |  |  | 0.96316 | 0.95579 | 0.94632 | 0.91474 | 0.90842 | 0.89263 | 0.87895 | 4.9632 | 4.9526 | 4.9389 | 4.8895 | 4.8379 | 4.7979 | 0.95895 | 0.95053 | 0.93895 | 0.90211 | 0.89474 | 0.87895 | 0.86316 | 4.9442 | 4.9326 | 4.9179 | 4.8611 | 4.8042 | 4.7589 | 0.95789 | 0.94947 | 0.93895 | 0.90211 | 0.89474 | 0.87684 | 0.86211 | 4.9432 | 4.9316 | 4.9158 | 4.8579 | 4.8 | 4.7558
| TAYNUILT | KILNINVER | MINIMUM HEADROOM | NM 83049 22251 | YES | YES | 0.076531 | 0.95474 | 0.91158 | 0.86737 | 0.83684 | 0.80947 | 0.77895 | 0.74737 | 0.71789 | 0.69158 | 0.66842 | -0.71158 | -0.79789 | -0.86632 | 0.96211 | 0.91474 | 0.86526 | 0.83263 | 0.80105 | 0.76737 | 0.73263 | 0.70105 | 0.67263 | 0.64632 | -0.46947 | -0.56105 | -0.63053 | 0.96 | 0.90842 | 0.85579 | 0.82105 | 0.79053 | 0.75579 | 0.72105 | 0.68842 | 0.65895 | 0.63053 | -0.75789 | -0.85474 | -0.93263
|  | KILNINVER | EE |  |  |  |  | 0.95474 | 0.93158 | 0.86737 | 0.83684 | 0.80947 | 0.77895 | 0.74737 | 0.71789 | 0.69158 | 0.66842 | -0.71158 | -0.79789 | -0.86632 | 0.96211 | 0.94105 | 0.86526 | 0.83263 | 0.80105 | 0.76737 | 0.73263 | 0.70105 | 0.67263 | 0.64632 | -0.46947 | -0.56105 | -0.63053 | 0.96 | 0.93368 | 0.85579 | 0.82105 | 0.79053 | 0.75579 | 0.72105 | 0.68842 | 0.65895 | 0.63053 | -0.75789 | -0.85474 | -0.93263
|  | KILNINVER | HT |  |  |  |  | 0.96316 | 0.91158 | 0.89263 | 0.86632 | 0.84 | 0.81263 | 0.78737 | 0.76105 | 0.73368 | 0.70737 | -0.43368 | -0.51579 | -0.57368 | 0.96842 | 0.91474 | 0.89368 | 0.86632 | 0.83579 | 0.80526 | 0.77579 | 0.74632 | 0.71789 | 0.68737 | -0.22421 | -0.31684 | -0.39474 | 0.96947 | 0.90842 | 0.88737 | 0.85789 | 0.82737 | 0.79789 | 0.76842 | 0.73684 | 0.70842 | 0.67789 | -0.45158 | -0.54947 | -0.63053
|  | KILNINVER | HE |  |  |  |  | 0.97684 | 0.96316 | 0.90947 | 0.89474 | 0.88211 | 0.86421 | 0.84632 | 0.83158 | 0.81474 | 0.80316 | 0.23789 | 0.19368 | 0.16105 | 0.98 | 0.96842 | 0.91368 | 0.89789 | 0.88421 | 0.86526 | 0.84632 | 0.83053 | 0.81368 | 0.79895 | 0.34105 | 0.29474 | 0.26 | 0.98421 | 0.97053 | 0.90737 | 0.89053 | 0.87684 | 0.85789 | 0.83789 | 0.82105 | 0.80421 | 0.78842 | 0.21895 | 0.16947 | 0.13263
|  | KILNINVER | FB |  |  |  |  | 0.98632 | 0.97684 | 0.96632 | 0.93895 | 0.93053 | 0.92105 | 0.91053 | 0.90211 | 0.88947 | 0.87579 | 0.82105 | 0.76421 | 0.72 | 0.98842 | 0.98105 | 0.97158 | 0.94842 | 0.93789 | 0.92842 | 0.91684 | 0.90632 | 0.89263 | 0.87579 | 0.81368 | 0.74842 | 0.69684 | 0.99053 | 0.98526 | 0.97368 | 0.94105 | 0.93053 | 0.92105 | 0.90947 | 0.89895 | 0.88526 | 0.86842 | 0.80632 | 0.74105 | 0.68842
| BEAULY | KILTARLITY | MINIMUM HEADROOM | NH 50271 41265 | YES | YES | 0 | 5.6379 | 5.6137 | 5.5884 | 5.5621 | 5.5389 | 5.5042 | 5.4705 | 5.4379 | 5.4032 | 5.3821 | 5.2737 | 5.2053 | 5.1547 | 5.6389 | 5.6042 | 5.5674 | 5.5295 | 5.4979 | 5.4505 | 5.4021 | 5.3547 | 5.3042 | 5.2758 | 5.1547 | 5.0495 | 4.9653 | 5.6621 | 5.6295 | 5.5947 | 5.5579 | 5.5274 | 5.48 | 5.4316 | 5.3842 | 5.3337 | 5.3053 | 5.1832 | 5.0779 | 4.9937
|  | KILTARLITY | EE |  |  |  |  | 5.6379 | 5.6137 | 5.5884 | 5.5621 | 5.5389 | 5.5095 | 5.4758 | 5.4379 | 5.4032 | 5.3821 | 5.2947 | 5.2295 | 5.1758 | 5.6389 | 5.6042 | 5.5674 | 5.5295 | 5.4979 | 5.4589 | 5.4116 | 5.3547 | 5.3042 | 5.2758 | 5.1547 | 5.0611 | 4.9874 | 5.6621 | 5.6295 | 5.5947 | 5.5579 | 5.5274 | 5.4895 | 5.4411 | 5.3842 | 5.3337 | 5.3053 | 5.1832 | 5.0895 | 5.0158
|  | KILTARLITY | HT |  |  |  |  | 5.6442 | 5.6211 | 5.5958 | 5.5684 | 5.5442 | 5.5042 | 5.4705 | 5.4389 | 5.4095 | 5.3821 | 5.2737 | 5.2053 | 5.1547 | 5.6484 | 5.6158 | 5.5811 | 5.5432 | 5.5095 | 5.4505 | 5.4021 | 5.3568 | 5.3158 | 5.28 | 5.1568 | 5.0495 | 4.9653 | 5.6716 | 5.6411 | 5.6074 | 5.5716 | 5.5389 | 5.48 | 5.4316 | 5.3863 | 5.3453 | 5.3095 | 5.1863 | 5.0779 | 4.9937
|  | KILTARLITY | HE |  |  |  |  | 5.6568 | 5.64 | 5.6232 | 5.6021 | 5.5842 | 5.5621 | 5.5347 | 5.5042 | 5.4779 | 5.4653 | 5.4105 | 5.3716 | 5.3432 | 5.6684 | 5.6453 | 5.6211 | 5.5926 | 5.5695 | 5.5411 | 5.5053 | 5.4589 | 5.4211 | 5.4021 | 5.3221 | 5.2653 | 5.22 | 5.6905 | 5.6674 | 5.6453 | 5.6179 | 5.5958 | 5.5684 | 5.5337 | 5.4884 | 5.4505 | 5.4316 | 5.3505 | 5.2937 | 5.2495
|  | KILTARLITY | FB |  |  |  |  | 5.6674 | 5.6579 | 5.6474 | 5.6358 | 5.6253 | 5.6147 | 5.5989 | 5.5832 | 5.5642 | 5.5495 | 5.4947 | 5.4505 | 5.4179 | 5.6811 | 5.6674 | 5.6516 | 5.6347 | 5.62 | 5.6042 | 5.58 | 5.5579 | 5.5284 | 5.5063 | 5.4274 | 5.3621 | 5.3105 | 5.7021 | 5.6895 | 5.6747 | 5.6579 | 5.6442 | 5.6295 | 5.6074 | 5.5863 | 5.5579 | 5.5368 | 5.4568 | 5.3916 | 5.34
| REDMOSS | KINCORTH | MINIMUM HEADROOM | NJ 94445 03252 | NO | YES | 5.1786 | 14.3061 | 13.8124 | 12.9797 | 12.4482 | 11.7513 | 11.6682 | 11.5818 | 11.4829 | 11.3534 | 11.2555 | 10.8608 | 10.6229 | 10.3797 | 13.06 | 12.3821 | 11.2242 | 10.4958 | 9.6779 | 9.5853 | 9.4895 | 9.3821 | 9.2347 | 9.1242 | 8.68 | 8.4326 | 8.1547 | 12.5051 | 11.8525 | 10.7378 | 10.0357 | 9.2483 | 9.1588 | 9.0651 | 8.9588 | 8.8157 | 8.7083 | 8.2778 | 8.0451 | 7.7714
|  | KINCORTH | EE |  |  |  |  | 14.3187 | 13.8124 | 13.0597 | 12.5261 | 11.8418 | 11.745 | 11.6271 | 11.4829 | 11.3534 | 11.2555 | 10.8608 | 10.6229 | 10.3797 | 13.08 | 12.3821 | 11.3368 | 10.5989 | 9.7842 | 9.6779 | 9.5463 | 9.3821 | 9.2347 | 9.1242 | 8.68 | 8.4326 | 8.1547 | 12.5241 | 11.8525 | 10.8462 | 10.1357 | 9.3504 | 9.2472 | 9.1188 | 8.9588 | 8.8157 | 8.7083 | 8.2778 | 8.0451 | 7.7714
|  | KINCORTH | HT |  |  |  |  | 14.3061 | 13.8271 | 12.9797 | 12.4482 | 11.7513 | 11.6682 | 11.5818 | 11.5018 | 11.4187 | 11.2987 | 10.9871 | 10.6587 | 10.4239 | 13.06 | 12.3989 | 11.2242 | 10.4958 | 9.6779 | 9.5853 | 9.4895 | 9.4011 | 9.3105 | 9.1758 | 8.92 | 8.5484 | 8.2126 | 12.5051 | 11.8693 | 10.7378 | 10.0357 | 9.2483 | 9.1588 | 9.0651 | 8.9788 | 8.8904 | 8.7588 | 8.5167 | 8.1557 | 7.8293
|  | KINCORTH | HE |  |  |  |  | 14.345 | 13.9092 | 13.1387 | 12.6082 | 11.9618 | 11.8945 | 11.7818 | 11.6924 | 11.6145 | 11.5524 | 11.3524 | 11.2071 | 11.0755 | 13.1105 | 12.5105 | 11.4389 | 10.7084 | 9.9242 | 9.8516 | 9.7263 | 9.6253 | 9.5379 | 9.4663 | 9.2421 | 9.0779 | 8.9274 | 12.5546 | 11.9767 | 10.9451 | 10.2409 | 9.4862 | 9.4146 | 9.2925 | 9.1946 | 9.1093 | 9.0409 | 8.822 | 8.663 | 8.5167
|  | KINCORTH | FB |  |  |  |  | 14.6124 | 14.5155 | 14.3071 | 14.1471 | 13.9061 | 13.7387 | 13.6197 | 13.4913 | 13.3861 | 13.3334 | 13.0145 | 12.7555 | 12.6261 | 13.4811 | 13.3505 | 13.0632 | 12.8442 | 12.5116 | 12.2832 | 12.1221 | 11.9495 | 11.8084 | 11.7411 | 11.3189 | 10.9768 | 10.8074 | 12.9114 | 12.7851 | 12.5083 | 12.2967 | 11.9767 | 11.7567 | 11.6009 | 11.4346 | 11.2978 | 11.2336 | 10.8241 | 10.4936 | 10.3293
| FORT WILLIAM | KINGAIRLOCH | MINIMUM HEADROOM | NM 76917 56652 | YES | NO | 0 | 0.12 | 0.11895 | 0.11789 | 0.11684 | 0.11474 | 0.11263 | 0.11158 | 0.10842 | 0.10737 | 0.10526 | 0.095789 | 0.085263 | 0.074737 | 0.11263 | 0.11263 | 0.11263 | 0.11158 | 0.11053 | 0.10947 | 0.10632 | 0.10316 | 0.10211 | 0.098947 | 0.090526 | 0.078947 | 0.067368 | 0.11053 | 0.10947 | 0.10737 | 0.10526 | 0.10316 | 0.1 | 0.097895 | 0.093684 | 0.091579 | 0.088421 | 0.078947 | 0.066316 | 0.054737
|  | KINGAIRLOCH | EE |  |  |  |  | 0.12 | 0.11895 | 0.11789 | 0.11684 | 0.11474 | 0.11263 | 0.11158 | 0.10842 | 0.10737 | 0.10526 | 0.095789 | 0.085263 | 0.074737 | 0.11263 | 0.11263 | 0.11263 | 0.11158 | 0.11053 | 0.10947 | 0.10632 | 0.10316 | 0.10211 | 0.098947 | 0.090526 | 0.078947 | 0.067368 | 0.11053 | 0.10947 | 0.10737 | 0.10526 | 0.10316 | 0.1 | 0.097895 | 0.093684 | 0.091579 | 0.088421 | 0.078947 | 0.066316 | 0.054737
|  | KINGAIRLOCH | HT |  |  |  |  | 0.12105 | 0.12 | 0.12 | 0.12 | 0.11895 | 0.11789 | 0.11789 | 0.11789 | 0.11684 | 0.11579 | 0.11053 | 0.10316 | 0.097895 | 0.11368 | 0.11368 | 0.11368 | 0.11263 | 0.11263 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.10632 | 0.097895 | 0.092632 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.10947 | 0.10737 | 0.10737 | 0.10526 | 0.10316 | 0.10105 | 0.095789 | 0.087368 | 0.081053
|  | KINGAIRLOCH | HE |  |  |  |  | 0.12105 | 0.12 | 0.12 | 0.12 | 0.11895 | 0.11895 | 0.11895 | 0.11789 | 0.11684 | 0.11684 | 0.11579 | 0.11368 | 0.11158 | 0.11368 | 0.11368 | 0.11368 | 0.11263 | 0.11263 | 0.11263 | 0.11263 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.10947 | 0.10737 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.10947 | 0.10947 | 0.10842 | 0.10737 | 0.10632 | 0.10632 | 0.10421 | 0.10105 | 0.097895
|  | KINGAIRLOCH | FB |  |  |  |  | 0.12105 | 0.12105 | 0.12105 | 0.12105 | 0.12105 | 0.12105 | 0.12105 | 0.12105 | 0.12 | 0.12 | 0.11895 | 0.11895 | 0.11789 | 0.11368 | 0.11368 | 0.11368 | 0.11368 | 0.11368 | 0.11368 | 0.11368 | 0.11368 | 0.11368 | 0.11368 | 0.11263 | 0.11158 | 0.11158 | 0.11263 | 0.11263 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.10842 | 0.10842
| DYCE | KINGSEAT | MINIMUM HEADROOM | NJ 89545 19709 | NO | YES | 1.0204 | 13.4711 | 13.2858 | 13.0637 | 12.7679 | 11.9479 | 11.0511 | 10.0795 | 9.8342 | 9.5995 | 9.5332 | 3.6816 | 3.4321 | 3.2374 | 12.5053 | 12.2905 | 12.0326 | 11.6884 | 10.7284 | 9.6768 | 8.5389 | 8.2558 | 7.9832 | 7.9084 | 2.7326 | 2.4505 | 2.2284 | 12.8834 | 12.6697 | 12.4118 | 12.0697 | 11.1118 | 10.0634 | 8.9287 | 8.6466 | 8.375 | 8.3013 | 2.1497 | 1.8676 | 1.6466
|  | KINGSEAT | EE |  |  |  |  | 13.4711 | 13.2858 | 13.1195 | 12.8837 | 12.0732 | 11.0511 | 10.0795 | 9.8342 | 9.5995 | 9.5332 | 3.6816 | 3.4321 | 3.2374 | 12.5053 | 12.2905 | 12.0979 | 11.8242 | 10.8737 | 9.6768 | 8.5389 | 8.2558 | 7.9832 | 7.9084 | 2.7326 | 2.4505 | 2.2284 | 12.8834 | 12.6697 | 12.4782 | 12.2045 | 11.2571 | 10.0634 | 8.9287 | 8.6466 | 8.375 | 8.3013 | 2.1497 | 1.8676 | 1.6466
|  | KINGSEAT | HT |  |  |  |  | 13.4858 | 13.2984 | 13.0637 | 12.7679 | 11.9479 | 11.7058 | 11.4942 | 11.2868 | 10.6426 | 9.6984 | 4.4426 | 4.1721 | 3.9826 | 12.5211 | 12.3053 | 12.0326 | 11.6884 | 10.7284 | 10.4484 | 10.2053 | 9.9663 | 9.2126 | 8.1063 | 3.3811 | 3.0516 | 2.7821 | 12.9003 | 12.6845 | 12.4118 | 12.0697 | 11.1118 | 10.8329 | 10.5908 | 10.3518 | 9.6003 | 8.4971 | 2.9897 | 2.6603 | 2.3897
|  | KINGSEAT | HE |  |  |  |  | 13.5363 | 13.3763 | 13.2058 | 12.9637 | 12.1742 | 11.2153 | 10.2468 | 10.0321 | 9.8058 | 9.7637 | 6.5047 | 6.3805 | 6.2637 | 12.58 | 12.3947 | 12.1968 | 11.9147 | 10.9895 | 9.8653 | 8.7316 | 8.4821 | 8.2189 | 8.1716 | 5.0242 | 4.8832 | 4.7495 | 12.9582 | 12.7739 | 12.5761 | 12.295 | 11.3718 | 10.2518 | 9.1213 | 8.8729 | 8.6097 | 8.5634 | 5.0255 | 4.8855 | 4.7518
|  | KINGSEAT | FB |  |  |  |  | 13.6195 | 13.5542 | 13.4784 | 13.39 | 13.2374 | 12.9142 | 12.47 | 11.8868 | 11.7216 | 11.6795 | 11.1574 | 10.5489 | 10.4342 | 12.6758 | 12.6 | 12.5116 | 12.4095 | 12.2316 | 11.8526 | 11.3316 | 10.6463 | 10.4526 | 10.4053 | 9.7989 | 9.0884 | 8.9568 | 13.0539 | 12.9792 | 12.8908 | 12.7887 | 12.6108 | 12.2329 | 11.7139 | 11.0308 | 10.8382 | 10.7908 | 10.1855 | 9.4771 | 9.3466
| BOAT OF GARTEN | KINGUSSIE | MINIMUM HEADROOM | NH 75429 00426 | NO | YES | 0.016327 | 7.5068 | 7.3795 | 7.2721 | 7.1668 | 7.0889 | 7.0016 | 6.8753 | 6.7647 | 6.6542 | 6.5921 | 5.2532 | 4.7816 | 4.6121 | 6.5211 | 6.3274 | 6.1958 | 6.0705 | 5.9789 | 5.88 | 5.7316 | 5.6 | 5.4684 | 5.3979 | 5.0842 | 3.8284 | 3.6295 | 6.8687 | 6.6761 | 6.5455 | 6.4213 | 6.3297 | 6.2297 | 6.0834 | 5.9518 | 5.8203 | 5.7497 | 5.4413 | 3.8813 | 3.6813
|  | KINGUSSIE | EE |  |  |  |  | 7.5068 | 7.3795 | 7.2721 | 7.1668 | 7.0889 | 7.0016 | 6.8753 | 6.7647 | 6.6542 | 6.5921 | 6.3174 | 4.7816 | 4.6121 | 6.5211 | 6.3274 | 6.1958 | 6.0705 | 5.9789 | 5.88 | 5.7316 | 5.6 | 5.4684 | 5.3979 | 5.0842 | 3.8284 | 3.6295 | 6.8687 | 6.6761 | 6.5455 | 6.4213 | 6.3297 | 6.2297 | 6.0834 | 5.9518 | 5.8203 | 5.7497 | 5.4413 | 3.8813 | 3.6813
|  | KINGUSSIE | HT |  |  |  |  | 7.5216 | 7.4026 | 7.3037 | 7.2111 | 7.1279 | 7.0216 | 6.9132 | 6.8058 | 6.7016 | 6.6437 | 5.2532 | 5.0184 | 4.8532 | 6.5432 | 6.3579 | 6.2326 | 6.1242 | 6.0274 | 5.9011 | 5.7726 | 5.6442 | 5.5221 | 5.4642 | 5.1295 | 4.0453 | 3.7979 | 6.8866 | 6.7076 | 6.5855 | 6.4761 | 6.3813 | 6.255 | 6.1276 | 6.0003 | 5.8803 | 5.8276 | 5.4939 | 4.1708 | 3.9255
|  | KINGUSSIE | HE |  |  |  |  | 7.5553 | 7.4458 | 7.3805 | 7.3121 | 7.2595 | 7.19 | 7.0984 | 7.0163 | 6.9342 | 6.9005 | 6.7416 | 6.0647 | 5.9742 | 6.5937 | 6.4253 | 6.3263 | 6.2463 | 6.1874 | 6.1105 | 6.0021 | 5.9053 | 5.8084 | 5.7684 | 5.5863 | 4.9979 | 4.8905 | 6.9276 | 6.775 | 6.6782 | 6.5982 | 6.5392 | 6.4613 | 6.3539 | 6.2582 | 6.1624 | 6.1213 | 5.9466 | 5.2329 | 5.1255
|  | KINGUSSIE | FB |  |  |  |  | 7.6037 | 7.5532 | 7.51 | 7.4805 | 7.4542 | 7.43 | 7.3889 | 7.3437 | 7.2911 | 7.2521 | 7.0658 | 6.9142 | 6.8016 | 6.6642 | 6.5842 | 6.5189 | 6.4747 | 6.4389 | 6.4032 | 6.3421 | 6.2832 | 6.2189 | 6.1716 | 5.9474 | 5.7674 | 5.6295 | 6.9866 | 6.9234 | 6.8676 | 6.8234 | 6.7876 | 6.7529 | 6.6918 | 6.6339 | 6.5708 | 6.5245 | 6.3034 | 6.1234 | 5.9876
| TAYNUILT | KINLOCH | MINIMUM HEADROOM | NM 52465 27215 | YES | YES | 0 | 0.95474 | 0.89368 | 0.85158 | 0.82105 | 0.79368 | 0.76421 | 0.73368 | 0.70737 | 0.68211 | 0.65789 | 0.56632 | 0.47895 | 0.41368 | 0.90211 | 0.83263 | 0.78316 | 0.74842 | 0.71789 | 0.68526 | 0.65053 | 0.62211 | 0.59368 | 0.56632 | 0.46316 | 0.36421 | 0.28842 | -2.0453 | -2.0516 | -2.0568 | -2.0653 | -2.0737 | -2.0821 | -2.0916 | -2.0989 | -2.1074 | -2.1179 | -2.1463 | -2.1674 | -2.1853
|  | KINLOCH | EE |  |  |  |  | 0.95474 | 0.93474 | 0.85158 | 0.82105 | 0.79368 | 0.76421 | 0.73368 | 0.70737 | 0.68211 | 0.65789 | 0.56632 | 0.47895 | 0.41368 | 0.90211 | 0.88 | 0.78316 | 0.74842 | 0.71789 | 0.68526 | 0.65053 | 0.62211 | 0.59368 | 0.56632 | 0.46316 | 0.36421 | 0.28842 | -2.0453 | -2.0516 | -2.0568 | -2.0632 | -2.0705 | -2.08 | -2.0916 | -2.0989 | -2.1063 | -2.1126 | -2.14 | -2.1589 | -2.1705
|  | KINLOCH | HT |  |  |  |  | 0.96 | 0.89368 | 0.87789 | 0.85263 | 0.82526 | 0.79789 | 0.77158 | 0.74421 | 0.71895 | 0.69053 | 0.57789 | 0.49263 | 0.43474 | 0.90842 | 0.83263 | 0.81368 | 0.78632 | 0.75579 | 0.72526 | 0.69474 | 0.66421 | 0.63579 | 0.60526 | 0.50211 | 0.4 | 0.31579 | -2.0442 | -2.0505 | -2.0568 | -2.0653 | -2.0737 | -2.0821 | -2.0905 | -2.0989 | -2.1074 | -2.1179 | -2.1463 | -2.1674 | -2.1853
|  | KINLOCH | HE |  |  |  |  | 0.97368 | 0.96105 | 0.88737 | 0.87684 | 0.86421 | 0.84947 | 0.83368 | 0.82 | 0.80526 | 0.78947 | 0.74105 | 0.69474 | 0.66211 | 0.92316 | 0.91053 | 0.82526 | 0.81263 | 0.79895 | 0.78316 | 0.76737 | 0.75263 | 0.73474 | 0.71789 | 0.66316 | 0.60947 | 0.57263 | -2.0411 | -2.0474 | -2.0516 | -2.0568 | -2.0642 | -2.0737 | -2.0842 | -2.0895 | -2.0947 | -2.0989 | -2.1116 | -2.12 | -2.1253
|  | KINLOCH | FB |  |  |  |  | 0.98105 | 0.97263 | 0.96421 | 0.93053 | 0.92211 | 0.91263 | 0.90421 | 0.89579 | 0.88421 | 0.86947 | 0.81368 | 0.75579 | 0.70947 | 0.92842 | 0.92211 | 0.91368 | 0.87368 | 0.86421 | 0.85368 | 0.84526 | 0.83579 | 0.82211 | 0.80526 | 0.74211 | 0.67579 | 0.62211 | -2.0379 | -2.0411 | -2.0432 | -2.0453 | -2.0484 | -2.0516 | -2.0547 | -2.0579 | -2.0611 | -2.0642 | -2.0768 | -2.0874 | -2.0926
| TUMMEL BRIDGE | KINLOCH RANNOCH | MINIMUM HEADROOM | NN 65927 58500 | YES | YES | 0 | 0.98421 | 0.96737 | 0.95158 | 0.93474 | 0.91263 | 0.88947 | 0.86632 | 0.84526 | 0.82211 | 0.8 | 0.72105 | 0.63579 | 0.56211 | 0.97895 | 0.96211 | 0.94421 | 0.92 | 0.89368 | 0.87053 | 0.84632 | 0.82421 | 0.80105 | 0.77789 | 0.69789 | 0.61158 | 0.53579 | 0.97579 | 0.95684 | 0.93895 | 0.91158 | 0.88211 | 0.85474 | 0.82842 | 0.80421 | 0.77895 | 0.75368 | 0.66316 | 0.56737 | 0.48211
|  | KINLOCH RANNOCH | EE |  |  |  |  | 0.98421 | 0.96737 | 0.95158 | 0.93474 | 0.91263 | 0.88947 | 0.86632 | 0.84526 | 0.82211 | 0.8 | 0.72105 | 0.63579 | 0.56211 | 0.97895 | 0.96211 | 0.94421 | 0.92 | 0.89368 | 0.87053 | 0.84632 | 0.82421 | 0.80105 | 0.77789 | 0.69789 | 0.61158 | 0.53579 | 0.97579 | 0.95684 | 0.93895 | 0.91158 | 0.88211 | 0.85474 | 0.82842 | 0.80421 | 0.77895 | 0.75368 | 0.66316 | 0.56737 | 0.48211
|  | KINLOCH RANNOCH | HT |  |  |  |  | 0.99053 | 0.98526 | 0.97789 | 0.96842 | 0.95368 | 0.94105 | 0.92737 | 0.91158 | 0.89474 | 0.88 | 0.80947 | 0.75053 | 0.70737 | 0.98632 | 0.98 | 0.97263 | 0.96 | 0.94211 | 0.92632 | 0.90842 | 0.89263 | 0.87579 | 0.86 | 0.8 | 0.73789 | 0.68421 | 0.98421 | 0.97684 | 0.96842 | 0.95579 | 0.93579 | 0.91684 | 0.89789 | 0.88105 | 0.86211 | 0.84421 | 0.77895 | 0.70947 | 0.64842
|  | KINLOCH RANNOCH | HE |  |  |  |  | 0.99474 | 0.98842 | 0.98316 | 0.97684 | 0.97053 | 0.96316 | 0.95684 | 0.94842 | 0.94211 | 0.93368 | 0.90211 | 0.86211 | 0.82842 | 0.99263 | 0.98526 | 0.98 | 0.97368 | 0.96526 | 0.95789 | 0.95053 | 0.94 | 0.93053 | 0.92 | 0.88421 | 0.84526 | 0.81053 | 0.99053 | 0.98316 | 0.97579 | 0.96947 | 0.96105 | 0.95263 | 0.94526 | 0.93368 | 0.92316 | 0.91158 | 0.87053 | 0.82632 | 0.78632
|  | KINLOCH RANNOCH | FB |  |  |  |  | 0.99895 | 0.99579 | 0.99368 | 0.99053 | 0.98842 | 0.98526 | 0.98211 | 0.98 | 0.97579 | 0.97053 | 0.94632 | 0.91474 | 0.88737 | 0.99684 | 0.99368 | 0.98947 | 0.98632 | 0.98421 | 0.98105 | 0.97684 | 0.97368 | 0.96737 | 0.95895 | 0.92526 | 0.88947 | 0.85895 | 0.99474 | 0.99053 | 0.98842 | 0.98421 | 0.98105 | 0.97789 | 0.97263 | 0.97053 | 0.96421 | 0.95579 | 0.92 | 0.88316 | 0.85158
| GRUDIE BRIDGE | KINLOCHEWE | MINIMUM HEADROOM | NH 03723 62321 | YES | NO | 0 | 1.0516 | 1.0389 | 1.0211 | 1 | 0.97895 | 0.95895 | 0.93895 | 0.91895 | 0.90105 | 0.88 | 0.81368 | 0.74737 | 0.69053 | 1.0084 | 0.99158 | 0.97474 | 0.95579 | 0.93579 | 0.91789 | 0.89895 | 0.88105 | 0.86421 | 0.84632 | 0.78737 | 0.72842 | 0.67895 | 0.96947 | 0.94842 | 0.92842 | 0.90526 | 0.88105 | 0.85895 | 0.83684 | 0.81368 | 0.79263 | 0.77158 | 0.69684 | 0.62211 | 0.55895
|  | KINLOCHEWE | EE |  |  |  |  | 1.0516 | 1.0389 | 1.0211 | 1 | 0.97895 | 0.95895 | 0.93895 | 0.91895 | 0.90105 | 0.88 | 0.81368 | 0.74737 | 0.69053 | 1.0084 | 0.99158 | 0.97474 | 0.95579 | 0.93579 | 0.91789 | 0.89895 | 0.88105 | 0.86421 | 0.84632 | 0.78737 | 0.72842 | 0.67895 | 0.96947 | 0.94842 | 0.92842 | 0.90526 | 0.88105 | 0.85895 | 0.83684 | 0.81368 | 0.79263 | 0.77158 | 0.69684 | 0.62211 | 0.55895
|  | KINLOCHEWE | HT |  |  |  |  | 1.0558 | 1.0505 | 1.0432 | 1.0284 | 1.0126 | 0.99895 | 0.98526 | 0.96947 | 0.95684 | 0.94105 | 0.88105 | 0.83368 | 0.8 | 1.0137 | 1.0011 | 0.99053 | 0.97684 | 0.96105 | 0.94526 | 0.93158 | 0.91579 | 0.90211 | 0.88737 | 0.83579 | 0.78526 | 0.74421 | 0.97789 | 0.96421 | 0.95263 | 0.93684 | 0.92 | 0.90421 | 0.88842 | 0.87158 | 0.85684 | 0.84 | 0.78526 | 0.72737 | 0.68105
|  | KINLOCHEWE | HE |  |  |  |  | 1.0568 | 1.0526 | 1.0484 | 1.0421 | 1.0358 | 1.0295 | 1.0179 | 1.0095 | 0.99895 | 0.99263 | 0.96 | 0.93053 | 0.90421 | 1.0179 | 1.0126 | 1.0053 | 0.99684 | 0.98842 | 0.98105 | 0.96947 | 0.96105 | 0.95158 | 0.94526 | 0.91263 | 0.88632 | 0.86211 | 0.98526 | 0.97579 | 0.96737 | 0.95684 | 0.94737 | 0.93895 | 0.92632 | 0.91684 | 0.90632 | 0.89789 | 0.86105 | 0.82842 | 0.79895
|  | KINLOCHEWE | FB |  |  |  |  | 1.0611 | 1.0589 | 1.0579 | 1.0558 | 1.0537 | 1.0516 | 1.0495 | 1.0453 | 1.0411 | 1.0326 | 1.0074 | 0.98 | 0.96 | 1.0211 | 1.02 | 1.0179 | 1.0126 | 1.0063 | 1.0021 | 0.99789 | 0.99263 | 0.98632 | 0.97895 | 0.94947 | 0.92105 | 0.89789 | 0.99158 | 0.98632 | 0.98211 | 0.97684 | 0.97053 | 0.96526 | 0.96105 | 0.95579 | 0.94947 | 0.94211 | 0.91158 | 0.88105 | 0.85789
| KINLOCHLEVEN | KINLOCHLEVEN | MINIMUM HEADROOM | NN 19285 62002 | NO | YES | 0 | 0.82316 | 0.74947 | 0.67368 | 0.58526 | 0.49474 | 0.36947 | 0.10737 | -0.095789 | -0.35368 | -0.56211 | -0.93895 | -1.2411 | -1.5274 | -5.5253 | -5.6116 | -5.6989 | -5.7905 | -5.8863 | -6.0032 | -6.2979 | -6.5242 | -6.7358 | -6.9379 | -7.3326 | -7.6642 | -7.9832 | -3.84 | -3.9284 | -4.0168 | -4.1116 | -4.2095 | -4.3884 | -4.6853 | -4.9137 | -5.2074 | -5.4421 | -5.8674 | -6.2032 | -6.5232
|  | KINLOCHLEVEN | EE |  |  |  |  | 0.82316 | 0.74947 | 0.67368 | 0.58526 | 0.49474 | 0.41158 | 0.32842 | -0.045263 | -0.35368 | -0.56211 | -0.93895 | -1.2411 | -1.5274 | -5.5253 | -5.6116 | -5.6989 | -5.7905 | -5.8863 | -5.9737 | -6.06 | -6.4463 | -6.7358 | -6.9379 | -7.3326 | -7.6642 | -7.9832 | -3.84 | -3.9284 | -4.0168 | -4.1116 | -4.2095 | -4.2989 | -4.3874 | -4.8579 | -5.2074 | -5.4421 | -5.8674 | -6.2032 | -6.5232
|  | KINLOCHLEVEN | HT |  |  |  |  | 0.86316 | 0.84105 | 0.81579 | 0.78632 | 0.75368 | 0.36947 | 0.10737 | -0.095789 | -0.17684 | -0.21474 | -0.39579 | -0.55895 | -0.68421 | -5.4747 | -5.5105 | -5.5453 | -5.5821 | -5.6232 | -6.0032 | -6.2979 | -6.5242 | -6.6074 | -6.64 | -6.7674 | -6.9042 | -7.0326 | -3.7895 | -3.8274 | -3.8642 | -3.9032 | -3.9474 | -4.3884 | -4.6853 | -4.9137 | -5.0053 | -5.0453 | -5.2095 | -5.3947 | -5.5705
|  | KINLOCHLEVEN | HE |  |  |  |  | 0.86526 | 0.84632 | 0.82211 | 0.79579 | 0.76842 | 0.73895 | 0.70947 | 0.32842 | 0.056842 | -0.094737 | -0.25789 | -0.38526 | -0.49789 | -5.4632 | -5.4958 | -5.5253 | -5.5568 | -5.5905 | -5.6253 | -5.6589 | -6.0295 | -6.3347 | -6.5021 | -6.6516 | -6.7463 | -6.8358 | -3.7758 | -3.8084 | -3.84 | -3.8716 | -3.9074 | -3.9421 | -3.9768 | -4.4337 | -4.7411 | -4.9126 | -5.0968 | -5.24 | -5.3674
|  | KINLOCHLEVEN | FB |  |  |  |  | 0.87789 | 0.87263 | 0.86737 | 0.86105 | 0.85579 | 0.84947 | 0.84105 | 0.83474 | 0.67263 | 0.56 | 0.28737 | 0.23263 | 0.18947 | -5.4421 | -5.4547 | -5.4663 | -5.4789 | -5.4926 | -5.5042 | -5.5179 | -5.5263 | -5.6905 | -5.82 | -6.1284 | -6.1832 | -6.2253 | -3.7537 | -3.7674 | -3.78 | -3.7937 | -3.8095 | -3.8232 | -3.8368 | -3.8484 | -4.0484 | -4.1758 | -4.4821 | -4.5432 | -4.5916
| FORT WILLIAM | KINLOCHMOIDART | MINIMUM HEADROOM | NM 71407 72091 | YES | NO | 0 | 1.0021 | 0.98316 | 0.96211 | 0.94105 | 0.91895 | 0.9 | 0.88105 | 0.86105 | 0.84 | 0.81789 | 0.74632 | 0.66526 | 0.58421 | 1.0011 | 0.98211 | 0.96211 | 0.94105 | 0.92105 | 0.90211 | 0.88316 | 0.86421 | 0.84421 | 0.82316 | 0.75474 | 0.67684 | 0.6 | 0.99789 | 0.98 | 0.95789 | 0.93684 | 0.91579 | 0.89579 | 0.87684 | 0.85684 | 0.83579 | 0.81368 | 0.74105 | 0.65895 | 0.57789
|  | KINLOCHMOIDART | EE |  |  |  |  | 1.0021 | 0.98316 | 0.96211 | 0.94105 | 0.91895 | 0.9 | 0.88105 | 0.86105 | 0.84 | 0.81789 | 0.74632 | 0.66526 | 0.58421 | 1.0011 | 0.98211 | 0.96211 | 0.94105 | 0.92105 | 0.90211 | 0.88316 | 0.86421 | 0.84421 | 0.82316 | 0.75474 | 0.67684 | 0.6 | 0.99789 | 0.98 | 0.95789 | 0.93684 | 0.91579 | 0.89579 | 0.87684 | 0.85684 | 0.83579 | 0.81368 | 0.74105 | 0.65895 | 0.57789
|  | KINLOCHMOIDART | HT |  |  |  |  | 1.0147 | 1.0105 | 1.0042 | 0.99789 | 0.99263 | 0.98632 | 0.98 | 0.97368 | 0.96737 | 0.96105 | 0.93053 | 0.9 | 0.87474 | 1.0105 | 1.0084 | 1.0021 | 0.99579 | 0.99053 | 0.98526 | 0.98 | 0.97263 | 0.96632 | 0.96 | 0.93684 | 0.90737 | 0.87684 | 1.0105 | 1.0053 | 0.99895 | 0.99263 | 0.98737 | 0.98105 | 0.97579 | 0.96947 | 0.96316 | 0.95789 | 0.93263 | 0.90211 | 0.87053
|  | KINLOCHMOIDART | HE |  |  |  |  | 1.0147 | 1.0105 | 1.0053 | 0.99895 | 0.99263 | 0.98632 | 0.98 | 0.97368 | 0.96842 | 0.96211 | 0.93789 | 0.90737 | 0.87579 | 1.0105 | 1.0084 | 1.0032 | 0.99789 | 0.99158 | 0.98526 | 0.98 | 0.97368 | 0.96842 | 0.96211 | 0.93895 | 0.90842 | 0.87789 | 1.0105 | 1.0053 | 1 | 0.99474 | 0.98842 | 0.98211 | 0.97684 | 0.96947 | 0.96421 | 0.95895 | 0.93474 | 0.90316 | 0.87158
|  | KINLOCHMOIDART | FB |  |  |  |  | 1.0168 | 1.0158 | 1.0158 | 1.0147 | 1.0137 | 1.0137 | 1.0116 | 1.0116 | 1.0084 | 1.0074 | 1.0032 | 0.99789 | 0.99368 | 1.0126 | 1.0116 | 1.0116 | 1.0105 | 1.0105 | 1.0105 | 1.0095 | 1.0084 | 1.0053 | 1.0053 | 1.0011 | 0.99579 | 0.99158 | 1.0137 | 1.0126 | 1.0105 | 1.0095 | 1.0095 | 1.0074 | 1.0063 | 1.0063 | 1.0032 | 1.0021 | 0.99789 | 0.99263 | 0.98842
| ELGIN | KINLOSS | MINIMUM HEADROOM | NJ 06695 61740 | NO | YES | 2.1224 | 14.2553 | 14.1826 | 14.1068 | 14.0237 | 13.9511 | 13.8647 | 13.7795 | 13.7016 | 13.6374 | 13.5868 | 13.3679 | 13.17 | 13.0195 | 13.4632 | 13.3832 | 13.3011 | 13.2084 | 13.1295 | 13.0347 | 12.9421 | 12.8568 | 12.7884 | 12.7326 | 12.4937 | 12.2758 | 12.1084 | 13.8371 | 13.7561 | 13.6729 | 13.5782 | 13.4992 | 13.4024 | 13.3087 | 13.2234 | 13.1539 | 13.0971 | 12.855 | 12.635 | 12.4645
|  | KINLOSS | EE |  |  |  |  | 14.2553 | 14.1826 | 14.1068 | 14.0237 | 13.9511 | 13.8647 | 13.7795 | 13.7016 | 13.6374 | 13.5868 | 13.3679 | 13.17 | 13.0195 | 13.4632 | 13.3832 | 13.3011 | 13.2084 | 13.1295 | 13.0347 | 12.9421 | 12.8568 | 12.7884 | 12.7326 | 12.4937 | 12.2758 | 12.1084 | 13.8371 | 13.7561 | 13.6729 | 13.5782 | 13.4992 | 13.4024 | 13.3087 | 13.2234 | 13.1539 | 13.0971 | 12.855 | 12.635 | 12.4645
|  | KINLOSS | HT |  |  |  |  | 14.2784 | 14.2163 | 14.1511 | 14.0795 | 14.0226 | 13.9647 | 13.9037 | 13.8584 | 13.8111 | 13.7679 | 13.5668 | 13.4174 | 13.3037 | 13.4895 | 13.4189 | 13.3495 | 13.2705 | 13.2084 | 13.1442 | 13.0758 | 13.0253 | 12.9737 | 12.9253 | 12.7453 | 12.5684 | 12.4084 | 13.8634 | 13.7929 | 13.7224 | 13.6424 | 13.5792 | 13.515 | 13.4476 | 13.3961 | 13.3445 | 13.2961 | 13.115 | 12.9382 | 12.7782
|  | KINLOSS | HE |  |  |  |  | 14.3311 | 14.2984 | 14.2711 | 14.2384 | 14.2121 | 14.17 | 14.1258 | 14.1016 | 14.0721 | 14.0563 | 13.9805 | 13.9111 | 13.8689 | 13.5453 | 13.5105 | 13.4789 | 13.4432 | 13.4147 | 13.3674 | 13.3189 | 13.2916 | 13.26 | 13.2421 | 13.1568 | 13.0768 | 13.0295 | 13.9213 | 13.8855 | 13.855 | 13.8192 | 13.7908 | 13.7434 | 13.695 | 13.6687 | 13.6371 | 13.6182 | 13.5329 | 13.4539 | 13.4066
|  | KINLOSS | FB |  |  |  |  | 14.3479 | 14.3311 | 14.3132 | 14.2942 | 14.2763 | 14.2553 | 14.2332 | 14.2153 | 14.1974 | 14.1753 | 14.0911 | 14.0016 | 13.9395 | 13.5653 | 13.5453 | 13.5242 | 13.5032 | 13.4832 | 13.46 | 13.4337 | 13.4147 | 13.3947 | 13.3695 | 13.2737 | 13.1726 | 13.1021 | 13.9403 | 13.9213 | 13.9003 | 13.8792 | 13.8592 | 13.835 | 13.8097 | 13.7908 | 13.7708 | 13.7455 | 13.6508 | 13.5497 | 13.4792
| BRACO | KIPPEN | MINIMUM HEADROOM | NS 66376 95628 | NO | YES | 0 | 8.7547 | 8.6747 | 8.5811 | 8.4558 | 8.3158 | 8.1768 | 8.0263 | 7.88 | 7.7284 | 7.5726 | 7.5337 | 6.8937 | 6.3905 | 6.9484 | 6.8579 | 6.7495 | 6.6032 | 6.4421 | 6.2811 | 6.1074 | 5.9347 | 5.7579 | 5.5758 | 5.5589 | 4.7695 | 4.0379 | 7.3863 | 7.3 | 7.1968 | 7.0589 | 6.9063 | 6.7537 | 6.5895 | 6.4274 | 6.2621 | 6.0905 | 6.1642 | 5.3937 | 4.6737
|  | KIPPEN | EE |  |  |  |  | 8.7547 | 8.6747 | 8.5811 | 8.4695 | 8.3526 | 8.2253 | 8.0916 | 7.9747 | 7.8516 | 7.7295 | 7.9589 | 7.4305 | 6.9611 | 6.9484 | 6.8579 | 6.7495 | 6.6189 | 6.4842 | 6.3389 | 6.1853 | 6.0505 | 5.9074 | 5.7642 | 5.8874 | 5.2621 | 4.7032 | 7.3863 | 7.3 | 7.1968 | 7.0737 | 6.9463 | 6.8074 | 6.6621 | 6.5337 | 6.4 | 6.2653 | 6.4821 | 5.8737 | 5.3274
|  | KIPPEN | HT |  |  |  |  | 8.7674 | 8.6874 | 8.5811 | 8.4558 | 8.3158 | 8.1768 | 8.0263 | 7.88 | 7.7284 | 7.5726 | 7.5337 | 6.8937 | 6.3905 | 6.9642 | 6.8716 | 6.7495 | 6.6032 | 6.4421 | 6.2811 | 6.1074 | 5.9347 | 5.7579 | 5.5758 | 5.5589 | 4.7695 | 4.0379 | 7.4011 | 7.3126 | 7.1968 | 7.0589 | 6.9063 | 6.7537 | 6.5895 | 6.4274 | 6.2621 | 6.0905 | 6.1642 | 5.3937 | 4.6737
|  | KIPPEN | HE |  |  |  |  | 8.8105 | 8.7505 | 8.6811 | 8.5916 | 8.4905 | 8.3821 | 8.2684 | 8.1695 | 8.0653 | 7.9632 | 8.2695 | 7.8126 | 7.3979 | 7.0126 | 6.9453 | 6.8642 | 6.7621 | 6.6463 | 6.5221 | 6.3926 | 6.2768 | 6.1579 | 6.0368 | 6.2442 | 5.6989 | 5.2032 | 7.4474 | 7.3821 | 7.3063 | 7.2084 | 7.0989 | 6.9811 | 6.8579 | 6.7484 | 6.6347 | 6.5221 | 6.82 | 6.3032 | 5.8189
|  | KIPPEN | FB |  |  |  |  | 8.8358 | 8.8042 | 8.7653 | 8.7211 | 8.6758 | 8.6263 | 8.5705 | 8.5158 | 8.4558 | 8.3863 | 8.8232 | 8.5137 | 8.2389 | 7.0411 | 7.0053 | 6.96 | 6.9095 | 6.8558 | 6.7989 | 6.7347 | 6.6705 | 6.6011 | 6.52 | 6.8895 | 6.5221 | 6.1937 | 7.4747 | 7.44 | 7.3968 | 7.3495 | 7.2989 | 7.2453 | 7.1842 | 7.1232 | 7.0568 | 6.9811 | 7.4253 | 7.0832 | 6.7779
| THURSO | KIRKWALL | MINIMUM HEADROOM | HY 44669 10987 | NO | YES | 7.6531 | 15.1211 | 14.0842 | 13.1558 | 11.0632 | 10.5011 | 10.2211 | 9.7653 | 9.0011 | 7.4874 | 6.0968 | -0.82526 | -1.5832 | -2.14 | 13.3189 | 12.1084 | 11.0232 | 8.5653 | 7.9168 | 7.6063 | 7.0842 | 6.1989 | 4.4305 | 2.8084 | -3.7326 | -4.6411 | -5.44 | 13.4063 | 12.3589 | 11.4095 | 8.9505 | 8.3032 | 7.9926 | 7.4695 | 6.5832 | 4.8147 | 3.1937 | -4.1516 | -5.06 | -5.8589
|  | KIRKWALL | EE |  |  |  |  | 15.1211 | 14.0842 | 13.1558 | 11.0632 | 10.5011 | 10.2211 | 9.8737 | 9.4663 | 8.9495 | 19.0021 | 8.7989 | 7.9484 | 7.3747 | 13.3189 | 12.1084 | 11.0232 | 8.5653 | 7.9168 | 7.6063 | 7.2158 | 6.7505 | 6.1558 | 18.8326 | 8.5116 | 7.5537 | 6.8979 | 13.4063 | 12.3589 | 11.4095 | 8.9505 | 8.3032 | 7.9926 | 7.6021 | 7.1368 | 6.5411 | 17.9926 | 6.6579 | 5.7084 | 5.0526
|  | KIRKWALL | HT |  |  |  |  | 15.1284 | 14.2621 | 13.2989 | 11.2337 | 10.6663 | 10.3979 | 9.7653 | 9.0011 | 7.4874 | 6.0968 | -0.82526 | -1.5832 | -2.14 | 13.3253 | 12.3147 | 11.1926 | 8.7684 | 8.1147 | 7.8137 | 7.0842 | 6.1989 | 4.4305 | 2.8084 | -3.7326 | -4.6411 | -5.44 | 13.4137 | 12.5379 | 11.5663 | 9.1547 | 8.5 | 8.1989 | 7.4695 | 6.5832 | 4.8147 | 3.1937 | -4.1516 | -5.06 | -5.8589
|  | KIRKWALL | HE |  |  |  |  | 15.2295 | 14.4611 | 13.6137 | 11.6242 | 11.1442 | 10.9505 | 10.6821 | 10.36 | 9.9179 | 9.7789 | 2.2274 | 1.7811 | 1.4411 | 13.44 | 12.5453 | 11.5526 | 9.2179 | 8.6653 | 8.4547 | 8.1579 | 7.7895 | 7.2779 | 7.12 | -1.0989 | -1.6074 | -1.9979 | 13.5158 | 12.74 | 11.8832 | 9.6042 | 9.0516 | 8.8411 | 8.5442 | 8.1758 | 7.6642 | 7.5063 | -1.12 | -1.6295 | -2.02
|  | KIRKWALL | FB |  |  |  |  | 15.8558 | 15.6442 | 15.3768 | 14.9747 | 14.4863 | 14.1221 | 13.8358 | 13.5558 | 13.3884 | 13.2516 | 11.1495 | 8.7168 | 8.3263 | 14.42 | 14.0789 | 13.6421 | 13.1474 | 12.5768 | 12.1526 | 11.8211 | 11.4968 | 11.3063 | 11.1505 | 8.6958 | 5.8474 | 5.3968 | 14.36 | 14.0642 | 13.6863 | 13.2579 | 12.7653 | 12.3968 | 12.1084 | 11.8253 | 11.6568 | 11.5179 | 9.0832 | 6.2326 | 5.7821
| BROADFORD | KISHORNHILL | MINIMUM HEADROOM | NG 88304 40591 | YES | YES | 0 | 0.99579 | 0.99263 | 0.58632 | 0.58421 | 0.58316 | 0.58105 | 0.57789 | 0.51474 | 0.40526 | 0.32842 | 0.28632 | 0.27368 | 0.26421 | 1.0568 | 1.0558 | 0.77158 | 0.76842 | 0.76632 | 0.76316 | 0.75895 | 0.65684 | 0.56 | 0.49158 | 0.45474 | 0.44316 | 0.43368 | 0.99158 | 0.98737 | 0.54842 | 0.54526 | 0.54211 | 0.53895 | 0.53368 | 0.39263 | 0.26737 | 0.17895 | 0.13158 | 0.11684 | 0.10632
|  | KISHORNHILL | EE |  |  |  |  | 0.99579 | 0.99263 | 0.58632 | 0.58421 | 0.58316 | 0.58105 | 0.57789 | 0.51474 | 0.40526 | 0.32842 | 0.28632 | 0.27368 | 0.26421 | 1.0568 | 1.0558 | 0.77158 | 0.76842 | 0.76632 | 0.76316 | 0.75895 | 0.65684 | 0.56 | 0.49158 | 0.45474 | 0.44316 | 0.43368 | 0.99158 | 0.98737 | 0.54842 | 0.54526 | 0.54211 | 0.53895 | 0.53368 | 0.39263 | 0.26737 | 0.17895 | 0.13158 | 0.11684 | 0.10632
|  | KISHORNHILL | HT |  |  |  |  | 0.99579 | 0.99368 | 0.99158 | 0.98842 | 0.98632 | 0.85579 | 0.74737 | 0.67474 | 0.64316 | 0.63789 | 0.62 | 0.60632 | 0.59895 | 1.0568 | 1.0558 | 1.0547 | 1.0526 | 1.0516 | 0.93684 | 0.81053 | 0.72421 | 0.68737 | 0.68211 | 0.66526 | 0.65158 | 0.63895 | 0.99263 | 0.98842 | 0.98526 | 0.98 | 0.97579 | 0.76947 | 0.64737 | 0.56316 | 0.52737 | 0.52211 | 0.50632 | 0.49158 | 0.48
|  | KISHORNHILL | HE |  |  |  |  | 0.99789 | 0.99474 | 0.99368 | 0.99158 | 0.99053 | 0.98737 | 0.98526 | 0.84842 | 0.73474 | 0.66316 | 0.65053 | 0.64211 | 0.63579 | 1.0579 | 1.0558 | 1.0547 | 1.0537 | 1.0526 | 1.0505 | 1.0484 | 0.92947 | 0.79474 | 0.71158 | 0.69684 | 0.68737 | 0.68 | 0.99579 | 0.99263 | 0.99053 | 0.98737 | 0.98526 | 0.98211 | 0.97895 | 0.76211 | 0.63158 | 0.55053 | 0.53579 | 0.52737 | 0.52
|  | KISHORNHILL | FB |  |  |  |  | 0.99789 | 0.99789 | 0.99579 | 0.99579 | 0.99368 | 0.99368 | 0.99158 | 0.99158 | 0.95579 | 0.90632 | 0.80632 | 0.79579 | 0.78842 | 1.0579 | 1.0579 | 1.0568 | 1.0568 | 1.0558 | 1.0558 | 1.0547 | 1.0547 | 1.0537 | 0.99684 | 0.87789 | 0.86737 | 0.85789 | 0.99684 | 0.99579 | 0.99368 | 0.99263 | 0.98947 | 0.98842 | 0.98632 | 0.98526 | 0.89368 | 0.82842 | 0.71263 | 0.70211 | 0.69263
| BROADFORD | KYLE | MINIMUM HEADROOM | NG 76499 27247 | NO | YES | 0 | 5.9063 | 7.1979 | 7.1916 | 7.1811 | 7.1484 | 6.5716 | 5.9358 | 5.1242 | 4.2937 | 3.7537 | 3.1937 | 3.0916 | 3.0179 | 4.9579 | 6.2305 | 6.2032 | 6.1663 | 6.1305 | 5.4495 | 4.6989 | 3.74 | 2.7589 | 2.1221 | 1.4684 | 1.3611 | 1.2674 | 5.2305 | 6.5221 | 6.5158 | 6.5053 | 6.4947 | 6.2484 | 5.5 | 4.5442 | 3.5663 | 2.9316 | 2.28 | 2.1726 | 2.0789
|  | KYLE | EE |  |  |  |  | 5.9063 | 7.1979 | 7.1916 | 7.1811 | 7.1484 | 7.1137 | 7.0789 | 6.5095 | 5.8684 | 5.0758 | 3.1958 | 3.1021 | 3.0368 | 4.9579 | 6.2305 | 6.2032 | 6.1663 | 6.1305 | 6.0916 | 6.0526 | 5.3811 | 4.6242 | 3.6874 | 1.4684 | 1.3611 | 1.2874 | 5.2305 | 6.5221 | 6.5158 | 6.5074 | 6.4968 | 6.4842 | 6.4705 | 6.18 | 5.4253 | 4.4916 | 2.28 | 2.1726 | 2.0989
|  | KYLE | HT |  |  |  |  | 5.9074 | 7.2 | 7.1916 | 7.1811 | 7.1663 | 6.5716 | 5.9358 | 5.1242 | 4.2937 | 3.7537 | 3.1937 | 3.0916 | 3.0179 | 4.9663 | 6.2432 | 6.2179 | 6.1884 | 6.1516 | 5.4495 | 4.6989 | 3.74 | 2.7589 | 2.1221 | 1.4968 | 1.3737 | 1.2674 | 5.2316 | 6.5242 | 6.5158 | 6.5053 | 6.4947 | 6.2484 | 5.5 | 4.5442 | 3.5663 | 2.9316 | 2.3074 | 2.1842 | 2.0789
|  | KYLE | HE |  |  |  |  | 5.9095 | 7.2021 | 7.1958 | 7.1874 | 7.1779 | 7.1663 | 7.1537 | 6.5642 | 5.8653 | 4.9653 | 3.3768 | 3.3253 | 3.2916 | 4.9853 | 6.2674 | 6.2516 | 6.2347 | 6.2137 | 6.1947 | 6.1747 | 5.4442 | 4.6179 | 3.5537 | 1.6758 | 1.6158 | 1.5779 | 5.2337 | 6.5263 | 6.52 | 6.5116 | 6.5021 | 6.4905 | 6.4779 | 6.2432 | 5.42 | 4.3579 | 2.4863 | 2.4274 | 2.3884
|  | KYLE | FB |  |  |  |  | 5.9147 | 7.2116 | 7.2084 | 7.2053 | 7.2011 | 7.1968 | 7.1937 | 7.1895 | 6.9463 | 6.6421 | 4.8737 | 4.7737 | 4.7263 | 4.9958 | 6.2832 | 6.2726 | 6.2611 | 6.2453 | 6.2326 | 6.2211 | 6.2095 | 5.8884 | 5.5295 | 3.4389 | 3.3232 | 3.2684 | 5.2389 | 6.5358 | 6.5326 | 6.5295 | 6.5253 | 6.5211 | 6.5179 | 6.5137 | 6.5095 | 6.3284 | 4.2442 | 4.1295 | 4.0747
| LAIRG | LAIRG | MINIMUM HEADROOM | NC 58798 07111 | YES | YES | 0 | 1.0874 | 1.0621 | 2.5389 | 2.5105 | 2.48 | 2.1537 | 1.94 | 1.7884 | 1.7137 | 1.6368 | 1.4084 | 1.3158 | 1.2516 | 0.80421 | 0.77789 | 2.2505 | 2.2179 | 2.1842 | 1.8011 | 1.5547 | 1.3811 | 1.2968 | 1.2095 | 0.96316 | 0.86737 | 0.77474 | 0.83789 | 0.81053 | 2.2832 | 2.2516 | 2.2189 | 1.8316 | 1.5821 | 1.4063 | 1.3211 | 1.2326 | 0.98421 | 0.88737 | 0.79474
|  | LAIRG | EE |  |  |  |  | 1.0874 | 1.0621 | 2.5389 | 2.5105 | 2.48 | 2.4484 | 2.4179 | 2.0926 | 1.8747 | 1.7095 | 1.4211 | 1.3368 | 1.28 | 0.80421 | 0.77789 | 2.2505 | 2.2179 | 2.1842 | 2.1495 | 2.1158 | 1.7347 | 1.4832 | 1.2926 | 0.96316 | 0.86947 | 0.80526 | 0.83789 | 0.81053 | 2.2832 | 2.2516 | 2.2189 | 2.1832 | 2.1495 | 1.7642 | 1.5095 | 1.3179 | 0.98421 | 0.89053 | 0.82526
|  | LAIRG | HT |  |  |  |  | 1.0937 | 1.0716 | 2.5495 | 2.5253 | 2.4947 | 2.1537 | 1.94 | 1.7884 | 1.7137 | 1.6368 | 1.4084 | 1.3158 | 1.2516 | 0.81263 | 0.78842 | 2.2642 | 2.2358 | 2.2021 | 1.8011 | 1.5547 | 1.3811 | 1.2968 | 1.2095 | 0.97579 | 0.86737 | 0.77474 | 0.84526 | 0.82105 | 2.2968 | 2.2695 | 2.2358 | 1.8316 | 1.5821 | 1.4063 | 1.3211 | 1.2326 | 0.99684 | 0.88737 | 0.79474
|  | LAIRG | HE |  |  |  |  | 1.1105 | 1.0937 | 2.58 | 2.5663 | 2.5453 | 2.5274 | 2.5095 | 2.1579 | 1.9379 | 1.7884 | 1.5821 | 1.5347 | 1.5074 | 0.83263 | 0.81368 | 2.2989 | 2.2832 | 2.2611 | 2.2411 | 2.2221 | 1.8084 | 1.5547 | 1.3811 | 1.1442 | 1.0916 | 1.0611 | 0.86526 | 0.84632 | 2.3316 | 2.3158 | 2.2937 | 2.2747 | 2.2558 | 1.8389 | 1.5821 | 1.4063 | 1.1674 | 1.1137 | 1.0821
|  | LAIRG | FB |  |  |  |  | 1.1211 | 1.1116 | 2.6021 | 2.5905 | 2.5789 | 2.5674 | 2.5568 | 2.5463 | 2.3968 | 2.2832 | 1.9632 | 1.9053 | 1.8663 | 0.84316 | 0.83263 | 2.3211 | 2.3095 | 2.2958 | 2.2832 | 2.2705 | 2.2589 | 2.0821 | 1.9474 | 1.5789 | 1.5137 | 1.4695 | 0.87579 | 0.86526 | 2.3537 | 2.3421 | 2.3284 | 2.3158 | 2.3042 | 2.2926 | 2.1147 | 1.9789 | 1.6063 | 1.5411 | 1.4958
| MYBSTER 1 | LATHERON | MINIMUM HEADROOM | ND 19924 33627 | YES | YES | 0.076531 | 2.7747 | 2.74 | 2.7074 | 2.6705 | 2.6316 | 2.4274 | 2.2874 | 2.1821 | 2.12 | 2.0821 | 1.9232 | 1.8116 | 1.7337 | 2.7326 | 2.6937 | 2.6568 | 2.6158 | 2.5726 | 2.3379 | 2.1758 | 2.0558 | 1.9863 | 1.9453 | 1.7874 | 1.6674 | 1.5579 | 2.7526 | 2.7137 | 2.6768 | 2.6358 | 2.5926 | 2.3568 | 2.1937 | 2.0737 | 2.0042 | 1.9632 | 1.8042 | 1.6842 | 1.5747
|  | LATHERON | EE |  |  |  |  | 2.7747 | 2.74 | 2.7074 | 2.6705 | 2.6316 | 2.5874 | 2.5484 | 2.3389 | 2.1958 | 2.0926 | 1.9421 | 1.8347 | 1.7505 | 2.7326 | 2.6937 | 2.6568 | 2.6158 | 2.5726 | 2.5242 | 2.4811 | 2.24 | 2.0747 | 1.9558 | 1.7874 | 1.6674 | 1.5726 | 2.7526 | 2.7137 | 2.6768 | 2.6358 | 2.5926 | 2.5442 | 2.5011 | 2.2579 | 2.0926 | 1.9726 | 1.8042 | 1.6842 | 1.5895
|  | LATHERON | HT |  |  |  |  | 2.7842 | 2.7526 | 2.7221 | 2.6884 | 2.6474 | 2.4274 | 2.2874 | 2.1821 | 2.12 | 2.0821 | 1.9232 | 1.8116 | 1.7337 | 2.7432 | 2.7084 | 2.6747 | 2.6379 | 2.5916 | 2.3379 | 2.1758 | 2.0558 | 1.9863 | 1.9453 | 1.8032 | 1.6674 | 1.5579 | 2.7642 | 2.7284 | 2.6947 | 2.6579 | 2.6116 | 2.3568 | 2.1937 | 2.0737 | 2.0042 | 1.9632 | 1.82 | 1.6842 | 1.5747
|  | LATHERON | HE |  |  |  |  | 2.8084 | 2.7863 | 2.7663 | 2.7432 | 2.7158 | 2.6895 | 2.6589 | 2.4442 | 2.3063 | 2.22 | 2.1421 | 2.0768 | 2.0284 | 2.7705 | 2.7463 | 2.7242 | 2.7 | 2.6695 | 2.6421 | 2.6095 | 2.36 | 2.2 | 2.1 | 2.0137 | 1.94 | 1.8842 | 2.7905 | 2.7663 | 2.7442 | 2.72 | 2.6895 | 2.6621 | 2.6295 | 2.3789 | 2.2189 | 2.1179 | 2.0316 | 1.9568 | 1.9011
|  | LATHERON | FB |  |  |  |  | 2.8221 | 2.8074 | 2.7926 | 2.7779 | 2.7611 | 2.7442 | 2.7284 | 2.7116 | 2.6137 | 2.5358 | 2.3684 | 2.2937 | 2.2347 | 2.7853 | 2.7684 | 2.7516 | 2.7358 | 2.7168 | 2.6979 | 2.68 | 2.6621 | 2.5484 | 2.4579 | 2.2663 | 2.1821 | 2.1147 | 2.8053 | 2.7895 | 2.7726 | 2.7568 | 2.7379 | 2.7189 | 2.7 | 2.6821 | 2.5684 | 2.4779 | 2.2853 | 2.2011 | 2.1326
| FIDDES | LAURENCEKIRK | MINIMUM HEADROOM | NO 70915 71028 | NO | YES | 0.17347 | 13.5679 | 13.3216 | 12.6847 | 12.3279 | 11.3889 | 10.2226 | 9.1605 | 8.8995 | 8.6153 | 8.4468 | 1.3005 | -2.0679 | -2.3353 | 11.9432 | 11.6674 | 10.9463 | 10.5453 | 9.4632 | 8.1063 | 6.8737 | 6.5737 | 6.2474 | 6.0611 | 0.75789 | -3.2274 | -3.5253 | 12.8761 | 12.5961 | 11.8624 | 11.455 | 10.3718 | 9.0266 | 7.8055 | 7.5087 | 7.1845 | 7.0013 | 1.0024 | -3.9418 | -4.2408
|  | LAURENCEKIRK | EE |  |  |  |  | 13.5679 | 13.3247 | 12.7205 | 12.3542 | 11.4195 | 10.2226 | 9.1605 | 8.8995 | 8.6153 | 8.5121 | 2.7647 | -2.0679 | -2.3353 | 11.9432 | 11.6716 | 10.9874 | 10.5737 | 9.4989 | 8.1063 | 6.8737 | 6.5737 | 6.2474 | 6.1326 | 0.75789 | -3.2274 | -3.5253 | 12.8761 | 12.5992 | 11.9045 | 11.4824 | 10.4066 | 9.0266 | 7.8055 | 7.5087 | 7.1845 | 7.0697 | 1.0024 | -3.9418 | -4.2408
|  | LAURENCEKIRK | HT |  |  |  |  | 13.5921 | 13.3216 | 12.6847 | 12.3279 | 11.3889 | 11.1163 | 10.7858 | 10.4216 | 9.5353 | 8.4468 | 1.3005 | -0.56895 | -0.81421 | 11.9705 | 11.6674 | 10.9463 | 10.5453 | 9.4632 | 9.1505 | 8.7684 | 8.3505 | 7.3263 | 6.0611 | 1.2768 | -1.96 | -2.3021 | 12.9045 | 12.5961 | 11.8624 | 11.455 | 10.3718 | 10.0624 | 9.6845 | 9.2687 | 8.255 | 7.0013 | 1.6445 | -2.3324 | -2.6755
|  | LAURENCEKIRK | HE |  |  |  |  | 13.6489 | 13.4595 | 12.8795 | 12.5563 | 11.6668 | 10.5089 | 9.5068 | 9.3195 | 9.1195 | 9.0511 | 5.7321 | 3.3395 | 3.0237 | 12.0326 | 11.8211 | 11.1621 | 10.7989 | 9.7779 | 8.4305 | 7.2653 | 7.0505 | 6.8211 | 6.7421 | 3.42 | 1.3568 | 1 | 12.9676 | 12.7518 | 12.0824 | 11.7129 | 10.6866 | 9.3518 | 8.1971 | 7.9834 | 7.7561 | 7.6782 | 4.0687 | 1.6266 | 1.2592
|  | LAURENCEKIRK | FB |  |  |  |  | 13.7511 | 13.6711 | 13.2668 | 13.1458 | 12.9489 | 12.5574 | 12.0058 | 11.4005 | 11.2837 | 11.2226 | 10.6353 | 9.6658 | 9.2984 | 12.1474 | 12.0579 | 11.5989 | 11.4632 | 11.24 | 10.7958 | 10.1674 | 9.4611 | 9.3274 | 9.2589 | 8.58 | 7.4537 | 7.0274 | 13.0845 | 12.9929 | 12.5255 | 12.3876 | 12.1603 | 11.7087 | 11.0729 | 10.3729 | 10.2403 | 10.1718 | 9.4992 | 8.3834 | 7.9613
| STORNOWAY | LAXAY | MINIMUM HEADROOM | NB 33424 21925 | YES | YES | 0 | 1.2463 | 1.2358 | 6.5263 | 6.5147 | 6.5011 | 6.4863 | 6.4695 | 6.4579 | 6.4432 | 6.4284 | 6.3737 | 6.3147 | 6.2589 | 1.1526 | 1.1421 | 6.4189 | 6.3842 | 6.3526 | 6.3179 | 6.2811 | 6.2526 | 6.2211 | 6.1916 | 6.0884 | 5.9979 | 5.9284 | 0.97895 | 0.96632 | 6.2547 | 6.2432 | 6.2284 | 6.2116 | 6.1916 | 6.1789 | 6.1632 | 6.1484 | 6.0526 | 5.9642 | 5.8958
|  | LAXAY | EE |  |  |  |  | 1.2463 | 1.2358 | 6.5263 | 6.5158 | 6.5032 | 6.4874 | 6.4695 | 6.4579 | 6.4432 | 6.4316 | 6.3863 | 6.3221 | 6.2653 | 1.1526 | 1.1421 | 6.4189 | 6.3842 | 6.3526 | 6.3179 | 6.2811 | 6.2526 | 6.2211 | 6.1916 | 6.0884 | 5.9979 | 5.9326 | 0.97895 | 0.96632 | 6.2547 | 6.2432 | 6.2284 | 6.2116 | 6.1916 | 6.1789 | 6.1632 | 6.1495 | 6.0526 | 5.9642 | 5.9
|  | LAXAY | HT |  |  |  |  | 1.2474 | 1.2379 | 6.5263 | 6.5147 | 6.5011 | 6.4863 | 6.4737 | 6.4589 | 6.4442 | 6.4284 | 6.3737 | 6.3147 | 6.2589 | 1.1537 | 1.1442 | 6.4326 | 6.4032 | 6.3705 | 6.3379 | 6.3063 | 6.2737 | 6.2421 | 6.2105 | 6.1053 | 6.0074 | 5.9284 | 0.98105 | 0.96947 | 6.2568 | 6.2432 | 6.2284 | 6.2116 | 6.1979 | 6.1811 | 6.1653 | 6.1484 | 6.0695 | 5.9737 | 5.8958
|  | LAXAY | HE |  |  |  |  | 1.2505 | 1.2411 | 6.5337 | 6.5232 | 6.5095 | 6.4958 | 6.4789 | 6.4674 | 6.4579 | 6.4526 | 6.4326 | 6.4189 | 6.4105 | 1.1568 | 1.1474 | 6.44 | 6.4295 | 6.4158 | 6.4021 | 6.3853 | 6.3642 | 6.3453 | 6.3295 | 6.2747 | 6.2263 | 6.1947 | 0.98526 | 0.97474 | 6.2663 | 6.2558 | 6.2411 | 6.2263 | 6.2084 | 6.1968 | 6.1863 | 6.18 | 6.1579 | 6.1411 | 6.1305
|  | LAXAY | FB |  |  |  |  | 1.2568 | 1.2526 | 6.5484 | 6.5442 | 6.54 | 6.5347 | 6.5295 | 6.5253 | 6.52 | 6.5137 | 6.4926 | 6.4758 | 6.4663 | 1.1632 | 1.1589 | 6.4547 | 6.4505 | 6.4463 | 6.4411 | 6.4358 | 6.4284 | 6.4137 | 6.3947 | 6.3316 | 6.2674 | 6.2168 | 0.99263 | 0.98737 | 6.2821 | 6.2768 | 6.2726 | 6.2663 | 6.26 | 6.2547 | 6.2484 | 6.2421 | 6.2168 | 6.1968 | 6.1811
| COUPAR ANGUS | LEOCH | MINIMUM HEADROOM | NO 35945 36287 | YES | YES | 0 | -0.48632 | -0.57158 | -0.64842 | -0.69895 | -0.74737 | -0.80211 | -0.85684 | -0.90316 | -0.94842 | -0.98947 | -4.0926 | -4.8674 | -4.9789 | -1.0021 | -1.0979 | -1.1863 | -1.2411 | -1.2947 | -1.3526 | -1.4105 | -1.4611 | -1.5095 | -1.5537 | -3.9958 | -4.6463 | -4.7716 | -0.93053 | -1.0284 | -1.1158 | -1.1716 | -1.2242 | -1.2832 | -1.3411 | -1.3916 | -1.44 | -1.4842 | -4.5821 | -5.3747 | -5.5
|  | LEOCH | EE |  |  |  |  | -0.48632 | -0.57158 | -0.64842 | -0.69895 | -0.74737 | -0.80211 | -0.85684 | -0.90316 | -0.94842 | -0.98947 | -4.0926 | -4.8674 | -4.9789 | -1.0021 | -1.0979 | -1.1863 | -1.2411 | -1.2947 | -1.3526 | -1.4105 | -1.4611 | -1.5095 | -1.5537 | -3.9958 | -4.6463 | -4.7716 | -0.93053 | -1.0284 | -1.1158 | -1.1716 | -1.2242 | -1.2832 | -1.3411 | -1.3916 | -1.44 | -1.4842 | -4.5821 | -5.3747 | -5.5
|  | LEOCH | HT |  |  |  |  | -0.46947 | -0.55053 | -0.62737 | -0.67684 | -0.72526 | -0.77263 | -0.82105 | -0.86947 | -0.91789 | -0.94737 | -4.0337 | -4.1737 | -4.2779 | -0.98316 | -1.0747 | -1.1611 | -1.2158 | -1.2684 | -1.32 | -1.3716 | -1.4232 | -1.4747 | -1.4968 | -3.5116 | -4.0789 | -4.2253 | -0.91263 | -1.0042 | -1.0916 | -1.1453 | -1.1989 | -1.2495 | -1.3021 | -1.3537 | -1.4053 | -1.4232 | -3.9653 | -4.6453 | -4.7926
|  | LEOCH | HE |  |  |  |  | -0.43579 | -0.50105 | -0.56105 | -0.59263 | -0.62632 | -0.66632 | -0.70632 | -0.73684 | -0.76842 | -0.79158 | -2.0737 | -2.3989 | -2.4579 | -0.94421 | -1.0189 | -1.0874 | -1.1211 | -1.1568 | -1.1989 | -1.24 | -1.2726 | -1.3074 | -1.3326 | -2.3632 | -2.6411 | -2.7074 | -0.87368 | -0.94737 | -1.0168 | -1.0505 | -1.0863 | -1.1284 | -1.1705 | -1.2032 | -1.2368 | -1.2632 | -2.56 | -2.8947 | -2.9611
|  | LEOCH | FB |  |  |  |  | -0.41263 | -0.44842 | -0.48211 | -0.50316 | -0.52737 | -0.54842 | -0.57053 | -0.59263 | -0.61579 | -0.64316 | -0.73789 | -0.83263 | -0.90105 | -0.91895 | -0.96 | -0.99789 | -1.0221 | -1.0484 | -1.0726 | -1.0968 | -1.1211 | -1.1463 | -1.1758 | -1.2811 | -1.3853 | -1.4611 | -0.84842 | -0.88947 | -0.92737 | -0.95158 | -0.97789 | -1.0021 | -1.0263 | -1.0505 | -1.0758 | -1.1063 | -1.2105 | -1.3158 | -1.3916
| NAIRN | LETHEN | MINIMUM HEADROOM | NH 92307 50795 | YES | YES | 0 | 3.9179 | 3.8905 | 3.8674 | 3.8379 | 3.8063 | 3.7747 | 3.74 | 3.7147 | 3.6905 | 3.6663 | 3.5705 | 3.4789 | 3.4053 | 3.9126 | 3.8853 | 3.8611 | 3.8295 | 3.7979 | 3.7653 | 3.7295 | 3.7032 | 3.6779 | 3.6537 | 3.5547 | 3.46 | 3.3832 | 4.0442 | 4.0337 | 4.0263 | 4.0147 | 4.0021 | 3.9726 | 3.9368 | 3.9116 | 3.8863 | 3.8621 | 3.7653 | 3.6737 | 3.5979
|  | LETHEN | EE |  |  |  |  | 3.9179 | 3.8905 | 3.8674 | 3.8379 | 3.8063 | 3.7747 | 3.74 | 3.7147 | 3.6905 | 3.6663 | 3.5705 | 3.4789 | 3.4053 | 3.9126 | 3.8853 | 3.8611 | 3.8295 | 3.7979 | 3.7653 | 3.7295 | 3.7032 | 3.6779 | 3.6537 | 3.5547 | 3.46 | 3.3832 | 4.0442 | 4.0337 | 4.0263 | 4.0147 | 4.0021 | 3.9726 | 3.9368 | 3.9116 | 3.8863 | 3.8621 | 3.7653 | 3.6737 | 3.5979
|  | LETHEN | HT |  |  |  |  | 3.9263 | 3.9021 | 3.8811 | 3.8558 | 3.8253 | 3.7968 | 3.7695 | 3.7442 | 3.7179 | 3.6916 | 3.5705 | 3.4832 | 3.4189 | 3.9221 | 3.8979 | 3.8747 | 3.8495 | 3.8168 | 3.7874 | 3.76 | 3.7326 | 3.7063 | 3.68 | 3.5758 | 3.4789 | 3.3968 | 4.0463 | 4.0368 | 4.0284 | 4.0168 | 4.0053 | 3.9937 | 3.9684 | 3.9411 | 3.9158 | 3.8895 | 3.7895 | 3.6958 | 3.6147
|  | LETHEN | HE |  |  |  |  | 3.9421 | 3.9274 | 3.9116 | 3.8968 | 3.8768 | 3.8579 | 3.8368 | 3.8221 | 3.8053 | 3.7926 | 3.7411 | 3.6832 | 3.6389 | 3.9389 | 3.9242 | 3.9063 | 3.8926 | 3.8705 | 3.8516 | 3.8316 | 3.8147 | 3.7979 | 3.7853 | 3.7305 | 3.6705 | 3.6253 | 4.0495 | 4.0432 | 4.0347 | 4.0274 | 4.0168 | 4.0042 | 3.9895 | 3.9811 | 3.9726 | 3.9684 | 3.9389 | 3.88 | 3.8358
|  | LETHEN | FB |  |  |  |  | 3.9537 | 3.9453 | 3.9316 | 3.9221 | 3.9105 | 3.9 | 3.8884 | 3.8789 | 3.8684 | 3.8516 | 3.7979 | 3.7453 | 3.7074 | 3.9505 | 3.9411 | 3.9284 | 3.9179 | 3.9053 | 3.8947 | 3.8832 | 3.8737 | 3.8611 | 3.8432 | 3.7874 | 3.7337 | 3.6937 | 4.0558 | 4.0537 | 4.0484 | 4.0453 | 4.0421 | 4.0389 | 4.0347 | 4.0316 | 4.0274 | 4.0232 | 3.9958 | 3.9432 | 3.9053
| GRUDIE BRIDGE | LETTEREWE | MINIMUM HEADROOM | NG 93546 70082 | YES | NO | 0 | 0.097895 | 0.096842 | 0.094737 | 0.092632 | 0.089474 | 0.088421 | 0.086316 | 0.083158 | 0.082105 | 0.08 | 0.071579 | 0.064211 | 0.054737 | 0.097895 | 0.096842 | 0.094737 | 0.092632 | 0.090526 | 0.089474 | 0.086316 | 0.084211 | 0.083158 | 0.081053 | 0.073684 | 0.065263 | 0.056842 | 0.096842 | 0.095789 | 0.093684 | 0.091579 | 0.088421 | 0.087368 | 0.085263 | 0.082105 | 0.081053 | 0.077895 | 0.070526 | 0.062105 | 0.053684
|  | LETTEREWE | EE |  |  |  |  | 0.097895 | 0.096842 | 0.094737 | 0.092632 | 0.089474 | 0.088421 | 0.086316 | 0.083158 | 0.082105 | 0.08 | 0.071579 | 0.064211 | 0.054737 | 0.097895 | 0.096842 | 0.094737 | 0.092632 | 0.090526 | 0.089474 | 0.086316 | 0.084211 | 0.083158 | 0.081053 | 0.073684 | 0.065263 | 0.056842 | 0.096842 | 0.095789 | 0.093684 | 0.091579 | 0.088421 | 0.087368 | 0.085263 | 0.082105 | 0.081053 | 0.077895 | 0.070526 | 0.062105 | 0.053684
|  | LETTEREWE | HT |  |  |  |  | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.094737 | 0.091579 | 0.088421 | 0.086316 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.094737 | 0.092632 | 0.089474 | 0.086316 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.094737 | 0.094737 | 0.093684 | 0.091579 | 0.088421 | 0.085263
|  | LETTEREWE | HE |  |  |  |  | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.094737 | 0.092632 | 0.089474 | 0.086316 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.094737 | 0.092632 | 0.089474 | 0.086316 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.095789 | 0.094737 | 0.094737 | 0.094737 | 0.093684 | 0.091579 | 0.088421 | 0.085263
|  | LETTEREWE | FB |  |  |  |  | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.096842
| ELGIN | LHANBRYDE | MINIMUM HEADROOM | NJ 27940 61640 | NO | YES | 0 | 4.9232 | 4.8705 | 4.8242 | 4.7789 | 4.7411 | 4.7053 | 4.6663 | 4.6232 | 4.58 | 4.5537 | 4.4884 | 4.3863 | 4.3095 | 4.8179 | 4.6874 | 4.6021 | 4.5526 | 4.5105 | 4.4705 | 4.4274 | 4.3811 | 4.3326 | 4.3032 | 4.2716 | 4.1526 | 4.0611 | 4.8189 | 4.6937 | 4.6116 | 4.5632 | 4.5211 | 4.4832 | 4.4411 | 4.3958 | 4.3484 | 4.3189 | 4.3084 | 4.1926 | 4.1042
|  | LHANBRYDE | EE |  |  |  |  | 4.9232 | 4.8705 | 4.8379 | 4.7895 | 4.7547 | 4.7147 | 4.6726 | 4.6232 | 4.58 | 4.5537 | 4.4958 | 4.3895 | 4.3095 | 4.8179 | 4.6874 | 4.6189 | 4.5642 | 4.5263 | 4.4821 | 4.4358 | 4.3811 | 4.3326 | 4.3032 | 4.2716 | 4.1526 | 4.0611 | 4.8189 | 4.6937 | 4.6274 | 4.5747 | 4.5368 | 4.4947 | 4.4495 | 4.3958 | 4.3484 | 4.3189 | 4.3084 | 4.1926 | 4.1042
|  | LHANBRYDE | HT |  |  |  |  | 4.9274 | 4.8758 | 4.8242 | 4.7789 | 4.7411 | 4.7053 | 4.6663 | 4.6284 | 4.5926 | 4.6347 | 4.4884 | 4.3863 | 4.3105 | 4.8263 | 4.6989 | 4.6021 | 4.5526 | 4.5105 | 4.4705 | 4.4274 | 4.3863 | 4.3474 | 4.4274 | 4.2937 | 4.1747 | 4.0674 | 4.8274 | 4.7042 | 4.6116 | 4.5632 | 4.5211 | 4.4832 | 4.4411 | 4.4011 | 4.3621 | 4.46 | 4.3305 | 4.2137 | 4.1095
|  | LHANBRYDE | HE |  |  |  |  | 4.9389 | 4.8926 | 4.8653 | 4.8421 | 4.8189 | 4.7895 | 4.7495 | 4.7179 | 4.6874 | 4.6747 | 4.6811 | 4.5484 | 4.5179 | 4.8537 | 4.7379 | 4.6758 | 4.6295 | 4.6 | 4.5674 | 4.5242 | 4.4895 | 4.4558 | 4.4411 | 4.48 | 4.3 | 4.2653 | 4.8537 | 4.7421 | 4.6821 | 4.6379 | 4.6084 | 4.5768 | 4.5337 | 4.5 | 4.4674 | 4.4526 | 4.5116 | 4.3158 | 4.2821
|  | LHANBRYDE | FB |  |  |  |  | 4.9663 | 4.9453 | 4.9316 | 4.9211 | 4.9105 | 4.9 | 4.8916 | 4.8789 | 4.8632 | 4.8526 | 4.7958 | 4.7074 | 4.6579 | 4.9211 | 4.8663 | 4.8358 | 4.8147 | 4.7947 | 4.7768 | 4.76 | 4.7347 | 4.7021 | 4.6832 | 4.5768 | 4.4758 | 4.4189 | 4.9179 | 4.8663 | 4.8358 | 4.8158 | 4.7968 | 4.7789 | 4.7632 | 4.7389 | 4.7063 | 4.6884 | 4.5853 | 4.4874 | 4.4326
| FORT WILLIAM | LIDDESDALE | MINIMUM HEADROOM | NM 78116 59480 | YES | NO | 0 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789
|  | LIDDESDALE | EE |  |  |  |  | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789
|  | LIDDESDALE | HT |  |  |  |  | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789
|  | LIDDESDALE | HE |  |  |  |  | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789
|  | LIDDESDALE | FB |  |  |  |  | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789 | 0.075789
| KEITH 1 | LIMEHILLOCKS | MINIMUM HEADROOM | NJ 52093 50703 | YES | YES | 0 | 1.39 | 1.3647 | 1.3395 | 1.3111 | 1.2837 | 1.2489 | 1.2047 | 1.1689 | 1.1363 | 1.1132 | -0.89316 | -1.4468 | -1.4963 | 1.3784 | 1.3489 | 1.3216 | 1.29 | 1.2605 | 1.2205 | 1.1711 | 1.13 | 1.0942 | 1.0689 | 0.95105 | -1.0068 | -1.0616 | 1.3774 | 1.3489 | 1.3205 | 1.2879 | 1.2584 | 1.2205 | 1.17 | 1.13 | 1.0932 | 1.0689 | 0.94368 | -1.5068 | -1.5637
|  | LIMEHILLOCKS | EE |  |  |  |  | 1.39 | 1.3647 | 1.3395 | 1.3111 | 1.2837 | 1.2563 | 1.2195 | 1.1795 | 1.1426 | 1.1205 | 1.0037 | -1.4468 | -1.4963 | 1.3784 | 1.3489 | 1.3216 | 1.29 | 1.2605 | 1.23 | 1.1911 | 1.1447 | 1.1037 | 1.0805 | 0.95105 | -1.0068 | -1.0616 | 1.3774 | 1.3489 | 1.3205 | 1.2879 | 1.2584 | 1.2279 | 1.1868 | 1.1416 | 1.1005 | 1.0763 | 0.94368 | -1.5068 | -1.5637
|  | LIMEHILLOCKS | HT |  |  |  |  | 1.3963 | 1.3742 | 1.3437 | 1.3121 | 1.2858 | 1.2489 | 1.2047 | 1.1689 | 1.1363 | 1.1132 | -0.89316 | -0.97421 | -1.0311 | 1.3847 | 1.3605 | 1.3268 | 1.29 | 1.2605 | 1.2205 | 1.1711 | 1.13 | 1.0942 | 1.0689 | 0.96789 | -0.61737 | -0.69947 | 1.3847 | 1.3595 | 1.3268 | 1.29 | 1.2616 | 1.2205 | 1.17 | 1.13 | 1.0932 | 1.0689 | 0.96579 | -1.0184 | -1.1047
|  | LIMEHILLOCKS | HE |  |  |  |  | 1.4132 | 1.3963 | 1.3805 | 1.3595 | 1.3447 | 1.3247 | 1.2932 | 1.2616 | 1.2332 | 1.2226 | 1.1711 | 0.18895 | 0.16474 | 1.4037 | 1.3858 | 1.3689 | 1.3447 | 1.3289 | 1.3089 | 1.2721 | 1.2374 | 1.2058 | 1.1932 | 1.1353 | 0.35947 | 0.33421 | 1.4037 | 1.3847 | 1.3679 | 1.3447 | 1.3289 | 1.3079 | 1.2721 | 1.2374 | 1.2047 | 1.1932 | 1.1332 | 0.15105 | 0.12158
|  | LIMEHILLOCKS | FB |  |  |  |  | 1.4226 | 1.4132 | 1.4047 | 1.3932 | 1.3826 | 1.3721 | 1.3605 | 1.3458 | 1.3268 | 1.3142 | 1.2479 | 1.1879 | 1.1511 | 1.4142 | 1.4037 | 1.3932 | 1.3805 | 1.37 | 1.3574 | 1.3458 | 1.3289 | 1.3068 | 1.2932 | 1.2174 | 1.1489 | 1.1058 | 1.4142 | 1.4037 | 1.3932 | 1.3805 | 1.3689 | 1.3574 | 1.3447 | 1.3289 | 1.3058 | 1.2921 | 1.2174 | 1.1489 | 1.1058
| ARDMORE | LOCH CARNAN | MINIMUM HEADROOM | NF 83230 42735 | NO | YES | 0 | 6.2659 | 6.2648 | 6.2638 | 6.2617 | 6.2606 | 6.2564 | 6.2543 | 6.2522 | 6.2501 | 6.248 | 6.2396 | 6.2333 | 6.2301 | 7.368 | 7.3669 | 7.3659 | 7.3638 | 7.3627 | 7.3596 | 7.3575 | 7.3554 | 7.3533 | 7.3512 | 7.3448 | 7.3396 | 7.3354 | 5.6901 | 5.6891 | 5.688 | 5.6859 | 5.6848 | 5.6817 | 5.6796 | 5.6775 | 5.6754 | 5.6733 | 5.6669 | 5.6617 | 5.6575
|  | LOCH CARNAN | EE |  |  |  |  | 6.2659 | 6.2648 | 6.2638 | 6.2617 | 6.2606 | 6.2564 | 6.2543 | 6.2522 | 6.2501 | 13.0291 | 13.0217 | 13.0164 | 13.0122 | 7.368 | 7.3669 | 7.3659 | 7.3638 | 7.3627 | 7.3596 | 7.3575 | 7.3554 | 7.3533 | 15.7722 | 15.7659 | 15.7617 | 15.7585 | 5.6901 | 5.6891 | 5.688 | 5.6859 | 5.6848 | 5.6817 | 5.6796 | 5.6775 | 5.6754 | 14.768 | 14.7512 | 14.7354 | 14.7238
|  | LOCH CARNAN | HT |  |  |  |  | 6.268 | 6.2648 | 6.2638 | 6.2617 | 6.2606 | 6.2575 | 6.2543 | 6.2522 | 6.2501 | 6.248 | 6.2396 | 6.2333 | 6.2301 | 7.3691 | 7.3669 | 7.3659 | 7.3638 | 7.3627 | 7.3596 | 7.3575 | 7.3554 | 7.3533 | 7.3512 | 7.3448 | 7.3396 | 7.3354 | 5.6912 | 5.6891 | 5.688 | 5.6859 | 5.6848 | 5.6817 | 5.6796 | 5.6775 | 5.6754 | 5.6733 | 5.6669 | 5.6617 | 5.6575
|  | LOCH CARNAN | HE |  |  |  |  | 6.268 | 6.2659 | 6.2648 | 6.2627 | 6.2617 | 6.2596 | 6.2564 | 6.2543 | 6.2533 | 6.2533 | 6.2491 | 6.2469 | 6.2459 | 7.3691 | 7.3669 | 7.3659 | 7.3648 | 7.3638 | 7.3617 | 7.3585 | 7.3564 | 7.3554 | 7.3554 | 7.3522 | 7.3501 | 7.3491 | 5.6912 | 5.6891 | 5.688 | 5.6869 | 5.6859 | 5.6838 | 5.6806 | 5.6785 | 5.6775 | 5.6775 | 5.6743 | 5.6722 | 5.6712
|  | LOCH CARNAN | FB |  |  |  |  | 6.2691 | 6.268 | 6.268 | 6.2669 | 6.2659 | 6.2648 | 6.2638 | 6.2627 | 6.2627 | 6.2617 | 6.2575 | 6.2554 | 6.2533 | 7.3701 | 7.3691 | 7.3691 | 7.368 | 7.368 | 7.3669 | 7.3659 | 7.3648 | 7.3648 | 7.3638 | 7.3606 | 7.3585 | 7.3564 | 5.6922 | 5.6912 | 5.6912 | 5.6901 | 5.6901 | 5.6891 | 5.688 | 5.6869 | 5.6869 | 5.6859 | 5.6827 | 5.6806 | 5.6785
| GRUDIE BRIDGE | LOCH GLASCARNOCH | MINIMUM HEADROOM | NH 31620 71996 | YES | NO | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | LOCH GLASCARNOCH | EE |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | LOCH GLASCARNOCH | HT |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | LOCH GLASCARNOCH | HE |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  | LOCH GLASCARNOCH | FB |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| FORT WILLIAM | LOCHALINE | MINIMUM HEADROOM | NM 67939 45444 | YES | NO | 0 | 0.97895 | 0.96526 | 0.94947 | 0.93368 | 0.91789 | 0.90105 | 0.88632 | 0.87263 | 0.85684 | 0.84316 | 0.79158 | 0.73895 | 0.69053 | 0.97895 | 0.96421 | 0.94842 | 0.93263 | 0.91579 | 0.89895 | 0.88316 | 0.86842 | 0.85263 | 0.83895 | 0.78421 | 0.72947 | 0.67895 | 0.97684 | 0.96 | 0.94316 | 0.92632 | 0.90842 | 0.88947 | 0.87368 | 0.85789 | 0.84 | 0.82526 | 0.76842 | 0.70842 | 0.65579
|  | LOCHALINE | EE |  |  |  |  | 0.97895 | 0.96526 | 0.94947 | 0.93368 | 0.91789 | 0.90105 | 0.88632 | 0.87263 | 0.85684 | 0.84316 | 0.79158 | 0.73895 | 0.69053 | 0.97895 | 0.96421 | 0.94842 | 0.93263 | 0.91579 | 0.89895 | 0.88316 | 0.86842 | 0.85263 | 0.83895 | 0.78421 | 0.72947 | 0.67895 | 0.97684 | 0.96 | 0.94316 | 0.92632 | 0.90842 | 0.88947 | 0.87368 | 0.85789 | 0.84 | 0.82526 | 0.76842 | 0.70842 | 0.65579
|  | LOCHALINE | HT |  |  |  |  | 0.98632 | 0.97895 | 0.96842 | 0.96 | 0.94947 | 0.94105 | 0.93158 | 0.92316 | 0.91263 | 0.90211 | 0.86105 | 0.82632 | 0.80211 | 0.98526 | 0.97789 | 0.96737 | 0.95895 | 0.94947 | 0.94105 | 0.93158 | 0.92211 | 0.91158 | 0.90211 | 0.86947 | 0.83263 | 0.80211 | 0.98421 | 0.97579 | 0.96526 | 0.95474 | 0.94421 | 0.93579 | 0.92526 | 0.91368 | 0.90316 | 0.89263 | 0.85474 | 0.81368 | 0.78
|  | LOCHALINE | HE |  |  |  |  | 0.98947 | 0.98316 | 0.97789 | 0.97158 | 0.96421 | 0.95895 | 0.94947 | 0.94211 | 0.93474 | 0.93053 | 0.90947 | 0.88632 | 0.86526 | 0.98842 | 0.98316 | 0.97789 | 0.97158 | 0.96421 | 0.95789 | 0.94842 | 0.94211 | 0.93474 | 0.92947 | 0.90737 | 0.88421 | 0.86211 | 0.98842 | 0.98105 | 0.97579 | 0.96842 | 0.96105 | 0.95368 | 0.94421 | 0.93684 | 0.92947 | 0.92421 | 0.89895 | 0.87368 | 0.85053
|  | LOCHALINE | FB |  |  |  |  | 0.99368 | 0.99158 | 0.98737 | 0.98526 | 0.98105 | 0.97789 | 0.97368 | 0.97158 | 0.96737 | 0.96211 | 0.94737 | 0.93053 | 0.91684 | 0.99368 | 0.99053 | 0.98737 | 0.98421 | 0.98 | 0.97684 | 0.97263 | 0.97053 | 0.96526 | 0.96105 | 0.94316 | 0.92632 | 0.91263 | 0.99368 | 0.99053 | 0.98632 | 0.98316 | 0.97895 | 0.97474 | 0.97158 | 0.96842 | 0.96316 | 0.95895 | 0.94 | 0.92211 | 0.90737
| GRUDIE BRIDGE | LOCHCARRON | MINIMUM HEADROOM | NG 91944 41839 | YES | NO | 0 | 2.4095 | 2.3358 | 2.26 | 2.1789 | 2.0947 | 1.5126 | 0.52 | -0.70842 | -1.9232 | -2.7042 | -5.0789 | -8.1421 | -8.2463 | 2.52 | 2.4547 | 2.3853 | 2.3126 | 2.2358 | 1.5158 | 0.36211 | -1.0674 | -2.4811 | -3.3863 | -6.0874 | -8.4042 | -8.4695 | 2.4168 | 2.3379 | 2.2558 | 2.1705 | 2.0832 | 1.5337 | 0.36947 | -1.0705 | -2.4937 | -3.4105 | -6.1516 | -9.2505 | -9.3684
|  | LOCHCARRON | EE |  |  |  |  | 2.4095 | 2.3358 | 2.26 | 2.1789 | 2.0947 | 2.0158 | 1.9379 | 1.1568 | 0.12316 | -1.1653 | -4.8421 | -5.8232 | -6.0768 | 2.52 | 2.4547 | 2.3853 | 2.3126 | 2.2358 | 2.1579 | 2.0758 | 1.2537 | 0.10211 | -1.3589 | -5.5126 | -6.5379 | -6.7284 | 2.4168 | 2.3379 | 2.2558 | 2.1705 | 2.0832 | 2.0021 | 1.92 | 1.1368 | -0.075789 | -1.5874 | -5.8926 | -7.0326 | -7.32
|  | LOCHCARRON | HT |  |  |  |  | 2.4526 | 2.4189 | 2.3874 | 2.3537 | 2.3126 | 1.5126 | 0.52 | -0.70842 | -1.9232 | -2.7042 | -5.0789 | -5.2221 | -5.3263 | 2.5579 | 2.5263 | 2.4947 | 2.4621 | 2.4211 | 1.5158 | 0.36211 | -1.0674 | -2.4811 | -3.3863 | -6.0874 | -6.2063 | -6.3032 | 2.4695 | 2.4411 | 2.4116 | 2.3832 | 2.3526 | 1.5337 | 0.36947 | -1.0705 | -2.4937 | -3.4105 | -6.1516 | -6.32 | -6.4684
|  | LOCHCARRON | HE |  |  |  |  | 2.4653 | 2.4368 | 2.4105 | 2.3821 | 2.3526 | 2.3221 | 2.2905 | 1.4516 | 0.34211 | -1.0895 | -4.2189 | -8.1421 | -8.2463 | 2.5716 | 2.5453 | 2.52 | 2.4937 | 2.4653 | 2.4368 | 2.4074 | 1.4632 | 0.17579 | -1.4947 | -5.1232 | -8.4042 | -8.4695 | 2.4716 | 2.4442 | 2.4168 | 2.3884 | 2.3611 | 2.3295 | 2.2979 | 1.4653 | 0.16421 | -1.5179 | -5.1874 | -9.2505 | -9.3684
|  | LOCHCARRON | FB |  |  |  |  | 2.4842 | 2.4726 | 2.4621 | 2.4495 | 2.4379 | 2.4242 | 2.4137 | 2.4021 | 2.0474 | 1.5674 | -1.1495 | -2.0958 | -2.1389 | 2.5895 | 2.5779 | 2.5663 | 2.5558 | 2.5442 | 2.5295 | 2.52 | 2.5074 | 2.1011 | 1.5379 | -1.64 | -2.74 | -2.7832 | 2.4916 | 2.4832 | 2.4758 | 2.4684 | 2.46 | 2.4526 | 2.4453 | 2.4379 | 2.1558 | 1.5905 | -1.5947 | -2.7042 | -2.7537
| TAYNUILT | LOCHDONHEAD | MINIMUM HEADROOM | NM 72902 34134 | YES | YES | 0 | 0.98526 | 0.93895 | 0.89053 | 0.86842 | 0.85684 | 0.80526 | 0.75579 | 0.72632 | 0.65368 | 0.48421 | 0.12316 | 0.090526 | 0.065263 | 1.1832 | 1.1811 | 1.1411 | 1.1179 | 1.1063 | 1.0495 | 0.99158 | 0.95789 | 0.87474 | 0.67789 | 0.26105 | 0.22421 | 0.19579 | 1.1989 | 1.1747 | 1.1253 | 1.1011 | 1.0895 | 1.0337 | 0.97684 | 0.94316 | 0.86105 | 0.66737 | 0.25579 | 0.22 | 0.19158
|  | LOCHDONHEAD | EE |  |  |  |  | 0.98526 | 0.97053 | 0.89053 | 0.86842 | 0.85684 | 0.80526 | 0.75579 | 0.72632 | 0.71579 | 0.70632 | 0.12316 | 0.090526 | 0.065263 | 1.1832 | 1.1811 | 1.1411 | 1.1179 | 1.1063 | 1.0495 | 0.99158 | 0.95789 | 0.94632 | 0.93579 | 0.26105 | 0.22421 | 0.19579 | 1.1989 | 1.1968 | 1.1253 | 1.1011 | 1.0895 | 1.0337 | 0.97684 | 0.94316 | 0.93263 | 0.92105 | 0.25579 | 0.22 | 0.19158
|  | LOCHDONHEAD | HT |  |  |  |  | 0.98842 | 0.93895 | 0.90526 | 0.88632 | 0.87579 | 0.84316 | 0.78526 | 0.74421 | 0.65368 | 0.48421 | 0.12947 | 0.097895 | 0.075789 | 1.1842 | 1.1811 | 1.1558 | 1.1358 | 1.1263 | 1.0926 | 1.0263 | 0.97895 | 0.87474 | 0.67789 | 0.27789 | 0.23895 | 0.20842 | 1.2 | 1.1747 | 1.1411 | 1.12 | 1.1095 | 1.0737 | 1.0105 | 0.96421 | 0.86105 | 0.66737 | 0.27368 | 0.23474 | 0.20421
|  | LOCHDONHEAD | HE |  |  |  |  | 0.99263 | 0.98 | 0.90421 | 0.88947 | 0.88526 | 0.85579 | 0.80526 | 0.76632 | 0.76316 | 0.75474 | 0.18632 | 0.16842 | 0.15579 | 1.1842 | 1.1821 | 1.1547 | 1.14 | 1.1358 | 1.1053 | 1.0484 | 1.0032 | 1 | 0.99158 | 0.33158 | 0.31263 | 0.29789 | 1.2 | 1.1979 | 1.14 | 1.1242 | 1.1189 | 1.0874 | 1.0326 | 0.98842 | 0.98421 | 0.97579 | 0.32632 | 0.30737 | 0.29263
|  | LOCHDONHEAD | FB |  |  |  |  | 0.99579 | 0.98947 | 0.97474 | 0.94737 | 0.94316 | 0.92842 | 0.90421 | 0.88632 | 0.88211 | 0.87579 | 0.71263 | 0.48842 | 0.47053 | 1.1863 | 1.1853 | 1.1842 | 1.1832 | 1.1811 | 1.18 | 1.1547 | 1.1358 | 1.1316 | 1.1263 | 0.94105 | 0.68105 | 0.66105 | 1.2021 | 1.2011 | 1.2 | 1.1832 | 1.1789 | 1.1653 | 1.14 | 1.12 | 1.1158 | 1.1095 | 0.92632 | 0.67053 | 0.65053
| KILLIN | LOCHEARNHEAD | MINIMUM HEADROOM | NN 58766 24177 | YES | YES | 0.10204 | 0.94632 | 0.90737 | 0.81158 | 0.76526 | 0.71789 | 0.66947 | 0.62211 | 0.57789 | 0.53263 | 0.48842 | 0.32632 | 0.15474 | -0.0021053 | 0.94737 | 0.90947 | 0.80526 | 0.75789 | 0.70947 | 0.66316 | 0.61579 | 0.56947 | 0.52526 | 0.48211 | 0.32 | 0.14842 | -0.0084211 | 0.94211 | 0.89789 | 0.79053 | 0.73789 | 0.68421 | 0.63158 | 0.57684 | 0.52632 | 0.47684 | 0.42737 | 0.24526 | 0.049474 | -0.12842
|  | LOCHEARNHEAD | EE |  |  |  |  | 0.94632 | 0.90737 | 0.81158 | 0.76526 | 0.71789 | 0.66947 | 0.62211 | 0.57789 | 0.53263 | 0.48842 | 0.32632 | 0.15474 | -0.0021053 | 0.94737 | 0.90947 | 0.80526 | 0.75789 | 0.70947 | 0.66316 | 0.61579 | 0.56947 | 0.52526 | 0.48211 | 0.32 | 0.14842 | -0.0084211 | 0.94211 | 0.89789 | 0.79053 | 0.73789 | 0.68421 | 0.63158 | 0.57684 | 0.52632 | 0.47684 | 0.42737 | 0.24526 | 0.049474 | -0.12842
|  | LOCHEARNHEAD | HT |  |  |  |  | 0.96316 | 0.93684 | 0.90947 | 0.87789 | 0.84105 | 0.80632 | 0.76842 | 0.73263 | 0.69474 | 0.65789 | 0.48421 | 0.34 | 0.23053 | 0.96 | 0.93474 | 0.90632 | 0.87368 | 0.83368 | 0.79789 | 0.75789 | 0.72 | 0.67895 | 0.64211 | 0.49684 | 0.33474 | 0.19263 | 0.95895 | 0.92947 | 0.89895 | 0.86421 | 0.82211 | 0.78316 | 0.74 | 0.7 | 0.65684 | 0.61579 | 0.46105 | 0.28421 | 0.12737
|  | LOCHEARNHEAD | HE |  |  |  |  | 0.97368 | 0.95474 | 0.93474 | 0.91158 | 0.88737 | 0.85895 | 0.83053 | 0.80526 | 0.78 | 0.75579 | 0.66105 | 0.56 | 0.46632 | 0.97368 | 0.95474 | 0.93474 | 0.91158 | 0.88737 | 0.85789 | 0.82947 | 0.80316 | 0.77579 | 0.75263 | 0.65474 | 0.55053 | 0.45684 | 0.97158 | 0.95053 | 0.92947 | 0.90316 | 0.87474 | 0.84421 | 0.81263 | 0.78421 | 0.75368 | 0.72737 | 0.62 | 0.50316 | 0.39579
|  | LOCHEARNHEAD | FB |  |  |  |  | 0.98737 | 0.97579 | 0.96632 | 0.95579 | 0.94526 | 0.93368 | 0.92 | 0.90947 | 0.89368 | 0.87684 | 0.80842 | 0.73368 | 0.67158 | 0.98526 | 0.97474 | 0.96526 | 0.95263 | 0.94105 | 0.92947 | 0.91474 | 0.90316 | 0.88526 | 0.86632 | 0.79053 | 0.70632 | 0.63789 | 0.98632 | 0.97474 | 0.96421 | 0.95158 | 0.93895 | 0.92632 | 0.91053 | 0.89895 | 0.88105 | 0.86105 | 0.78421 | 0.69789 | 0.62526
| LYNDHURST | LOCHEE | MINIMUM HEADROOM | NO 38065 31416 | NO | YES | 0.10204 | 23.788 | 23.7638 | 23.7417 | 23.7101 | 23.6764 | 23.6427 | 23.6038 | 23.5691 | 23.5322 | 23.4891 | 23.0996 | 22.7796 | 22.5606 | 22.3074 | 22.2832 | 22.2611 | 22.2295 | 22.1958 | 22.0926 | 21.9758 | 21.8768 | 21.7821 | 21.6726 | 21.2811 | 20.8853 | 20.5758 | 22.5729 | 22.4824 | 22.4087 | 22.2982 | 22.1982 | 22.0876 | 21.9824 | 21.8939 | 21.8087 | 21.7097 | 21.3529 | 21.0013 | 20.7245
|  | LOCHEE | EE |  |  |  |  | 23.788 | 23.7638 | 23.7427 | 23.7185 | 23.688 | 23.6469 | 23.6038 | 23.5691 | 23.5364 | 23.5069 | 23.2185 | 22.9112 | 22.6733 | 22.3074 | 22.2832 | 22.2621 | 22.2379 | 22.2042 | 22.0926 | 21.9758 | 21.8768 | 21.7821 | 21.6726 | 21.32 | 20.9674 | 20.6968 | 22.5729 | 22.4824 | 22.4087 | 22.2982 | 22.1982 | 22.0876 | 21.9824 | 21.8939 | 21.8087 | 21.7097 | 21.3908 | 21.0771 | 20.8382
|  | LOCHEE | HT |  |  |  |  | 23.7933 | 23.7669 | 23.7417 | 23.7101 | 23.6764 | 23.6427 | 23.6069 | 23.5701 | 23.5322 | 23.4891 | 23.0996 | 22.7796 | 22.5606 | 22.3126 | 22.2863 | 22.2611 | 22.2295 | 22.1958 | 22.1537 | 22.0558 | 21.9558 | 21.8558 | 21.7274 | 21.2811 | 20.8853 | 20.5758 | 22.5961 | 22.5118 | 22.4413 | 22.3382 | 22.235 | 22.1424 | 22.0518 | 21.9613 | 21.8708 | 21.7539 | 21.3529 | 21.0013 | 20.7245
|  | LOCHEE | HE |  |  |  |  | 23.7996 | 23.7743 | 23.7554 | 23.728 | 23.6964 | 23.6543 | 23.6112 | 23.5838 | 23.5575 | 23.5438 | 23.4796 | 23.4364 | 23.3859 | 22.3189 | 22.2937 | 22.2747 | 22.2474 | 22.2158 | 22.1737 | 22.1305 | 22.1032 | 22.0768 | 22.0632 | 21.8832 | 21.6695 | 21.5274 | 22.6445 | 22.5792 | 22.535 | 22.4645 | 22.4003 | 22.3213 | 22.2571 | 22.2013 | 22.1445 | 22.0834 | 21.8855 | 21.6971 | 21.5718
|  | LOCHEE | FB |  |  |  |  | 23.8101 | 23.7985 | 23.7859 | 23.7733 | 23.7585 | 23.7427 | 23.7269 | 23.7112 | 23.6943 | 23.6764 | 23.6101 | 23.5543 | 23.5248 | 22.3295 | 22.3179 | 22.3053 | 22.2926 | 22.2779 | 22.2621 | 22.2463 | 22.2305 | 22.2137 | 22.1958 | 22.1253 | 21.8968 | 21.7053 | 22.7287 | 22.6918 | 22.655 | 22.6129 | 22.5687 | 22.5213 | 22.4729 | 22.4329 | 22.3876 | 22.3255 | 22.1182 | 21.9087 | 21.7403
| PORT ANN | LOCHGILPHEAD | MINIMUM HEADROOM | NR 86092 88371 | NO | YES | 0.16837 | 23.9105 | 23.8747 | 23.8116 | 23.6158 | 23.5074 | 23.3874 | 23.2505 | 23.0505 | 22.8495 | 22.4937 | 21.4084 | 21.0547 | 20.8284 | 22.0189 | 21.9863 | 21.9632 | 21.9074 | 21.8611 | 21.74 | 21.5821 | 21.3968 | 21.1232 | 20.7158 | 19.5389 | 19.1495 | 18.8979 | 16.2842 | 16.0505 | 15.8463 | 15.6242 | 15.5021 | 15.3684 | 15.2147 | 14.9842 | 14.7463 | 14.3316 | 13.0705 | 12.6684 | 12.4063
|  | LOCHGILPHEAD | EE |  |  |  |  | 23.9105 | 23.8747 | 23.8116 | 23.6158 | 23.5074 | 23.3874 | 23.2505 | 23.0505 | 22.8663 | 22.7705 | 21.4084 | 21.0547 | 20.8284 | 22.0189 | 21.9863 | 21.9632 | 21.9074 | 21.8611 | 21.74 | 21.6021 | 21.3968 | 21.2095 | 21.1147 | 19.5389 | 19.1495 | 18.8979 | 16.2842 | 16.1674 | 15.8463 | 15.6242 | 15.5021 | 15.3684 | 15.2147 | 14.9842 | 14.7716 | 14.6653 | 13.0705 | 12.6684 | 12.4063
|  | LOCHGILPHEAD | HT |  |  |  |  | 23.92 | 23.8916 | 23.8589 | 23.7453 | 23.6411 | 23.5095 | 23.2853 | 23.1063 | 22.8495 | 22.4937 | 21.5737 | 21.2568 | 21.0716 | 22.0263 | 21.9989 | 21.9674 | 21.9326 | 21.8947 | 21.8158 | 21.5821 | 21.3979 | 21.1232 | 20.7158 | 19.7474 | 19.3705 | 19.0916 | 16.3232 | 16.0505 | 15.9221 | 15.7726 | 15.6568 | 15.5074 | 15.2484 | 15.0432 | 14.7463 | 14.3316 | 13.3558 | 12.9768 | 12.6947
|  | LOCHGILPHEAD | HE |  |  |  |  | 23.9326 | 23.9042 | 23.8842 | 23.8547 | 23.8211 | 23.7653 | 23.6263 | 23.4663 | 23.32 | 23.2695 | 22.1611 | 21.9863 | 21.8947 | 22.0389 | 22.0116 | 21.9926 | 21.9642 | 21.9305 | 21.8863 | 21.84 | 21.7747 | 21.6242 | 21.5726 | 20.3305 | 20.1358 | 20.0305 | 16.3916 | 16.3158 | 16.0263 | 15.9421 | 15.88 | 15.8063 | 15.6505 | 15.4642 | 15.2958 | 15.2389 | 13.9347 | 13.7337 | 13.6242
|  | LOCHGILPHEAD | FB |  |  |  |  | 23.9463 | 23.9347 | 23.9221 | 23.9084 | 23.8947 | 23.8789 | 23.8642 | 23.8484 | 23.8337 | 23.7853 | 23.2579 | 22.6747 | 22.5432 | 22.0516 | 22.0411 | 22.0274 | 22.0147 | 22.0011 | 21.9863 | 21.9716 | 21.9558 | 21.9411 | 21.9221 | 21.5484 | 20.8989 | 20.7442 | 16.4242 | 16.3832 | 16.3379 | 16.2032 | 16.1568 | 16.1116 | 16.0684 | 15.9926 | 15.8874 | 15.8242 | 15.2074 | 14.5242 | 14.3684
| CLACHAN | LOCHGOILHEAD | MINIMUM HEADROOM | NN 20159 01862 | YES | YES | 0 | -0.24842 | -0.27474 | -0.30316 | -0.33368 | -0.36316 | -0.39158 | -0.41684 | -0.44632 | -0.47368 | -0.50211 | -0.60211 | -0.70632 | -0.80842 | -0.28947 | -0.30526 | -0.32211 | -0.35053 | -0.38211 | -0.41158 | -0.43895 | -0.46842 | -0.49684 | -0.52632 | -0.63158 | -0.74 | -0.84842 | -0.35474 | -0.37789 | -0.40316 | -0.42842 | -0.45368 | -0.47789 | -0.50105 | -0.52632 | -0.54947 | -0.57474 | -0.67474 | -0.79474 | -0.91263
|  | LOCHGOILHEAD | EE |  |  |  |  | -0.24842 | -0.27474 | -0.30316 | -0.33368 | -0.36316 | -0.39158 | -0.41684 | -0.44632 | -0.47368 | -0.50211 | -0.60211 | -0.70632 | -0.80842 | -0.28947 | -0.30526 | -0.32211 | -0.35053 | -0.38211 | -0.41158 | -0.43895 | -0.46842 | -0.49684 | -0.52632 | -0.63158 | -0.74 | -0.84842 | -0.35474 | -0.37789 | -0.40316 | -0.42842 | -0.45368 | -0.47789 | -0.50105 | -0.52632 | -0.54947 | -0.57474 | -0.67474 | -0.79474 | -0.91263
|  | LOCHGOILHEAD | HT |  |  |  |  | -0.23158 | -0.24211 | -0.25368 | -0.26526 | -0.27684 | -0.28947 | -0.30105 | -0.31368 | -0.32632 | -0.33789 | -0.39579 | -0.44421 | -0.48421 | -0.28105 | -0.28947 | -0.29684 | -0.30632 | -0.31579 | -0.32632 | -0.33579 | -0.34526 | -0.35368 | -0.36421 | -0.40316 | -0.45684 | -0.50737 | -0.34 | -0.34737 | -0.35684 | -0.36421 | -0.37368 | -0.38211 | -0.39053 | -0.4 | -0.40947 | -0.41789 | -0.45263 | -0.49263 | -0.53158
|  | LOCHGOILHEAD | HE |  |  |  |  | -0.23053 | -0.23895 | -0.24737 | -0.25684 | -0.26632 | -0.27684 | -0.28842 | -0.29789 | -0.30842 | -0.31789 | -0.35368 | -0.39684 | -0.43895 | -0.27684 | -0.28421 | -0.28842 | -0.29474 | -0.30211 | -0.31053 | -0.31789 | -0.32526 | -0.33053 | -0.33789 | -0.37263 | -0.41684 | -0.46105 | -0.33895 | -0.34737 | -0.35474 | -0.36211 | -0.37158 | -0.38 | -0.38947 | -0.39789 | -0.40632 | -0.41474 | -0.44421 | -0.48 | -0.51579
|  | LOCHGOILHEAD | FB |  |  |  |  | -0.22421 | -0.22737 | -0.22947 | -0.23263 | -0.23684 | -0.24105 | -0.24316 | -0.24737 | -0.25053 | -0.25474 | -0.27158 | -0.28737 | -0.30105 | -0.27263 | -0.27579 | -0.27789 | -0.28211 | -0.28421 | -0.28947 | -0.29158 | -0.29474 | -0.29895 | -0.30316 | -0.31895 | -0.33579 | -0.34947 | -0.33368 | -0.33579 | -0.33789 | -0.34 | -0.34316 | -0.34526 | -0.34632 | -0.34947 | -0.35158 | -0.35368 | -0.36316 | -0.37158 | -0.37789
| GRUDIE BRIDGE | LOCHINVER | MINIMUM HEADROOM | NC 09516 22243 | YES | NO | 0 | 0.89053 | 0.87895 | 0.86842 | 0.85579 | 0.84211 | 0.62211 | 0.47158 | 0.36421 | 0.30421 | 0.27579 | 0.14632 | 0.057895 | 0.0010526 | 0.86526 | 0.84 | 0.81474 | 0.78211 | 0.74737 | 0.51789 | 0.36 | 0.23789 | 0.16842 | 0.13684 | 0.0010526 | -0.10105 | -0.17789 | 0.82105 | 0.80947 | 0.79895 | 0.78632 | 0.77158 | 0.54632 | 0.36737 | 0.24 | 0.17053 | 0.13895 | 0.0042105 | -0.098947 | -0.17474
|  | LOCHINVER | EE |  |  |  |  | 0.89053 | 0.87895 | 0.86842 | 0.85579 | 0.84211 | 0.80842 | 0.77579 | 0.55158 | 0.40105 | 0.29158 | 0.15895 | 0.070526 | 0.0073684 | 0.86526 | 0.84 | 0.81474 | 0.78211 | 0.74737 | 0.71263 | 0.68 | 0.44316 | 0.28421 | 0.15368 | 0.0010526 | -0.10105 | -0.17474 | 0.82105 | 0.80947 | 0.79895 | 0.78632 | 0.77158 | 0.75474 | 0.73474 | 0.46526 | 0.28632 | 0.15579 | 0.0042105 | -0.098947 | -0.17158
|  | LOCHINVER | HT |  |  |  |  | 0.89263 | 0.88105 | 0.87053 | 0.85789 | 0.84211 | 0.62211 | 0.47158 | 0.36421 | 0.30421 | 0.27579 | 0.14632 | 0.057895 | 0.0010526 | 0.87263 | 0.84842 | 0.82737 | 0.8 | 0.76632 | 0.51789 | 0.36 | 0.23789 | 0.16842 | 0.13684 | 0.014737 | -0.093684 | -0.17789 | 0.82316 | 0.81263 | 0.80105 | 0.78737 | 0.77263 | 0.54632 | 0.36737 | 0.24 | 0.17053 | 0.13895 | 0.016842 | -0.090526 | -0.17474
|  | LOCHINVER | HE |  |  |  |  | 0.89789 | 0.88737 | 0.88105 | 0.87053 | 0.85895 | 0.84526 | 0.83263 | 0.63895 | 0.48842 | 0.39368 | 0.33368 | 0.28526 | 0.25474 | 0.88947 | 0.87158 | 0.85895 | 0.84211 | 0.82211 | 0.80316 | 0.78526 | 0.53474 | 0.37684 | 0.27368 | 0.20421 | 0.14842 | 0.11263 | 0.82842 | 0.81895 | 0.81263 | 0.80105 | 0.79053 | 0.77684 | 0.76316 | 0.56842 | 0.38947 | 0.27579 | 0.20632 | 0.15158 | 0.11474
|  | LOCHINVER | FB |  |  |  |  | 0.90316 | 0.89895 | 0.89474 | 0.89053 | 0.88632 | 0.88 | 0.87579 | 0.87053 | 0.80842 | 0.72737 | 0.56105 | 0.50211 | 0.45789 | 0.89895 | 0.88842 | 0.87895 | 0.86842 | 0.85579 | 0.84421 | 0.83368 | 0.82211 | 0.71158 | 0.62632 | 0.45158 | 0.39053 | 0.34421 | 0.83474 | 0.83053 | 0.82632 | 0.82211 | 0.81684 | 0.81158 | 0.80737 | 0.80105 | 0.76526 | 0.66737 | 0.46947 | 0.40211 | 0.34947
| LUNANHEAD | LOCHSIDE | MINIMUM HEADROOM | NO 45151 50548 | NO | YES | 6.102 | 24.9558 | 24.8642 | 24.7768 | 24.6442 | 24.5747 | 24.5105 | 24.4495 | 24.3274 | 24.1495 | 24.0653 | 22.8495 | 20.6147 | 20.28 | 23.16 | 23.0558 | 22.9568 | 22.8053 | 22.7284 | 22.6568 | 22.5884 | 22.4505 | 22.2463 | 22.1526 | 20.8137 | 18.3305 | 17.8505 | 24.2832 | 24.1779 | 24.0779 | 23.9253 | 23.8474 | 23.7747 | 23.7063 | 23.5674 | 23.3611 | 23.2663 | 21.9168 | 19.4105 | 18.9326
|  | LOCHSIDE | EE |  |  |  |  | 26.8179 | 26.7305 | 26.4642 | 26.2695 | 26.1295 | 25.9758 | 25.7274 | 25.3789 | 25.0611 | 24.9295 | 22.8495 | 21.4432 | 21.0884 | 25.4989 | 25.2379 | 24.9379 | 24.7168 | 24.5611 | 24.3926 | 24.1147 | 23.7168 | 23.3537 | 23.2074 | 20.8137 | 19.1926 | 18.7937 | 26.5053 | 26.3558 | 26.0842 | 25.86 | 25.7032 | 25.5337 | 25.2526 | 24.8495 | 24.4842 | 24.3358 | 21.9168 | 20.2789 | 19.8747
|  | LOCHSIDE | HT |  |  |  |  | 26.8263 | 26.6842 | 26.4705 | 26.18 | 26.0389 | 25.7874 | 25.3926 | 25.1389 | 24.7737 | 24.2495 | 22.9063 | 20.6147 | 20.28 | 25.5105 | 25.1874 | 24.9453 | 24.6137 | 24.4568 | 24.1716 | 23.72 | 23.4347 | 23.0168 | 22.4168 | 21.0137 | 18.3305 | 17.8505 | 26.5147 | 26.3358 | 26.0905 | 25.7558 | 25.5979 | 25.3105 | 24.8537 | 24.5653 | 24.1442 | 23.5368 | 22.1189 | 19.4105 | 18.9326
|  | LOCHSIDE | HE |  |  |  |  | 26.8411 | 26.7958 | 26.6632 | 26.4968 | 26.4147 | 26.3211 | 25.9968 | 25.7042 | 25.4505 | 25.3737 | 23.7011 | 22.5463 | 22.3653 | 25.5684 | 25.44 | 25.1653 | 24.9779 | 24.8905 | 24.7916 | 24.4242 | 24.0905 | 23.8011 | 23.7137 | 21.7789 | 20.4432 | 20.2368 | 26.5505 | 26.4653 | 26.3137 | 26.1242 | 26.0368 | 25.9368 | 25.5663 | 25.2284 | 24.9358 | 24.8484 | 22.8916 | 21.5411 | 21.3326
|  | LOCHSIDE | FB |  |  |  |  | 24.9558 | 24.8642 | 24.7768 | 24.6442 | 24.5747 | 24.5105 | 24.4495 | 24.3274 | 24.1495 | 24.0653 | 23.1937 | 22.2747 | 22.0274 | 23.16 | 23.0558 | 22.9568 | 22.8053 | 22.7284 | 22.6568 | 22.5884 | 22.4505 | 22.2463 | 22.1526 | 21.1516 | 20.0937 | 19.8116 | 24.2832 | 24.1779 | 24.0779 | 23.9253 | 23.8474 | 23.7747 | 23.7063 | 23.5674 | 23.3611 | 23.2663 | 22.2547 | 21.1842 | 20.8989
| BRIDGE OF DUN | LOGIE PERT | MINIMUM HEADROOM | NO 67764 64427 | YES | YES | 0 | 3.1926 | 3.1853 | 3.18 | 3.1716 | 3.1653 | 3.1579 | 3.1779 | 3.1758 | 3.1726 | 3.1705 | 0.52316 | 0.50632 | 0.49368 | 4.6295 | 4.6168 | 4.6042 | 4.5874 | 4.5737 | 4.5568 | 4.5716 | 4.5568 | 4.5432 | 4.5305 | 2.2937 | 2.2505 | 2.22 | 4.7105 | 4.6979 | 4.6853 | 4.6705 | 4.6547 | 4.64 | 4.6579 | 4.6432 | 4.6305 | 4.6179 | 1.7442 | 1.7032 | 1.6716
|  | LOGIE PERT | EE |  |  |  |  | 3.1926 | 3.1853 | 3.18 | 3.1716 | 3.1653 | 3.1579 | 3.2084 | 3.2 | 3.1937 | 3.1874 | 0.52316 | 0.50632 | 0.49368 | 4.6295 | 4.6168 | 4.6042 | 4.5874 | 4.5737 | 4.5568 | 4.5716 | 4.5568 | 4.5432 | 4.5305 | 2.2937 | 2.2505 | 2.22 | 4.7105 | 4.6979 | 4.6853 | 4.6705 | 4.6547 | 4.64 | 4.6579 | 4.6432 | 4.6305 | 4.6179 | 1.7442 | 1.7032 | 1.6716
|  | LOGIE PERT | HT |  |  |  |  | 3.1937 | 3.1884 | 3.1821 | 3.1768 | 3.2305 | 3.2242 | 3.22 | 3.2147 | 3.2095 | 3.2042 | 1.0695 | 1.0568 | 1.0474 | 4.6337 | 4.6232 | 4.6126 | 4.5989 | 4.6179 | 4.6042 | 4.5926 | 4.5811 | 4.5684 | 4.5568 | 2.7768 | 2.7368 | 2.7053 | 4.7147 | 4.7042 | 4.6937 | 4.6811 | 4.7032 | 4.6884 | 4.6789 | 4.6684 | 4.6558 | 4.6453 | 2.3432 | 2.3042 | 2.2716
|  | LOGIE PERT | HE |  |  |  |  | 3.1989 | 3.1958 | 3.1937 | 3.1916 | 3.1874 | 3.1832 | 3.1779 | 3.1758 | 3.1726 | 3.1705 | 2.1053 | 2.1011 | 2.0979 | 4.6442 | 4.6379 | 4.6326 | 4.6274 | 4.6211 | 4.6147 | 4.6074 | 4.6011 | 4.5937 | 4.5874 | 3.7084 | 3.6895 | 3.6758 | 4.7242 | 4.7179 | 4.7137 | 4.7084 | 4.7021 | 4.6968 | 4.6884 | 4.6832 | 4.6758 | 4.6695 | 3.5179 | 3.5 | 3.4874
|  | LOGIE PERT | FB |  |  |  |  | 3.2 | 3.1979 | 3.1968 | 3.1958 | 3.1947 | 3.1926 | 3.1916 | 3.1895 | 3.1884 | 3.1853 | 3.1789 | 3.1726 | 3.1695 | 4.6474 | 4.6432 | 4.6389 | 4.6347 | 4.6305 | 4.6263 | 4.6232 | 4.6179 | 4.6137 | 4.6063 | 4.5821 | 4.5589 | 4.5389 | 4.7274 | 4.7242 | 4.7189 | 4.7158 | 4.7116 | 4.7074 | 4.7042 | 4.7 | 4.6958 | 4.6884 | 4.6653 | 4.6432 | 4.6253
| MILTON OF CRAIGIE | LONGHAUGH | MINIMUM HEADROOM | NO 42768 33789 | NO | YES | 5.102 | 18.1426 | 17.1889 | 16.0058 | 14.9753 | 13.7847 | 13.5826 | 13.3826 | 13.2153 | 13.0553 | 12.8879 | 11.9153 | 11.4079 | 11.0721 | 17.4995 | 16.3984 | 15.0258 | 13.8237 | 12.43 | 12.2079 | 11.9879 | 11.8037 | 11.6268 | 11.4395 | 10.5132 | 9.8816 | 9.4068 | 17.8689 | 16.7563 | 15.3668 | 14.1616 | 12.7668 | 12.5447 | 12.3247 | 12.1395 | 11.9637 | 11.7753 | 10.8489 | 10.2184 | 9.7426
|  | LONGHAUGH | EE |  |  |  |  | 18.1753 | 17.1889 | 16.0058 | 14.9753 | 13.7847 | 13.5826 | 13.3826 | 13.2153 | 13.0553 | 12.8879 | 12.0826 | 11.5942 | 11.2563 | 17.5384 | 16.3984 | 15.0258 | 13.8237 | 12.43 | 12.2079 | 11.9879 | 11.8037 | 11.6268 | 11.4395 | 10.5332 | 9.9858 | 9.6058 | 17.9089 | 16.7563 | 15.3668 | 14.1616 | 12.7668 | 12.5447 | 12.3247 | 12.1395 | 11.9637 | 11.7753 | 10.87 | 10.3205 | 9.9405
|  | LONGHAUGH | HT |  |  |  |  | 18.1426 | 17.3111 | 16.0605 | 15.0384 | 13.8353 | 13.6753 | 13.5237 | 13.3721 | 13.2153 | 12.9163 | 11.9153 | 11.4079 | 11.0721 | 17.4995 | 16.5374 | 15.0889 | 13.8995 | 12.4921 | 12.3163 | 12.15 | 11.9847 | 11.8132 | 11.4763 | 10.5132 | 9.8816 | 9.4068 | 17.8689 | 16.8963 | 15.4321 | 14.2363 | 12.8289 | 12.6532 | 12.4868 | 12.3216 | 12.15 | 11.8132 | 10.8489 | 10.2184 | 9.7426
|  | LONGHAUGH | HE |  |  |  |  | 18.2121 | 17.4742 | 16.3279 | 15.3458 | 14.1911 | 14.0268 | 13.8826 | 13.7753 | 13.6637 | 13.5521 | 12.9721 | 12.6658 | 12.4826 | 17.5774 | 16.7258 | 15.3942 | 14.2532 | 12.9026 | 12.7237 | 12.57 | 12.4532 | 12.33 | 12.2037 | 11.5405 | 11.1942 | 10.9868 | 17.9479 | 17.0868 | 15.7395 | 14.5911 | 13.2395 | 13.0605 | 12.9068 | 12.79 | 12.6668 | 12.5405 | 11.8774 | 11.5311 | 11.3237
|  | LONGHAUGH | FB |  |  |  |  | 18.9016 | 18.7742 | 18.3784 | 18.0679 | 17.5837 | 17.2321 | 16.9711 | 16.7795 | 16.6616 | 16.5553 | 16.0647 | 15.5784 | 15.3363 | 18.5237 | 18.2321 | 17.7742 | 17.4153 | 16.8563 | 16.4511 | 16.15 | 15.9321 | 15.7984 | 15.6816 | 15.1289 | 14.5774 | 14.3037 | 18.9047 | 18.6111 | 18.1479 | 17.7847 | 17.2184 | 16.8089 | 16.5058 | 16.2847 | 16.15 | 16.0321 | 15.4742 | 14.9174 | 14.6416
| INVERNESS | LONGMAN DRIVE | MINIMUM HEADROOM | NH 67139 46770 | NO | YES | 0 | 25.9424 | 25.9 | 25.8553 | 25.7558 | 25.6866 | 25.6153 | 25.4904 | 25.2615 | 25.1374 | 24.5666 | 21.9392 | 21.6481 | 21.4914 | 25.2616 | 25.2215 | 25.1801 | 25.1014 | 25.0441 | 24.9739 | 24.791 | 24.571 | 24.4673 | 23.5771 | 20.6631 | 20.3968 | 20.275 | 25.9386 | 25.8729 | 25.7925 | 25.619 | 25.5107 | 25.3421 | 25.104 | 24.8089 | 24.6669 | 23.9652 | 20.8867 | 20.5512 | 20.3699
|  | LONGMAN DRIVE | EE |  |  |  |  | 25.9424 | 25.9 | 25.8553 | 25.7558 | 25.6866 | 25.6153 | 25.4904 | 25.2615 | 25.1374 | 25.0419 | 23.9154 | 23.7728 | 23.541 | 25.2616 | 25.2215 | 25.1801 | 25.1014 | 25.0441 | 24.9964 | 24.7966 | 24.571 | 24.4878 | 24.4173 | 23.3525 | 23.2876 | 23.0207 | 25.9386 | 25.8729 | 25.7925 | 25.619 | 25.5107 | 25.4128 | 25.104 | 24.8089 | 24.6669 | 24.5588 | 23.2509 | 23.2038 | 22.938
|  | LONGMAN DRIVE | HT |  |  |  |  | 25.949 | 25.9106 | 25.8702 | 25.7949 | 25.7227 | 25.6168 | 25.51 | 25.3309 | 25.2234 | 24.7942 | 24.0416 | 23.7376 | 23.5231 | 25.2694 | 25.2322 | 25.1923 | 25.1397 | 25.0802 | 24.9739 | 24.791 | 24.6345 | 24.5577 | 24.1374 | 23.6778 | 23.3198 | 23.0099 | 25.9457 | 25.8958 | 25.8258 | 25.7003 | 25.5879 | 25.3421 | 25.107 | 24.8886 | 24.7677 | 24.2689 | 23.601 | 23.234 | 22.9241
|  | LONGMAN DRIVE | HE |  |  |  |  | 25.9626 | 25.9305 | 25.9056 | 25.8457 | 25.8101 | 25.7561 | 25.6709 | 25.5736 | 25.498 | 25.4314 | 23.8885 | 23.8679 | 23.4474 | 25.284 | 25.2524 | 25.2276 | 25.1734 | 25.1377 | 25.0883 | 24.9798 | 24.8124 | 24.7553 | 24.7083 | 23.1229 | 23.2664 | 22.6604 | 25.9604 | 25.926 | 25.8994 | 25.7905 | 25.7358 | 25.6235 | 25.3973 | 25.1794 | 25.0856 | 25.0085 | 23.2038 | 23.2952 | 22.6313
|  | LONGMAN DRIVE | FB |  |  |  |  | 25.9703 | 25.9544 | 25.937 | 25.9081 | 25.8889 | 25.8692 | 25.8252 | 25.772 | 25.3386 | 24.5666 | 21.9392 | 21.6481 | 21.4914 | 25.2959 | 25.2799 | 25.2631 | 25.2371 | 25.2189 | 25.1998 | 25.1495 | 25.0902 | 24.4673 | 23.5771 | 20.6631 | 20.3968 | 20.275 | 25.9686 | 25.951 | 25.932 | 25.8998 | 25.8675 | 25.833 | 25.7076 | 25.5595 | 24.87 | 23.9652 | 20.8867 | 20.5512 | 20.3699
| ELGIN | LOSSIEMOUTH | MINIMUM HEADROOM | NJ 23203 69923 | NO | YES | 0 | 11.8558 | 11.8263 | 11.8021 | 11.7621 | 11.6442 | 11.5074 | 11.3758 | 11.2516 | 11.1316 | 11.0221 | 10.5453 | 10.2589 | 10.0389 | 11.6674 | 11.3505 | 11.2263 | 11.0779 | 10.9379 | 10.7768 | 10.6232 | 10.4768 | 10.3337 | 10.2032 | 9.6716 | 9.3432 | 9.0726 | 11.4779 | 11.3189 | 11.2074 | 11.0758 | 10.9495 | 10.7989 | 10.6421 | 10.4947 | 10.3495 | 10.22 | 9.6832 | 9.3568 | 9.0832
|  | LOSSIEMOUTH | EE |  |  |  |  | 11.8558 | 11.8263 | 11.8021 | 11.7621 | 11.6442 | 11.5074 | 11.3758 | 11.2516 | 11.1316 | 11.0221 | 10.5779 | 10.2842 | 10.0579 | 11.6674 | 11.3505 | 11.2263 | 11.0779 | 10.9379 | 10.7768 | 10.6232 | 10.4768 | 10.3337 | 10.2032 | 9.6716 | 9.3432 | 9.0895 | 11.4779 | 11.3189 | 11.2074 | 11.0758 | 10.9495 | 10.7989 | 10.6421 | 10.4947 | 10.3495 | 10.22 | 9.6832 | 9.3568 | 9.1
|  | LOSSIEMOUTH | HT |  |  |  |  | 11.8621 | 11.8347 | 11.8032 | 11.7695 | 11.6821 | 11.5558 | 11.4295 | 11.3032 | 11.1716 | 11.0516 | 10.5453 | 10.2589 | 10.0389 | 11.6747 | 11.3937 | 11.2716 | 11.1358 | 10.9874 | 10.8379 | 10.6884 | 10.5368 | 10.3821 | 10.2411 | 9.7379 | 9.3821 | 9.0726 | 11.4842 | 11.3579 | 11.2474 | 11.1253 | 10.9916 | 10.8568 | 10.7084 | 10.5568 | 10.4 | 10.2568 | 9.7558 | 9.3958 | 9.0832
|  | LOSSIEMOUTH | HE |  |  |  |  | 11.8705 | 11.8421 | 11.82 | 11.7905 | 11.7558 | 11.7095 | 11.6316 | 11.5368 | 11.4421 | 11.3705 | 11.0589 | 10.8884 | 10.7842 | 11.6863 | 11.4811 | 11.3926 | 11.2895 | 11.1853 | 11.0653 | 10.9421 | 10.8305 | 10.7179 | 10.6295 | 10.2505 | 10.0442 | 9.9179 | 11.4926 | 11.4347 | 11.3547 | 11.2621 | 11.1663 | 11.0568 | 10.9432 | 10.8421 | 10.74 | 10.6495 | 10.2674 | 10.0589 | 9.9316
|  | LOSSIEMOUTH | FB |  |  |  |  | 11.8874 | 11.8758 | 11.8642 | 11.8516 | 11.8368 | 11.8232 | 11.8084 | 11.7926 | 11.7768 | 11.7263 | 11.4547 | 11.2432 | 11.1011 | 11.7042 | 11.5684 | 11.5126 | 11.4537 | 11.3947 | 11.3316 | 11.2642 | 11.1968 | 11.1189 | 11.0358 | 10.7084 | 10.4537 | 10.2811 | 11.5095 | 11.4979 | 11.4653 | 11.4116 | 11.3589 | 11.3021 | 11.2421 | 11.1811 | 11.1116 | 11.0379 | 10.7284 | 10.4716 | 10.2968
| BROADFORD | LOWER OLLACH | MINIMUM HEADROOM | NG 51241 37001 | YES | YES | 0 | 0.99263 | 0.98632 | 0.98 | 0.97263 | 0.96421 | 0.95579 | 0.94526 | 0.93895 | 0.93053 | 0.92316 | 0.89579 | 0.87263 | 0.85579 | 0.93263 | 0.91789 | 0.90316 | 0.88421 | 0.86842 | 0.85158 | 0.83368 | 0.81895 | 0.80316 | 0.78842 | 0.73579 | 0.68632 | 0.64947 | 0.95368 | 0.94105 | 0.92947 | 0.91474 | 0.9 | 0.88526 | 0.87053 | 0.85789 | 0.84421 | 0.83053 | 0.78526 | 0.74316 | 0.71053
|  | LOWER OLLACH | EE |  |  |  |  | 0.99263 | 0.98632 | 0.98 | 0.97263 | 0.96421 | 0.95579 | 0.94526 | 0.93895 | 0.93053 | 0.92316 | 0.89579 | 0.87263 | 0.85579 | 0.93263 | 0.91789 | 0.90316 | 0.88421 | 0.86842 | 0.85158 | 0.83368 | 0.81895 | 0.80316 | 0.78842 | 0.73579 | 0.68632 | 0.64947 | 0.95368 | 0.94105 | 0.92947 | 0.91474 | 0.9 | 0.88526 | 0.87053 | 0.85789 | 0.84421 | 0.83053 | 0.78526 | 0.74316 | 0.71053
|  | LOWER OLLACH | HT |  |  |  |  | 0.99579 | 0.99053 | 0.98526 | 0.98 | 0.97368 | 0.96842 | 0.96 | 0.95474 | 0.94737 | 0.94 | 0.91474 | 0.89789 | 0.88421 | 0.93895 | 0.92316 | 0.91053 | 0.89895 | 0.87895 | 0.86316 | 0.84737 | 0.83263 | 0.81684 | 0.80105 | 0.74316 | 0.69158 | 0.64947 | 0.95895 | 0.94842 | 0.93789 | 0.92737 | 0.91368 | 0.90105 | 0.88842 | 0.87579 | 0.86316 | 0.85158 | 0.80632 | 0.76632 | 0.73263
|  | LOWER OLLACH | HE |  |  |  |  | 0.99684 | 0.99368 | 0.98947 | 0.98421 | 0.97789 | 0.97158 | 0.96316 | 0.96 | 0.95368 | 0.95158 | 0.94 | 0.93053 | 0.92316 | 0.94737 | 0.93895 | 0.93053 | 0.92211 | 0.91158 | 0.90105 | 0.89158 | 0.88316 | 0.87263 | 0.86737 | 0.83789 | 0.81263 | 0.79579 | 0.96421 | 0.95895 | 0.95158 | 0.94316 | 0.93579 | 0.92526 | 0.91684 | 0.90947 | 0.9 | 0.89579 | 0.87368 | 0.85158 | 0.83684
|  | LOWER OLLACH | FB |  |  |  |  | 1.0011 | 0.99789 | 0.99684 | 0.99474 | 0.99263 | 0.99158 | 0.98947 | 0.98737 | 0.98526 | 0.98316 | 0.97368 | 0.96632 | 0.96105 | 0.95368 | 0.94737 | 0.94211 | 0.93579 | 0.92947 | 0.92316 | 0.91684 | 0.91158 | 0.90316 | 0.89579 | 0.86632 | 0.83684 | 0.80947 | 0.97053 | 0.96526 | 0.96105 | 0.95684 | 0.95158 | 0.94842 | 0.94316 | 0.93895 | 0.93368 | 0.92842 | 0.90632 | 0.88421 | 0.86632
| KILLIN | LUBNAIG | MINIMUM HEADROOM | NN 57455 13800 | YES | YES | 0 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19789 | 0.19789 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19789 | 0.19789
|  | LUBNAIG | EE |  |  |  |  | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19789 | 0.19789 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19789 | 0.19789
|  | LUBNAIG | HT |  |  |  |  | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.19789 | 0.19789 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.19789 | 0.19789
|  | LUBNAIG | HE |  |  |  |  | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2
|  | LUBNAIG | FB |  |  |  |  | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.2
| LUNANHEAD | LUNANHEAD | MINIMUM HEADROOM | NO 47042 51733 | NO | YES | 0.98776 | 13.6995 | 13.6026 | 13.5142 | 13.41 | 13.3163 | 13.21 | 13.1037 | 12.9921 | 12.8268 | 12.7216 | 8.2468 | -0.25211 | -5.4047 | 12.4421 | 12.3326 | 12.2316 | 12.1126 | 12.0074 | 11.8905 | 11.7737 | 11.6432 | 11.4516 | 11.3337 | 6.3632 | -1.4632 | -9.0421 | 12.8792 | 12.7687 | 12.6666 | 12.5476 | 12.4424 | 12.3234 | 12.2066 | 12.0803 | 11.8897 | 11.7708 | 6.6329 | -1.5408 | -9.0934
|  | LUNANHEAD | EE |  |  |  |  | 13.6995 | 13.6026 | 13.5142 | 13.41 | 13.3163 | 13.21 | 13.1037 | 12.9921 | 12.8711 | 12.7826 | 8.2468 | 3.4005 | -0.30579 | 12.4421 | 12.3326 | 12.2316 | 12.1126 | 12.0074 | 11.8905 | 11.7737 | 11.6484 | 11.5105 | 11.4116 | 6.3632 | 1.56 | -2.7916 | 12.8792 | 12.7687 | 12.6666 | 12.5476 | 12.4424 | 12.3234 | 12.2066 | 12.0813 | 11.9434 | 11.8434 | 6.6329 | 1.3224 | -3.0197
|  | LUNANHEAD | HT |  |  |  |  | 13.73 | 13.6437 | 13.5584 | 13.4658 | 13.37 | 13.2753 | 13.1395 | 12.9942 | 12.8268 | 12.7216 | 11.7163 | -0.25211 | -5.4047 | 12.4768 | 12.3768 | 12.2811 | 12.1779 | 12.0716 | 11.9663 | 11.8105 | 11.6432 | 11.4516 | 11.3337 | 10.5032 | -1.4632 | -9.0368 | 12.9139 | 12.8161 | 12.7203 | 12.6161 | 12.5097 | 12.4034 | 12.2476 | 12.0803 | 11.8897 | 11.7708 | 10.8045 | -1.5408 | -9.0934
|  | LUNANHEAD | HE |  |  |  |  | 13.79 | 13.7279 | 13.6753 | 13.6142 | 13.5542 | 13.4826 | 13.4089 | 13.3332 | 13.2395 | 13.19 | 9.2237 | 5.7942 | 2.2005 | 12.5474 | 12.4779 | 12.4168 | 12.3516 | 12.2863 | 12.2105 | 12.1316 | 12.0463 | 11.9411 | 11.8832 | 7.3032 | 3.6284 | -0.59789 | 12.9845 | 12.9161 | 12.855 | 12.7887 | 12.7234 | 12.6466 | 12.5676 | 12.4824 | 12.3782 | 12.3192 | 7.6845 | 3.8108 | -0.40395
|  | LUNANHEAD | FB |  |  |  |  | 13.8237 | 13.7826 | 13.7416 | 13.7005 | 13.6584 | 13.6174 | 13.5763 | 13.5342 | 13.4826 | 13.4268 | 10.6174 | 8.2542 | -4.5374 | 12.5832 | 12.5368 | 12.4905 | 12.4442 | 12.3968 | 12.3505 | 12.3032 | 12.2558 | 12.1958 | 12.1316 | 8.7947 | 6.0211 | -9.0421 | 13.0213 | 12.975 | 12.9276 | 12.8813 | 12.8339 | 12.7876 | 12.7403 | 12.6939 | 12.6339 | 12.5708 | 9.2434 | 6.4771 | -8.5408
| PORT ANN | LUSSAGIVEN | MINIMUM HEADROOM | NR 63461 86798 | YES | YES | 0 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.096842 | 0.10421 | 0.10421 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.10421 | 0.10421 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.098947 | 0.097895 | 0.097895
|  | LUSSAGIVEN | EE |  |  |  |  | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.10421 | 0.10421 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.097895 | 0.097895 | 0.10421 | 0.10421 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.1 | 0.097895 | 0.097895
|  | LUSSAGIVEN | HT |  |  |  |  | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.096842 | 0.10421 | 0.10421 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.10421 | 0.10421 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.098947 | 0.097895 | 0.097895
|  | LUSSAGIVEN | HE |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105
|  | LUSSAGIVEN | FB |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211
| LYNDHURST | LYNDHURST | MINIMUM HEADROOM | NO 37434 32575 | NO | YES | 0 | 16.0058 | 15.9868 | 15.9721 | 15.9532 | 15.9342 | 15.9089 | 15.8805 | 15.8605 | 15.8405 | 15.8216 | 9.6616 | 3.4511 | -1.1016 | 14.8011 | 14.7821 | 14.7684 | 14.7274 | 14.6874 | 14.64 | 14.5811 | 14.5337 | 14.4853 | 14.4253 | 7.9389 | -0.22737 | -5.6137 | 15.3266 | 15.3076 | 15.2939 | 15.2761 | 15.2529 | 15.1897 | 15.1276 | 15.0834 | 15.0403 | 14.9855 | 8.6171 | 0.47605 | -4.8934
|  | LYNDHURST | EE |  |  |  |  | 16.0058 | 15.9868 | 15.9721 | 15.9532 | 15.9342 | 15.9089 | 15.8805 | 15.8605 | 15.8405 | 15.8226 | 14.4363 | 13.4037 | 12.0511 | 14.8011 | 14.7821 | 14.7684 | 14.7274 | 14.6874 | 14.64 | 14.5811 | 14.5337 | 14.4853 | 14.4253 | 12.7547 | 11.5632 | 9.9842 | 15.3266 | 15.3076 | 15.2939 | 15.2761 | 15.2529 | 15.1897 | 15.1276 | 15.0834 | 15.0403 | 14.9855 | 13.3929 | 12.1982 | 10.6297
|  | LYNDHURST | HT |  |  |  |  | 16.0089 | 15.9921 | 15.9753 | 15.9542 | 15.9342 | 15.9132 | 15.8932 | 15.8711 | 15.85 | 15.8216 | 9.6616 | 5.9489 | 4.0858 | 14.8032 | 14.7874 | 14.7716 | 14.7463 | 14.7042 | 14.6674 | 14.6326 | 14.5968 | 14.5484 | 14.4389 | 8.5789 | 3.3105 | 0.56 | 15.3297 | 15.3139 | 15.2971 | 15.2771 | 15.2571 | 15.2329 | 15.1887 | 15.1424 | 15.095 | 14.9971 | 9.2497 | 4.0034 | 1.2613
|  | LYNDHURST | HE |  |  |  |  | 16.0132 | 15.9984 | 15.9879 | 15.97 | 15.9511 | 15.9279 | 15.9037 | 15.8868 | 15.8711 | 15.8616 | 14.7079 | 13.7395 | 12.4416 | 14.8074 | 14.7926 | 14.7832 | 14.7663 | 14.7474 | 14.7242 | 14.7 | 14.6768 | 14.6537 | 14.6263 | 13.0611 | 11.9411 | 10.4305 | 15.3339 | 15.3182 | 15.3087 | 15.2918 | 15.2729 | 15.2497 | 15.2255 | 15.2087 | 15.1939 | 15.1845 | 13.7013 | 12.5782 | 11.0697
|  | LYNDHURST | FB |  |  |  |  | 16.0311 | 16.0226 | 16.0142 | 16.0047 | 15.9953 | 15.9858 | 15.9753 | 15.9668 | 15.9574 | 15.9458 | 10.3542 | 3.4511 | -1.1016 | 14.8232 | 14.8147 | 14.8074 | 14.7979 | 14.7895 | 14.78 | 14.7705 | 14.7621 | 14.7526 | 14.7411 | 7.9389 | -0.22737 | -5.6137 | 15.3497 | 15.3413 | 15.3329 | 15.3245 | 15.315 | 15.3066 | 15.2961 | 15.2876 | 15.2782 | 15.2666 | 8.6171 | 0.47605 | -4.8934
| THURSO | LYNESS | MINIMUM HEADROOM | ND 30350 94625 | YES | YES | 0 | 1.0095 | 1.0042 | 0.99789 | 0.98737 | 0.98 | 0.97053 | 0.96105 | 0.95263 | 0.94421 | 0.93579 | 0.90526 | 0.88 | 0.86211 | 0.99579 | 0.99368 | 0.98842 | 0.97579 | 0.96737 | 0.95684 | 0.94632 | 0.93684 | 0.92842 | 0.91789 | 0.88737 | 0.85684 | 0.83368 | 0.98526 | 0.98 | 0.97263 | 0.96316 | 0.95579 | 0.94737 | 0.93789 | 0.93053 | 0.92316 | 0.91474 | 0.88842 | 0.85789 | 0.83474
|  | LYNESS | EE |  |  |  |  | 1.0095 | 1.0042 | 0.99789 | 0.98737 | 0.98 | 0.97053 | 0.96105 | 0.95263 | 0.94421 | 0.93579 | 0.90842 | 0.88211 | 0.86211 | 0.99579 | 0.99368 | 0.98842 | 0.97579 | 0.96737 | 0.95684 | 0.94632 | 0.93684 | 0.92842 | 0.91789 | 0.88737 | 0.85684 | 0.83368 | 0.98526 | 0.98 | 0.97263 | 0.96316 | 0.95579 | 0.94737 | 0.93789 | 0.93053 | 0.92316 | 0.91474 | 0.88842 | 0.85789 | 0.83474
|  | LYNESS | HT |  |  |  |  | 1.0116 | 1.0053 | 1.0011 | 0.99263 | 0.98421 | 0.97579 | 0.96632 | 0.95789 | 0.94947 | 0.94105 | 0.90526 | 0.88 | 0.86316 | 0.99684 | 0.99368 | 0.99158 | 0.98316 | 0.97368 | 0.96421 | 0.95368 | 0.94421 | 0.93474 | 0.92421 | 0.89158 | 0.86 | 0.83579 | 0.98842 | 0.98105 | 0.97579 | 0.96842 | 0.96 | 0.95263 | 0.94316 | 0.93579 | 0.92737 | 0.91895 | 0.89158 | 0.86105 | 0.83684
|  | LYNESS | HE |  |  |  |  | 1.0147 | 1.0105 | 1.0063 | 1.0032 | 0.99895 | 0.99474 | 0.98947 | 0.98421 | 0.97895 | 0.97368 | 0.95789 | 0.94526 | 0.93579 | 0.99789 | 0.99474 | 0.99263 | 0.99053 | 0.98737 | 0.98421 | 0.98 | 0.97579 | 0.96842 | 0.96316 | 0.94526 | 0.92947 | 0.91895 | 0.99368 | 0.98842 | 0.98316 | 0.98 | 0.97474 | 0.96947 | 0.96421 | 0.96 | 0.95368 | 0.94947 | 0.93474 | 0.92316 | 0.91368
|  | LYNESS | FB |  |  |  |  | 1.0158 | 1.0147 | 1.0116 | 1.0095 | 1.0074 | 1.0042 | 1.0021 | 0.99895 | 0.99579 | 0.99053 | 0.97263 | 0.95368 | 0.94105 | 0.99789 | 0.99789 | 0.99684 | 0.99579 | 0.99474 | 0.99263 | 0.99158 | 0.98947 | 0.98632 | 0.98 | 0.96 | 0.93684 | 0.92211 | 0.99474 | 0.99263 | 0.98947 | 0.98632 | 0.98316 | 0.98 | 0.97684 | 0.97368 | 0.97053 | 0.96632 | 0.94947 | 0.93158 | 0.92
| STORNOWAY | MAARUIG | MINIMUM HEADROOM | NB 19162 06332 | YES | YES | 0 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19789 | 0.19684 | 0.19684 | 0.19684 | 0.19579 | 0.19474 | 0.19368 | 0.19263 | 0.19158 | 0.19789 | 0.19684 | 0.19684 | 0.19474 | 0.19474 | 0.19368 | 0.19158 | 0.19158 | 0.19053 | 0.18842 | 0.18632 | 0.18316 | 0.18105 | 0.21263 | 0.21263 | 0.21158 | 0.20947 | 0.20947 | 0.20842 | 0.20632 | 0.20632 | 0.20526 | 0.20421 | 0.20211 | 0.19895 | 0.19684
|  | MAARUIG | EE |  |  |  |  | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19789 | 0.19789 | 0.19684 | 0.19684 | 0.19684 | 0.19474 | 0.19474 | 0.19368 | 0.19263 | 0.19789 | 0.19684 | 0.19684 | 0.19474 | 0.19474 | 0.19368 | 0.19158 | 0.19158 | 0.19053 | 0.18842 | 0.18632 | 0.18421 | 0.18211 | 0.21263 | 0.21263 | 0.21158 | 0.20947 | 0.20947 | 0.20842 | 0.20632 | 0.20632 | 0.20632 | 0.20421 | 0.20211 | 0.19895 | 0.19789
|  | MAARUIG | HT |  |  |  |  | 0.2 | 0.19895 | 0.19895 | 0.19789 | 0.19789 | 0.19789 | 0.19684 | 0.19684 | 0.19579 | 0.19579 | 0.19368 | 0.19263 | 0.19158 | 0.19895 | 0.19684 | 0.19684 | 0.19579 | 0.19474 | 0.19474 | 0.19263 | 0.19263 | 0.19053 | 0.19053 | 0.18632 | 0.18316 | 0.18105 | 0.21368 | 0.21263 | 0.21158 | 0.21053 | 0.20947 | 0.20947 | 0.20737 | 0.20737 | 0.20526 | 0.20526 | 0.20211 | 0.19895 | 0.19684
|  | MAARUIG | HE |  |  |  |  | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19684 | 0.19684 | 0.19684 | 0.19579 | 0.19579 | 0.19579 | 0.19579 | 0.19474 | 0.2 | 0.19789 | 0.19789 | 0.19684 | 0.19684 | 0.19474 | 0.19474 | 0.19474 | 0.19368 | 0.19263 | 0.19158 | 0.19053 | 0.18947 | 0.21368 | 0.21263 | 0.21263 | 0.21263 | 0.21263 | 0.21053 | 0.20947 | 0.20947 | 0.20842 | 0.20737 | 0.20632 | 0.20526 | 0.20421
|  | MAARUIG | FB |  |  |  |  | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19789 | 0.19684 | 0.19684 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.19684 | 0.19684 | 0.19684 | 0.19684 | 0.19579 | 0.19368 | 0.19158 | 0.19053 | 0.21368 | 0.21368 | 0.21368 | 0.21263 | 0.21263 | 0.21263 | 0.21263 | 0.21158 | 0.21158 | 0.21053 | 0.20842 | 0.20632 | 0.20632
| LYNDHURST | MACALPINE ROAD | MINIMUM HEADROOM | NO 38034 33691 | NO | YES | 0 | -7.1842 | -7.3253 | -7.3979 | -7.4779 | -7.6263 | -7.7358 | -7.8453 | -7.9379 | -8.0326 | -8.14 | -8.5568 | -8.8158 | -8.9926 | 14.5116 | 14.2232 | 14.0958 | 13.9568 | 13.6621 | 13.4884 | 13.3221 | 13.1726 | 13.0158 | 12.8389 | 12.2411 | 11.7389 | 11.3642 | 15.8642 | 15.5968 | 15.4779 | 15.3463 | 15.0726 | 14.9084 | 14.7516 | 14.6105 | 14.4632 | 14.2947 | 13.7453 | 13.2737 | 12.9232
|  | MACALPINE ROAD | EE |  |  |  |  | -7.1842 | -7.3253 | -7.3979 | -7.4779 | -7.6263 | -7.7358 | -7.8453 | -7.9379 | -8.0326 | -8.1179 | -8.4453 | -8.7011 | -8.8768 | 14.5116 | 14.2232 | 14.0958 | 13.9568 | 13.6621 | 13.4884 | 13.3221 | 13.1726 | 13.0158 | 12.8695 | 12.3063 | 11.8505 | 11.5347 | 15.8642 | 15.5968 | 15.4779 | 15.3463 | 15.0726 | 14.9084 | 14.7516 | 14.6105 | 14.4632 | 14.3253 | 13.8074 | 13.3811 | 13.0842
|  | MACALPINE ROAD | HT |  |  |  |  | -7.1621 | -7.2947 | -7.3705 | -7.4526 | -7.6074 | -7.6968 | -7.7989 | -7.9084 | -8.0274 | -8.14 | -8.5568 | -8.8158 | -8.9926 | 14.5537 | 14.2842 | 14.1621 | 14.0305 | 13.7253 | 13.5853 | 13.4137 | 13.2274 | 13.02 | 12.8389 | 12.2411 | 11.7389 | 11.3642 | 15.9032 | 15.6537 | 15.5379 | 15.4147 | 15.1305 | 14.9979 | 14.8358 | 14.6611 | 14.4674 | 14.2947 | 13.7453 | 13.2737 | 12.9232
|  | MACALPINE ROAD | HE |  |  |  |  | -7.1168 | -7.2337 | -7.28 | -7.3411 | -7.4705 | -7.5632 | -7.6474 | -7.7126 | -7.7863 | -7.8368 | -8.0663 | -8.2158 | -8.3084 | 14.6453 | 14.4126 | 14.3379 | 14.2495 | 13.9968 | 13.8642 | 13.7568 | 13.6537 | 13.5337 | 13.4379 | 13 | 12.7221 | 12.5495 | 15.9874 | 15.7726 | 15.7011 | 15.6179 | 15.3821 | 15.2558 | 15.1526 | 15.0537 | 14.9411 | 14.8516 | 14.4442 | 14.1853 | 14.0242
|  | MACALPINE ROAD | FB |  |  |  |  | -7.0758 | -7.1653 | -7.2011 | -7.2379 | -7.2884 | -7.3368 | -7.3853 | -7.4263 | -7.4705 | -7.5221 | -7.7232 | -7.9021 | -8.0158 | 14.7189 | 14.5168 | 14.4537 | 14.3905 | 14.2958 | 14.2053 | 14.1158 | 14.0484 | 13.9726 | 13.8821 | 13.5179 | 13.1842 | 12.9568 | 16.0568 | 15.8716 | 15.8126 | 15.7526 | 15.6642 | 15.58 | 15.4968 | 15.4326 | 15.3621 | 15.2768 | 14.9368 | 14.6253 | 14.4147
| MACDUFF | MACDUFF | MINIMUM HEADROOM | NJ 70363 63908 | NO | YES | 0.019388 | 20.9463 | 20.5242 | 20.0474 | 19.44 | 18.6095 | 17.7484 | 16.8758 | 16.5453 | 16.1779 | 15.5958 | 4.2116 | 2.1084 | 1.5937 | 17.6368 | 16.9589 | 16.36 | 15.5968 | 14.5484 | 13.4695 | 12.3895 | 12.0126 | 11.5916 | 10.9189 | 4.4189 | -0.74842 | -1.5021 | 18.8842 | 18.2505 | 17.6916 | 16.98 | 16.0053 | 14.9979 | 13.9905 | 13.6358 | 13.24 | 12.6095 | 5.2695 | -1.3474 | -2.0568
|  | MACDUFF | EE |  |  |  |  | 20.9463 | 20.5242 | 20.0474 | 19.44 | 18.6095 | 17.7484 | 16.8758 | 16.5453 | 16.1779 | 15.9958 | 11.9768 | 7.8842 | 21.6368 | 17.6368 | 16.9589 | 16.36 | 15.5968 | 14.5484 | 13.4695 | 12.3895 | 12.0126 | 11.5916 | 11.3863 | 6.9705 | 3.4832 | 24.0495 | 18.8842 | 18.2505 | 17.6916 | 16.98 | 16.0053 | 14.9979 | 13.9905 | 13.6358 | 13.24 | 13.0463 | 8.6726 | 4.3726 | 25.6989
|  | MACDUFF | HT |  |  |  |  | 20.9537 | 20.6316 | 20.1358 | 19.5453 | 18.7063 | 18.5042 | 18.0663 | 17.5842 | 16.6168 | 15.5958 | 4.2116 | 2.1084 | 1.5937 | 17.6547 | 17.0937 | 16.4737 | 15.7337 | 14.6768 | 14.4379 | 13.8958 | 13.2989 | 12.1084 | 10.9189 | 4.4189 | -0.74842 | -1.5021 | 18.9 | 18.3768 | 17.7968 | 17.1074 | 16.1211 | 15.8937 | 15.3863 | 14.8274 | 13.7179 | 12.6095 | 5.2695 | -1.3474 | -2.0568
|  | MACDUFF | HE |  |  |  |  | 20.9726 | 20.7832 | 20.36 | 19.8411 | 19.0874 | 18.3095 | 17.5168 | 17.3221 | 17.0968 | 16.9947 | 12.6821 | 8.7853 | 22.6147 | 17.7547 | 17.2821 | 16.7505 | 16.1 | 15.1516 | 14.1758 | 13.1832 | 12.9484 | 12.6758 | 12.5495 | 8.2516 | 4.8463 | 24.0674 | 18.9947 | 18.5526 | 18.0579 | 17.4495 | 16.5663 | 15.6558 | 14.7295 | 14.5084 | 14.2505 | 14.1326 | 9.4905 | 5.4211 | 25.4116
|  | MACDUFF | FB |  |  |  |  | 21.0021 | 20.9821 | 20.9611 | 20.9379 | 20.8432 | 20.5021 | 20.0884 | 19.5958 | 19.4832 | 19.3737 | 18.5758 | 17.2232 | 16.6832 | 18.3884 | 18.1779 | 17.9232 | 17.7095 | 17.3621 | 16.9316 | 16.4084 | 15.7842 | 15.6484 | 15.5158 | 14.5242 | 12.8158 | 12.1695 | 19.5842 | 19.3884 | 19.1505 | 18.9505 | 18.6263 | 18.2253 | 17.7379 | 17.1579 | 17.0295 | 16.9042 | 15.9768 | 14.3863 | 13.7832
| CARRADALE 1 | MACHRIE | MINIMUM HEADROOM | NR 90092 33864 | YES | YES | 0 | 2.44 | 2.4021 | 2.3821 | 2.3611 | 2.3421 | 2.3179 | 2.2947 | 2.2768 | 2.2568 | 2.2389 | 2.1653 | 2.1074 | 2.0695 | 2.6768 | 2.6337 | 2.6105 | 2.5874 | 2.5663 | 2.54 | 2.5147 | 2.4947 | 2.4737 | 2.4537 | 2.3832 | 2.3189 | 2.2684 | 2.4611 | 2.4358 | 2.4221 | 2.4074 | 2.3926 | 2.3747 | 2.3558 | 2.3421 | 2.3274 | 2.3137 | 2.2653 | 2.22 | 2.1832
|  | MACHRIE | EE |  |  |  |  | 2.44 | 2.4021 | 2.3821 | 2.3611 | 2.3421 | 2.3179 | 2.2947 | 2.2768 | 2.2568 | 2.2389 | 2.1747 | 2.1168 | 2.0768 | 2.6768 | 2.6337 | 2.6105 | 2.5874 | 2.5663 | 2.54 | 2.5147 | 2.4947 | 2.4737 | 2.4537 | 2.3832 | 2.3189 | 2.2737 | 2.4611 | 2.4358 | 2.4221 | 2.4074 | 2.3926 | 2.3747 | 2.3558 | 2.3421 | 2.3274 | 2.3137 | 2.2653 | 2.2232 | 2.1958
|  | MACHRIE | HT |  |  |  |  | 2.4463 | 2.4095 | 2.3905 | 2.3716 | 2.3495 | 2.3284 | 2.3095 | 2.2905 | 2.2695 | 2.2495 | 2.1653 | 2.1074 | 2.0695 | 2.6842 | 2.6421 | 2.6211 | 2.6 | 2.5758 | 2.5526 | 2.5326 | 2.5116 | 2.4884 | 2.4663 | 2.3916 | 2.3221 | 2.2684 | 2.4653 | 2.44 | 2.4263 | 2.4126 | 2.3958 | 2.3789 | 2.3663 | 2.3505 | 2.3347 | 2.3179 | 2.2653 | 2.22 | 2.1832
|  | MACHRIE | HE |  |  |  |  | 2.4674 | 2.4421 | 2.4137 | 2.4011 | 2.3884 | 2.3737 | 2.3579 | 2.3463 | 2.3316 | 2.3232 | 2.2863 | 2.2568 | 2.2379 | 2.7074 | 2.68 | 2.6474 | 2.6337 | 2.62 | 2.6042 | 2.5874 | 2.5747 | 2.5589 | 2.5495 | 2.5095 | 2.4758 | 2.4547 | 2.4779 | 2.4611 | 2.4432 | 2.4326 | 2.4221 | 2.4105 | 2.3968 | 2.3874 | 2.3758 | 2.3695 | 2.3432 | 2.3221 | 2.3084
|  | MACHRIE | FB |  |  |  |  | 2.4779 | 2.4653 | 2.4474 | 2.4389 | 2.4295 | 2.42 | 2.4116 | 2.4021 | 2.3926 | 2.3811 | 2.3411 | 2.3011 | 2.2705 | 2.72 | 2.7053 | 2.6853 | 2.6758 | 2.6653 | 2.6547 | 2.6453 | 2.6347 | 2.6242 | 2.6116 | 2.5674 | 2.5221 | 2.4874 | 2.4853 | 2.4768 | 2.4663 | 2.4589 | 2.4526 | 2.4463 | 2.44 | 2.4326 | 2.4263 | 2.4179 | 2.3895 | 2.3611 | 2.3421
| FORT WILLIAM | MALLAIG | MINIMUM HEADROOM | NM 67637 94811 | YES | NO | 0 | 1.6097 | 1.5918 | 1.575 | 1.5539 | 1.5329 | 1.2624 | 0.82342 | 0.20868 | -0.070263 | -0.13237 | -0.32079 | -0.39342 | -0.44395 | 1.7518 | 1.7329 | 1.715 | 1.6908 | 1.6666 | 1.355 | 0.84658 | 0.135 | -0.18816 | -0.25974 | -0.46816 | -0.53974 | -0.61132 | 1.8771 | 1.8571 | 1.8392 | 1.8161 | 1.7908 | 1.4761 | 0.96132 | 0.24132 | -0.085 | -0.15763 | -0.36816 | -0.44079 | -0.51237
|  | MALLAIG | EE |  |  |  |  | 1.6097 | 1.5918 | 1.575 | 1.5539 | 1.5329 | 1.5087 | 1.4845 | 1.215 | 0.77711 | 0.14447 | -0.31553 | -0.37974 | -0.42289 | 1.7518 | 1.7329 | 1.715 | 1.6908 | 1.6666 | 1.6403 | 1.615 | 1.3034 | 0.795 | 0.062368 | -0.46816 | -0.53974 | -0.58816 | 1.8771 | 1.8571 | 1.8392 | 1.8161 | 1.7908 | 1.7645 | 1.7382 | 1.4234 | 0.90974 | 0.16868 | -0.36816 | -0.44079 | -0.49026
|  | MALLAIG | HT |  |  |  |  | 1.615 | 1.5982 | 1.5834 | 1.5645 | 1.5434 | 1.2624 | 0.82342 | 0.20868 | -0.070263 | -0.13237 | -0.32079 | -0.39342 | -0.44395 | 1.7592 | 1.7403 | 1.7234 | 1.7034 | 1.6803 | 1.355 | 0.84658 | 0.135 | -0.18816 | -0.25974 | -0.45342 | -0.53868 | -0.61132 | 1.8834 | 1.8655 | 1.8487 | 1.8287 | 1.8045 | 1.4761 | 0.96132 | 0.24132 | -0.085 | -0.15763 | -0.35342 | -0.43974 | -0.51237
|  | MALLAIG | HE |  |  |  |  | 1.6255 | 1.615 | 1.6055 | 1.5929 | 1.5792 | 1.5676 | 1.5539 | 1.2624 | 0.775 | 0.041316 | -0.19763 | -0.23447 | -0.25553 | 1.7708 | 1.7592 | 1.7487 | 1.735 | 1.7203 | 1.7076 | 1.6939 | 1.3561 | 0.79079 | -0.058684 | -0.33553 | -0.37553 | -0.39974 | 1.8961 | 1.8845 | 1.8739 | 1.8603 | 1.8455 | 1.8329 | 1.8182 | 1.4771 | 0.90553 | 0.045526 | -0.23447 | -0.27553 | -0.29974
|  | MALLAIG | FB |  |  |  |  | 1.6318 | 1.6245 | 1.6171 | 1.6108 | 1.6003 | 1.5929 | 1.5855 | 1.5782 | 1.4508 | 1.2371 | 0.47816 | 0.43605 | 0.40447 | 1.7771 | 1.7687 | 1.7613 | 1.7539 | 1.7424 | 1.7339 | 1.7255 | 1.7182 | 1.5708 | 1.3234 | 0.44447 | 0.39605 | 0.36026 | 1.9024 | 1.8939 | 1.8866 | 1.8792 | 1.8676 | 1.8592 | 1.8508 | 1.8434 | 1.6939 | 1.4434 | 0.55395 | 0.50553 | 0.46974
| KEITH 1 | MARNOCH | MINIMUM HEADROOM | NJ 61955 53001 | NO | YES | 0 | 4.7053 | 4.5726 | 4.4432 | 4.2937 | 4.2095 | 4.12 | 3.9884 | 3.8158 | 3.6105 | 3.5221 | 0.25895 | 0.052632 | -0.24737 | 4.6674 | 4.5189 | 4.3747 | 4.2053 | 4.1147 | 4.0189 | 3.8768 | 3.6811 | 3.4484 | 3.3547 | 1.6347 | 1.2863 | 0.96526 | 4.6684 | 4.52 | 4.3758 | 4.2074 | 4.1158 | 4.0211 | 3.8789 | 3.6842 | 3.4516 | 3.3579 | 1.1116 | -0.16 | -0.48737
|  | MARNOCH | EE |  |  |  |  | 4.7053 | 4.5726 | 4.4432 | 4.2937 | 4.2095 | 4.12 | 4.0316 | 3.9179 | 3.7895 | 3.7105 | 3.1863 | 0.052632 | -0.24737 | 4.6674 | 4.5189 | 4.3747 | 4.2053 | 4.1147 | 4.0189 | 3.9242 | 3.7989 | 3.6568 | 3.5705 | 2.9832 | 1.2863 | 0.96526 | 4.6684 | 4.52 | 4.3758 | 4.2074 | 4.1158 | 4.0211 | 3.9263 | 3.8011 | 3.6589 | 3.5726 | 2.9874 | -0.16 | -0.48737
|  | MARNOCH | HT |  |  |  |  | 4.7126 | 4.5926 | 4.4642 | 4.3189 | 4.2284 | 4.1411 | 3.9884 | 3.8158 | 3.6105 | 3.5221 | 0.25895 | 1.3621 | 1.0842 | 4.6758 | 4.5442 | 4.4 | 4.2379 | 4.1411 | 4.0463 | 3.8768 | 3.6811 | 3.4484 | 3.3547 | 2.9411 | 2.3716 | 2.0011 | 4.6768 | 4.5453 | 4.4011 | 4.24 | 4.1432 | 4.0484 | 3.8789 | 3.6842 | 3.4516 | 3.3579 | 2.9453 | 1.2032 | 0.82526
|  | MARNOCH | HE |  |  |  |  | 4.7747 | 4.6863 | 4.5905 | 4.4811 | 4.4326 | 4.38 | 4.3274 | 4.2421 | 4.1305 | 4.0895 | 1.2768 | 0.48 | 0.36 | 4.7421 | 4.6442 | 4.5358 | 4.4116 | 4.3611 | 4.3053 | 4.2495 | 4.1547 | 4.0295 | 3.9842 | 1.6347 | 1.8284 | 1.6958 | 4.7432 | 4.6442 | 4.5368 | 4.4126 | 4.3621 | 4.3063 | 4.2516 | 4.1568 | 4.0316 | 3.9863 | 1.1116 | 0.32947 | 0.19684
|  | MARNOCH | FB |  |  |  |  | 4.8011 | 4.74 | 4.6737 | 4.6095 | 4.5432 | 4.4821 | 4.4242 | 4.3695 | 4.3021 | 4.2421 | 3.8947 | 3.5726 | 3.3347 | 4.7779 | 4.7116 | 4.64 | 4.5705 | 4.4989 | 4.4337 | 4.3716 | 4.3137 | 4.2411 | 4.1768 | 3.7937 | 3.4432 | 3.1916 | 4.7779 | 4.7116 | 4.6411 | 4.5716 | 4.4989 | 4.4347 | 4.3726 | 4.3147 | 4.2421 | 4.1779 | 3.7958 | 3.4463 | 3.1947
| BEAULY | MARYBANK | MINIMUM HEADROOM | NH 46749 53948 | YES | YES | 0 | 3.7242 | 3.4558 | 3.1789 | 2.8642 | 2.4442 | 2.0716 | 1.6916 | 1.3021 | 0.90842 | 0.50421 | -0.88947 | -2.4168 | -3.9621 | 3.5989 | 3.2674 | 2.9263 | 2.5758 | 2.2158 | 1.8947 | 1.5663 | 1.2347 | 0.89368 | 0.50421 | -0.84105 | -2.3126 | -3.7968 | 3.5779 | 3.2011 | 2.7989 | 2.3863 | 1.9621 | 1.5863 | 1.2011 | 0.80737 | 0.40842 | -0.0010526 | -1.4158 | -2.9653 | -4.5316
|  | MARYBANK | EE |  |  |  |  | 3.7242 | 3.4558 | 3.1789 | 2.8642 | 2.4442 | 2.0716 | 1.6916 | 1.3021 | 0.90842 | 0.50421 | -0.88947 | -2.4168 | -3.9621 | 3.5989 | 3.2674 | 2.9263 | 2.5758 | 2.2158 | 1.8947 | 1.5663 | 1.2347 | 0.89368 | 0.50421 | -0.84105 | -2.3126 | -3.7968 | 3.5779 | 3.2011 | 2.7989 | 2.3863 | 1.9621 | 1.5863 | 1.2011 | 0.80737 | 0.40842 | -0.0010526 | -1.4158 | -2.9653 | -4.5316
|  | MARYBANK | HT |  |  |  |  | 3.9032 | 3.8189 | 3.7337 | 3.6463 | 3.5589 | 3.4716 | 3.3821 | 3.2947 | 3.2053 | 3.1158 | 2.6126 | 2.0074 | 1.5116 | 3.8158 | 3.7074 | 3.5968 | 3.4853 | 3.3726 | 3.26 | 3.1474 | 3.0358 | 2.9232 | 2.8095 | 2.3611 | 1.8084 | 1.2558 | 3.7905 | 3.6811 | 3.5705 | 3.4579 | 3.3432 | 3.2295 | 3.1053 | 2.9811 | 2.8568 | 2.7284 | 2.2284 | 1.6053 | 0.97474
|  | MARYBANK | HE |  |  |  |  | 3.9063 | 3.8221 | 3.7379 | 3.6547 | 3.5695 | 3.4821 | 3.3905 | 3.3074 | 3.2211 | 3.1411 | 2.7705 | 2.1779 | 1.5737 | 3.8263 | 3.7221 | 3.6179 | 3.5137 | 3.4084 | 3.3011 | 3.1916 | 3.0874 | 2.9821 | 2.8811 | 2.4642 | 1.9505 | 1.4389 | 3.8053 | 3.7011 | 3.5989 | 3.4926 | 3.3747 | 3.2516 | 3.1242 | 3.0032 | 2.8832 | 2.7642 | 2.2853 | 1.6842 | 1.0758
|  | MARYBANK | FB |  |  |  |  | 3.9684 | 3.9453 | 3.9232 | 3.9011 | 3.88 | 3.8579 | 3.8389 | 3.8179 | 3.7989 | 3.7789 | 3.7042 | 3.6232 | 3.5579 | 3.8937 | 3.8674 | 3.84 | 3.8105 | 3.78 | 3.7505 | 3.7232 | 3.6947 | 3.6674 | 3.6379 | 3.5284 | 3.4095 | 3.3126 | 3.8821 | 3.8484 | 3.8168 | 3.7863 | 3.7526 | 3.7221 | 3.6937 | 3.6642 | 3.6347 | 3.6042 | 3.4884 | 3.3611 | 3.2579
| LUNANHEAD | MARYTON | MINIMUM HEADROOM | NO 39206 53075 | NO | YES | 0 | 15.4258 | 15.2689 | 14.8479 | 14.3489 | 14.1879 | 14.0395 | 13.8974 | 13.7553 | 13.6111 | 13.4942 | 11.8321 | 11.5816 | 11.2763 | 13.6989 | 13.5263 | 13.0432 | 12.4695 | 12.2916 | 12.1305 | 11.9768 | 11.8221 | 11.6642 | 11.5379 | 10.0368 | 9.8189 | 9.4842 | 14.3634 | 14.1939 | 13.715 | 13.1476 | 12.9676 | 12.8076 | 12.6518 | 12.4982 | 12.3371 | 12.2076 | 10.4361 | 10.2434 | 9.9034
|  | MARYTON | EE |  |  |  |  | 15.4258 | 15.2689 | 14.8479 | 14.3489 | 14.1879 | 14.0395 | 13.8974 | 13.7553 | 13.6111 | 13.4942 | 11.8321 | 11.5816 | 11.2763 | 13.6989 | 13.5263 | 13.0432 | 12.4695 | 12.2916 | 12.1305 | 11.9768 | 11.8221 | 11.6642 | 11.5379 | 10.0368 | 9.8189 | 9.4842 | 14.3634 | 14.1939 | 13.715 | 13.1476 | 12.9676 | 12.8076 | 12.6518 | 12.4982 | 12.3371 | 12.2076 | 10.4361 | 10.2434 | 9.9034
|  | MARYTON | HT |  |  |  |  | 15.4616 | 15.3205 | 14.9026 | 14.4111 | 14.2405 | 14.1058 | 13.9626 | 13.8132 | 13.6584 | 13.5237 | 12.1868 | 11.7921 | 11.5058 | 13.7389 | 13.5832 | 13.1021 | 12.5368 | 12.3463 | 12.1989 | 12.04 | 11.8758 | 11.7042 | 11.5568 | 10.5168 | 10.0537 | 9.6505 | 14.4013 | 14.2529 | 13.7782 | 13.2203 | 13.0308 | 12.8834 | 12.7255 | 12.5634 | 12.3918 | 12.2434 | 11.0182 | 10.5571 | 10.1539
|  | MARYTON | HE |  |  |  |  | 15.5374 | 15.4258 | 15.0521 | 14.6132 | 14.5016 | 14.4058 | 14.2932 | 14.1995 | 14.0858 | 14.0205 | 13.2426 | 13.0395 | 12.8847 | 13.8253 | 13.7021 | 13.2716 | 12.7663 | 12.6442 | 12.5421 | 12.4221 | 12.3189 | 12.1937 | 12.1211 | 11.3905 | 11.1663 | 10.9947 | 14.4771 | 14.3645 | 13.9455 | 13.4466 | 13.3245 | 13.2224 | 13.1013 | 13.0003 | 12.875 | 12.8024 | 11.9655 | 11.7403 | 11.5676
|  | MARYTON | FB |  |  |  |  | 15.5847 | 15.5195 | 15.4026 | 15.2784 | 15.1563 | 15.0616 | 14.9868 | 14.9195 | 14.8521 | 14.7795 | 14.4574 | 14.1584 | 13.9542 | 13.8768 | 13.8053 | 13.6716 | 13.5284 | 13.3884 | 13.2832 | 13.1989 | 13.1232 | 13.0474 | 12.9663 | 12.6053 | 12.2674 | 12.0358 | 14.5245 | 14.4592 | 14.3403 | 14.2003 | 14.0624 | 13.9571 | 13.8739 | 13.7992 | 13.7245 | 13.6445 | 13.2855 | 12.9529 | 12.7224
| STRICHEN | MAUD | MINIMUM HEADROOM | NJ 92528 47491 | NO | YES | 0 | 7.6126 | 7.5505 | 7.4695 | 7.3705 | 7.2547 | 7.1442 | 6.9568 | 6.7411 | 6.4611 | 6.4 | 4.28 | 3.0242 | 2.8737 | 7.1926 | 7.1232 | 7.0305 | 6.9179 | 6.7863 | 6.6589 | 6.4432 | 6.1937 | 5.8684 | 5.8021 | 5.2263 | 2.9695 | 2.8011 | 7.3937 | 7.3232 | 7.2305 | 7.1189 | 6.9874 | 6.8611 | 6.6453 | 6.3968 | 6.0726 | 6.0053 | 5.3947 | 2.5379 | 2.3674
|  | MAUD | EE |  |  |  |  | 7.6126 | 7.5505 | 7.4695 | 7.3758 | 7.2695 | 7.1442 | 7.0326 | 6.8842 | 6.7032 | 6.6505 | 5.8453 | 3.0242 | 2.8737 | 7.1926 | 7.1232 | 7.0305 | 6.9221 | 6.8021 | 6.6589 | 6.5326 | 6.3621 | 6.1526 | 6.0947 | 5.24 | 2.9695 | 2.8011 | 7.3937 | 7.3232 | 7.2316 | 7.1232 | 7.0032 | 6.8611 | 6.7337 | 6.5642 | 6.3558 | 6.2979 | 5.3989 | 2.5379 | 2.3674
|  | MAUD | HT |  |  |  |  | 7.6274 | 7.5516 | 7.4695 | 7.3705 | 7.2547 | 7.1526 | 6.9568 | 6.7411 | 6.4611 | 6.4 | 4.28 | 3.5326 | 3.3937 | 7.2095 | 7.1232 | 7.0305 | 6.9179 | 6.7863 | 6.6695 | 6.4432 | 6.1937 | 5.8684 | 5.8021 | 5.2263 | 3.3926 | 3.1958 | 7.4095 | 7.3232 | 7.2305 | 7.1189 | 6.9874 | 6.8716 | 6.6453 | 6.3968 | 6.0726 | 6.0053 | 5.3947 | 3.0884 | 2.8937
|  | MAUD | HE |  |  |  |  | 7.6621 | 7.6179 | 7.5547 | 7.4821 | 7.3937 | 7.2811 | 7.1821 | 7.0358 | 6.8379 | 6.8053 | 6.2084 | 5.0895 | 5.0011 | 7.2495 | 7.1989 | 7.1284 | 7.0453 | 6.9453 | 6.8168 | 6.7042 | 6.5358 | 6.3053 | 6.2684 | 5.6042 | 4.7168 | 4.6168 | 7.4495 | 7.4 | 7.3284 | 7.2463 | 7.1463 | 7.0179 | 6.9063 | 6.7379 | 6.5084 | 6.4716 | 5.7916 | 4.66 | 4.5589
|  | MAUD | FB |  |  |  |  | 7.6863 | 7.6632 | 7.6379 | 7.6021 | 7.5632 | 7.5084 | 7.4558 | 7.4074 | 7.3295 | 7.3 | 6.9747 | 6.74 | 6.6547 | 7.2768 | 7.2495 | 7.2211 | 7.18 | 7.1358 | 7.0726 | 7.0116 | 6.9558 | 6.8653 | 6.8326 | 6.4547 | 6.1821 | 6.0853 | 7.4768 | 7.4495 | 7.4211 | 7.3811 | 7.3358 | 7.2726 | 7.2116 | 7.1568 | 7.0663 | 7.0337 | 6.6568 | 6.3853 | 6.2884
| DOUNREAY | MELVICH | MINIMUM HEADROOM | NC 88547 64274 | YES | YES | 0.061224 | 1.1463 | 1.1326 | 1.1211 | 1.1063 | 1.0916 | 1.0726 | 1.0589 | 1.0442 | 1.0305 | 1.0189 | 0.95895 | 0.91789 | 0.88947 | 1.0326 | 1.0158 | 1.0032 | 0.98632 | 0.96947 | 0.94842 | 0.93263 | 0.91684 | 0.90105 | 0.88842 | 0.83579 | 0.78211 | 0.74211 | 1.0463 | 1.0305 | 1.0189 | 1.0021 | 0.98737 | 0.96737 | 0.95158 | 0.93684 | 0.92211 | 0.90947 | 0.85789 | 0.80526 | 0.76526
|  | MELVICH | EE |  |  |  |  | 1.1463 | 1.1326 | 1.1211 | 1.1063 | 1.0916 | 1.0726 | 1.0589 | 1.0442 | 1.0305 | 1.0189 | 0.97263 | 0.93368 | 0.90211 | 1.0326 | 1.0158 | 1.0032 | 0.98632 | 0.96947 | 0.94842 | 0.93263 | 0.91684 | 0.90105 | 0.88842 | 0.83579 | 0.79053 | 0.75368 | 1.0463 | 1.0305 | 1.0189 | 1.0021 | 0.98737 | 0.96737 | 0.95158 | 0.93684 | 0.92211 | 0.90947 | 0.85789 | 0.81368 | 0.77789
|  | MELVICH | HT |  |  |  |  | 1.1505 | 1.1379 | 1.1263 | 1.1137 | 1.0947 | 1.0821 | 1.0684 | 1.0537 | 1.0389 | 1.0253 | 0.95895 | 0.91789 | 0.88947 | 1.0368 | 1.0232 | 1.0095 | 0.99579 | 0.97368 | 0.95895 | 0.94421 | 0.92737 | 0.91158 | 0.89579 | 0.83579 | 0.78211 | 0.74211 | 1.0505 | 1.0368 | 1.0242 | 1.0116 | 0.99053 | 0.97684 | 0.96211 | 0.94632 | 0.93158 | 0.91684 | 0.85789 | 0.80526 | 0.76526
|  | MELVICH | HE |  |  |  |  | 1.1589 | 1.1495 | 1.1432 | 1.1347 | 1.1263 | 1.1158 | 1.1074 | 1.0979 | 1.0905 | 1.0832 | 1.0568 | 1.0358 | 1.0211 | 1.0442 | 1.0358 | 1.0284 | 1.02 | 1.0105 | 0.99895 | 0.99053 | 0.98105 | 0.97158 | 0.96421 | 0.93368 | 0.90842 | 0.89263 | 1.06 | 1.0505 | 1.0432 | 1.0347 | 1.0253 | 1.0137 | 1.0053 | 0.99579 | 0.98737 | 0.98 | 0.95158 | 0.92842 | 0.91263
|  | MELVICH | FB |  |  |  |  | 1.1642 | 1.1589 | 1.1526 | 1.1484 | 1.1421 | 1.1368 | 1.1305 | 1.1253 | 1.12 | 1.1116 | 1.0853 | 1.0579 | 1.0368 | 1.0495 | 1.0453 | 1.0389 | 1.0337 | 1.0274 | 1.0211 | 1.0137 | 1.0084 | 1.0021 | 0.99263 | 0.96316 | 0.93053 | 0.90526 | 1.0653 | 1.06 | 1.0537 | 1.0484 | 1.0421 | 1.0358 | 1.0295 | 1.0232 | 1.0168 | 1.0084 | 0.98105 | 0.95053 | 0.92632
| CHARLESTON | MENZIESHILL | MINIMUM HEADROOM | NO 35918 31022 | NO | YES | 0 | 20.0742 | 19.8121 | 19.6395 | 19.5563 | 19.4626 | 19.3479 | 19.2342 | 19.1426 | 19.0479 | 18.9532 | 18.4995 | 18.2195 | 18.0205 | 20.3516 | 20.2316 | 19.9579 | 19.8432 | 19.7189 | 19.5695 | 19.4274 | 19.3074 | 19.1853 | 19.0621 | 18.4547 | 17.8747 | 17.4337 | 21.7576 | 21.6103 | 21.2545 | 21.1082 | 20.9524 | 20.7682 | 20.5955 | 20.4471 | 20.2966 | 20.1397 | 19.4913 | 18.9239 | 18.4903
|  | MENZIESHILL | EE |  |  |  |  | 20.0742 | 19.8121 | 19.6395 | 19.5563 | 19.4626 | 19.3479 | 19.2342 | 19.1426 | 19.0479 | 18.9574 | 18.6184 | 18.3479 | 18.1595 | 20.3516 | 20.2316 | 19.9579 | 19.8432 | 19.7189 | 19.5695 | 19.4274 | 19.3074 | 19.1853 | 19.0621 | 18.5147 | 18.0126 | 17.6537 | 21.7576 | 21.6103 | 21.2545 | 21.1082 | 20.9524 | 20.7682 | 20.5955 | 20.4471 | 20.2966 | 20.1397 | 19.5513 | 19.0597 | 18.7082
|  | MENZIESHILL | HT |  |  |  |  | 20.0816 | 19.8489 | 19.6616 | 19.5784 | 19.4784 | 19.3879 | 19.2911 | 19.1868 | 19.0837 | 18.9532 | 18.4995 | 18.2195 | 18.0205 | 20.3579 | 20.2874 | 19.9958 | 19.8895 | 19.7547 | 19.6389 | 19.5137 | 19.3768 | 19.2442 | 19.0695 | 18.4547 | 17.8747 | 17.4337 | 21.7639 | 21.6808 | 21.3092 | 21.1787 | 21.0103 | 20.8692 | 20.7134 | 20.5429 | 20.3808 | 20.1597 | 19.4913 | 18.9239 | 18.4903
|  | MENZIESHILL | HE |  |  |  |  | 20.1279 | 19.9047 | 19.7521 | 19.69 | 19.6121 | 19.5153 | 19.43 | 19.3647 | 19.2953 | 19.2416 | 19.0037 | 18.8426 | 18.7416 | 20.3726 | 20.3316 | 20.1316 | 20.0558 | 19.9589 | 19.84 | 19.7432 | 19.6611 | 19.5726 | 19.4947 | 19.1547 | 18.9253 | 18.7653 | 21.7787 | 21.7376 | 21.4797 | 21.3924 | 21.2808 | 21.1429 | 21.0355 | 20.9366 | 20.8282 | 20.725 | 20.2808 | 19.9808 | 19.7924
|  | MENZIESHILL | FB |  |  |  |  | 20.2405 | 20.1742 | 20.0953 | 20.0384 | 19.9784 | 19.9226 | 19.8668 | 19.8111 | 19.7563 | 19.7005 | 19.4805 | 19.2784 | 19.1542 | 20.3926 | 20.3747 | 20.3558 | 20.3358 | 20.3126 | 20.2895 | 20.2663 | 20.2421 | 20.2011 | 20.1242 | 19.8158 | 19.5274 | 19.3442 | 21.7987 | 21.7808 | 21.7618 | 21.7418 | 21.7187 | 21.6955 | 21.6724 | 21.6482 | 21.5997 | 21.5061 | 21.1292 | 20.7534 | 20.5092
| KINTORE | METHLICK | MINIMUM HEADROOM | NJ 85339 36835 | NO | YES | 0.11224 | -1.2032 | 0.083158 | 0.071579 | 0.057895 | 0.041053 | 0.026316 | 0.0063158 | -0.0073684 | -0.025263 | -0.041053 | -0.91158 | -0.94316 | -1.0589 | -2.4621 | -1.2032 | -1.24 | -1.2842 | -1.3263 | -1.3726 | -1.4137 | -1.4895 | -1.5421 | -1.5853 | -2.4568 | -2.5958 | -2.7937 | 1.8916 | 3.1547 | 3.1221 | 3.0821 | 3.0442 | 3.0011 | 2.96 | 2.8863 | 2.8347 | 2.7926 | 1.6937 | 1.5716 | 1.3558
|  | METHLICK | EE |  |  |  |  | -1.2032 | 0.083158 | 0.072632 | 0.061053 | 0.045263 | 0.026316 | 0.0063158 | -0.0073684 | -0.023158 | -0.034737 | -0.91158 | -0.94316 | -1.0589 | -2.4621 | -1.2032 | -1.24 | -1.2842 | -1.3263 | -1.3726 | -1.4137 | -1.4642 | -1.5253 | -1.5642 | -2.4568 | -2.5958 | -2.7937 | 1.8916 | 3.1547 | 3.1221 | 3.0821 | 3.0442 | 3.0011 | 2.96 | 2.9105 | 2.8516 | 2.8137 | 1.6937 | 1.5716 | 1.3558
|  | METHLICK | HT |  |  |  |  | -1.2032 | 0.085263 | 0.071579 | 0.057895 | 0.041053 | 0.026316 | 0.0094737 | -0.0073684 | -0.025263 | -0.041053 | -0.76632 | -0.87684 | -0.90105 | -2.4537 | -1.1884 | -1.2253 | -1.2642 | -1.3074 | -1.3474 | -1.4116 | -1.4895 | -1.5421 | -1.5853 | -2.3137 | -2.4726 | -2.6684 | 1.9 | 3.1684 | 3.1347 | 3.0989 | 3.06 | 3.0232 | 2.9621 | 2.8863 | 2.8347 | 2.7926 | 1.8874 | 1.7463 | 1.5379
|  | METHLICK | HE |  |  |  |  | -1.1989 | 0.090526 | 0.081053 | 0.069474 | 0.055789 | 0.037895 | 0.018947 | 0.0073684 | -0.0063158 | -0.010526 | -0.36316 | -0.37684 | -0.42421 | -2.4284 | -1.1537 | -1.1779 | -1.2042 | -1.2316 | -1.2621 | -1.2937 | -1.3305 | -1.3758 | -1.3989 | -1.8116 | -1.88 | -1.9811 | 1.9221 | 3.1979 | 3.1758 | 3.1526 | 3.1263 | 3.0979 | 3.0684 | 3.0347 | 2.9947 | 2.9737 | 2.4726 | 2.4116 | 2.3063
|  | METHLICK | FB |  |  |  |  | -1.1905 | 0.10632 | 0.10211 | 0.097895 | 0.093684 | 0.088421 | 0.083158 | 0.078947 | 0.073684 | 0.068421 | 0.047368 | 0.030526 | 0.022105 | -2.4137 | -1.1263 | -1.1411 | -1.1568 | -1.1737 | -1.1884 | -1.2042 | -1.2179 | -1.2389 | -1.2621 | -1.3653 | -1.4558 | -1.5253 | 1.9358 | 3.2242 | 3.2105 | 3.1968 | 3.1821 | 3.1684 | 3.1537 | 3.1411 | 3.1232 | 3.1021 | 3.0074 | 2.92 | 2.8537
| SHETLAND | MID YELL | MINIMUM HEADROOM | HU4817291442 | YES | YES | 0 | 0.97895 | 0.96526 | 0.95368 | 0.94211 | 0.93158 | 0.91895 | 0.90526 | 0.89474 | 0.88421 | 0.87368 | 0.83263 | 0.80105 | 0.77895 | 1.0032 | 0.99789 | 0.99368 | 0.98947 | 0.98316 | 0.97789 | 0.97053 | 0.96526 | 0.95895 | 0.95263 | 0.92 | 0.88316 | 0.85474 | 0.98632 | 0.97684 | 0.96947 | 0.96211 | 0.95474 | 0.94526 | 0.93579 | 0.92842 | 0.92105 | 0.91368 | 0.88632 | 0.86421 | 0.84526
|  | MID YELL | EE |  |  |  |  | 0.97895 | 0.96526 | 0.95368 | 0.94211 | 0.93158 | 0.91895 | 0.90526 | 0.89474 | 0.88421 | 0.87368 | 0.83684 | 0.80526 | 0.78316 | 1.0032 | 0.99789 | 0.99368 | 0.98947 | 0.98526 | 0.97789 | 0.97053 | 0.96526 | 0.96 | 0.95474 | 0.92 | 0.88316 | 0.85789 | 0.98632 | 0.97684 | 0.96947 | 0.96211 | 0.95474 | 0.94526 | 0.93579 | 0.92842 | 0.92105 | 0.91368 | 0.88632 | 0.86526 | 0.85263
|  | MID YELL | HT |  |  |  |  | 0.98316 | 0.97053 | 0.96 | 0.94737 | 0.93579 | 0.92421 | 0.91368 | 0.90211 | 0.88947 | 0.87895 | 0.83263 | 0.80105 | 0.77895 | 1.0042 | 0.99895 | 0.99474 | 0.98947 | 0.98316 | 0.97789 | 0.97158 | 0.96632 | 0.95895 | 0.95263 | 0.92421 | 0.88632 | 0.85474 | 0.98842 | 0.98 | 0.97263 | 0.96526 | 0.95579 | 0.94842 | 0.94 | 0.93158 | 0.92211 | 0.91368 | 0.88737 | 0.86421 | 0.84526
|  | MID YELL | HE |  |  |  |  | 0.98947 | 0.98105 | 0.97368 | 0.96737 | 0.95789 | 0.94842 | 0.93789 | 0.93053 | 0.92211 | 0.91789 | 0.89684 | 0.88 | 0.86947 | 1.0042 | 1 | 0.99684 | 0.99368 | 0.98737 | 0.98105 | 0.97368 | 0.96947 | 0.96421 | 0.96316 | 0.95474 | 0.94947 | 0.94526 | 0.99053 | 0.98526 | 0.98 | 0.97579 | 0.96842 | 0.96 | 0.95158 | 0.94632 | 0.94 | 0.93684 | 0.92316 | 0.91263 | 0.90526
|  | MID YELL | FB |  |  |  |  | 0.99579 | 0.99053 | 0.98526 | 0.97895 | 0.97368 | 0.96737 | 0.96316 | 0.95684 | 0.95158 | 0.94526 | 0.92316 | 0.9 | 0.88211 | 1.0074 | 1.0063 | 1.0042 | 1.0021 | 1 | 0.99789 | 0.99579 | 0.99368 | 0.99158 | 0.98947 | 0.98105 | 0.97368 | 0.96632 | 0.99579 | 0.99263 | 0.98947 | 0.98526 | 0.98211 | 0.97789 | 0.97474 | 0.97158 | 0.96737 | 0.96421 | 0.94947 | 0.93474 | 0.92526
| KINTORE | MIDMAR | MINIMUM HEADROOM | NJ 68253 06875 | YES | YES | 0 | 4.4368 | 4.3642 | 4.2737 | 6.9495 | 6.9 | 6.8411 | 6.7811 | 6.7221 | 6.6611 | 6.62 | 5.2516 | 2.8916 | 2.7779 | 4.5032 | 4.4284 | 4.3263 | 6.5895 | 6.5368 | 6.4716 | 6.4042 | 6.3389 | 6.2716 | 6.2263 | 5.2663 | 3.1484 | 3.0179 | 4.4116 | 4.3326 | 4.2337 | 6.7011 | 6.6484 | 6.5853 | 6.52 | 6.4537 | 6.3842 | 6.3379 | 5.1716 | 2.5589 | 2.4295
|  | MIDMAR | EE |  |  |  |  | 4.4368 | 4.3737 | 4.2926 | 6.9495 | 6.9 | 6.8484 | 6.7863 | 6.7221 | 6.6611 | 6.62 | 5.4726 | 2.8916 | 2.7779 | 4.5032 | 4.4379 | 4.3484 | 6.5895 | 6.5368 | 6.4789 | 6.4116 | 6.3389 | 6.2716 | 6.2263 | 5.2663 | 3.1484 | 3.0179 | 4.4116 | 4.3432 | 4.2547 | 6.7011 | 6.6484 | 6.5937 | 6.5274 | 6.4537 | 6.3842 | 6.3379 | 5.1716 | 2.5589 | 2.4295
|  | MIDMAR | HT |  |  |  |  | 4.4453 | 4.3642 | 4.2737 | 6.9547 | 6.9011 | 6.8411 | 6.7811 | 6.7274 | 6.6747 | 6.6263 | 5.2516 | 3.5326 | 3.4179 | 4.5116 | 4.4284 | 4.3263 | 6.5968 | 6.5368 | 6.4716 | 6.4042 | 6.3463 | 6.2884 | 6.2358 | 5.4432 | 3.6811 | 3.5158 | 4.4211 | 4.3326 | 4.2337 | 6.7074 | 6.6495 | 6.5853 | 6.52 | 6.4611 | 6.4021 | 6.3474 | 5.3905 | 3.2295 | 3.0642
|  | MIDMAR | HE |  |  |  |  | 4.4705 | 4.4232 | 4.3653 | 7.0495 | 7.0168 | 6.9516 | 6.8979 | 6.8463 | 6.7989 | 6.7768 | 6.2947 | 3.1653 | 3.1 | 4.5389 | 4.4895 | 4.4295 | 6.7053 | 6.6705 | 6.5989 | 6.5389 | 6.4821 | 6.4284 | 6.4032 | 5.9937 | 3.4674 | 3.3958 | 4.4495 | 4.3979 | 4.3347 | 6.8116 | 6.7779 | 6.7084 | 6.6505 | 6.5947 | 6.5432 | 6.5189 | 6.0232 | 2.8758 | 2.8
|  | MIDMAR | FB |  |  |  |  | 4.9579 | 4.9368 | 4.9126 | 7.6421 | 7.62 | 7.5863 | 7.5547 | 7.5295 | 7.4979 | 7.4716 | 7.36 | 7.2589 | 7.1842 | 4.9284 | 4.9042 | 4.8779 | 7.2011 | 7.1758 | 7.1368 | 7.1011 | 7.0705 | 7.0347 | 7.0042 | 6.8768 | 6.7589 | 6.6726 | 4.9463 | 4.9232 | 4.8979 | 7.4232 | 7.4 | 7.3632 | 7.3284 | 7.3 | 7.2663 | 7.2368 | 7.1084 | 6.9905 | 6.9032
| BRIDGE OF DUN | MILL RD | MINIMUM HEADROOM | NO 71317 57683 | NO | YES | 0.76735 | 14.4305 | 14.4042 | 14.3832 | 14.3547 | 14.3032 | 14.1863 | 14.0674 | 13.9632 | 13.8547 | 13.7516 | 13.3484 | 12.9821 | 12.6968 | 12.3853 | 12.2958 | 12.2032 | 12.0642 | 11.9411 | 11.8105 | 11.6779 | 11.56 | 11.4379 | 11.3211 | 10.8842 | 10.4632 | 10.12 | 13.0304 | 12.9493 | 12.8651 | 12.7409 | 12.6304 | 12.5114 | 12.3893 | 12.283 | 12.1725 | 12.0662 | 11.6683 | 11.2904 | 10.9862
|  | MILL RD | EE |  |  |  |  | 14.4305 | 14.4042 | 14.3832 | 14.3579 | 14.3032 | 14.1863 | 14.0674 | 13.9632 | 13.8547 | 13.7516 | 13.3632 | 12.9947 | 12.6968 | 12.3853 | 12.2958 | 12.2032 | 12.0642 | 11.9411 | 11.8105 | 11.6779 | 11.56 | 11.4379 | 11.3211 | 10.8842 | 10.4632 | 10.12 | 13.0304 | 12.9493 | 12.8651 | 12.7409 | 12.6304 | 12.5114 | 12.3893 | 12.283 | 12.1725 | 12.0662 | 11.6683 | 11.2904 | 10.9862
|  | MILL RD | HT |  |  |  |  | 14.4358 | 14.4116 | 14.3842 | 14.3547 | 14.3211 | 14.2716 | 14.1611 | 14.0516 | 13.9432 | 13.8274 | 13.3484 | 12.9821 | 12.7158 | 12.4126 | 12.3337 | 12.2537 | 12.1516 | 12.0295 | 11.9105 | 11.7863 | 11.6632 | 11.5411 | 11.4126 | 10.9737 | 10.5337 | 10.1505 | 13.0557 | 12.983 | 12.9104 | 12.8178 | 12.7062 | 12.5978 | 12.4862 | 12.3736 | 12.263 | 12.1451 | 11.7472 | 11.3514 | 11.0072
|  | MILL RD | HE |  |  |  |  | 14.4421 | 14.4158 | 14.3979 | 14.3705 | 14.3379 | 14.2958 | 14.2526 | 14.2263 | 14.2 | 14.1853 | 14.0295 | 13.8337 | 13.6779 | 12.4674 | 12.4084 | 12.3579 | 12.3 | 12.2432 | 12.1768 | 12.1105 | 12.0453 | 11.9663 | 11.8958 | 11.6547 | 11.4305 | 11.2516 | 13.1041 | 13.0483 | 13.003 | 12.9483 | 12.8946 | 12.8314 | 12.7683 | 12.7072 | 12.6357 | 12.5725 | 12.3546 | 12.1536 | 11.9936
|  | MILL RD | FB |  |  |  |  | 14.4526 | 14.4411 | 14.4295 | 14.4158 | 14.4021 | 14.3863 | 14.3716 | 14.3558 | 14.3389 | 14.3211 | 14.1832 | 13.9326 | 13.7253 | 12.5021 | 12.4632 | 12.4232 | 12.3821 | 12.3411 | 12.2979 | 12.2579 | 12.2158 | 12.16 | 12.0842 | 11.8126 | 11.5253 | 11.2842 | 13.1357 | 13.0999 | 13.063 | 13.0262 | 12.9883 | 12.9493 | 12.9114 | 12.8736 | 12.823 | 12.7536 | 12.5093 | 12.2514 | 12.0378
| ABERNETHY | MILNATHORT | MINIMUM HEADROOM | NO 11900 05074 | NO | YES | 0.091837 | 17.0416 | 16.6942 | 16.4711 | 39.7758 | 39.5442 | 39.2453 | 39.0179 | 40.2432 | 40.0337 | 39.8968 | 39.3684 | 37.28 | 36.8484 | 14.8568 | 14.4642 | 14.2126 | 36.9368 | 36.6811 | 36.3474 | 36.0989 | 37.2579 | 37.0253 | 36.8758 | 36.5705 | 34.64 | 34.1558 | 14.2971 | 13.9003 | 13.6455 | 36.9916 | 36.7337 | 36.3979 | 36.1484 | 37.4137 | 37.1789 | 37.0284 | 36.7884 | 34.4874 | 34
|  | MILNATHORT | EE |  |  |  |  | 17.0416 | 16.6942 | 16.4711 | 39.7758 | 39.5463 | 39.2453 | 39.0179 | 40.2432 | 40.0337 | 39.8968 | 39.5126 | 37.28 | 36.8484 | 14.8568 | 14.4642 | 14.2126 | 36.9368 | 36.6811 | 36.3474 | 36.0989 | 37.2579 | 37.0253 | 36.8758 | 36.5705 | 34.64 | 34.1558 | 14.2971 | 13.9003 | 13.6455 | 36.9916 | 36.7337 | 36.3979 | 36.1484 | 37.4137 | 37.1789 | 37.0284 | 36.7884 | 34.4874 | 34
|  | MILNATHORT | HT |  |  |  |  | 17.0742 | 16.7511 | 16.4837 | 39.7863 | 39.5442 | 39.3568 | 39.1568 | 40.3726 | 40.4316 | 40.2063 | 39.3684 | 37.42 | 37 | 14.8958 | 14.5295 | 14.2305 | 36.9547 | 36.6874 | 36.4832 | 36.2642 | 37.4147 | 37.6032 | 37.3558 | 36.5758 | 34.8389 | 34.2432 | 14.3361 | 13.9666 | 13.6645 | 37.0116 | 36.7421 | 36.5358 | 36.3147 | 37.5716 | 37.8295 | 37.5811 | 36.7947 | 34.7632 | 34.1611
|  | MILNATHORT | HE |  |  |  |  | 17.1974 | 16.9311 | 16.7521 | 40.1189 | 39.9411 | 39.7021 | 39.5126 | 40.7979 | 40.6389 | 40.5663 | 40.1779 | 39.1863 | 38.9274 | 15.0337 | 14.7316 | 14.5305 | 37.3274 | 37.1316 | 36.8684 | 36.6621 | 37.8884 | 37.7126 | 37.6305 | 37.1968 | 36.3126 | 36.02 | 14.475 | 14.1708 | 13.9676 | 37.3874 | 37.1905 | 36.9242 | 36.7168 | 38.0505 | 37.8726 | 37.7905 | 37.3526 | 36.32 | 36.0242
|  | MILNATHORT | FB |  |  |  |  | 17.3963 | 17.2774 | 17.1679 | 40.6263 | 40.5284 | 40.4158 | 40.3116 | 41.6137 | 41.4979 | 41.4084 | 40.9863 | 40.5674 | 40.2789 | 15.2589 | 15.1242 | 15 | 37.8979 | 37.7874 | 37.6611 | 37.5453 | 38.7853 | 38.6547 | 38.5568 | 38.0832 | 37.6126 | 37.2842 | 14.7034 | 14.5666 | 14.4413 | 37.9632 | 37.8516 | 37.7242 | 37.6063 | 38.9547 | 38.8221 | 38.7242 | 38.2463 | 37.7705 | 37.44
| MILTON OF CRAIGIE | MILTON OF CRAIGIE | MINIMUM HEADROOM | NO 43137 31857 | NO | YES | 0 | 17.1421 | 17.1158 | 17.0947 | 17.0653 | 17.1147 | 17.0989 | 17.0842 | 17.0684 | 17.0516 | 17.0337 | 17.9621 | 12.9137 | 8.2368 | 15.2095 | 15.1832 | 15.1621 | 15.1326 | 15.1821 | 15.1663 | 15.1516 | 15.1358 | 15.1189 | 15.1011 | 15.6263 | 8.1274 | 2.6032 | 17.3768 | 17.3505 | 17.3295 | 17.3 | 17.3495 | 17.3337 | 17.3189 | 17.3032 | 17.2863 | 17.2684 | 16.2768 | 9.0147 | 3.5011
|  | MILTON OF CRAIGIE | EE |  |  |  |  | 17.1421 | 17.1158 | 17.0947 | 17.0684 | 24.3642 | 24.3221 | 24.2779 | 24.2421 | 24.2084 | 24.1789 | 22.8147 | 21.6432 | 20.1884 | 15.2095 | 15.1832 | 15.1621 | 15.1358 | 22.4316 | 22.3895 | 22.3453 | 22.3095 | 22.2758 | 22.2463 | 19.8684 | 18.4979 | 16.7884 | 17.3768 | 17.3505 | 17.3295 | 17.3032 | 24.0768 | 23.6653 | 23.5274 | 23.3747 | 23.2358 | 23.1337 | 20.3568 | 19.0358 | 17.3895
|  | MILTON OF CRAIGIE | HT |  |  |  |  | 17.1484 | 17.1221 | 17.0947 | 17.0653 | 24.3568 | 24.3232 | 24.2874 | 24.2505 | 24.2126 | 24.1705 | 17.9621 | 14.0726 | 12.0958 | 15.2158 | 15.1895 | 15.1621 | 15.1326 | 22.4242 | 22.3905 | 22.3547 | 22.3179 | 22.28 | 22.2379 | 15.6263 | 10.1389 | 7.2284 | 17.3832 | 17.3568 | 17.3295 | 17.3 | 23.9589 | 23.8558 | 23.7516 | 23.6579 | 23.4253 | 22.9126 | 16.2768 | 10.9958 | 8.1158
|  | MILTON OF CRAIGIE | HE |  |  |  |  | 17.1547 | 17.1284 | 17.1105 | 17.0821 | 24.3768 | 24.3337 | 24.2895 | 24.2621 | 24.2358 | 24.2221 | 23.28 | 22.2274 | 20.8695 | 15.2221 | 15.1958 | 15.1779 | 15.1495 | 22.4442 | 22.4011 | 22.3568 | 22.3295 | 22.3032 | 22.2895 | 20.4 | 19.1632 | 17.5621 | 17.3895 | 17.3632 | 17.3453 | 17.3168 | 24.2358 | 23.8537 | 23.7337 | 23.6316 | 23.5368 | 23.4695 | 20.8726 | 19.6811 | 18.1411
|  | MILTON OF CRAIGIE | FB |  |  |  |  | 17.1663 | 17.1547 | 17.1421 | 17.1295 | 17.1147 | 17.0989 | 17.0842 | 17.0684 | 17.0516 | 17.0337 | 20.3337 | 12.9137 | 8.2368 | 15.2337 | 15.2221 | 15.2095 | 15.1968 | 15.1821 | 15.1663 | 15.1516 | 15.1358 | 15.1189 | 15.1011 | 16.8905 | 8.1274 | 2.6032 | 17.4011 | 17.3895 | 17.3768 | 17.3642 | 17.3495 | 17.3337 | 17.3189 | 17.3032 | 17.2863 | 17.2684 | 17.5032 | 9.0147 | 3.5011
| STRICHEN | MINTLAW | MINIMUM HEADROOM | NK 00897 48662 | NO | YES | 0.087755 | -6.5563 | -6.8532 | -7.1447 | -7.4963 | -7.6374 | -7.8374 | -8.0532 | -8.2489 | -8.4605 | -9.17 | -14.0879 | -17.6847 | -17.8584 | 10.6516 | 10.06 | 9.4768 | 8.7684 | 8.5147 | 8.1463 | 7.7453 | 7.3811 | 6.9853 | 5.5189 | 2.5916 | -1.1211 | -1.4253 | 11.235 | 10.715 | 10.2034 | 9.515 | 9.2645 | 8.8982 | 8.5003 | 8.1392 | 7.7403 | 6.2687 | 2.4276 | -2.3839 | -2.685
|  | MINTLAW | EE |  |  |  |  | -6.5563 | -6.8532 | -7.1447 | -7.4963 | -7.6374 | -7.8374 | -8.0374 | -8.2058 | -8.39 | -9.0879 | -12.95 | -17.6847 | -17.8584 | 10.6516 | 10.06 | 9.4768 | 8.7684 | 8.5147 | 8.1463 | 7.7811 | 7.4705 | 7.1263 | 5.6663 | 2.5916 | -1.1211 | -1.4253 | 11.235 | 10.715 | 10.2034 | 9.515 | 9.2645 | 8.8982 | 8.5361 | 8.2266 | 7.8813 | 6.415 | 2.4276 | -2.3839 | -2.685
|  | MINTLAW | HT |  |  |  |  | -6.55 | -6.8174 | -7.1216 | -7.4742 | -7.6342 | -7.8289 | -8.0532 | -8.2489 | -8.4605 | -9.17 | -14.0879 | -16.1879 | -16.37 | 10.6589 | 10.1316 | 9.5263 | 8.8221 | 8.5337 | 8.1705 | 7.7453 | 7.3811 | 6.9853 | 5.5189 | 3.0916 | 0.015789 | -0.36947 | 11.2424 | 10.7782 | 10.2455 | 9.5687 | 9.2824 | 8.9213 | 8.5003 | 8.1392 | 7.7403 | 6.2687 | 3.1076 | -0.87868 | -1.2587
|  | MINTLAW | HE |  |  |  |  | -6.5174 | -6.7574 | -7.0289 | -7.3563 | -7.4753 | -7.6542 | -7.8479 | -8.0058 | -8.17 | -8.8353 | -12.5742 | -14.4868 | -14.5858 | 10.7126 | 10.2368 | 9.6884 | 9.0263 | 8.8179 | 8.4884 | 8.1347 | 7.8368 | 7.5295 | 6.1221 | 3.2305 | 1.7316 | 1.5474 | 11.2908 | 10.8718 | 10.3908 | 9.7718 | 9.5645 | 9.2382 | 8.8866 | 8.5908 | 8.2855 | 6.8739 | 3.0529 | 1.0961 | 0.91711
|  | MINTLAW | FB |  |  |  |  | -6.3237 | -6.4142 | -6.5237 | -6.6279 | -6.7268 | -6.8405 | -6.9468 | -7.03 | -7.1153 | -7.5511 | -7.7384 | -7.8963 | -7.9942 | 11.1053 | 10.9263 | 10.7063 | 10.4989 | 10.3032 | 10.0768 | 9.8653 | 9.7063 | 9.54 | 8.6358 | 8.3021 | 8.02 | 7.8411 | 11.635 | 11.4771 | 11.2845 | 11.1024 | 10.9297 | 10.7308 | 10.5455 | 10.4045 | 10.2582 | 9.3834 | 9.0529 | 8.7729 | 8.595
| BRIDGE OF DUN | MONTROSE NORTH | MINIMUM HEADROOM | NO 71226 59070 | NO | YES | 0.0010204 | 15.2068 | 14.6521 | 13.4826 | 36.8916 | 36.7632 | 36.6095 | 36.4547 | 36.1558 | 35.7284 | 35.6253 | 34.7989 | 34.4126 | 34.1884 | 12.6663 | 12.0516 | 10.7474 | 33.5926 | 33.4537 | 33.2874 | 33.1211 | 32.7905 | 32.3179 | 32.2084 | 31.2989 | 30.8789 | 30.6358 | 13.8076 | 13.1803 | 11.8466 | 35.3137 | 35.1726 | 35.0032 | 34.8347 | 34.4968 | 34.0147 | 33.9032 | 32.9547 | 32.5179 | 32.2653
|  | MONTROSE NORTH | EE |  |  |  |  | 15.3911 | 14.6521 | 13.4826 | 36.8916 | 36.7632 | 36.6095 | 36.4547 | 36.2558 | 36.0432 | 35.9558 | 34.7989 | 34.4126 | 34.1884 | 12.8737 | 12.0516 | 10.7474 | 33.5926 | 33.4537 | 33.2874 | 33.1211 | 32.9032 | 32.6695 | 32.5768 | 31.2989 | 30.8789 | 30.6358 | 14.0203 | 13.1803 | 11.8466 | 35.3137 | 35.1726 | 35.0032 | 34.8347 | 34.6116 | 34.3747 | 34.28 | 32.9547 | 32.5179 | 32.2653
|  | MONTROSE NORTH | HT |  |  |  |  | 15.2626 | 14.7058 | 13.6795 | 37.0989 | 36.9589 | 36.82 | 36.4979 | 36.1558 | 35.7284 | 35.6253 | 34.8232 | 34.5326 | 34.32 | 12.7295 | 12.1105 | 10.9674 | 33.8253 | 33.6737 | 33.5232 | 33.1674 | 32.7905 | 32.3179 | 32.2084 | 31.4105 | 31.0779 | 30.7895 | 13.8718 | 13.2403 | 12.0718 | 35.5516 | 35.3979 | 35.2442 | 34.8811 | 34.4968 | 34.0147 | 33.9032 | 33.0737 | 32.7295 | 32.4305
|  | MONTROSE NORTH | HE |  |  |  |  | 15.2068 | 14.9784 | 13.8447 | 37.2937 | 37.1958 | 37.0737 | 36.9505 | 36.8147 | 36.6779 | 36.6284 | 36.0463 | 35.4316 | 35.1811 | 12.6663 | 12.4147 | 11.1505 | 34.0411 | 33.9347 | 33.8042 | 33.6726 | 33.5242 | 33.3747 | 33.3211 | 32.6789 | 31.9968 | 31.7211 | 13.8076 | 13.5508 | 12.2582 | 35.7716 | 35.6642 | 35.5316 | 35.3979 | 35.2474 | 35.0947 | 35.04 | 34.3853 | 33.6842 | 33.3958
|  | MONTROSE NORTH | FB |  |  |  |  | 16.3132 | 16.1374 | 16.0005 | 39.4368 | 39.36 | 39.2916 | 39.2305 | 39.1821 | 39.14 | 39.1011 | 38.8768 | 38.3179 | 37.9642 | 14.6147 | 14.2674 | 14 | 36.7821 | 36.64 | 36.5158 | 36.4084 | 36.3263 | 36.2568 | 36.1968 | 35.8242 | 35.2063 | 34.8137 | 15.4718 | 15.2729 | 15.1129 | 38.5747 | 38.4295 | 38.3032 | 38.1937 | 38.1095 | 38.04 | 37.9779 | 37.5979 | 36.9674 | 36.5674
| TARLAND | MOSSAT | MINIMUM HEADROOM | NJ 47470 19897 | NO | YES | 0 | 2.6547 | 2.5516 | 7.7147 | 7.5937 | 7.5495 | 7.5042 | 7.4568 | 7.4158 | 7.3747 | 7.3347 | 4.3063 | 4.1516 | 4.0389 | 2.3453 | 2.2263 | 7.3737 | 7.2316 | 7.1821 | 7.1316 | 7.0789 | 7.0337 | 6.9874 | 6.9421 | 6.7726 | 4.3011 | 4.1411 | 2.3453 | 2.2263 | 7.3737 | 7.2326 | 7.1832 | 7.1326 | 7.08 | 7.0347 | 6.9884 | 6.9432 | 6.7737 | 3.6905 | 3.5253
|  | MOSSAT | EE |  |  |  |  | 2.6547 | 2.5516 | 7.7147 | 7.5937 | 7.5495 | 7.5042 | 7.4568 | 7.4158 | 7.3747 | 7.3347 | 7.1832 | 7.0358 | 6.9179 | 2.3453 | 2.2263 | 7.3737 | 7.2316 | 7.1821 | 7.1316 | 7.0789 | 7.0337 | 6.9874 | 6.9421 | 6.7726 | 6.6042 | 6.4674 | 2.3453 | 2.2263 | 7.3737 | 7.2326 | 7.1832 | 7.1326 | 7.08 | 7.0347 | 6.9884 | 6.9432 | 6.7737 | 6.6053 | 6.4695
|  | MOSSAT | HT |  |  |  |  | 2.66 | 2.5747 | 7.7358 | 7.6232 | 7.5747 | 7.5326 | 7.4895 | 7.4474 | 7.4042 | 7.3589 | 4.3063 | 4.1516 | 4.0389 | 2.3505 | 2.2516 | 7.3979 | 7.2674 | 7.2126 | 7.1653 | 7.1179 | 7.0705 | 7.0232 | 6.9726 | 6.7916 | 4.3011 | 4.1411 | 2.3516 | 2.2526 | 7.3979 | 7.2684 | 7.2137 | 7.1663 | 7.1189 | 7.0716 | 7.0242 | 6.9737 | 6.7937 | 3.6905 | 3.5253
|  | MOSSAT | HE |  |  |  |  | 2.6821 | 2.6084 | 7.7853 | 7.6863 | 7.66 | 7.6316 | 7.6021 | 7.5768 | 7.5484 | 7.5221 | 7.4389 | 5.9663 | 5.8947 | 2.3758 | 2.2916 | 7.4547 | 7.3389 | 7.3105 | 7.28 | 7.2484 | 7.22 | 7.1895 | 7.1589 | 7.0653 | 5.8474 | 5.7695 | 2.3768 | 2.2916 | 7.4558 | 7.34 | 7.3116 | 7.2811 | 7.2495 | 7.2211 | 7.1905 | 7.16 | 7.0663 | 5.5358 | 5.4537
|  | MOSSAT | FB |  |  |  |  | 2.7516 | 2.7221 | 7.9432 | 7.9105 | 7.8747 | 7.8484 | 7.8242 | 7.8011 | 7.7821 | 7.7568 | 7.6726 | 7.5853 | 7.5116 | 2.4579 | 2.4242 | 7.6389 | 7.6 | 7.56 | 7.5284 | 7.5011 | 7.4758 | 7.4537 | 7.4242 | 7.3295 | 7.2295 | 7.1442 | 2.4579 | 2.4242 | 7.6389 | 7.6011 | 7.56 | 7.5295 | 7.5011 | 7.4758 | 7.4537 | 7.4253 | 7.3295 | 7.2305 | 7.1453
| THURSO | MOUNT PLEASANT | MINIMUM HEADROOM | ND 12706 67832 | YES | YES | 0.45918 | 14.4716 | 14.3874 | 14.3116 | 14.2295 | 14.1453 | 13.1947 | 12.4326 | 11.7126 | 11.3853 | 11.0989 | 10.3158 | 10.0621 | 9.8821 | 14.0821 | 13.9842 | 13.8979 | 13.8063 | 13.7116 | 12.5895 | 11.7116 | 10.8811 | 10.5074 | 10.1811 | 9.3189 | 9.0474 | 8.8105 | 14.5245 | 14.4276 | 14.3424 | 14.2508 | 14.1582 | 13.0518 | 12.1855 | 11.3666 | 10.9992 | 10.6761 | 9.8203 | 9.5497 | 9.3139
|  | MOUNT PLEASANT | EE |  |  |  |  | 14.4716 | 14.3874 | 14.3116 | 14.2295 | 14.1453 | 14.0505 | 13.9579 | 13.0116 | 12.2411 | 11.4632 | 10.34 | 10.0979 | 9.9211 | 14.0821 | 13.9842 | 13.8979 | 13.8063 | 13.7116 | 13.6074 | 13.5063 | 12.3905 | 11.5021 | 10.6032 | 9.3189 | 9.0474 | 8.8484 | 14.5245 | 14.4276 | 14.3424 | 14.2508 | 14.1582 | 14.0539 | 13.9539 | 12.8539 | 11.9782 | 11.0929 | 9.8203 | 9.5497 | 9.3518
|  | MOUNT PLEASANT | HT |  |  |  |  | 14.4947 | 14.4221 | 14.3484 | 14.2716 | 14.1863 | 13.1947 | 12.4326 | 11.7126 | 11.3853 | 11.0989 | 10.3158 | 10.0621 | 9.8821 | 14.1105 | 14.0242 | 13.9411 | 13.8558 | 13.7611 | 12.5895 | 11.7116 | 10.8811 | 10.5074 | 10.1811 | 9.3684 | 9.0632 | 8.8105 | 14.5518 | 14.4676 | 14.3855 | 14.3003 | 14.2066 | 13.0518 | 12.1855 | 11.3666 | 10.9992 | 10.6761 | 9.8708 | 9.5655 | 9.3139
|  | MOUNT PLEASANT | HE |  |  |  |  | 14.5474 | 14.4926 | 14.4453 | 14.3947 | 14.3316 | 14.2653 | 14.1968 | 13.1758 | 12.3695 | 11.5653 | 10.7842 | 10.6453 | 10.5495 | 14.1274 | 14.1011 | 14.0579 | 14 | 13.9305 | 13.8589 | 13.7863 | 12.5758 | 11.6442 | 10.7126 | 9.8158 | 9.6611 | 9.5537 | 14.5718 | 14.5455 | 14.4992 | 14.4424 | 14.3729 | 14.3024 | 14.2297 | 13.0371 | 12.1192 | 11.2013 | 10.3161 | 10.1634 | 10.0571
|  | MOUNT PLEASANT | FB |  |  |  |  | 14.5747 | 14.5411 | 14.5063 | 14.4705 | 14.4326 | 14.3926 | 14.3537 | 14.3147 | 13.8695 | 13.4811 | 12.1653 | 11.9958 | 11.8695 | 14.1411 | 14.1305 | 14.1189 | 14.0832 | 14.0379 | 13.9916 | 13.9484 | 13.9042 | 13.3768 | 12.9168 | 11.3947 | 11.2063 | 11.0642 | 14.5855 | 14.575 | 14.5634 | 14.5245 | 14.4803 | 14.435 | 14.3918 | 14.3487 | 13.8287 | 13.375 | 11.875 | 11.6876 | 11.5476
| BEAULY | MUIR OF ORD | MINIMUM HEADROOM | NH 53420 48534 | NO | YES | 0 | 21.1 | 21.0516 | 21.0137 | 20.9632 | 20.9053 | 19.4821 | 18.1442 | 17.0316 | 16.2116 | 15.7516 | 13.0442 | 12.6453 | 12.3516 | 20.5326 | 20.2074 | 19.98 | 19.5558 | 19.3979 | 17.3053 | 15.7368 | 14.4379 | 13.4874 | 12.9579 | 10.5926 | 10.1484 | 9.82 | 21.0484 | 20.7263 | 20.4958 | 20.0653 | 19.9063 | 17.7968 | 16.2284 | 14.9284 | 13.9779 | 13.4474 | 10.6253 | 10.1758 | 9.8442
|  | MUIR OF ORD | EE |  |  |  |  | 21.1 | 21.0516 | 21.0147 | 20.9695 | 20.9168 | 20.8453 | 20.5242 | 19.0221 | 17.7147 | 16.6505 | 13.0442 | 12.6453 | 12.3516 | 20.5326 | 20.2074 | 19.98 | 19.5558 | 19.3979 | 19.2221 | 18.6358 | 16.7895 | 15.26 | 14.0168 | 10.5926 | 10.1484 | 9.82 | 21.0484 | 20.7263 | 20.4958 | 20.0653 | 19.9063 | 19.7274 | 19.1347 | 17.2758 | 15.7442 | 14.5 | 10.6253 | 10.1758 | 9.8442
|  | MUIR OF ORD | HT |  |  |  |  | 21.1053 | 21.0621 | 21.0137 | 20.9632 | 20.9053 | 19.4821 | 18.1442 | 17.0316 | 16.2116 | 15.7516 | 13.3484 | 12.9284 | 12.6305 | 20.5737 | 20.2663 | 20.0432 | 19.6326 | 19.4642 | 17.3053 | 15.7368 | 14.4379 | 13.4874 | 12.9579 | 10.9189 | 10.4137 | 9.9947 | 21.0874 | 20.7884 | 20.5621 | 20.1463 | 19.9779 | 17.7968 | 16.2284 | 14.9284 | 13.9779 | 13.4474 | 11.0495 | 10.5442 | 10.1232
|  | MUIR OF ORD | HE |  |  |  |  | 21.1179 | 21.0737 | 21.0442 | 21.0011 | 20.9484 | 20.8832 | 20.8158 | 19.28 | 17.9221 | 16.8579 | 14.8989 | 14.6611 | 14.4958 | 20.6663 | 20.3937 | 20.2189 | 19.8526 | 19.7368 | 19.4589 | 19.0874 | 17.0789 | 15.4863 | 14.2389 | 12.2632 | 11.9947 | 11.8074 | 21.1758 | 20.9168 | 20.74 | 20.3695 | 20.2526 | 19.9705 | 19.5958 | 17.5705 | 15.9768 | 14.7284 | 12.5726 | 12.3032 | 12.1147
|  | MUIR OF ORD | FB |  |  |  |  | 21.1484 | 21.1337 | 21.1179 | 21.1011 | 21.0821 | 21.0632 | 21.0432 | 21.0232 | 20.7884 | 20.2516 | 18.3137 | 18.0432 | 17.8411 | 20.7505 | 20.6221 | 20.5189 | 20.3411 | 20.2705 | 20.1989 | 19.9884 | 19.7874 | 18.9126 | 18.1832 | 15.9147 | 15.6095 | 15.3779 | 21.2168 | 21.1358 | 21.0368 | 20.8621 | 20.7905 | 20.7189 | 20.5063 | 20.3032 | 19.4189 | 18.6811 | 16.4084 | 16.1021 | 15.8695
| BEAULY | MUIREND | MINIMUM HEADROOM | NH 64508 54337 | YES | YES | 0 | 3.2315 | 3.1788 | 3.1273 | 3.0041 | 2.9673 | 2.5062 | 2.0073 | 1.6788 | 1.5367 | 1.4967 | 1.3231 | 1.2062 | 1.1273 | 2.7767 | 2.7273 | 2.6778 | 2.5641 | 2.5283 | 2.0146 | 1.3841 | 0.99884 | 0.83358 | 0.79042 | 0.63147 | 0.49042 | 0.37674 | 3.0978 | 3.0315 | 2.9641 | 2.7988 | 2.7536 | 2.122 | 1.5083 | 1.1262 | 0.96095 | 0.91884 | 0.75884 | 0.61884 | 0.50516
|  | MUIREND | EE |  |  |  |  | 3.2315 | 3.1788 | 3.1273 | 3.0041 | 2.9673 | 2.9262 | 2.6852 | 2.3346 | 1.9083 | 1.5946 | 1.3557 | 1.2399 | 1.1557 | 2.7767 | 2.7273 | 2.6778 | 2.5641 | 2.5283 | 2.4894 | 2.2652 | 1.8041 | 1.2746 | 0.90411 | 0.63147 | 0.502 | 0.40516 | 3.0978 | 3.0315 | 2.9641 | 2.7988 | 2.7536 | 2.7041 | 2.3778 | 1.9157 | 1.4009 | 1.0315 | 0.75989 | 0.63042 | 0.53358
|  | MUIREND | HT |  |  |  |  | 3.2409 | 3.1915 | 3.1399 | 3.0178 | 2.9778 | 2.5062 | 2.0073 | 1.6788 | 1.5367 | 1.4967 | 1.3231 | 1.2062 | 1.1273 | 2.7841 | 2.7378 | 2.6894 | 2.5757 | 2.5378 | 2.0146 | 1.3841 | 0.99884 | 0.83358 | 0.79042 | 0.63147 | 0.49042 | 0.37674 | 3.1094 | 3.0483 | 2.982 | 2.8188 | 2.7704 | 2.122 | 1.5083 | 1.1262 | 0.96095 | 0.91884 | 0.75884 | 0.61884 | 0.50516
|  | MUIREND | HE |  |  |  |  | 3.2641 | 3.222 | 3.182 | 3.0704 | 3.0399 | 2.9536 | 2.8199 | 2.4157 | 1.9567 | 1.6536 | 1.5641 | 1.4936 | 1.4452 | 2.8062 | 2.7673 | 2.7294 | 2.6262 | 2.5967 | 2.5146 | 2.3904 | 1.9031 | 1.3273 | 0.97042 | 0.86726 | 0.78726 | 0.73253 | 3.1378 | 3.0873 | 3.0367 | 2.8862 | 2.8515 | 2.7378 | 2.5599 | 2.0115 | 1.4525 | 1.0978 | 0.99463 | 0.91568 | 0.85989
|  | MUIREND | FB |  |  |  |  | 3.2831 | 3.2631 | 3.2378 | 3.1862 | 3.1694 | 3.1525 | 3.0841 | 3.0178 | 2.8599 | 2.6715 | 2.2946 | 2.2188 | 2.162 | 2.8252 | 2.8062 | 2.782 | 2.7346 | 2.7188 | 2.7031 | 2.6388 | 2.5778 | 2.4315 | 2.2346 | 1.7388 | 1.6483 | 1.5799 | 3.1609 | 3.1357 | 3.1041 | 3.0367 | 3.0146 | 2.9936 | 2.902 | 2.8115 | 2.5957 | 2.3357 | 1.8546 | 1.7662 | 1.6988
| NAIRN | NAIRN CENTRAL | MINIMUM HEADROOM | NH 88496 56295 | NO | YES | 0.72143 | 16.7721 | 16.7121 | 16.5111 | 16.1405 | 15.9563 | 15.0416 | 14.0637 | 12.8858 | 11.8079 | 11.2942 | 10.2142 | 9.6289 | 9.2226 | 14.9768 | 14.6284 | 14.2379 | 13.7789 | 13.5621 | 12.4158 | 11.2684 | 9.8958 | 8.6453 | 8.0568 | 6.9611 | 6.3021 | 5.7274 | 15.5434 | 15.2171 | 14.8508 | 14.4213 | 14.2161 | 13.1455 | 12.0371 | 10.6655 | 9.4139 | 8.8245 | 7.7287 | 7.0708 | 6.4961
|  | NAIRN CENTRAL | EE |  |  |  |  | 16.7721 | 16.7121 | 16.5111 | 16.1405 | 15.9563 | 15.7511 | 15.3942 | 14.6026 | 13.6195 | 12.4226 | 10.33 | 9.7647 | 9.3374 | 14.9768 | 14.6284 | 14.2379 | 13.7789 | 13.5621 | 13.3242 | 12.8937 | 11.9189 | 10.7726 | 9.3758 | 6.9611 | 6.3242 | 5.8411 | 15.5434 | 15.2171 | 14.8508 | 14.4213 | 14.2161 | 13.9876 | 13.5824 | 12.6718 | 11.5403 | 10.1434 | 7.7287 | 7.0929 | 6.6087
|  | NAIRN CENTRAL | HT |  |  |  |  | 16.7816 | 16.7237 | 16.5753 | 16.2216 | 16.0226 | 15.0416 | 14.0637 | 12.8858 | 11.8079 | 11.2942 | 10.2142 | 9.6289 | 9.2226 | 15.0347 | 14.7042 | 14.3211 | 13.8853 | 13.6526 | 12.4158 | 11.2684 | 9.8958 | 8.6453 | 8.0568 | 7.0105 | 6.3021 | 5.7274 | 15.5982 | 15.2876 | 14.9287 | 14.5192 | 14.2982 | 13.1455 | 12.0371 | 10.6655 | 9.4139 | 8.8245 | 7.7782 | 7.0708 | 6.4961
|  | NAIRN CENTRAL | HE |  |  |  |  | 16.8016 | 16.7458 | 16.7058 | 16.4658 | 16.3332 | 16.1205 | 15.8984 | 15.1068 | 14.1005 | 12.8142 | 11.3142 | 10.9732 | 10.7247 | 15.1579 | 14.8758 | 14.5579 | 14.1832 | 14.0316 | 13.7842 | 13.5253 | 12.5263 | 11.3242 | 9.8147 | 8.0737 | 7.6874 | 7.4032 | 15.7139 | 15.4487 | 15.1508 | 14.7992 | 14.6539 | 14.4182 | 14.1718 | 13.2413 | 12.0929 | 10.5845 | 8.8424 | 8.455 | 8.1718
|  | NAIRN CENTRAL | FB |  |  |  |  | 16.8342 | 16.8153 | 16.7942 | 16.7711 | 16.7468 | 16.7216 | 16.6805 | 16.5595 | 16.1953 | 15.7332 | 13.6626 | 13.2889 | 13.0047 | 15.2916 | 15.1505 | 14.9737 | 14.7821 | 14.6895 | 14.5958 | 14.4463 | 14.2989 | 13.84 | 13.2547 | 10.7705 | 10.3484 | 10.0221 | 15.8403 | 15.7087 | 15.5434 | 15.3634 | 15.2761 | 15.1866 | 15.0466 | 14.9076 | 14.4803 | 13.9361 | 11.5392 | 11.1171 | 10.7908
| STRICHEN | NEW PITSLIGO | MINIMUM HEADROOM | NJ 88529 54853 | NO | YES | 0 | 6.0863 | 6.0579 | 6.0305 | 5.9968 | 5.9611 | 5.9274 | 5.8674 | 5.7842 | 5.6768 | 5.6411 | 1.1211 | 0.23789 | -1.8547 | 6.0516 | 6.0189 | 5.9884 | 5.9505 | 5.9105 | 5.8737 | 5.8063 | 5.7105 | 5.5863 | 5.5484 | 1.94 | 1.2168 | -0.47158 | 6.0516 | 6.02 | 5.9895 | 5.9516 | 5.9116 | 5.8747 | 5.8063 | 5.7105 | 5.5874 | 5.5495 | 1.0305 | 0.14105 | -1.9537
|  | NEW PITSLIGO | EE |  |  |  |  | 6.0863 | 6.0579 | 6.0305 | 5.9968 | 5.9611 | 5.9274 | 5.8937 | 5.8453 | 5.7863 | 5.7547 | 5.0526 | 2.8979 | 2.8147 | 6.0516 | 6.0189 | 5.9884 | 5.9505 | 5.9105 | 5.8737 | 5.8379 | 5.7832 | 5.7147 | 5.6811 | 5.0221 | 3.2632 | 3.1716 | 6.0516 | 6.02 | 5.9895 | 5.9516 | 5.9116 | 5.8747 | 5.8379 | 5.7842 | 5.7158 | 5.6821 | 4.9305 | 2.7516 | 2.6568
|  | NEW PITSLIGO | HT |  |  |  |  | 6.0947 | 6.0674 | 6.04 | 6.0084 | 5.9726 | 5.9421 | 5.8674 | 5.7842 | 5.6768 | 5.6411 | 3.4505 | 3.3295 | 3.2432 | 6.0611 | 6.0305 | 6 | 5.9642 | 5.9253 | 5.8916 | 5.8063 | 5.7105 | 5.5863 | 5.5484 | 5.0432 | 3.6242 | 3.5042 | 6.0611 | 6.0305 | 6 | 5.9653 | 5.9263 | 5.8926 | 5.8063 | 5.7105 | 5.5874 | 5.5495 | 4.9705 | 3.2053 | 3.0811
|  | NEW PITSLIGO | HE |  |  |  |  | 6.1137 | 6.0947 | 6.0789 | 6.0621 | 6.04 | 6.02 | 5.9979 | 5.9484 | 5.8842 | 5.8663 | 1.1211 | 0.23789 | -1.8547 | 6.0821 | 6.0621 | 6.0453 | 6.0263 | 6.0032 | 5.9811 | 5.9579 | 5.9011 | 5.8274 | 5.8074 | 1.94 | 1.2168 | -0.47158 | 6.0832 | 6.0621 | 6.0453 | 6.0263 | 6.0032 | 5.9811 | 5.9579 | 5.9011 | 5.8284 | 5.8084 | 1.0305 | 0.14105 | -1.9537
|  | NEW PITSLIGO | FB |  |  |  |  | 6.1232 | 6.1126 | 6.1011 | 6.0895 | 6.0758 | 6.0642 | 6.0526 | 6.0411 | 6.02 | 6.0011 | 5.8368 | 5.7147 | 5.6632 | 6.0937 | 6.0811 | 6.0674 | 6.0558 | 6.04 | 6.0263 | 6.0137 | 6.0011 | 5.9768 | 5.9547 | 5.7653 | 5.6253 | 5.5653 | 6.0937 | 6.0811 | 6.0684 | 6.0558 | 6.0411 | 6.0274 | 6.0137 | 6.0011 | 5.9768 | 5.9558 | 5.7663 | 5.6263 | 5.5663
| DUNOON | NEWTON | MINIMUM HEADROOM | NS 04939 98621 | YES | YES | 0 | 0.33474 | 0.33053 | 0.32737 | 0.32211 | 0.31579 | 0.30842 | 0.30105 | 0.29474 | 0.28737 | 0.28105 | 0.25895 | 0.23263 | 0.20947 | 0.31789 | 0.31474 | 0.30947 | 0.30421 | 0.29895 | 0.29263 | 0.28737 | 0.28105 | 0.27579 | 0.27053 | 0.24632 | 0.22105 | 0.19579 | 0.32 | 0.31474 | 0.30737 | 0.3 | 0.29263 | 0.28421 | 0.27684 | 0.26947 | 0.26105 | 0.25474 | 0.22947 | 0.20105 | 0.17579
|  | NEWTON | EE |  |  |  |  | 0.33474 | 0.33053 | 0.32737 | 0.32211 | 0.31579 | 0.30842 | 0.30105 | 0.29474 | 0.28737 | 0.28105 | 0.25895 | 0.23263 | 0.20947 | 0.31789 | 0.31474 | 0.30947 | 0.30421 | 0.29895 | 0.29263 | 0.28737 | 0.28105 | 0.27579 | 0.27053 | 0.24632 | 0.22105 | 0.19579 | 0.32 | 0.31474 | 0.30737 | 0.3 | 0.29263 | 0.28421 | 0.27684 | 0.26947 | 0.26105 | 0.25474 | 0.22947 | 0.20105 | 0.17579
|  | NEWTON | HT |  |  |  |  | 0.33579 | 0.33368 | 0.33263 | 0.33053 | 0.32737 | 0.32316 | 0.32105 | 0.31474 | 0.31053 | 0.30526 | 0.28632 | 0.26947 | 0.25789 | 0.31895 | 0.31684 | 0.31579 | 0.31053 | 0.30632 | 0.30105 | 0.29789 | 0.29263 | 0.28842 | 0.28421 | 0.26947 | 0.25368 | 0.24 | 0.32211 | 0.32 | 0.31789 | 0.31368 | 0.30632 | 0.30211 | 0.29895 | 0.29263 | 0.28737 | 0.28316 | 0.26632 | 0.24737 | 0.23053
|  | NEWTON | HE |  |  |  |  | 0.33684 | 0.33474 | 0.33368 | 0.33053 | 0.32947 | 0.32737 | 0.32526 | 0.32421 | 0.32211 | 0.31895 | 0.30947 | 0.3 | 0.29158 | 0.32 | 0.31789 | 0.31684 | 0.31474 | 0.31263 | 0.31053 | 0.30947 | 0.30632 | 0.30316 | 0.29895 | 0.29053 | 0.28316 | 0.27684 | 0.32316 | 0.32105 | 0.31895 | 0.31579 | 0.31368 | 0.31158 | 0.30947 | 0.30526 | 0.30211 | 0.29789 | 0.28632 | 0.27579 | 0.26737
|  | NEWTON | FB |  |  |  |  | 0.33789 | 0.33789 | 0.33684 | 0.33579 | 0.33474 | 0.33474 | 0.33368 | 0.33368 | 0.33158 | 0.33158 | 0.32526 | 0.31579 | 0.31368 | 0.32 | 0.32 | 0.31895 | 0.31895 | 0.31789 | 0.31684 | 0.31579 | 0.31474 | 0.31263 | 0.31053 | 0.30211 | 0.29158 | 0.28842 | 0.32421 | 0.32316 | 0.32211 | 0.32211 | 0.32105 | 0.32 | 0.31895 | 0.31789 | 0.31579 | 0.31474 | 0.30421 | 0.29474 | 0.29053
| REDMOSS | NEWTONHILL | MINIMUM HEADROOM | NO 90190 93653 | NO | YES | 0.30612 | 15.4279 | 14.0637 | 27.1274 | 25.2263 | 23.8411 | 22.4537 | 20.9358 | 20.4053 | 19.84 | 19.6768 | 16.6147 | 14.3411 | 13.9389 | 12.8579 | 11.2716 | 23.3158 | 21.0347 | 19.3726 | 17.7368 | 15.9621 | 15.3474 | 14.6916 | 14.5116 | 11.1095 | 9.0747 | 8.6158 | 14.0687 | 12.4761 | 24.9132 | 22.69 | 21.0437 | 19.4121 | 17.6437 | 17.03 | 16.3763 | 16.1974 | 12.8037 | 10.31 | 9.8511
|  | NEWTONHILL | EE |  |  |  |  | 15.4426 | 14.0637 | 27.1274 | 25.2674 | 23.9442 | 22.4537 | 20.9358 | 20.4053 | 19.84 | 19.7768 | 16.7895 | 14.3411 | 13.9389 | 12.8758 | 11.2716 | 23.3158 | 21.0832 | 19.4947 | 17.7368 | 15.9621 | 15.3474 | 14.6916 | 14.6253 | 11.1389 | 9.0747 | 8.6158 | 14.0866 | 12.4761 | 24.9132 | 22.7374 | 21.1647 | 19.4121 | 17.6437 | 17.03 | 16.3763 | 16.3111 | 12.8342 | 10.31 | 9.8511
|  | NEWTONHILL | HT |  |  |  |  | 15.4279 | 14.1847 | 27.1516 | 25.2263 | 23.8411 | 23.28 | 22.6589 | 22.0558 | 20.8789 | 19.6768 | 16.6147 | 14.5411 | 14.1516 | 12.8579 | 11.4116 | 23.3453 | 21.0347 | 19.3726 | 18.7116 | 17.9895 | 17.2916 | 15.9158 | 14.5116 | 11.1095 | 9.2832 | 8.7253 | 14.0687 | 12.6161 | 24.9416 | 22.69 | 21.0437 | 20.3847 | 19.6647 | 18.9689 | 17.5974 | 16.1974 | 12.8037 | 10.6089 | 10.0532
|  | NEWTONHILL | HE |  |  |  |  | 15.4795 | 14.3153 | 27.4021 | 25.5716 | 24.2947 | 22.8674 | 21.3074 | 20.7832 | 20.2105 | 20.18 | 17.5505 | 14.4189 | 14.1726 | 12.9147 | 11.56 | 23.6379 | 21.4411 | 19.9084 | 18.2158 | 16.3905 | 15.7811 | 15.1137 | 15.0811 | 12 | 9.5389 | 9.2558 | 14.1255 | 12.7655 | 25.2279 | 23.0868 | 21.5784 | 19.8911 | 18.0711 | 17.4626 | 16.7974 | 16.7647 | 13.6932 | 10.5279 | 10.2447
|  | NEWTONHILL | FB |  |  |  |  | 16.1289 | 16.0058 | 30.0105 | 29.4653 | 28.9274 | 28.2589 | 27.4726 | 26.5989 | 26.2979 | 26.2632 | 25.3126 | 24.3263 | 24.0968 | 13.9789 | 13.5284 | 26.6937 | 26.0589 | 25.4347 | 24.6568 | 23.7274 | 22.6789 | 22.3211 | 22.2832 | 21.1558 | 19.98 | 19.7095 | 15.1603 | 14.7424 | 28.2795 | 27.6426 | 27.0153 | 26.2332 | 25.3153 | 24.2921 | 23.9426 | 23.9068 | 22.8058 | 21.6489 | 21.3795
| ALNESS | NIGG | MINIMUM HEADROOM | NH 79490 69773 | YES | YES | 0 | 1.2895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 1.0084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 1.1758 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258
|  | NIGG | EE |  |  |  |  | 1.2895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 1.0084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 1.1758 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258
|  | NIGG | HT |  |  |  |  | 1.2895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 1.0084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 1.1758 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258
|  | NIGG | HE |  |  |  |  | 1.2895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 1.0084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 1.1758 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258
|  | NIGG | FB |  |  |  |  | 1.2895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 29.3895 | 1.0084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 27.6084 | 1.1758 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258 | 28.5258
| CHARLESTON | NINEWELLS | MINIMUM HEADROOM | NO 35148 30641 | NO | YES | 0.86735 | 14.3279 | 14.1921 | 14.0984 | 13.4563 | 13.4121 | 13.3574 | 13.1984 | 13.1532 | 13.1111 | 13.0679 | 12.9142 | 12.7763 | 12.6658 | 14.8758 | 14.6916 | 14.5663 | 13.1653 | 13.1021 | 13.0253 | 12.6716 | 12.6116 | 12.5547 | 12.4937 | 12.2874 | 12.0779 | 11.8821 | 15.6403 | 15.3603 | 15.1603 | 13.5287 | 13.4613 | 13.3813 | 13.0276 | 12.9624 | 12.9024 | 12.8361 | 12.615 | 12.3939 | 12.2192
|  | NINEWELLS | EE |  |  |  |  | 14.3279 | 14.1921 | 14.0984 | 13.4563 | 13.4121 | 13.3574 | 13.1984 | 13.1532 | 13.1111 | 13.0679 | 12.9142 | 12.7763 | 12.6658 | 14.8758 | 14.6916 | 14.5663 | 13.1653 | 13.1021 | 13.0253 | 12.6716 | 12.6116 | 12.5547 | 12.4937 | 12.2874 | 12.0832 | 11.9253 | 15.6403 | 15.3603 | 15.1603 | 13.5287 | 13.4613 | 13.3813 | 13.0276 | 12.9624 | 12.9024 | 12.8361 | 12.615 | 12.3939 | 12.2192
|  | NINEWELLS | HT |  |  |  |  | 14.3416 | 14.2153 | 14.1237 | 13.4868 | 13.4437 | 13.4026 | 13.3626 | 13.3226 | 13.2658 | 13.1868 | 12.9395 | 12.8111 | 12.7174 | 14.8916 | 14.7179 | 14.5958 | 13.2042 | 13.1358 | 13.0737 | 13.0137 | 12.9558 | 12.8568 | 12.7032 | 12.3 | 12.0779 | 11.8821 | 15.6613 | 15.3971 | 15.2013 | 13.5792 | 13.5118 | 13.4487 | 13.3887 | 13.3287 | 13.2297 | 13.0761 | 12.6729 | 12.4455 | 12.2445
|  | NINEWELLS | HE |  |  |  |  | 14.3637 | 14.2416 | 14.1647 | 13.5395 | 13.5089 | 13.4679 | 13.3247 | 13.2963 | 13.2689 | 13.2458 | 13.1689 | 13.0963 | 13.0416 | 14.9189 | 14.7516 | 14.6484 | 13.3074 | 13.2663 | 13.2116 | 12.8821 | 12.8442 | 12.8032 | 12.7663 | 12.6505 | 12.5305 | 12.4442 | 15.7003 | 15.4455 | 15.2834 | 13.6824 | 13.6403 | 13.5845 | 13.2571 | 13.2182 | 13.1771 | 13.1403 | 13.0192 | 12.8939 | 12.8013
|  | NINEWELLS | FB |  |  |  |  | 14.3953 | 14.3553 | 14.3111 | 14.2921 | 14.2711 | 14.2511 | 14.2047 | 14.1711 | 14.1532 | 14.1321 | 14.0553 | 13.9795 | 13.93 | 14.9621 | 14.9063 | 14.8453 | 14.8221 | 14.7968 | 14.7726 | 14.7095 | 14.6653 | 14.6432 | 14.6179 | 14.5263 | 14.4337 | 14.3695 | 15.7624 | 15.6782 | 15.5855 | 15.5539 | 15.5192 | 15.4866 | 15.3918 | 15.3266 | 15.2982 | 15.2613 | 15.1297 | 14.9887 | 14.8887
| THURSO | NORTH HOY | MINIMUM HEADROOM | HY 25681 02549 | YES | YES | 0 | 0.21053 | 0.21053 | 0.21053 | 0.20842 | 0.20737 | 0.20632 | 0.20421 | 0.20316 | 0.20105 | 0.2 | 0.19368 | 0.18737 | 0.18526 | 0.19895 | 0.19789 | 0.19789 | 0.19474 | 0.19263 | 0.19158 | 0.18947 | 0.18842 | 0.18526 | 0.18316 | 0.17684 | 0.16947 | 0.16632 | 0.20211 | 0.20211 | 0.20105 | 0.19789 | 0.19684 | 0.19579 | 0.19263 | 0.19158 | 0.18947 | 0.18737 | 0.18105 | 0.17474 | 0.17158
|  | NORTH HOY | EE |  |  |  |  | 0.21053 | 0.21053 | 0.21053 | 0.20842 | 0.20737 | 0.20632 | 0.20421 | 0.20421 | 0.20105 | 0.2 | 0.19474 | 0.18737 | 0.18526 | 0.19895 | 0.19789 | 0.19789 | 0.19474 | 0.19263 | 0.19158 | 0.18947 | 0.18842 | 0.18526 | 0.18316 | 0.17684 | 0.16947 | 0.16632 | 0.20211 | 0.20211 | 0.20105 | 0.19789 | 0.19684 | 0.19579 | 0.19263 | 0.19158 | 0.18947 | 0.18737 | 0.18105 | 0.17474 | 0.17158
|  | NORTH HOY | HT |  |  |  |  | 0.21053 | 0.21053 | 0.21053 | 0.20947 | 0.20842 | 0.20632 | 0.20526 | 0.20316 | 0.20316 | 0.2 | 0.19368 | 0.18737 | 0.18632 | 0.19895 | 0.19789 | 0.19789 | 0.19684 | 0.19474 | 0.19158 | 0.19053 | 0.18842 | 0.18737 | 0.18421 | 0.17789 | 0.17053 | 0.16737 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.19789 | 0.19579 | 0.19474 | 0.19158 | 0.19053 | 0.18842 | 0.18211 | 0.17474 | 0.17263
|  | NORTH HOY | HE |  |  |  |  | 0.21158 | 0.21053 | 0.21053 | 0.21053 | 0.20947 | 0.20947 | 0.20842 | 0.20737 | 0.20737 | 0.20737 | 0.20632 | 0.20526 | 0.20421 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19684 | 0.19684 | 0.19579 | 0.19474 | 0.19474 | 0.19368 | 0.19263 | 0.19053 | 0.18947 | 0.20421 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.19895 | 0.19789 | 0.19789 | 0.19684 | 0.19579 | 0.19368 | 0.19368
|  | NORTH HOY | FB |  |  |  |  | 0.21158 | 0.21158 | 0.21053 | 0.21053 | 0.21053 | 0.21053 | 0.21053 | 0.21053 | 0.20947 | 0.20947 | 0.20737 | 0.20632 | 0.20526 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19789 | 0.19789 | 0.19684 | 0.19579 | 0.19368 | 0.19158 | 0.19053 | 0.20421 | 0.20421 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.19895 | 0.19684 | 0.19579 | 0.19474
| BEAULY | NORTH KESSOCK | MINIMUM HEADROOM | NH 65004 48461 | YES | YES | 0 | 3.9074 | 3.8779 | 3.8495 | 3.7705 | 3.7379 | 3.1158 | 2.7011 | 2.4547 | 2.3484 | 2.3168 | 2.1863 | 2.0958 | 2.0337 | 3.9853 | 3.9516 | 3.92 | 3.8274 | 3.7895 | 3.0432 | 2.5474 | 2.2526 | 2.1274 | 2.0937 | 1.9632 | 1.8611 | 1.7716 | 3.9832 | 3.9726 | 3.9632 | 3.9147 | 3.8779 | 3.1316 | 2.6347 | 2.34 | 2.2147 | 2.1811 | 2.0505 | 1.9484 | 1.86
|  | NORTH KESSOCK | EE |  |  |  |  | 3.9074 | 3.8779 | 3.8495 | 3.7705 | 3.7379 | 3.7021 | 3.4874 | 2.9642 | 2.6253 | 2.3874 | 2.2032 | 2.1179 | 2.0526 | 3.9853 | 3.9516 | 3.92 | 3.8274 | 3.7895 | 3.7495 | 3.4947 | 2.8674 | 2.4611 | 2.1768 | 1.9632 | 1.8653 | 1.7895 | 3.9832 | 3.9726 | 3.9632 | 3.9147 | 3.8779 | 3.8379 | 3.5832 | 2.9547 | 2.5484 | 2.2653 | 2.0505 | 1.9537 | 1.8779
|  | NORTH KESSOCK | HT |  |  |  |  | 3.9158 | 3.8895 | 3.8632 | 3.7832 | 3.7495 | 3.1158 | 2.7011 | 2.4547 | 2.3484 | 2.3168 | 2.1863 | 2.0958 | 2.0337 | 3.9958 | 3.9653 | 3.9358 | 3.8421 | 3.8053 | 3.0432 | 2.5474 | 2.2526 | 2.1274 | 2.0937 | 1.9737 | 1.8611 | 1.7716 | 3.9842 | 3.9747 | 3.9632 | 3.9295 | 3.8926 | 3.1316 | 2.6347 | 2.34 | 2.2147 | 2.1811 | 2.0611 | 1.9484 | 1.86
|  | NORTH KESSOCK | HE |  |  |  |  | 3.9358 | 3.9158 | 3.9 | 3.8295 | 3.8053 | 3.7389 | 3.62 | 3 | 2.6505 | 2.4316 | 2.36 | 2.3084 | 2.2684 | 4.0189 | 3.9968 | 3.9789 | 3.8958 | 3.8695 | 3.7926 | 3.6526 | 2.9074 | 2.4884 | 2.2242 | 2.1432 | 2.0832 | 2.0358 | 3.9884 | 3.9789 | 3.9716 | 3.9611 | 3.9505 | 3.8811 | 3.7411 | 2.9958 | 2.5768 | 2.3126 | 2.2305 | 2.1705 | 2.1242
|  | NORTH KESSOCK | FB |  |  |  |  | 3.9474 | 3.9358 | 3.9232 | 3.8895 | 3.8758 | 3.86 | 3.8 | 3.74 | 3.4937 | 3.3147 | 2.9832 | 2.9232 | 2.8779 | 4.0316 | 4.0179 | 4.0032 | 3.9642 | 3.9474 | 3.9305 | 3.8579 | 3.7874 | 3.4916 | 3.2768 | 2.8811 | 2.8116 | 2.7589 | 3.9947 | 3.9905 | 3.9874 | 3.9832 | 3.9789 | 3.9747 | 3.9463 | 3.8758 | 3.58 | 3.3653 | 2.9695 | 2.9 | 2.8474
| BROADFORD | NOSTIE BRIDGE | MINIMUM HEADROOM | NG 85209 27252 | YES | YES | 0 | 0.47158 | 0.44316 | 0.41474 | 0.37368 | 0.32526 | 0.27263 | 0.22211 | 0.17684 | 0.13474 | 0.086316 | -0.18526 | -0.33263 | -0.44632 | 0.34842 | 0.30421 | 0.26316 | 0.20842 | 0.15474 | 0.096842 | 0.041053 | -0.0073684 | -0.053684 | -0.10842 | -0.40842 | -0.57474 | -0.70737 | 0.36316 | 0.32316 | 0.28526 | 0.23474 | 0.18737 | 0.13263 | 0.082105 | 0.035789 | -0.010526 | -0.064211 | -0.36211 | -0.52947 | -0.66632
|  | NOSTIE BRIDGE | EE |  |  |  |  | 0.47158 | 0.44316 | 0.41474 | 0.37368 | 0.32526 | 0.27263 | 0.22211 | 0.17684 | 0.13474 | 0.086316 | -0.17895 | -0.32737 | -0.44632 | 0.34842 | 0.30421 | 0.26316 | 0.20842 | 0.15474 | 0.096842 | 0.041053 | -0.0073684 | -0.053684 | -0.10842 | -0.40842 | -0.57474 | -0.70737 | 0.36316 | 0.32316 | 0.28526 | 0.23474 | 0.18737 | 0.13263 | 0.082105 | 0.035789 | -0.010526 | -0.064211 | -0.36211 | -0.52947 | -0.66632
|  | NOSTIE BRIDGE | HT |  |  |  |  | 0.48 | 0.45474 | 0.43053 | 0.4 | 0.35368 | 0.30632 | 0.26316 | 0.21895 | 0.17474 | 0.095789 | -0.18526 | -0.33263 | -0.43368 | 0.35368 | 0.32316 | 0.28632 | 0.24316 | 0.18421 | 0.13263 | 0.085263 | 0.035789 | -0.012632 | -0.10316 | -0.38316 | -0.55579 | -0.70211 | 0.37474 | 0.34105 | 0.30842 | 0.26737 | 0.21579 | 0.16842 | 0.12526 | 0.08 | 0.034737 | -0.053684 | -0.32947 | -0.5 | -0.64632
|  | NOSTIE BRIDGE | HE |  |  |  |  | 0.49579 | 0.47684 | 0.46105 | 0.44211 | 0.42 | 0.39579 | 0.37158 | 0.35053 | 0.32947 | 0.30211 | 0.10632 | 0.02 | -0.044211 | 0.35789 | 0.34632 | 0.33789 | 0.31474 | 0.28526 | 0.25579 | 0.22632 | 0.19789 | 0.16842 | 0.13474 | -0.091579 | -0.18947 | -0.26211 | 0.39474 | 0.37368 | 0.35368 | 0.33053 | 0.30316 | 0.27474 | 0.24632 | 0.22105 | 0.19368 | 0.16316 | -0.044211 | -0.14 | -0.21158
|  | NOSTIE BRIDGE | FB |  |  |  |  | 0.50842 | 0.49789 | 0.48632 | 0.47474 | 0.46316 | 0.45053 | 0.43789 | 0.42632 | 0.41158 | 0.39158 | 0.22526 | 0.12632 | 0.048421 | 0.36526 | 0.36105 | 0.35684 | 0.35158 | 0.33474 | 0.31579 | 0.29579 | 0.27789 | 0.25474 | 0.22526 | 0.032632 | -0.08 | -0.17053 | 0.40842 | 0.39684 | 0.38316 | 0.36737 | 0.35053 | 0.33368 | 0.31579 | 0.3 | 0.28 | 0.25474 | 0.083158 | -0.027368 | -0.11579
| TAYNUILT | OBAN | MINIMUM HEADROOM | NM 85643 29338 | NO | YES | 0 | 28.4221 | 28.3716 | 28.3326 | 28.2779 | 28.2158 | 28.1547 | 27.8516 | 27.3179 | 26.3937 | 25.5358 | 23.3432 | 22.6895 | 22.2484 | 25.6053 | 25.5547 | 25.5158 | 25.4611 | 25.3979 | 25.1579 | 24.6389 | 24.0232 | 22.9474 | 21.9516 | 19.4053 | 18.6632 | 18.1611 | 24.1074 | 23.5821 | 23.2411 | 22.9726 | 22.7737 | 22.3916 | 21.8737 | 21.2589 | 20.1853 | 19.1916 | 16.6505 | 15.9095 | 15.4074
|  | OBAN | EE |  |  |  |  | 28.4221 | 28.3716 | 28.3347 | 28.2905 | 28.2337 | 28.1558 | 28.0737 | 27.68 | 27.1116 | 26.9537 | 23.3432 | 22.6895 | 22.2484 | 25.6053 | 25.5547 | 25.5179 | 25.4726 | 25.4168 | 25.2589 | 24.9295 | 24.4516 | 23.7937 | 23.6147 | 19.4053 | 18.6632 | 18.1611 | 24.1074 | 23.9042 | 23.2411 | 22.9726 | 22.7737 | 22.4926 | 22.1642 | 21.6874 | 21.0305 | 20.8526 | 16.6505 | 15.9095 | 15.4074
|  | OBAN | HT |  |  |  |  | 28.4295 | 28.3842 | 28.3326 | 28.2779 | 28.2158 | 28.1547 | 27.8516 | 27.3179 | 26.3937 | 25.5358 | 23.3968 | 22.8284 | 22.4263 | 25.6126 | 25.5674 | 25.5158 | 25.4611 | 25.3979 | 25.1579 | 24.6389 | 24.0232 | 22.9474 | 21.9516 | 19.6347 | 18.96 | 18.3884 | 24.1558 | 23.5821 | 23.3432 | 22.9863 | 22.7821 | 22.3916 | 21.8737 | 21.2589 | 20.1853 | 19.1916 | 16.8789 | 16.2053 | 15.6347
|  | OBAN | HE |  |  |  |  | 28.4463 | 28.4021 | 28.3695 | 28.3232 | 28.2653 | 28.1905 | 28.1116 | 28.0663 | 27.4832 | 27.3958 | 24.3726 | 24.0621 | 23.8411 | 25.6295 | 25.5853 | 25.5526 | 25.5063 | 25.4484 | 25.3737 | 25.2947 | 24.9158 | 24.2179 | 24.12 | 20.5811 | 20.2305 | 19.9779 | 24.2632 | 24.1211 | 23.4947 | 23.3011 | 23.1968 | 23.0305 | 22.5874 | 22.1505 | 21.4547 | 21.3568 | 17.8242 | 17.4737 | 17.2221
|  | OBAN | FB |  |  |  |  | 28.4674 | 28.4484 | 28.4274 | 28.4053 | 28.38 | 28.3547 | 28.3284 | 28.3021 | 28.2747 | 28.2442 | 27.44 | 25.9505 | 25.6368 | 25.6505 | 25.6316 | 25.6105 | 25.5884 | 25.5632 | 25.5379 | 25.5116 | 25.4853 | 25.4579 | 25.4274 | 24.1474 | 22.4116 | 22.0505 | 24.3126 | 24.2442 | 24.1695 | 23.8853 | 23.8084 | 23.7147 | 23.6147 | 23.4463 | 23.1274 | 23.0126 | 21.3842 | 19.6516 | 19.2905
| MILTON OF CRAIGIE | OLD CRAIGIE ROAD | MINIMUM HEADROOM | NO 42156 32130 | NO | YES | 0 | 9.7284 | 9.5568 | 9.4495 | 9.3558 | 9.2474 | 9.1211 | 9.0053 | 8.9116 | 8.8221 | 8.7158 | 8.2916 | 7.9705 | 7.7568 | 10.46 | 10.2653 | 10.1432 | 10.0389 | 9.9189 | 9.78 | 9.6537 | 9.5505 | 9.4526 | 9.3347 | 8.9779 | 8.5989 | 8.3 | 11.0558 | 10.9032 | 10.8063 | 10.72 | 10.6211 | 10.4905 | 10.3632 | 10.2611 | 10.1621 | 10.0442 | 9.6874 | 9.3074 | 9.0074
|  | OLD CRAIGIE ROAD | EE |  |  |  |  | 9.7284 | 9.5568 | 9.4495 | 9.3558 | 9.2474 | 9.1211 | 9.0053 | 8.9116 | 8.8221 | 8.7158 | 8.3905 | 8.1232 | 7.8958 | 10.46 | 10.2653 | 10.1432 | 10.0389 | 9.9189 | 9.78 | 9.6537 | 9.5505 | 9.4526 | 9.3347 | 8.9779 | 8.7063 | 8.4505 | 11.0558 | 10.9032 | 10.8063 | 10.72 | 10.6211 | 10.4905 | 10.3632 | 10.2611 | 10.1621 | 10.0442 | 9.6874 | 9.4158 | 9.16
|  | OLD CRAIGIE ROAD | HT |  |  |  |  | 9.7547 | 9.5958 | 9.4863 | 9.3937 | 9.28 | 9.1842 | 9.0905 | 8.9968 | 8.9 | 8.7695 | 8.2916 | 7.9705 | 7.7568 | 10.4895 | 10.3084 | 10.1863 | 10.0842 | 9.9589 | 9.8537 | 9.7516 | 9.6495 | 9.5442 | 9.4 | 8.9979 | 8.5989 | 8.3 | 11.08 | 10.9379 | 10.8379 | 10.7526 | 10.6484 | 10.56 | 10.4632 | 10.36 | 10.2547 | 10.1095 | 9.7084 | 9.3074 | 9.0074
|  | OLD CRAIGIE ROAD | HE |  |  |  |  | 9.82 | 9.6842 | 9.6063 | 9.5463 | 9.4642 | 9.3653 | 9.2853 | 9.2253 | 9.1621 | 9.0916 | 8.8863 | 8.6884 | 8.5611 | 10.5642 | 10.4105 | 10.3232 | 10.2589 | 10.1695 | 10.0611 | 9.9758 | 9.9116 | 9.8421 | 9.7632 | 9.5347 | 9.3116 | 9.1674 | 11.1379 | 11.0158 | 10.9463 | 10.8895 | 10.8137 | 10.72 | 10.6442 | 10.5874 | 10.5284 | 10.4653 | 10.2453 | 10.0211 | 9.8768
|  | OLD CRAIGIE ROAD | FB |  |  |  |  | 9.9347 | 9.8663 | 9.8126 | 9.7653 | 9.7147 | 9.6611 | 9.6032 | 9.5547 | 9.5011 | 9.4358 | 9.2242 | 9.0179 | 8.8653 | 10.7032 | 10.6179 | 10.5579 | 10.5042 | 10.4474 | 10.3884 | 10.3232 | 10.2695 | 10.2105 | 10.1368 | 9.9011 | 9.6695 | 9.4968 | 11.2453 | 11.1789 | 11.1305 | 11.0874 | 11.0411 | 10.9926 | 10.94 | 10.8958 | 10.8474 | 10.7874 | 10.5937 | 10.3811 | 10.2074
| KINTORE | OLDMELDRUM | MINIMUM HEADROOM | NJ 81659 27360 | NO | YES | 0.22143 | 7.6821 | 7.3263 | 28.3263 | 27.8916 | 27.5337 | 27.2558 | 26.8611 | 26.6674 | 26.4779 | 26.2874 | 22.8484 | 22.5274 | 22.3053 | 6.7116 | 6.2937 | 26.1337 | 25.6221 | 25.2032 | 24.8789 | 24.4179 | 24.1937 | 23.9758 | 23.7579 | 20.6979 | 20.3295 | 20.0737 | 7.0295 | 6.6074 | 26.9921 | 26.4753 | 26.0521 | 25.7237 | 25.2584 | 25.0321 | 24.8121 | 24.5911 | 21.0047 | 20.6332 | 20.3753
|  | OLDMELDRUM | EE |  |  |  |  | 7.6821 | 7.3263 | 28.3368 | 27.9611 | 27.6116 | 27.2558 | 26.8611 | 26.6674 | 26.4779 | 26.4021 | 22.8484 | 22.5274 | 22.3053 | 6.7116 | 6.2937 | 26.1463 | 25.7032 | 25.2937 | 24.8789 | 24.4179 | 24.1937 | 23.9758 | 23.8895 | 20.6979 | 20.3295 | 20.0737 | 7.0295 | 6.6074 | 27.0047 | 26.5574 | 26.1437 | 25.7237 | 25.2584 | 25.0321 | 24.8121 | 24.7237 | 21.0047 | 20.6332 | 20.3753
|  | OLDMELDRUM | HT |  |  |  |  | 7.6905 | 7.3684 | 28.3263 | 27.8916 | 27.5337 | 27.3684 | 27.1653 | 26.9947 | 26.6821 | 26.2874 | 23.2547 | 22.9274 | 22.7 | 6.7211 | 6.3432 | 26.1337 | 25.6221 | 25.2032 | 25.0147 | 24.7789 | 24.5842 | 24.22 | 23.7579 | 21.0789 | 20.6811 | 20.3526 | 7.0389 | 6.6568 | 26.9921 | 26.4753 | 26.0521 | 25.8616 | 25.6237 | 25.4268 | 25.0584 | 24.5911 | 21.4889 | 21.0879 | 20.7553
|  | OLDMELDRUM | HE |  |  |  |  | 7.7358 | 7.4547 | 28.4779 | 28.1116 | 27.7905 | 27.4663 | 27.0432 | 26.8726 | 26.7011 | 26.6568 | 24.7705 | 24.6263 | 24.4947 | 6.7737 | 6.4432 | 26.3095 | 25.8789 | 25.5032 | 25.1253 | 24.6295 | 24.4326 | 24.2337 | 24.1821 | 22.3537 | 22.1874 | 22.0347 | 7.0916 | 6.7579 | 27.17 | 26.7353 | 26.3553 | 25.9732 | 25.4721 | 25.2732 | 25.0732 | 25.0205 | 22.9742 | 22.8068 | 22.6521
|  | OLDMELDRUM | FB |  |  |  |  | 8.0811 | 7.9663 | 29.1684 | 29.0526 | 28.9368 | 28.7989 | 28.6305 | 28.4 | 28.3021 | 28.2537 | 27.7811 | 27.3537 | 27.2158 | 7.1811 | 7.0453 | 27.1221 | 26.9874 | 26.8516 | 26.6884 | 26.4905 | 26.2179 | 26.1042 | 26.0495 | 25.4947 | 24.9937 | 24.8326 | 7.5042 | 7.3663 | 27.9921 | 27.8553 | 27.7184 | 27.5532 | 27.3532 | 27.0774 | 26.9626 | 26.9068 | 26.3468 | 25.8405 | 25.6784
| THURSO | ORMLIE | MINIMUM HEADROOM | ND 10757 67408 | NO | YES | 0 | 14.2016 | 14.1132 | 14.0321 | 13.9332 | 13.8268 | 12.5016 | 10.9321 | 8.9521 | 6.9005 | 5.5784 | 2.3763 | 1.9868 | 1.6805 | 13.4021 | 13.3063 | 13.2168 | 13.1063 | 12.9895 | 11.4389 | 9.5989 | 7.2747 | 4.8674 | 3.3189 | -0.15789 | -0.63789 | -1.0084 | 13.7782 | 13.6824 | 13.5929 | 13.4824 | 13.3655 | 11.8203 | 9.9855 | 7.6687 | 5.2676 | 3.7245 | 0.16447 | -0.33868 | -0.69237
|  | ORMLIE | EE |  |  |  |  | 14.2016 | 14.1132 | 14.0321 | 13.9332 | 13.8268 | 13.71 | 13.5426 | 12.2584 | 10.7447 | 8.6963 | 2.7037 | 2.0047 | 1.6805 | 13.4021 | 13.3063 | 13.2168 | 13.1063 | 12.9895 | 12.8621 | 12.6726 | 11.1684 | 9.3926 | 6.9863 | 0.15684 | -0.63789 | -0.99263 | 13.7782 | 13.6824 | 13.5929 | 13.4824 | 13.3655 | 13.2382 | 13.0497 | 11.5508 | 9.7803 | 7.3813 | 0.45395 | -0.33868 | -0.69237
|  | ORMLIE | HT |  |  |  |  | 14.2163 | 14.1353 | 14.0563 | 13.9711 | 13.8563 | 12.5016 | 10.9321 | 8.9521 | 6.9005 | 5.5784 | 2.3763 | 1.9868 | 1.6889 | 13.42 | 13.3316 | 13.2463 | 13.1537 | 13.0263 | 11.4389 | 9.5989 | 7.2747 | 4.8674 | 3.3189 | -0.15789 | -0.60105 | -1.0084 | 13.7961 | 13.7076 | 13.6234 | 13.5297 | 13.4034 | 11.8203 | 9.9855 | 7.6687 | 5.2676 | 3.7245 | 0.16447 | -0.27868 | -0.685
|  | ORMLIE | HE |  |  |  |  | 14.2826 | 14.2279 | 14.1805 | 14.1311 | 14.0647 | 14.0058 | 13.8784 | 12.4911 | 10.8416 | 8.5247 | 3.5784 | 3.0405 | 2.8868 | 13.4916 | 13.4337 | 13.3821 | 13.3284 | 13.2568 | 13.1937 | 13.0516 | 11.4232 | 9.4853 | 6.7579 | 1.0253 | 0.40421 | 0.23053 | 13.8676 | 13.8087 | 13.7582 | 13.7045 | 13.6329 | 13.5697 | 13.4287 | 11.8045 | 9.8718 | 7.1539 | 1.3918 | 0.77184 | 0.59816
|  | ORMLIE | FB |  |  |  |  | 14.2826 | 14.2384 | 14.1911 | 14.1405 | 14.0868 | 14.0321 | 13.9647 | 13.8984 | 13.2847 | 12.5216 | 7.9742 | 7.0153 | 6.7837 | 13.4947 | 13.4463 | 13.3958 | 13.3411 | 13.2842 | 13.2253 | 13.1505 | 13.0779 | 12.3611 | 11.4663 | 6.1316 | 5.0253 | 4.7737 | 13.8708 | 13.8224 | 13.7718 | 13.7171 | 13.6603 | 13.6013 | 13.5266 | 13.455 | 12.7392 | 11.8476 | 6.5287 | 5.4255 | 5.1739
| DUNOON | OTTER FERRY | MINIMUM HEADROOM | NR 93352 84713 | YES | YES | 0 | 0.98 | 0.94526 | 0.92 | 0.90632 | 0.89263 | 0.87789 | 0.86316 | 0.85053 | 0.83789 | 0.82632 | 0.78105 | 0.73895 | 0.70526 | 1.0179 | 0.97789 | 0.94947 | 0.93368 | 0.92 | 0.90316 | 0.88842 | 0.87368 | 0.86 | 0.84737 | 0.79789 | 0.75263 | 0.71579 | 0.99684 | 0.96 | 0.93368 | 0.91789 | 0.90421 | 0.88842 | 0.87263 | 0.86 | 0.84632 | 0.83368 | 0.78632 | 0.74105 | 0.70526
|  | OTTER FERRY | EE |  |  |  |  | 0.98 | 0.97158 | 0.92 | 0.90632 | 0.89263 | 0.87789 | 0.86316 | 0.85053 | 0.83789 | 0.82632 | 0.78105 | 0.73895 | 0.70526 | 1.0179 | 1.0084 | 0.94947 | 0.93368 | 0.92 | 0.90316 | 0.88842 | 0.87368 | 0.86 | 0.84737 | 0.79789 | 0.75263 | 0.71579 | 0.99684 | 0.98842 | 0.93368 | 0.91789 | 0.90421 | 0.88842 | 0.87263 | 0.86 | 0.84632 | 0.83368 | 0.78632 | 0.74105 | 0.70526
|  | OTTER FERRY | HT |  |  |  |  | 0.98526 | 0.94526 | 0.93684 | 0.92737 | 0.91368 | 0.90105 | 0.88842 | 0.87684 | 0.86526 | 0.85158 | 0.8 | 0.75895 | 0.73263 | 1.0232 | 0.97789 | 0.96947 | 0.95684 | 0.94211 | 0.92842 | 0.91368 | 0.90211 | 0.88842 | 0.87263 | 0.82632 | 0.77895 | 0.74 | 0.99895 | 0.96 | 0.95263 | 0.94105 | 0.92737 | 0.91368 | 0.9 | 0.88842 | 0.87579 | 0.86105 | 0.81579 | 0.77053 | 0.73474
|  | OTTER FERRY | HE |  |  |  |  | 0.99053 | 0.98316 | 0.93895 | 0.93368 | 0.92737 | 0.92105 | 0.91368 | 0.90737 | 0.90105 | 0.89263 | 0.86947 | 0.84526 | 0.83158 | 1.0295 | 1.0232 | 0.97053 | 0.96421 | 0.95789 | 0.95158 | 0.94421 | 0.93684 | 0.92947 | 0.92 | 0.89579 | 0.86842 | 0.85263 | 1 | 0.99579 | 0.95368 | 0.94842 | 0.94211 | 0.93579 | 0.92737 | 0.92105 | 0.91368 | 0.90526 | 0.88105 | 0.85474 | 0.84
|  | OTTER FERRY | FB |  |  |  |  | 0.99368 | 0.98947 | 0.98526 | 0.96632 | 0.96211 | 0.95684 | 0.95263 | 0.94947 | 0.94316 | 0.93789 | 0.91053 | 0.88526 | 0.86526 | 1.0326 | 1.0284 | 1.0242 | 1.0011 | 0.99684 | 0.99263 | 0.98737 | 0.98421 | 0.97684 | 0.97053 | 0.94 | 0.90947 | 0.88526 | 1.0011 | 1 | 0.99895 | 0.98316 | 0.97789 | 0.97368 | 0.96947 | 0.96526 | 0.95895 | 0.95263 | 0.92421 | 0.89789 | 0.87474
| DUDHOPE | OVERGATE | MINIMUM HEADROOM | NO 40033 30155 | NO | YES | 0.05102 | 32.42 | 32.2558 | 32.4 | 32.3737 | 31.9853 | 31.9547 | 31.6979 | 31.4558 | 31.2474 | 31.2074 | 30.9463 | 30.34 | 30.18 | 30.3958 | 30.3874 | 30.3905 | 30.3842 | 30.3589 | 30.3432 | 30.1189 | 29.8 | 29.5116 | 29.4568 | 29.1021 | 28.3442 | 28.0747 | 31.3805 | 31.3237 | 31.37 | 31.3574 | 31.2174 | 31.1974 | 31.0732 | 30.7395 | 30.4521 | 30.3974 | 30.0426 | 29.2868 | 29.0174
|  | OVERGATE | EE |  |  |  |  | 32.4274 | 32.2558 | 33.1305 | 33.0053 | 32.9432 | 32.8747 | 32.7137 | 32.4337 | 32.1884 | 32.1242 | 31.5821 | 31.3158 | 31.1305 | 30.3958 | 30.3884 | 30.8589 | 30.8516 | 30.8411 | 30.8274 | 30.8126 | 30.7989 | 30.7874 | 30.7758 | 30.0768 | 29.7168 | 29.4663 | 31.3826 | 31.3237 | 32.7837 | 32.7668 | 32.7521 | 32.7342 | 32.6437 | 32.2647 | 31.9268 | 31.8416 | 31.1026 | 30.7426 | 30.4921
|  | OVERGATE | HT |  |  |  |  | 32.42 | 33.2568 | 33.0421 | 32.8389 | 32.7747 | 32.6179 | 32.2568 | 32.0674 | 31.9547 | 31.8853 | 31.5674 | 30.34 | 30.18 | 30.3968 | 30.8663 | 30.8568 | 30.8463 | 30.8347 | 30.8211 | 30.8084 | 30.7284 | 30.5779 | 30.4863 | 30.14 | 28.3442 | 28.0747 | 31.3805 | 32.8005 | 32.7742 | 32.7479 | 32.7195 | 32.5111 | 32.0132 | 31.7532 | 31.6026 | 31.5121 | 31.1658 | 29.2868 | 29.0174
|  | OVERGATE | HE |  |  |  |  | 32.4211 | 32.2874 | 33.1337 | 33.0063 | 31.9853 | 31.9547 | 31.6979 | 31.4558 | 31.2474 | 31.2074 | 30.9463 | 30.8074 | 30.7042 | 30.3979 | 30.3874 | 30.86 | 30.8505 | 30.3589 | 30.3432 | 30.1189 | 29.8 | 29.5116 | 29.4568 | 29.1021 | 28.9158 | 28.7768 | 31.3816 | 31.3321 | 32.7847 | 32.7658 | 31.2174 | 31.1974 | 31.0732 | 30.7395 | 30.4521 | 30.3974 | 30.0426 | 29.8563 | 29.7184
|  | OVERGATE | FB |  |  |  |  | 32.5295 | 32.4716 | 32.4 | 32.3737 | 32.3537 | 32.3337 | 32.3137 | 32.2295 | 32.0884 | 32.0484 | 31.6547 | 32.3579 | 32.2284 | 30.4011 | 30.3958 | 30.3905 | 30.3842 | 30.3779 | 30.3716 | 30.3653 | 30.3579 | 30.3505 | 30.3432 | 30.0653 | 30.7695 | 30.7558 | 31.4184 | 31.3963 | 31.37 | 31.3574 | 31.3468 | 31.3363 | 31.3258 | 31.2942 | 31.2447 | 31.2268 | 31.0174 | 32.17 | 31.9942
| CASSLEY | OVERSCAIG | MINIMUM HEADROOM | NC 39711 25382 | YES | YES | 0 | 0.15211 | 0.15105 | 0.14789 | 0.14579 | 0.14368 | 0.14263 | 0.13947 | 0.13632 | 0.13526 | 0.13316 | 0.12368 | 0.11632 | 0.10684 | 0.15 | 0.15 | 0.14789 | 0.14579 | 0.14368 | 0.14263 | 0.13842 | 0.13632 | 0.13526 | 0.13316 | 0.12474 | 0.11632 | 0.10789 | 0.14895 | 0.14789 | 0.14579 | 0.14368 | 0.14263 | 0.14053 | 0.13737 | 0.13421 | 0.13316 | 0.13105 | 0.12158 | 0.11421 | 0.10474
|  | OVERSCAIG | EE |  |  |  |  | 0.15211 | 0.15105 | 0.14789 | 0.14579 | 0.14368 | 0.14263 | 0.13947 | 0.13632 | 0.13526 | 0.13316 | 0.12368 | 0.11632 | 0.10684 | 0.15 | 0.15 | 0.14789 | 0.14579 | 0.14368 | 0.14263 | 0.13842 | 0.13632 | 0.13526 | 0.13316 | 0.12474 | 0.11632 | 0.10789 | 0.14895 | 0.14789 | 0.14579 | 0.14368 | 0.14263 | 0.14053 | 0.13737 | 0.13421 | 0.13316 | 0.13105 | 0.12158 | 0.11421 | 0.10474
|  | OVERSCAIG | HT |  |  |  |  | 0.15316 | 0.15211 | 0.15211 | 0.15105 | 0.15105 | 0.14895 | 0.14895 | 0.14789 | 0.14789 | 0.14684 | 0.14263 | 0.13947 | 0.13737 | 0.15105 | 0.15 | 0.15 | 0.14895 | 0.14895 | 0.14789 | 0.14789 | 0.14579 | 0.14579 | 0.14579 | 0.14158 | 0.13947 | 0.13632 | 0.15 | 0.15 | 0.15 | 0.14895 | 0.14895 | 0.14684 | 0.14684 | 0.14474 | 0.14474 | 0.14368 | 0.14053 | 0.13842 | 0.13526
|  | OVERSCAIG | HE |  |  |  |  | 0.15316 | 0.15211 | 0.15211 | 0.15211 | 0.15105 | 0.15105 | 0.15 | 0.14895 | 0.14789 | 0.14684 | 0.14474 | 0.14263 | 0.13947 | 0.15105 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.14895 | 0.14789 | 0.14684 | 0.14684 | 0.14474 | 0.14158 | 0.13842 | 0.15 | 0.15 | 0.15 | 0.14895 | 0.14895 | 0.14789 | 0.14789 | 0.14684 | 0.14579 | 0.14474 | 0.14263 | 0.13947 | 0.13737
|  | OVERSCAIG | FB |  |  |  |  | 0.15316 | 0.15316 | 0.15316 | 0.15316 | 0.15316 | 0.15316 | 0.15316 | 0.15211 | 0.15211 | 0.15211 | 0.15211 | 0.15 | 0.15 | 0.15105 | 0.15105 | 0.15105 | 0.15105 | 0.15105 | 0.15105 | 0.15105 | 0.15 | 0.14895 | 0.14895 | 0.14895 | 0.14684 | 0.14684 | 0.15105 | 0.15105 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.14684 | 0.14684
| KINTORE | PARK | MINIMUM HEADROOM | NO 79107 99434 | YES | YES | 0 | 1.4368 | 1.4042 | 1.3716 | 1.3263 | 1.2863 | 1.2347 | 1.1726 | 1.1221 | 1.0768 | 1.0389 | 0.86632 | 0.73263 | 0.64211 | 1.0589 | 1.0179 | 0.98211 | 0.93053 | 0.88737 | 0.82947 | 0.75895 | 0.70316 | 0.65263 | 0.61053 | 0.45895 | 0.29579 | 0.16526 | 1.1526 | 1.1126 | 1.0768 | 1.0253 | 0.98211 | 0.92421 | 0.85368 | 0.79789 | 0.74737 | 0.70526 | 0.55368 | 0.39053 | 0.25895
|  | PARK | EE |  |  |  |  | 1.4368 | 1.4042 | 1.3716 | 1.3274 | 1.2895 | 1.2463 | 1.2 | 1.1442 | 1.0916 | 1.0589 | 0.90421 | 0.78211 | 0.68211 | 1.0589 | 1.0179 | 0.98211 | 0.93263 | 0.89053 | 0.84316 | 0.79263 | 0.72947 | 0.67053 | 0.63368 | 0.45895 | 0.32105 | 0.20737 | 1.1526 | 1.1126 | 1.0768 | 1.0274 | 0.98526 | 0.93789 | 0.88737 | 0.82421 | 0.76526 | 0.72842 | 0.55368 | 0.41579 | 0.30211
|  | PARK | HT |  |  |  |  | 1.44 | 1.4189 | 1.3821 | 1.3263 | 1.2863 | 1.2347 | 1.1726 | 1.1221 | 1.0768 | 1.0389 | 0.86632 | 0.73263 | 0.64211 | 1.0705 | 1.0347 | 0.99368 | 0.93053 | 0.88737 | 0.82947 | 0.75895 | 0.70316 | 0.65263 | 0.61053 | 0.46105 | 0.29579 | 0.16526 | 1.1621 | 1.1295 | 1.0884 | 1.0253 | 0.98211 | 0.92421 | 0.85368 | 0.79789 | 0.74737 | 0.70526 | 0.55579 | 0.39053 | 0.25895
|  | PARK | HE |  |  |  |  | 1.4453 | 1.4316 | 1.4232 | 1.3905 | 1.3684 | 1.3368 | 1.2874 | 1.24 | 1.1979 | 1.1779 | 1.0989 | 1.0368 | 0.97895 | 1.0947 | 1.0674 | 1.0442 | 1.0053 | 0.98105 | 0.94737 | 0.89263 | 0.83895 | 0.79158 | 0.76947 | 0.67895 | 0.60842 | 0.54211 | 1.1811 | 1.1579 | 1.1379 | 1.1 | 1.0758 | 1.0421 | 0.98737 | 0.93368 | 0.88632 | 0.86421 | 0.77368 | 0.70316 | 0.63684
|  | PARK | FB |  |  |  |  | 1.4547 | 1.4505 | 1.4442 | 1.44 | 1.4305 | 1.4168 | 1.4042 | 1.3832 | 1.3579 | 1.3347 | 1.2463 | 1.1674 | 1.1084 | 1.1105 | 1.0958 | 1.0811 | 1.0663 | 1.0484 | 1.0326 | 1.0189 | 0.99474 | 0.96526 | 0.94 | 0.84 | 0.74947 | 0.68105 | 1.1947 | 1.1832 | 1.1716 | 1.1589 | 1.1432 | 1.1274 | 1.1137 | 1.0895 | 1.06 | 1.0347 | 0.93474 | 0.84421 | 0.77579
| ALNESS | PEDDIESTON | MINIMUM HEADROOM | NH 74198 63656 | NO | YES | 0 | 2.8789 | 2.8579 | 2.7853 | 2.7642 | 2.74 | 2.6168 | 2.5263 | 2.4589 | 2.4179 | 2.3947 | 2.2884 | 2.2063 | 2.1484 | 2.4379 | 2.4189 | 2.3526 | 2.3326 | 2.3105 | 2.2105 | 2.1389 | 2.0853 | 2.0516 | 2.0316 | 1.92 | 1.8295 | 1.7547 | 2.4789 | 2.4663 | 2.44 | 2.4284 | 2.4147 | 2.3621 | 2.2632 | 2.1853 | 2.1389 | 2.1147 | 2.0011 | 1.9095 | 1.8347
|  | PEDDIESTON | EE |  |  |  |  | 2.8789 | 2.8579 | 2.7853 | 2.7642 | 2.74 | 2.7147 | 2.6863 | 2.5558 | 2.4642 | 2.3968 | 2.2958 | 2.2147 | 2.1495 | 2.4379 | 2.4189 | 2.3526 | 2.3326 | 2.3105 | 2.2863 | 2.26 | 2.1589 | 2.0863 | 2.0337 | 1.92 | 1.8295 | 1.7547 | 2.4789 | 2.4663 | 2.44 | 2.4284 | 2.4147 | 2.3989 | 2.3821 | 2.2979 | 2.1937 | 2.1168 | 2.0011 | 1.9095 | 1.8347
|  | PEDDIESTON | HT |  |  |  |  | 2.8821 | 2.8663 | 2.7937 | 2.7758 | 2.7516 | 2.6168 | 2.5263 | 2.4589 | 2.4179 | 2.3947 | 2.2884 | 2.2063 | 2.1484 | 2.4421 | 2.4263 | 2.36 | 2.3442 | 2.32 | 2.2105 | 2.1389 | 2.0853 | 2.0516 | 2.0316 | 1.9347 | 1.8389 | 1.7558 | 2.48 | 2.4705 | 2.4432 | 2.4326 | 2.4168 | 2.3621 | 2.2632 | 2.1853 | 2.1389 | 2.1147 | 2.0168 | 1.92 | 1.8358
|  | PEDDIESTON | HE |  |  |  |  | 2.8874 | 2.88 | 2.8137 | 2.8021 | 2.7863 | 2.7705 | 2.7526 | 2.6274 | 2.5379 | 2.4832 | 2.4347 | 2.3842 | 2.3442 | 2.4516 | 2.4389 | 2.3789 | 2.3674 | 2.3526 | 2.3368 | 2.32 | 2.2147 | 2.1453 | 2.1021 | 2.0632 | 2.02 | 1.9747 | 2.4842 | 2.4747 | 2.4505 | 2.4432 | 2.4316 | 2.4189 | 2.4053 | 2.3632 | 2.2789 | 2.2158 | 2.1611 | 2.1021 | 2.0568
|  | PEDDIESTON | FB |  |  |  |  | 2.8947 | 2.8916 | 2.8642 | 2.8558 | 2.8474 | 2.8379 | 2.8284 | 2.8211 | 2.7684 | 2.7242 | 2.6105 | 2.5611 | 2.5253 | 2.4621 | 2.4537 | 2.4253 | 2.4179 | 2.4095 | 2.4011 | 2.3916 | 2.3842 | 2.3368 | 2.2968 | 2.2063 | 2.1663 | 2.1379 | 2.4926 | 2.4884 | 2.4768 | 2.4716 | 2.4674 | 2.4621 | 2.4558 | 2.4516 | 2.4326 | 2.4158 | 2.3547 | 2.3032 | 2.2632
| PETERHEAD GRANGE | PETERHEAD GRANGE | MINIMUM HEADROOM | NK 11738 46516 | NO | YES | 0.93265 | 20.58 | 20.1695 | 19.86 | 19.4947 | 18.1495 | 16.9516 | 15.6947 | 15.3884 | 15.0505 | 14.7305 | 2.5147 | -2.0432 | -7.7126 | 19.4916 | 19.0295 | 18.6811 | 18.2716 | 16.7284 | 15.3558 | 13.9179 | 13.5789 | 13.2032 | 12.8505 | -0.10632 | -5.3568 | -11.9084 | 20.0842 | 19.6211 | 19.2705 | 18.86 | 17.3126 | 15.9347 | 14.4926 | 14.1526 | 13.7747 | 13.4221 | -0.29579 | -5.5653 | -12.1389
|  | PETERHEAD GRANGE | EE |  |  |  |  | 20.58 | 20.1695 | 19.86 | 19.5137 | 18.2042 | 16.9516 | 15.6947 | 15.3884 | 15.0505 | 14.8211 | 2.5147 | -2.0432 | -7.7126 | 19.4916 | 19.0295 | 18.6811 | 18.2926 | 16.7895 | 15.3558 | 13.9179 | 13.5789 | 13.2032 | 12.9505 | -0.10632 | -5.3568 | -11.9084 | 20.0842 | 19.6211 | 19.2705 | 18.8811 | 17.3737 | 15.9347 | 14.4926 | 14.1526 | 13.7747 | 13.5221 | -0.29579 | -5.5653 | -12.1389
|  | PETERHEAD GRANGE | HT |  |  |  |  | 20.6358 | 20.2674 | 19.9011 | 19.4947 | 18.1495 | 17.8558 | 17.5084 | 17.1326 | 16.1463 | 14.7305 | 7.5347 | 2.8168 | -4.9516 | 19.5547 | 19.1379 | 18.7274 | 18.2716 | 16.7284 | 16.4032 | 16.0168 | 15.5989 | 14.4737 | 12.8505 | 5.76 | 2.32 | -8.9137 | 20.1484 | 19.7305 | 19.3179 | 18.86 | 17.3126 | 16.9863 | 16.6 | 16.18 | 15.0516 | 13.4221 | 5.7358 | 2.2832 | -8.9905
|  | PETERHEAD GRANGE | HE |  |  |  |  | 20.78 | 20.4937 | 20.2389 | 19.9568 | 18.7189 | 17.54 | 16.2621 | 16.0042 | 15.6811 | 15.5337 | 5.1968 | 1.2737 | -4.1263 | 19.7158 | 19.3937 | 19.1095 | 18.7937 | 17.3737 | 16.0242 | 14.56 | 14.2737 | 13.9126 | 13.7484 | 2.2505 | -2.2811 | -8.5316 | 20.3095 | 19.9874 | 19.7011 | 19.3842 | 17.96 | 16.6053 | 15.1368 | 14.8495 | 14.4874 | 14.3232 | 2.4979 | -2.0495 | -8.3232
|  | PETERHEAD GRANGE | FB |  |  |  |  | 21.0958 | 20.9411 | 20.7926 | 20.6632 | 20.3558 | 19.9295 | 19.3726 | 18.6474 | 18.4853 | 18.3505 | 16.6011 | 12.0179 | 11.6368 | 20.0768 | 19.9011 | 19.7337 | 19.5884 | 19.2379 | 18.7484 | 18.1074 | 17.2737 | 17.0905 | 16.94 | 14.9347 | 9.6389 | 9.2074 | 20.6716 | 20.4958 | 20.3274 | 20.1811 | 19.8295 | 19.3389 | 18.6958 | 17.8589 | 17.6758 | 17.5253 | 15.5126 | 10.1979 | 9.7653
| PETERHEAD GRANGE | PETERHEAD NORTH STREET | MINIMUM HEADROOM | NK 13470 46450 | NO | YES | 0.54184 | 24.8126 | 24.7979 | 24.7853 | 24.7695 | 24.7505 | 24.7305 | 24.7053 | 24.6453 | 24.5863 | 24.5284 | 24.3053 | 24.2379 | 24.0589 | 23.3863 | 23.3684 | 23.3505 | 23.2863 | 23.2126 | 23.1379 | 23.0611 | 22.9884 | 22.9179 | 22.8463 | 22.5758 | 22.6337 | 22.3642 | 22.0389 | 22.0042 | 21.9632 | 21.8937 | 21.8274 | 21.7611 | 21.6926 | 21.6284 | 21.5653 | 21.5032 | 21.2621 | 21.3642 | 21.1274
|  | PETERHEAD NORTH STREET | EE |  |  |  |  | 24.8126 | 24.7979 | 24.7853 | 24.7695 | 24.7505 | 24.7305 | 24.7053 | 24.6453 | 24.5863 | 24.5284 | 24.3053 | 24.2821 | 24.0926 | 23.3863 | 23.3684 | 23.3505 | 23.2863 | 23.2126 | 23.1379 | 23.0611 | 22.9884 | 22.9179 | 22.8463 | 22.5758 | 22.6337 | 22.4 | 22.0389 | 22.0042 | 21.9632 | 21.8937 | 21.8274 | 21.7611 | 21.6926 | 21.6284 | 21.5653 | 21.5032 | 21.2621 | 21.3642 | 21.16
|  | PETERHEAD NORTH STREET | HT |  |  |  |  | 24.8126 | 24.8021 | 24.7863 | 24.7705 | 24.7516 | 24.7326 | 24.7116 | 24.6916 | 24.6326 | 24.5684 | 24.4821 | 24.2379 | 24.0589 | 23.3884 | 23.3747 | 23.3558 | 23.3316 | 23.2621 | 23.1916 | 23.1189 | 23.0474 | 22.9768 | 22.9011 | 22.9589 | 22.6389 | 22.3642 | 22.0463 | 22.0179 | 21.9853 | 21.9368 | 21.8705 | 21.8074 | 21.7421 | 21.6789 | 21.6158 | 21.5484 | 21.6474 | 21.3674 | 21.1274
|  | PETERHEAD NORTH STREET | HE |  |  |  |  | 24.8179 | 24.8063 | 24.7958 | 24.7821 | 24.7663 | 24.7463 | 24.7263 | 24.7105 | 24.6947 | 24.6853 | 24.6442 | 24.5421 | 24.4347 | 23.3958 | 23.3821 | 23.3695 | 23.3547 | 23.3368 | 23.3147 | 23.2937 | 23.2684 | 23.2253 | 23.1842 | 23.0253 | 22.8758 | 22.7411 | 22.0663 | 22.0432 | 22.0211 | 21.9968 | 21.9705 | 21.94 | 21.9105 | 21.8737 | 21.8326 | 21.7926 | 21.6526 | 21.5221 | 21.4053
|  | PETERHEAD NORTH STREET | FB |  |  |  |  | 24.8232 | 24.8168 | 24.8116 | 24.8042 | 24.7968 | 24.7895 | 24.7821 | 24.7737 | 24.7663 | 24.7547 | 24.7189 | 24.6253 | 24.5053 | 23.4021 | 23.3947 | 23.3874 | 23.3779 | 23.3695 | 23.36 | 23.3516 | 23.3411 | 23.3295 | 23.2874 | 23.1347 | 22.9621 | 22.8116 | 22.0768 | 22.0611 | 22.0463 | 22.0284 | 22.0126 | 21.9947 | 21.9779 | 21.9589 | 21.9347 | 21.8937 | 21.7568 | 21.6063 | 21.4758
| FORT WILLIAM | PINEGROVE | MINIMUM HEADROOM | NN 10496 73556 | NO | NO | 0 | 13.7053 | 13.6453 | 13.5874 | 13.4505 | 13.3768 | 12.9379 | 12.7811 | 12.6189 | 12.5547 | 12.3168 | 11.6263 | 11.3905 | 11.2274 | 12.4168 | 12.3937 | 12.3758 | 12.3516 | 12.3232 | 11.8126 | 11.6316 | 11.4442 | 11.3737 | 11.0979 | 10.3284 | 10.0611 | 9.8474 | 12.8326 | 12.8116 | 12.7779 | 12.6558 | 12.5874 | 12.1042 | 11.9253 | 11.7411 | 11.6705 | 11.3989 | 10.64 | 10.3758 | 10.1653
|  | PINEGROVE | EE |  |  |  |  | 13.7053 | 13.6453 | 13.5874 | 13.4505 | 13.3768 | 13.2937 | 12.9021 | 12.7463 | 12.5926 | 12.48 | 11.6537 | 11.4189 | 11.2368 | 12.4168 | 12.3937 | 12.3758 | 12.3516 | 12.3253 | 12.2337 | 11.7758 | 11.5958 | 11.4189 | 11.2895 | 10.3284 | 10.0611 | 9.8526 | 12.8326 | 12.8116 | 12.7779 | 12.6558 | 12.5874 | 12.5042 | 12.0674 | 11.8905 | 11.7147 | 11.5884 | 10.64 | 10.3758 | 10.1705
|  | PINEGROVE | HT |  |  |  |  | 13.7211 | 13.6684 | 13.6168 | 13.4895 | 13.4126 | 12.9379 | 12.7811 | 12.6189 | 12.5547 | 12.3168 | 11.6263 | 11.3905 | 11.2274 | 12.42 | 12.4 | 12.3789 | 12.3516 | 12.3232 | 11.8126 | 11.6316 | 11.4442 | 11.3737 | 11.0979 | 10.3674 | 10.0821 | 9.8474 | 12.8347 | 12.8168 | 12.7968 | 12.6895 | 12.6189 | 12.1042 | 11.9253 | 11.7411 | 11.6705 | 11.3989 | 10.6789 | 10.3968 | 10.1653
|  | PINEGROVE | HE |  |  |  |  | 13.7589 | 13.7189 | 13.6832 | 13.5779 | 13.5295 | 13.3242 | 13.1168 | 13.0105 | 12.9021 | 12.8189 | 12.04 | 11.8958 | 11.7905 | 12.4284 | 12.4084 | 12.3926 | 12.3674 | 12.3432 | 12.2674 | 12.0284 | 11.9063 | 11.7811 | 11.6842 | 10.7716 | 10.6063 | 10.4853 | 12.8411 | 12.8221 | 12.8074 | 12.7674 | 12.7232 | 12.5337 | 12.3158 | 12.1958 | 12.0726 | 11.9768 | 11.0779 | 10.9147 | 10.7947
|  | PINEGROVE | FB |  |  |  |  | 13.8 | 13.7758 | 13.7495 | 13.6968 | 13.6663 | 13.6347 | 13.5242 | 13.4189 | 13.3495 | 13.3084 | 12.6874 | 12.5316 | 12.4042 | 12.4389 | 12.4305 | 12.4221 | 12.4105 | 12.4 | 12.3884 | 12.3726 | 12.3579 | 12.2895 | 12.2421 | 11.5168 | 11.3389 | 11.1916 | 12.8505 | 12.8432 | 12.8347 | 12.8263 | 12.8168 | 12.8063 | 12.7221 | 12.6284 | 12.5589 | 12.5179 | 11.8126 | 11.6368 | 11.4926
| TUMMEL BRIDGE | PITLOCHRY | MINIMUM HEADROOM | NN 95756 58991 | NO | YES | 0.10204 | 3.7983 | 3.7225 | 3.6467 | 3.5541 | 3.4899 | 3.3699 | 3.2657 | 3.1699 | 3.1014 | 3.0488 | 2.8162 | 2.5993 | 2.4488 | 5.3311 | 5.2458 | 5.1605 | 5.0521 | 4.9805 | 4.8416 | 4.7184 | 4.6068 | 4.5289 | 4.4689 | 4.2268 | 3.9911 | 3.7679 | 5.3862 | 5.2989 | 5.2105 | 5.101 | 5.0294 | 4.8915 | 4.7715 | 4.6599 | 4.582 | 4.5231 | 4.282 | 4.0484 | 3.8441
|  | PITLOCHRY | EE |  |  |  |  | 3.7983 | 3.7225 | 3.6467 | 3.5541 | 3.4899 | 3.3699 | 3.2657 | 3.1699 | 3.1014 | 3.0488 | 2.8372 | 2.6351 | 2.4751 | 5.3311 | 5.2458 | 5.1605 | 5.0521 | 4.9805 | 4.8416 | 4.7184 | 4.6068 | 4.5289 | 4.4689 | 4.2268 | 3.9932 | 3.8089 | 5.3862 | 5.2989 | 5.2105 | 5.101 | 5.0294 | 4.8915 | 4.7715 | 4.6599 | 4.582 | 4.5231 | 4.282 | 4.0484 | 3.8641
|  | PITLOCHRY | HT |  |  |  |  | 3.813 | 3.7436 | 3.6699 | 3.5857 | 3.5214 | 3.4225 | 3.3204 | 3.2193 | 3.1425 | 3.0793 | 2.8162 | 2.5993 | 2.4488 | 5.35 | 5.2711 | 5.1858 | 5.09 | 5.0184 | 4.9005 | 4.7805 | 4.6616 | 4.5721 | 4.5005 | 4.2511 | 3.9911 | 3.7679 | 5.4041 | 5.3241 | 5.2399 | 5.142 | 5.0705 | 4.9547 | 4.8378 | 4.721 | 4.6347 | 4.5631 | 4.3189 | 4.0631 | 3.8441
|  | PITLOCHRY | HE |  |  |  |  | 3.8499 | 3.7962 | 3.7446 | 3.6836 | 3.6467 | 3.5667 | 3.4867 | 3.413 | 3.3593 | 3.333 | 3.2151 | 3.1014 | 3.0162 | 5.3921 | 5.3311 | 5.27 | 5.2016 | 5.1626 | 5.0721 | 4.9816 | 4.8942 | 4.8321 | 4.8016 | 4.6647 | 4.5311 | 4.43 | 5.4473 | 5.3852 | 5.3252 | 5.2547 | 5.2157 | 5.1231 | 5.0336 | 4.9463 | 4.8862 | 4.8557 | 4.722 | 4.5884 | 4.4894
|  | PITLOCHRY | FB |  |  |  |  | 3.8783 | 3.8488 | 3.8162 | 3.7836 | 3.7593 | 3.7204 | 3.6772 | 3.632 | 3.5993 | 3.5667 | 3.4414 | 3.3099 | 3.2057 | 5.4226 | 5.3889 | 5.3511 | 5.3142 | 5.2858 | 5.2416 | 5.1911 | 5.1395 | 5.1016 | 5.0647 | 4.9174 | 4.7595 | 4.6321 | 5.4789 | 5.4441 | 5.4062 | 5.3684 | 5.341 | 5.2957 | 5.2452 | 5.1915 | 5.1536 | 5.1168 | 4.9726 | 4.8199 | 4.6957
| ARDMORE | POLLACHAR | MINIMUM HEADROOM | NF 75073 14513 | NO | YES | 0 | 3.8158 | 3.7568 | 3.6979 | 3.6589 | 3.6211 | 3.5768 | 3.2695 | 3.22 | 3.1726 | 3.2105 | 1.1842 | 1.0411 | 0.94105 | 3.6095 | 3.5905 | 3.5547 | 3.4937 | 3.4379 | 3.3758 | 2.9958 | 2.9421 | 2.8895 | 2.9389 | 1.2221 | 1.0537 | 0.91474 | 3.5853 | 3.5684 | 3.5526 | 3.4947 | 3.4389 | 3.3779 | 2.9989 | 2.9442 | 2.8926 | 2.9411 | 0.87684 | 0.70947 | 0.57053
|  | POLLACHAR | EE |  |  |  |  | 3.8158 | 3.7789 | 3.6979 | 3.6589 | 3.6211 | 3.5768 | 3.2695 | 3.22 | 3.1726 | 4.4547 | 2.1242 | 1.9811 | 1.8768 | 3.6095 | 3.5905 | 3.5547 | 3.4937 | 3.4379 | 3.3758 | 2.9958 | 2.9421 | 2.8895 | 4.4958 | 2.4989 | 2.3474 | 2.2358 | 3.5853 | 3.5684 | 3.5526 | 3.4947 | 3.4389 | 3.3779 | 2.9989 | 2.9442 | 2.8926 | 4.3463 | 1.92 | 1.7632 | 1.6484
|  | POLLACHAR | HT |  |  |  |  | 3.8263 | 3.7568 | 3.7221 | 3.6842 | 3.6463 | 3.6074 | 3.5695 | 3.5295 | 3.4211 | 3.2105 | 1.1842 | 1.0411 | 0.94105 | 3.6137 | 3.5916 | 3.5705 | 3.5484 | 3.4926 | 3.4379 | 3.3832 | 3.3274 | 3.1821 | 2.9389 | 1.2221 | 1.0537 | 0.91474 | 3.5884 | 3.5716 | 3.5526 | 3.5326 | 3.4937 | 3.4389 | 3.3842 | 3.3284 | 3.1832 | 2.9411 | 0.87684 | 0.70947 | 0.57053
|  | POLLACHAR | HE |  |  |  |  | 3.8484 | 3.8211 | 3.7537 | 3.7274 | 3.6979 | 3.6653 | 3.4274 | 3.3947 | 3.3621 | 3.3411 | 2.2242 | 2.1495 | 2.0979 | 3.62 | 3.6021 | 3.5853 | 3.5663 | 3.5453 | 3.5189 | 3.18 | 3.1442 | 3.1084 | 3.0853 | 2.0884 | 2.0053 | 1.9484 | 3.5937 | 3.5768 | 3.5653 | 3.5474 | 3.5263 | 3.5011 | 3.1821 | 3.1463 | 3.1105 | 3.0863 | 1.9137 | 1.8295 | 1.7716
|  | POLLACHAR | FB |  |  |  |  | 3.8632 | 3.8484 | 3.8337 | 3.7979 | 3.7821 | 3.7653 | 3.7063 | 3.6095 | 3.5863 | 3.5589 | 3.4295 | 3.2853 | 3.2095 | 3.6305 | 3.6232 | 3.6158 | 3.6063 | 3.5979 | 3.5884 | 3.5653 | 3.3811 | 3.3547 | 3.3242 | 3.1779 | 3.0126 | 2.9274 | 3.6032 | 3.5968 | 3.5905 | 3.5832 | 3.5758 | 3.5674 | 3.5589 | 3.3821 | 3.3558 | 3.3263 | 3.1789 | 3.0147 | 2.9295
| FORT WILLIAM | POOR HOUSE | MINIMUM HEADROOM | NM 71766 70148 | YES | NO | 0 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1
|  | POOR HOUSE | EE |  |  |  |  | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1
|  | POOR HOUSE | HT |  |  |  |  | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1
|  | POOR HOUSE | HE |  |  |  |  | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105
|  | POOR HOUSE | FB |  |  |  |  | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211
| PORT ANN | PORT ASKAIG | MINIMUM HEADROOM | NR 42082 68818 | NO | YES | 0 | 1.1397 | 0.89968 | 0.63968 | 0.39863 | 0.11968 | -0.083474 | -0.10558 | -0.12347 | -0.14242 | -0.15821 | -0.26874 | -0.33084 | -0.37926 | 1.1355 | 0.85442 | 0.54916 | 0.266 | -0.061368 | -0.30032 | -0.32453 | -0.34558 | -0.36663 | -0.38558 | -0.51189 | -0.58242 | -0.63716 | 1.1355 | 0.85442 | 0.55126 | 0.26916 | -0.058211 | -0.29611 | -0.32032 | -0.34032 | -0.36137 | -0.38032 | -0.50663 | -0.57716 | -0.63295
|  | PORT ASKAIG | EE |  |  |  |  | 1.1397 | 1.126 | 0.81126 | 0.48284 | 0.19653 | -0.083474 | -0.10558 | -0.12347 | -0.14242 | -0.15821 | -0.26874 | -0.33084 | -0.37926 | 1.1355 | 1.1207 | 0.75021 | 0.36495 | 0.028105 | -0.30032 | -0.32453 | -0.34558 | -0.36663 | -0.38558 | -0.51189 | -0.58242 | -0.63716 | 1.1355 | 1.1207 | 0.75126 | 0.36705 | 0.031263 | -0.29611 | -0.32032 | -0.34032 | -0.36137 | -0.38032 | -0.50663 | -0.57716 | -0.63295
|  | PORT ASKAIG | HT |  |  |  |  | 1.1439 | 0.89968 | 0.63968 | 0.39863 | 0.11968 | 0.10074 | 0.081789 | 0.061789 | 0.037579 | 0.0038947 | -0.10453 | -0.16347 | -0.20453 | 1.1407 | 0.85442 | 0.54916 | 0.266 | -0.061368 | -0.083474 | -0.10558 | -0.12663 | -0.15505 | -0.194 | -0.29926 | -0.37189 | -0.43084 | 1.1407 | 0.85442 | 0.55126 | 0.26916 | -0.058211 | -0.080316 | -0.10137 | -0.12347 | -0.15084 | -0.18979 | -0.29505 | -0.36663 | -0.42558
|  | PORT ASKAIG | HE |  |  |  |  | 1.1534 | 1.1439 | 0.83442 | 0.52179 | 0.246 | -0.023474 | -0.030842 | -0.042421 | -0.052947 | -0.062421 | -0.14874 | -0.18032 | -0.20558 | 1.1513 | 1.1418 | 0.77758 | 0.41021 | 0.086 | -0.22979 | -0.23926 | -0.25189 | -0.26242 | -0.274 | -0.37295 | -0.40979 | -0.43821 | 1.1513 | 1.1418 | 0.77863 | 0.41232 | 0.089158 | -0.22558 | -0.23505 | -0.24768 | -0.25821 | -0.26979 | -0.36874 | -0.40558 | -0.434
|  | PORT ASKAIG | FB |  |  |  |  | 1.1565 | 1.1513 | 1.146 | 1.0155 | 0.88495 | 0.77232 | 0.65021 | 0.64389 | 0.63653 | 0.626 | 0.57337 | 0.51442 | 0.48179 | 1.1555 | 1.1502 | 1.1428 | 0.98916 | 0.83653 | 0.70495 | 0.56074 | 0.55337 | 0.54495 | 0.53337 | 0.47337 | 0.40495 | 0.36705 | 1.1555 | 1.1502 | 1.1428 | 0.99021 | 0.83758 | 0.706 | 0.56179 | 0.55547 | 0.54705 | 0.53442 | 0.47547 | 0.40705 | 0.36916
| PORT ANN | PORT ELLEN | MINIMUM HEADROOM | NR 36459 45513 | YES | YES | 0 | 3.9168 | 3.7053 | 3.5916 | 3.5463 | 3.5158 | 3.4779 | 3.4347 | 3.3747 | 3.3042 | 3.1316 | 2.6547 | 2.5558 | 2.4832 | 3.9126 | 3.6884 | 3.5674 | 3.52 | 3.4884 | 3.4495 | 3.4042 | 3.3421 | 3.2674 | 3.0842 | 2.58 | 2.4768 | 2.4 | 4.5032 | 4.4958 | 4.4168 | 4.3663 | 4.3326 | 4.2916 | 4.2442 | 4.1768 | 4.0968 | 3.9 | 3.36 | 3.2495 | 3.1684
|  | PORT ELLEN | EE |  |  |  |  | 3.9168 | 3.8884 | 3.5916 | 3.5463 | 3.5158 | 3.4853 | 3.4347 | 3.3747 | 3.32 | 3.2937 | 2.6547 | 2.5558 | 2.4832 | 3.9126 | 3.8821 | 3.5674 | 3.52 | 3.4884 | 3.4568 | 3.4042 | 3.3421 | 3.2842 | 3.2568 | 2.58 | 2.4768 | 2.4 | 4.5032 | 4.4958 | 4.4168 | 4.3663 | 4.3326 | 4.2989 | 4.2442 | 4.1768 | 4.1158 | 4.0863 | 3.36 | 3.2495 | 3.1684
|  | PORT ELLEN | HT |  |  |  |  | 3.9232 | 3.7053 | 3.6263 | 3.5484 | 3.5189 | 3.4779 | 3.4379 | 3.4063 | 3.3042 | 3.1316 | 2.7305 | 2.6389 | 2.5726 | 3.92 | 3.6884 | 3.6053 | 3.5232 | 3.4926 | 3.4495 | 3.4074 | 3.3737 | 3.2674 | 3.0842 | 2.6842 | 2.5832 | 2.4968 | 4.5042 | 4.4979 | 4.4568 | 4.3695 | 4.3368 | 4.2916 | 4.2463 | 4.2116 | 4.0968 | 3.9 | 3.4726 | 3.3642 | 3.2726
|  | PORT ELLEN | HE |  |  |  |  | 3.9389 | 3.9158 | 3.6158 | 3.5737 | 3.56 | 3.5432 | 3.4979 | 3.4579 | 3.4221 | 3.4084 | 2.8442 | 2.7916 | 2.7568 | 3.9358 | 3.9116 | 3.5937 | 3.5495 | 3.5358 | 3.5179 | 3.4716 | 3.4284 | 3.3916 | 3.3768 | 2.78 | 2.7253 | 2.6884 | 4.5074 | 4.5 | 4.4442 | 4.3968 | 4.3821 | 4.3653 | 4.3147 | 4.2695 | 4.2295 | 4.2147 | 3.5726 | 3.5137 | 3.4747
|  | PORT ELLEN | FB |  |  |  |  | 3.9516 | 3.9421 | 3.92 | 3.8053 | 3.7947 | 3.7842 | 3.7747 | 3.7547 | 3.7242 | 3.7084 | 3.4821 | 3.2158 | 3.1653 | 3.9484 | 3.9389 | 3.9158 | 3.7937 | 3.7832 | 3.7726 | 3.7632 | 3.7421 | 3.7095 | 3.6926 | 3.4537 | 3.1726 | 3.1189 | 4.5095 | 4.5074 | 4.5042 | 4.5011 | 4.4979 | 4.4937 | 4.4905 | 4.4863 | 4.4821 | 4.4779 | 4.2958 | 3.9937 | 3.9368
| DUNVEGAN | PORTREE | MINIMUM HEADROOM | NG 48102 44602 | NO | YES | 0 | 8.6842 | 8.5611 | 8.3958 | 8.2032 | 8.0832 | 6.4063 | 4.6674 | 3.0484 | 2.0716 | 1.5168 | 0.095789 | -0.28211 | -0.59263 | 7.9463 | 7.9137 | 7.8842 | 7.8484 | 7.8095 | 6.0211 | 3.9768 | 2.0737 | 0.93053 | 0.28632 | -1.1853 | -1.5484 | -1.8347 | 7.4021 | 7.2916 | 7.1505 | 6.9884 | 6.8779 | 5.6968 | 4.3474 | 2.4432 | 1.2968 | 0.64842 | -0.99263 | -1.4179 | -1.7684
|  | PORTREE | EE |  |  |  |  | 8.6842 | 8.5611 | 8.3958 | 8.2032 | 8.0832 | 7.9611 | 7.5979 | 5.9347 | 4.1937 | 2.5411 | 0.095789 | -0.28211 | -0.59263 | 7.9463 | 7.9137 | 7.8842 | 7.8484 | 7.8095 | 7.7653 | 7.5337 | 5.5905 | 3.5547 | 1.6242 | -1.1853 | -1.5484 | -1.8347 | 7.4021 | 7.2916 | 7.1505 | 6.9884 | 6.8779 | 6.7653 | 6.4779 | 5.2442 | 3.8137 | 1.8695 | -0.99263 | -1.4179 | -1.7684
|  | PORTREE | HT |  |  |  |  | 8.7221 | 8.6274 | 8.4884 | 8.3347 | 8.2337 | 6.4063 | 4.6674 | 3.0484 | 2.0716 | 1.5168 | 0.32421 | 0.0084211 | -0.21684 | 7.9558 | 7.9305 | 7.9032 | 7.8747 | 7.8411 | 6.0211 | 3.9768 | 2.0737 | 0.93053 | 0.28632 | -0.99684 | -1.3453 | -1.6411 | 7.4411 | 7.3611 | 7.2495 | 7.1274 | 7.0389 | 5.6968 | 4.3474 | 2.4432 | 1.2968 | 0.64842 | -0.65158 | -1.0242 | -1.3442
|  | PORTREE | HE |  |  |  |  | 8.7663 | 8.6874 | 8.5716 | 8.4442 | 8.3842 | 8.2337 | 8.0221 | 6.2116 | 4.3526 | 2.6116 | 0.85053 | 0.65579 | 0.50737 | 7.9632 | 7.9379 | 7.9189 | 7.8916 | 7.8642 | 7.8263 | 7.7884 | 5.8105 | 3.6221 | 1.5705 | -0.48211 | -0.68 | -0.82211 | 7.4747 | 7.4074 | 7.3137 | 7.2105 | 7.1547 | 7.0316 | 6.8642 | 5.5358 | 3.9832 | 1.9305 | -0.13789 | -0.35895 | -0.52737
|  | PORTREE | FB |  |  |  |  | 8.7989 | 8.76 | 8.6989 | 8.6379 | 8.6032 | 8.5663 | 8.4495 | 8.3389 | 7.5632 | 6.7432 | 4 | 3.7589 | 3.6158 | 7.9779 | 7.9695 | 7.9611 | 7.9505 | 7.94 | 7.9284 | 7.9168 | 7.9053 | 7.3579 | 6.3895 | 3.1589 | 2.8853 | 2.7232 | 7.5042 | 7.4737 | 7.4263 | 7.3779 | 7.3495 | 7.3179 | 7.2295 | 7.1442 | 6.5768 | 5.9747 | 3.5484 | 3.2716 | 3.1063
| MACDUFF | PORTSOY | MINIMUM HEADROOM | NJ 58491 65037 | YES | YES | 0.35714 | 1.5559 | 1.5275 | 1.4927 | 1.4464 | 1.4064 | 1.3612 | 1.3201 | 1.2801 | 1.2401 | 1.2033 | -12.7799 | -20.3052 | -24.0441 | 1.2359 | 1.1969 | 1.1569 | 1.1054 | 1.0601 | 1.0106 | 0.96537 | 0.92116 | 0.87695 | 0.83484 | -10.9167 | -22.7136 | -28.2167 | 1.2285 | 1.1959 | 1.1633 | 1.118 | 1.0738 | 1.0243 | 0.97905 | 0.93589 | 0.89168 | 0.84958 | -10.8494 | -22.9841 | -28.4704
|  | PORTSOY | EE |  |  |  |  | 1.5559 | 1.5275 | 1.4927 | 1.4464 | 1.4064 | 1.3612 | 1.3201 | 1.2801 | 1.2401 | 1.2033 | -1.4378 | -5.2599 | -7.9357 | 1.2359 | 1.1969 | 1.1569 | 1.1054 | 1.0601 | 1.0106 | 0.96537 | 0.92116 | 0.87695 | 0.83484 | -2.2578 | -5.9631 | -9.1009 | 1.2285 | 1.1959 | 1.1633 | 1.118 | 1.0738 | 1.0243 | 0.97905 | 0.93589 | 0.89168 | 0.84958 | -2.202 | -6.3525 | -9.4904
|  | PORTSOY | HT |  |  |  |  | 1.558 | 1.5412 | 1.5064 | 1.4696 | 1.4254 | 1.3843 | 1.3422 | 1.3001 | 1.2601 | 1.218 | -12.7799 | -20.3052 | -24.0441 | 1.2464 | 1.2117 | 1.1738 | 1.1327 | 1.0833 | 1.038 | 0.99063 | 0.94537 | 0.90116 | 0.85379 | -10.9167 | -22.7136 | -28.2167 | 1.2369 | 1.2075 | 1.1759 | 1.1412 | 1.0959 | 1.0506 | 1.0043 | 0.95905 | 0.91484 | 0.86853 | -10.8494 | -22.9841 | -28.4704
|  | PORTSOY | HE |  |  |  |  | 1.5633 | 1.5517 | 1.5443 | 1.5285 | 1.5033 | 1.4748 | 1.4454 | 1.4212 | 1.3948 | 1.3717 | -1.2062 | -3.8283 | -6.4525 | 1.2727 | 1.2464 | 1.2243 | 1.1991 | 1.1717 | 1.1412 | 1.1106 | 1.0833 | 1.0548 | 1.0275 | -1.9946 | -4.7599 | -7.8388 | 1.258 | 1.2359 | 1.2169 | 1.1948 | 1.1706 | 1.1433 | 1.1159 | 1.0927 | 1.0675 | 1.0401 | -1.942 | -4.882 | -7.962
|  | PORTSOY | FB |  |  |  |  | 1.5685 | 1.5633 | 1.558 | 1.5517 | 1.5464 | 1.5306 | 1.5138 | 1.4991 | 1.4812 | 1.4559 | -0.51568 | -7.7378 | -17.1115 | 1.2854 | 1.2696 | 1.2527 | 1.2348 | 1.218 | 1.2001 | 1.1822 | 1.1664 | 1.1464 | 1.118 | -1.1936 | -9.6767 | -20.7167 | 1.2696 | 1.2559 | 1.2422 | 1.2264 | 1.2127 | 1.198 | 1.1822 | 1.1685 | 1.1517 | 1.1285 | -1.1504 | -9.6136 | -20.6199
| WOODHILL | QUEENS LANE NORTH | MINIMUM HEADROOM | NJ 92224 05823 | NO | NO | 0 | 12.0018 | 11.9292 | 28.8505 | 28.7842 | 28.7042 | 28.6126 | 28.5232 | 28.4442 | 28.3695 | 28.2895 | 27.9684 | 27.7084 | 27.5137 | 13.8442 | 13.7968 | 29.86 | 29.8126 | 29.7547 | 29.6937 | 29.6232 | 29.5653 | 29.5074 | 29.36 | 28.7642 | 28.2168 | 27.6263 | 14.2662 | 14.2241 | 30.73 | 30.6837 | 30.6321 | 30.5805 | 30.5142 | 30.4616 | 30.4079 | 30.3479 | 29.8479 | 29.3121 | 28.7332
|  | QUEENS LANE NORTH | EE |  |  |  |  | 12.0018 | 11.9292 | 28.8505 | 28.7842 | 28.7042 | 28.6126 | 28.5232 | 28.4442 | 28.3695 | 28.2895 | 28.0053 | 27.7747 | 27.5905 | 13.8442 | 13.7968 | 29.86 | 29.8168 | 29.7642 | 29.6937 | 29.6232 | 29.5653 | 29.5074 | 29.36 | 28.7642 | 28.2168 | 27.7126 | 14.2662 | 14.2241 | 30.73 | 30.6921 | 30.6458 | 30.5805 | 30.5142 | 30.4616 | 30.4079 | 30.3626 | 29.8479 | 29.3121 | 28.8184
|  | QUEENS LANE NORTH | HT |  |  |  |  | 12.0155 | 11.9513 | 28.8642 | 28.7968 | 28.7126 | 28.6389 | 28.5642 | 28.4863 | 28.4053 | 28.3021 | 27.9684 | 27.7084 | 27.5137 | 13.8516 | 13.8095 | 29.8632 | 29.8126 | 29.7547 | 29.7 | 29.6421 | 29.5821 | 29.5179 | 29.4463 | 28.9 | 28.2474 | 27.6263 | 14.2714 | 14.2357 | 30.73 | 30.6837 | 30.6321 | 30.5816 | 30.5279 | 30.4721 | 30.4121 | 30.3479 | 29.9816 | 29.3416 | 28.7332
|  | QUEENS LANE NORTH | HE |  |  |  |  | 12.0418 | 11.9829 | 28.9158 | 28.8632 | 28.7926 | 28.7168 | 28.6316 | 28.5758 | 28.5211 | 28.4758 | 28.3189 | 28.2 | 28.1011 | 13.8642 | 13.8211 | 29.8884 | 29.8453 | 29.7895 | 29.7232 | 29.6516 | 29.6063 | 29.5621 | 29.5368 | 29.4274 | 29.3379 | 29.0611 | 14.2809 | 14.242 | 30.7489 | 30.7079 | 30.6563 | 30.5921 | 30.5237 | 30.4805 | 30.4395 | 30.4184 | 30.3205 | 30.2521 | 30.1395
|  | QUEENS LANE NORTH | FB |  |  |  |  | 12.0682 | 12.0345 | 28.9811 | 28.9495 | 28.9126 | 28.8779 | 28.8432 | 28.8042 | 28.7663 | 28.7179 | 28.5568 | 28.4074 | 28.3 | 13.8832 | 13.8621 | 29.9411 | 29.9179 | 29.8916 | 29.8653 | 29.84 | 29.8116 | 29.7842 | 29.7516 | 29.6379 | 29.5389 | 29.3095 | 14.2988 | 14.2799 | 30.7984 | 30.7774 | 30.7542 | 30.73 | 30.7058 | 30.6805 | 30.6553 | 30.6268 | 30.5247 | 30.4374 | 30.3858
| THURSO | RACKWICK | MINIMUM HEADROOM | ND 20206 99857 | YES | YES | 0 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10421 | 0.10316 | 0.10316 | 0.10105 | 0.10105 | 0.10105 | 0.098947 | 0.098947 | 0.096842 | 0.1 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.093684 | 0.091579 | 0.091579 | 0.091579 | 0.089474 | 0.088421 | 0.087368 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.094737 | 0.094737 | 0.092632 | 0.091579 | 0.089474
|  | RACKWICK | EE |  |  |  |  | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10421 | 0.10316 | 0.10316 | 0.10105 | 0.10105 | 0.10105 | 0.098947 | 0.098947 | 0.096842 | 0.1 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.093684 | 0.091579 | 0.091579 | 0.091579 | 0.089474 | 0.088421 | 0.087368 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.094737 | 0.094737 | 0.092632 | 0.091579 | 0.089474
|  | RACKWICK | HT |  |  |  |  | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10316 | 0.10316 | 0.10105 | 0.1 | 0.098947 | 0.1 | 0.1 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.094737 | 0.094737 | 0.092632 | 0.090526 | 0.089474 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.096842 | 0.094737 | 0.092632 | 0.092632
|  | RACKWICK | HE |  |  |  |  | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.095789 | 0.095789 | 0.094737 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.096842
|  | RACKWICK | FB |  |  |  |  | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.095789 | 0.095789 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.097895 | 0.097895
| FORT WILLIAM | RAHOY | MINIMUM HEADROOM | NM 69621 49222 | YES | NO | 0 | 0.99368 | 0.98316 | 0.97263 | 0.96105 | 0.94947 | 0.94 | 0.92947 | 0.91895 | 0.90842 | 0.89789 | 0.86 | 0.81789 | 0.77368 | 0.99368 | 0.98421 | 0.97368 | 0.96316 | 0.95263 | 0.94316 | 0.93368 | 0.92316 | 0.91263 | 0.90211 | 0.86632 | 0.82632 | 0.78421 | 0.99263 | 0.98316 | 0.97263 | 0.96105 | 0.94947 | 0.93895 | 0.92947 | 0.91789 | 0.90737 | 0.89579 | 0.85789 | 0.81579 | 0.77158
|  | RAHOY | EE |  |  |  |  | 0.99368 | 0.98316 | 0.97263 | 0.96105 | 0.94947 | 0.94 | 0.92947 | 0.91895 | 0.90842 | 0.89789 | 0.86 | 0.81789 | 0.77368 | 0.99368 | 0.98421 | 0.97368 | 0.96316 | 0.95263 | 0.94316 | 0.93368 | 0.92316 | 0.91263 | 0.90211 | 0.86632 | 0.82632 | 0.78421 | 0.99263 | 0.98316 | 0.97263 | 0.96105 | 0.94947 | 0.93895 | 0.92947 | 0.91789 | 0.90737 | 0.89579 | 0.85789 | 0.81579 | 0.77158
|  | RAHOY | HT |  |  |  |  | 1 | 0.99789 | 0.99474 | 0.99158 | 0.98842 | 0.98526 | 0.98316 | 0.98 | 0.97684 | 0.97368 | 0.95684 | 0.94 | 0.92632 | 1 | 0.99684 | 0.99474 | 0.99158 | 0.98842 | 0.98632 | 0.98421 | 0.98105 | 0.97789 | 0.97474 | 0.96316 | 0.94632 | 0.93053 | 1 | 0.99684 | 0.99368 | 0.99053 | 0.98737 | 0.98421 | 0.98211 | 0.97895 | 0.97579 | 0.97263 | 0.96 | 0.94211 | 0.92526
|  | RAHOY | HE |  |  |  |  | 1 | 0.99789 | 0.99474 | 0.99158 | 0.98842 | 0.98632 | 0.98211 | 0.98 | 0.97684 | 0.97368 | 0.96 | 0.94421 | 0.92737 | 1 | 0.99684 | 0.99474 | 0.99158 | 0.98842 | 0.98632 | 0.98316 | 0.98105 | 0.97789 | 0.97474 | 0.96211 | 0.94737 | 0.93158 | 1 | 0.99684 | 0.99368 | 0.99053 | 0.98737 | 0.98526 | 0.98105 | 0.97895 | 0.97579 | 0.97263 | 0.95895 | 0.94316 | 0.92632
|  | RAHOY | FB |  |  |  |  | 1.0021 | 1.0011 | 1.0011 | 1 | 1 | 0.99895 | 0.99895 | 0.99895 | 0.99789 | 0.99684 | 0.99474 | 0.99263 | 0.98947 | 1.0011 | 1.0011 | 1 | 1 | 0.99895 | 0.99789 | 0.99789 | 0.99789 | 0.99684 | 0.99579 | 0.99474 | 0.99158 | 0.98947 | 1.0011 | 1.0011 | 1 | 1 | 0.99895 | 0.99789 | 0.99789 | 0.99789 | 0.99684 | 0.99579 | 0.99368 | 0.99158 | 0.98947
| INVERNESS | RAIGMORE | MINIMUM HEADROOM | NH 68427 44693 | NO | YES | 0.52245 | 25.3553 | 25.3324 | 25.3116 | 25.2908 | 25.2643 | 25.2414 | 25.2055 | 24.969 | 24.4781 | 22.8958 | 17.8808 | 17.5175 | 17.3899 | 24.8772 | 24.8357 | 24.7948 | 24.7325 | 24.6852 | 24.6149 | 24.3376 | 24.0323 | 23.4182 | 21.5563 | 15.657 | 15.2349 | 15.088 | 25.6827 | 25.6175 | 25.5315 | 25.381 | 25.2878 | 25.0707 | 24.7948 | 24.4902 | 23.876 | 22.02 | 16.1379 | 15.7179 | 15.571
|  | RAIGMORE | EE |  |  |  |  | 25.3553 | 25.3324 | 25.313 | 25.2908 | 25.2643 | 25.2428 | 25.2055 | 24.969 | 24.9146 | 24.8544 | 23.353 | 23.037 | 22.8428 | 24.8772 | 24.8357 | 24.7948 | 24.7325 | 24.6852 | 24.6665 | 24.3734 | 24.0323 | 23.9735 | 23.9062 | 22.154 | 21.7936 | 21.5721 | 25.6827 | 25.6175 | 25.5315 | 25.381 | 25.2878 | 25.2262 | 24.8299 | 24.4902 | 24.4307 | 24.3641 | 22.6169 | 22.2565 | 22.035
|  | RAIGMORE | HT |  |  |  |  | 25.3574 | 25.3359 | 25.3116 | 25.2994 | 25.27 | 25.2414 | 25.2105 | 25.0565 | 24.997 | 24.3678 | 23.2398 | 22.9761 | 22.7905 | 24.8844 | 24.8464 | 24.8041 | 24.7798 | 24.7289 | 24.6149 | 24.3376 | 24.1334 | 24.0703 | 23.3343 | 22.1046 | 21.7828 | 21.5184 | 25.6848 | 25.6461 | 25.5644 | 25.4677 | 25.3681 | 25.0707 | 24.7948 | 24.5912 | 24.5282 | 23.7943 | 22.5682 | 22.2471 | 21.9827
|  | RAIGMORE | HE |  |  |  |  | 25.3639 | 25.3417 | 25.3266 | 25.3044 | 25.2772 | 25.2571 | 25.2213 | 25.1991 | 25.1754 | 25.1367 | 22.5963 | 22.3755 | 22.2337 | 24.9023 | 24.8693 | 24.8414 | 24.7912 | 24.7518 | 24.7117 | 24.5705 | 24.3168 | 24.2745 | 24.2301 | 21.2453 | 20.9909 | 20.8168 | 25.6913 | 25.6691 | 25.6526 | 25.5415 | 25.477 | 25.3444 | 25.0269 | 24.7747 | 24.7324 | 24.688 | 21.7125 | 21.4588 | 21.2811
|  | RAIGMORE | FB |  |  |  |  | 25.3696 | 25.3617 | 25.3531 | 25.3438 | 25.3338 | 25.3238 | 25.313 | 25.3016 | 24.4781 | 22.8958 | 17.8808 | 17.5175 | 17.3899 | 24.9195 | 24.903 | 24.8851 | 24.8593 | 24.8407 | 24.8213 | 24.7604 | 24.6909 | 23.4182 | 21.5563 | 15.657 | 15.2349 | 15.088 | 25.697 | 25.6891 | 25.6805 | 25.6712 | 25.6368 | 25.5988 | 25.4275 | 25.2305 | 23.876 | 22.02 | 16.1379 | 15.7179 | 15.571
| ARBROATH | REDFORD | MINIMUM HEADROOM | NO 55879 44046 | YES | YES | 0 | -0.2 | -0.23579 | -0.26632 | -0.30947 | -0.34316 | -0.39579 | -0.45368 | -0.49368 | -0.53368 | -0.57053 | -4.1547 | -5.3179 | -5.3811 | -0.85368 | -0.89368 | -0.92842 | -0.97789 | -1.0137 | -1.0747 | -1.1411 | -1.1874 | -1.2316 | -1.2716 | -5.1695 | -6.0779 | -6.1505 | -0.52737 | -0.56211 | -0.59053 | -0.63158 | -0.66316 | -0.71368 | -0.76737 | -0.80632 | -0.85053 | -0.89053 | -5.0021 | -6.1568 | -6.2295
|  | REDFORD | EE |  |  |  |  | -0.2 | -0.23579 | -0.26632 | -0.30421 | -0.33579 | -0.37263 | -0.41684 | -0.47053 | -0.51895 | -0.54842 | -4.1547 | -5.3179 | -5.3811 | -0.85368 | -0.89368 | -0.92842 | -0.97158 | -1.0074 | -1.0463 | -1.0968 | -1.1579 | -1.2137 | -1.2474 | -5.1695 | -6.0779 | -6.1505 | -0.52737 | -0.56211 | -0.59053 | -0.62632 | -0.65684 | -0.69158 | -0.73368 | -0.78421 | -0.83263 | -0.86632 | -5.0021 | -6.1568 | -6.2295
|  | REDFORD | HT |  |  |  |  | -0.18947 | -0.22105 | -0.25158 | -0.30947 | -0.34316 | -0.39579 | -0.45368 | -0.49368 | -0.53368 | -0.57053 | -2.2937 | -2.3905 | -2.4632 | -0.84105 | -0.87579 | -0.91053 | -0.97789 | -1.0137 | -1.0747 | -1.1411 | -1.1874 | -1.2316 | -1.2716 | -1.9568 | -2.7411 | -2.8442 | -0.51789 | -0.54737 | -0.57684 | -0.63158 | -0.66316 | -0.71368 | -0.76737 | -0.80632 | -0.85053 | -0.89053 | -1.7326 | -2.7095 | -2.8105
|  | REDFORD | HE |  |  |  |  | -0.16526 | -0.18842 | -0.20632 | -0.24105 | -0.26316 | -0.28842 | -0.33684 | -0.37789 | -0.41789 | -0.43474 | -3.4263 | -3.9021 | -3.9337 | -0.81368 | -0.83895 | -0.85895 | -0.89789 | -0.92105 | -0.94737 | -1.0042 | -1.0505 | -1.0958 | -1.1158 | -4.5516 | -4.9263 | -4.9621 | -0.49579 | -0.51684 | -0.53368 | -0.56737 | -0.58842 | -0.61263 | -0.66 | -0.69789 | -0.73474 | -0.75158 | -4.2558 | -4.7295 | -4.7653
|  | REDFORD | FB |  |  |  |  | -0.15474 | -0.16842 | -0.18211 | -0.19684 | -0.21263 | -0.22632 | -0.24105 | -0.26211 | -0.28842 | -0.30632 | -0.39263 | -0.46842 | -0.51263 | -0.80211 | -0.81789 | -0.83368 | -0.84947 | -0.86632 | -0.88211 | -0.89789 | -0.92316 | -0.95368 | -0.97368 | -1.0726 | -1.16 | -1.2126 | -0.48421 | -0.49789 | -0.51053 | -0.52526 | -0.53895 | -0.55263 | -0.56632 | -0.58632 | -0.61158 | -0.62737 | -0.70947 | -0.78 | -0.83158
| BURGHMUIR | REDGORTON | MINIMUM HEADROOM | NO 07650 28860 | NO | YES | 0.20306 | 14.3858 | 13.8511 | 13.2089 | 12.3142 | 11.7153 | 10.6363 | 9.7342 | 8.9511 | 8.1605 | 7.4268 | 3.1279 | 2.6595 | 2.4153 | 12.64 | 12.0042 | 11.2505 | 10.2074 | 9.5137 | 8.2558 | 7.2084 | 6.2979 | 5.3779 | 4.5232 | 0.36632 | -0.94526 | -1.2916 | 13.0571 | 12.435 | 11.6992 | 10.6813 | 9.9908 | 8.7276 | 7.6792 | 6.7666 | 5.8455 | 4.9982 | 0.82974 | -0.47447 | -0.82184
|  | REDGORTON | EE |  |  |  |  | 14.3858 | 13.8511 | 13.2089 | 12.3142 | 11.7542 | 10.6363 | 9.7342 | 8.9511 | 8.1605 | 7.4542 | 3.8637 | 2.7553 | 2.4995 | 12.64 | 12.0042 | 11.2505 | 10.2074 | 9.5568 | 8.2558 | 7.2084 | 6.2979 | 5.3779 | 4.5547 | 0.36632 | -0.91368 | -1.1989 | 13.0571 | 12.435 | 11.6992 | 10.6813 | 10.0308 | 8.7276 | 7.6792 | 6.7666 | 5.8455 | 5.0213 | 0.82974 | -0.45553 | -0.74395
|  | REDGORTON | HT |  |  |  |  | 14.4121 | 13.89 | 13.2437 | 12.3489 | 11.7153 | 10.8216 | 10.0047 | 9.1784 | 8.2847 | 7.4268 | 3.1279 | 2.6595 | 2.4153 | 12.6716 | 12.0484 | 11.2916 | 10.2484 | 9.5137 | 8.4726 | 7.5232 | 6.56 | 5.5211 | 4.5232 | 0.37895 | -0.94526 | -1.2916 | 13.0876 | 12.4803 | 11.7413 | 10.7234 | 9.9908 | 8.9487 | 7.9992 | 7.035 | 5.9961 | 4.9982 | 0.85079 | -0.47447 | -0.82184
|  | REDGORTON | HE |  |  |  |  | 14.4826 | 13.9858 | 13.3816 | 12.5247 | 11.9974 | 11.0616 | 10.1595 | 9.3889 | 8.5974 | 7.9142 | 4.4405 | 3.4553 | 3.3068 | 12.7526 | 12.16 | 11.4453 | 10.4474 | 9.8347 | 8.7463 | 7.6947 | 6.7968 | 5.8737 | 5.0737 | 1.0095 | -0.13789 | -0.30526 | 13.1666 | 12.5897 | 11.8929 | 10.9192 | 10.3129 | 9.2224 | 8.1708 | 7.2729 | 6.3487 | 5.5487 | 1.4813 | 0.33184 | 0.16342
|  | REDGORTON | FB |  |  |  |  | 14.7332 | 14.5026 | 14.2321 | 13.9195 | 13.7342 | 13.3047 | 12.8458 | 12.37 | 11.9132 | 11.5268 | 9.4195 | 8.4353 | 8.2605 | 13.0505 | 12.7747 | 12.4526 | 12.0789 | 11.8589 | 11.3558 | 10.82 | 10.2642 | 9.7295 | 9.28 | 6.8168 | 5.6737 | 5.4737 | 13.4582 | 13.1897 | 12.8739 | 12.5097 | 12.295 | 11.8045 | 11.2824 | 10.7403 | 10.2087 | 9.7582 | 7.295 | 6.1497 | 5.9497
| REDMOSS | REDMOSS | MINIMUM HEADROOM | NJ 94562 01919 | NO | YES | 0.5102 | 34.0705 | 32.9842 | 31.8653 | 30.3926 | 29.3832 | 27.2274 | 26.6611 | 26.1516 | 25.6642 | 25.3095 | 24.3295 | 23.7684 | 23.3474 | 32.5758 | 31.2137 | 29.8042 | 27.9495 | 26.6853 | 23.9653 | 23.2632 | 22.6326 | 22.0326 | 21.5989 | 20.4042 | 19.7979 | 19.2358 | 33.6905 | 32.3484 | 30.9568 | 29.08 | 27.8011 | 25.0495 | 24.34 | 23.7021 | 23.0947 | 22.6579 | 21.4516 | 20.84 | 20.2726
|  | REDMOSS | EE |  |  |  |  | 34.0779 | 32.9842 | 31.8758 | 30.4821 | 29.5295 | 27.7179 | 26.8495 | 26.2411 | 25.6653 | 25.5 | 24.3295 | 23.8263 | 23.4084 | 32.5884 | 31.2137 | 29.8168 | 28.0621 | 26.8663 | 24.5874 | 23.5063 | 22.7495 | 22.0337 | 21.8368 | 20.4042 | 19.7979 | 19.2905 | 33.7021 | 32.3484 | 30.9695 | 29.1926 | 27.9842 | 25.6789 | 24.5863 | 23.8221 | 23.0979 | 22.8989 | 21.4516 | 20.84 | 20.3263
|  | REDMOSS | HT |  |  |  |  | 34.0705 | 33.0811 | 31.8653 | 30.3926 | 29.3832 | 27.2274 | 26.6611 | 26.1516 | 25.6642 | 25.3095 | 24.3505 | 23.7684 | 23.3474 | 32.5758 | 31.3326 | 29.8042 | 27.9495 | 26.6853 | 23.9653 | 23.2632 | 22.6326 | 22.0326 | 21.5989 | 20.5926 | 19.8758 | 19.2358 | 33.6905 | 32.4653 | 30.9568 | 29.08 | 27.8011 | 25.0495 | 24.34 | 23.7021 | 23.0947 | 22.6579 | 21.6421 | 20.9179 | 20.2726
|  | REDMOSS | HE |  |  |  |  | 34.1232 | 33.2063 | 32.1158 | 30.7547 | 29.8547 | 27.7853 | 27.2084 | 26.6726 | 26.1589 | 26.0547 | 25.2263 | 24.9726 | 24.7358 | 32.6389 | 31.4863 | 30.1116 | 28.3968 | 27.2695 | 24.6621 | 23.9495 | 23.2811 | 22.6411 | 22.5147 | 21.4884 | 21.1821 | 20.8937 | 33.7537 | 32.6168 | 31.2621 | 29.5326 | 28.3916 | 25.7547 | 25.0347 | 24.3579 | 23.7116 | 23.5842 | 22.5463 | 22.2379 | 21.9453
|  | REDMOSS | FB |  |  |  |  | 38.4884 | 34.9568 | 34.5305 | 34.1232 | 33.68 | 32.9042 | 32.2368 | 31.8979 | 31.5684 | 31.4737 | 30.8768 | 30.2979 | 30.0474 | 36.5253 | 33.6947 | 33.1589 | 32.6474 | 32.0905 | 31.1126 | 30.2716 | 29.8484 | 29.4358 | 29.3221 | 28.5895 | 27.8758 | 27.5674 | 38.3621 | 34.7937 | 34.2653 | 33.7611 | 33.2116 | 32.2474 | 31.4189 | 31.0011 | 30.5842 | 30.4684 | 29.7295 | 29.0074 | 28.6968
| CASSLEY | RHICONICH | MINIMUM HEADROOM | NC 25554 52924 | YES | YES | 0.096939 | 0.82842 | 0.80316 | 0.78 | 0.75263 | 0.72211 | 0.69158 | 0.66105 | 0.63368 | 0.60737 | 0.58526 | 0.49263 | 0.40842 | 0.34947 | 0.87895 | 0.86632 | 0.85579 | 0.84526 | 0.83053 | 0.81579 | 0.78211 | 0.74842 | 0.71474 | 0.68632 | 0.56737 | 0.45579 | 0.36526 | 1.0032 | 0.99158 | 0.98211 | 0.97263 | 0.93368 | 0.89263 | 0.85263 | 0.81684 | 0.78211 | 0.75263 | 0.62737 | 0.50947 | 0.42632
|  | RHICONICH | EE |  |  |  |  | 0.82842 | 0.80316 | 0.78 | 0.75263 | 0.72211 | 0.69158 | 0.66105 | 0.63368 | 0.60737 | 0.58526 | 0.49263 | 0.40842 | 0.34947 | 0.87895 | 0.86632 | 0.85579 | 0.84526 | 0.83053 | 0.81579 | 0.78211 | 0.74842 | 0.71474 | 0.68632 | 0.56737 | 0.45579 | 0.37789 | 1.0032 | 0.99158 | 0.98211 | 0.97263 | 0.93368 | 0.89263 | 0.85263 | 0.81684 | 0.78211 | 0.75263 | 0.62737 | 0.50947 | 0.42632
|  | RHICONICH | HT |  |  |  |  | 0.83368 | 0.81368 | 0.79474 | 0.77053 | 0.74211 | 0.71579 | 0.68737 | 0.66211 | 0.63579 | 0.61053 | 0.49263 | 0.41053 | 0.35053 | 0.88105 | 0.86947 | 0.86 | 0.84526 | 0.83158 | 0.81895 | 0.80421 | 0.78211 | 0.74842 | 0.71579 | 0.58947 | 0.47263 | 0.36526 | 1.0042 | 0.99474 | 0.98632 | 0.97368 | 0.96211 | 0.92737 | 0.89158 | 0.85789 | 0.82316 | 0.78947 | 0.65789 | 0.53895 | 0.42632
|  | RHICONICH | HE |  |  |  |  | 0.84737 | 0.83263 | 0.82 | 0.80421 | 0.78737 | 0.76947 | 0.75053 | 0.73368 | 0.71684 | 0.70526 | 0.65579 | 0.61263 | 0.58316 | 0.88526 | 0.87579 | 0.86842 | 0.85895 | 0.84737 | 0.83368 | 0.82 | 0.80947 | 0.79895 | 0.79474 | 0.77474 | 0.72421 | 0.68526 | 1.0074 | 0.99895 | 0.99263 | 0.98316 | 0.97263 | 0.96 | 0.94526 | 0.93579 | 0.92632 | 0.92316 | 0.85895 | 0.79579 | 0.75474
|  | RHICONICH | FB |  |  |  |  | 0.85684 | 0.84842 | 0.83895 | 0.83053 | 0.82105 | 0.81053 | 0.80105 | 0.79263 | 0.78316 | 0.76737 | 0.71579 | 0.66526 | 0.62842 | 0.89053 | 0.88737 | 0.88316 | 0.87895 | 0.87474 | 0.87053 | 0.86526 | 0.86105 | 0.85684 | 0.84947 | 0.82947 | 0.77263 | 0.71789 | 1.0137 | 1.0105 | 1.0063 | 1.0032 | 1 | 0.99579 | 0.99158 | 0.98842 | 0.98421 | 0.97895 | 0.92105 | 0.84737 | 0.79158
| DUDHOPE | ROSEBANK STREET | MINIMUM HEADROOM | NO 39943 31150 | NO | YES | 0.40816 | 24.9226 | 24.7679 | 24.5763 | 24.4016 | 24.2237 | 23.3226 | 23.1163 | 22.9437 | 22.7742 | 22.5889 | 21.6921 | 21.0605 | 20.6163 | 22.0158 | 21.9411 | 21.7853 | 21.6432 | 21.4947 | 20.7979 | 20.62 | 20.4747 | 20.3305 | 20.1053 | 19.2053 | 18.3337 | 17.6274 | 22.695 | 22.6171 | 22.5266 | 22.4392 | 22.2729 | 21.1287 | 20.8855 | 20.6813 | 20.4824 | 20.2603 | 19.4066 | 18.5834 | 17.9139
|  | ROSEBANK STREET | EE |  |  |  |  | 24.9226 | 24.7879 | 24.5763 | 24.4016 | 24.2237 | 23.3226 | 23.1163 | 22.9437 | 22.7742 | 22.5889 | 21.9121 | 21.3026 | 20.8374 | 22.0158 | 21.9537 | 21.7853 | 21.6432 | 21.4947 | 20.7979 | 20.62 | 20.4747 | 20.3305 | 20.1053 | 19.2642 | 18.4842 | 17.8832 | 22.695 | 22.6182 | 22.5266 | 22.4392 | 22.2729 | 21.1287 | 20.8855 | 20.6813 | 20.4824 | 20.2603 | 19.4634 | 18.7287 | 18.1624
|  | ROSEBANK STREET | HT |  |  |  |  | 24.9553 | 24.7679 | 24.6058 | 24.4458 | 24.2553 | 23.3963 | 23.2289 | 23.0658 | 22.8879 | 22.6437 | 21.6921 | 21.0605 | 20.6163 | 22.0211 | 21.9411 | 21.8053 | 21.6716 | 21.5116 | 20.8495 | 20.7063 | 20.5653 | 20.4116 | 20.2 | 19.2053 | 18.3337 | 17.6274 | 22.7097 | 22.6171 | 22.5297 | 22.4403 | 22.3213 | 21.2276 | 21.0318 | 20.8424 | 20.635 | 20.3445 | 19.4066 | 18.5834 | 17.9139
|  | ROSEBANK STREET | HE |  |  |  |  | 25.0311 | 24.9332 | 24.75 | 24.6353 | 24.5079 | 23.6595 | 23.5226 | 23.4132 | 23.2974 | 23.1784 | 22.73 | 22.3563 | 22.0995 | 22.0305 | 21.9779 | 21.9189 | 21.8189 | 21.7074 | 21.0484 | 20.9232 | 20.8274 | 20.7263 | 20.6305 | 20.26 | 19.8568 | 19.5232 | 22.7403 | 22.6729 | 22.5887 | 22.515 | 22.4297 | 21.5676 | 21.4171 | 21.2918 | 21.1582 | 21.0108 | 20.4718 | 20.015 | 19.7013
|  | ROSEBANK STREET | FB |  |  |  |  | 25.0721 | 25.0079 | 24.9395 | 24.8289 | 24.7489 | 24.6637 | 24.57 | 24.49 | 24.3942 | 24.2732 | 23.8468 | 23.4121 | 23.0921 | 22.0495 | 22.0242 | 21.9958 | 21.9663 | 21.9168 | 21.8442 | 21.7653 | 21.6958 | 21.6158 | 21.5147 | 21.1579 | 20.8 | 20.5432 | 22.7655 | 22.7287 | 22.6866 | 22.6318 | 22.5845 | 22.5339 | 22.4813 | 22.4308 | 22.3771 | 22.3108 | 21.8487 | 21.3213 | 20.9266
| KEITH 2 | ROTHES | MINIMUM HEADROOM | NJ 27901 49693 | NO | YES | 0 | 6.6189 | 6.5905 | 6.5589 | 6.5295 | 6.4779 | 6.4105 | 6.3326 | 6.2232 | 6.1453 | 6.0916 | 5.8853 | 6.0947 | 5.9526 | 5.8063 | 5.76 | 5.6842 | 5.6084 | 5.5421 | 5.4642 | 5.3726 | 5.2347 | 5.14 | 5.0779 | 4.8316 | 5.1179 | 4.9568 | 6.4989 | 6.4179 | 6.3421 | 6.2674 | 6.2 | 6.1232 | 6.0316 | 5.9 | 5.8095 | 5.7495 | 5.5147 | 5.7789 | 5.6242
|  | ROTHES | EE |  |  |  |  | 6.62 | 6.5926 | 6.5653 | 6.5368 | 6.5 | 6.44 | 6.3747 | 6.2768 | 6.1874 | 6.14 | 5.8853 | 13.9968 | 13.7916 | 5.8063 | 5.76 | 5.7063 | 5.6295 | 5.5674 | 5.5 | 5.4253 | 5.3063 | 5.1926 | 5.1379 | 4.8316 | 12.9232 | 12.7021 | 6.4989 | 6.4179 | 6.3632 | 6.2884 | 6.2253 | 6.1589 | 6.0842 | 5.9674 | 5.86 | 5.8074 | 5.5147 | 13.6116 | 13.3937
|  | ROTHES | HT |  |  |  |  | 6.6189 | 6.5905 | 6.5589 | 6.5295 | 6.4779 | 6.4105 | 6.3326 | 6.2232 | 6.1453 | 6.0916 | 14.1789 | 13.9526 | 13.7716 | 5.8063 | 5.7737 | 5.6842 | 5.6084 | 5.5421 | 5.4642 | 5.3726 | 5.2347 | 5.14 | 5.0779 | 4.8411 | 12.9316 | 12.6884 | 6.5063 | 6.4316 | 6.3421 | 6.2674 | 6.2 | 6.1232 | 6.0316 | 5.9 | 5.8095 | 5.7495 | 5.5221 | 13.6189 | 13.3779
|  | ROTHES | HE |  |  |  |  | 6.6411 | 6.6232 | 6.6063 | 6.5874 | 6.5642 | 6.5379 | 6.5116 | 6.4495 | 6.3821 | 6.3589 | 6.2316 | 14.4758 | 14.4137 | 5.8295 | 5.8095 | 5.7916 | 5.7432 | 5.7063 | 5.6695 | 5.6 | 5.5053 | 5.4242 | 5.3968 | 5.2411 | 13.4674 | 13.3926 | 6.5495 | 6.5011 | 6.4547 | 6.4011 | 6.3642 | 6.3274 | 6.2589 | 6.1642 | 6.0832 | 6.0558 | 5.9063 | 14.1379 | 14.0663
|  | ROTHES | FB |  |  |  |  | 6.6326 | 6.6105 | 6.5895 | 6.5674 | 6.5453 | 6.5232 | 6.5 | 6.4779 | 6.4547 | 6.4316 | 6.2863 | 6.0947 | 5.9526 | 5.8242 | 5.8011 | 5.7789 | 5.7558 | 5.7326 | 5.7105 | 5.6863 | 5.6632 | 5.6021 | 5.5611 | 5.34 | 5.1179 | 4.9568 | 6.5989 | 6.5579 | 6.52 | 6.4821 | 6.4463 | 6.4116 | 6.3758 | 6.3263 | 6.26 | 6.2189 | 5.9979 | 5.7789 | 5.6242
| DUNOON | ROTHESAY | MINIMUM HEADROOM | NS 08636 64647 | NO | YES | 0 | 14.0921 | 14.0037 | 13.9237 | 13.8026 | 13.7026 | 13.5911 | 13.4679 | 13.3416 | 13.2205 | 13.13 | 12.7332 | 12.3984 | 12.1437 | 14.5347 | 14.5053 | 14.4789 | 14.4463 | 14.4084 | 14.2979 | 14.1663 | 14.0316 | 13.9032 | 13.8063 | 13.3832 | 13.0242 | 12.7505 | 14.8434 | 14.7455 | 14.6561 | 14.5203 | 14.4097 | 14.2855 | 14.1497 | 14.0097 | 13.8761 | 13.775 | 13.335 | 12.9592 | 12.6729
|  | ROTHESAY | EE |  |  |  |  | 14.0921 | 14.0037 | 13.9237 | 13.8026 | 13.7026 | 13.5911 | 13.4679 | 13.3416 | 13.2205 | 13.13 | 12.7332 | 12.3984 | 12.1437 | 14.5347 | 14.5053 | 14.4789 | 14.4474 | 14.4126 | 14.2979 | 14.1663 | 14.0316 | 13.9032 | 13.8063 | 13.3832 | 13.0242 | 12.7505 | 14.8434 | 14.7455 | 14.6561 | 14.5203 | 14.4097 | 14.2855 | 14.1497 | 14.0097 | 13.8761 | 13.775 | 13.335 | 12.9592 | 12.6729
|  | ROTHESAY | HT |  |  |  |  | 14.1195 | 14.0332 | 13.9332 | 13.8268 | 13.7268 | 13.6237 | 13.5005 | 13.3837 | 13.2732 | 13.1721 | 12.7426 | 12.4174 | 12.1858 | 14.5432 | 14.5126 | 14.4821 | 14.4463 | 14.4084 | 14.3337 | 14.2011 | 14.0779 | 13.96 | 13.8526 | 13.48 | 13.1137 | 12.8021 | 14.8739 | 14.7792 | 14.6676 | 14.5497 | 14.4382 | 14.3245 | 14.1866 | 14.0582 | 13.9361 | 13.8245 | 13.4371 | 13.0539 | 12.7287
|  | ROTHESAY | HE |  |  |  |  | 14.1689 | 14.1026 | 14.0426 | 13.9795 | 13.9237 | 13.8595 | 13.7732 | 13.6911 | 13.6037 | 13.5532 | 13.3395 | 13.1616 | 13.0321 | 14.5526 | 14.5232 | 14.5011 | 14.4726 | 14.4379 | 14.3937 | 14.3463 | 14.3158 | 14.2863 | 14.2653 | 14.0379 | 13.8474 | 13.7084 | 14.9308 | 14.8592 | 14.7918 | 14.7224 | 14.6645 | 14.5971 | 14.5034 | 14.4118 | 14.315 | 14.2592 | 14.0213 | 13.8224 | 13.6771
|  | ROTHESAY | FB |  |  |  |  | 14.1921 | 14.1574 | 14.1184 | 14.0795 | 14.0405 | 14.0016 | 13.9626 | 13.9142 | 13.85 | 13.7911 | 13.5321 | 13.2795 | 13.0963 | 14.5642 | 14.5505 | 14.5368 | 14.5211 | 14.5053 | 14.4884 | 14.4716 | 14.4537 | 14.4337 | 14.4126 | 14.2358 | 13.9642 | 13.7674 | 14.9571 | 14.9171 | 14.875 | 14.8318 | 14.7887 | 14.7466 | 14.7034 | 14.6508 | 14.5792 | 14.5129 | 14.2234 | 13.9392 | 13.7318
| THURSO | ROUSAY | MINIMUM HEADROOM | HY 43876 30573 | YES | YES | 0 | -0.20842 | -0.21053 | -0.21263 | -0.21474 | -0.21684 | -0.22421 | -0.23053 | -0.23579 | -0.24211 | -0.24737 | -2.2295 | -2.2505 | -2.2642 | -0.26737 | -0.27368 | -0.27895 | -0.28632 | -0.29263 | -0.30105 | -0.30842 | -0.31474 | -0.32211 | -0.32842 | -1.8916 | -1.9137 | -1.9284 | -0.28 | -0.28632 | -0.29158 | -0.29789 | -0.30421 | -0.30947 | -0.31579 | -0.32105 | -0.32632 | -0.33158 | -2.3326 | -2.3516 | -2.3632
|  | ROUSAY | EE |  |  |  |  | -0.20842 | -0.21053 | -0.21263 | -0.21474 | -0.21684 | -0.22421 | -0.23053 | -0.23579 | -0.24211 | -0.24737 | -2.2295 | -2.2505 | -2.2642 | -0.26737 | -0.27368 | -0.27895 | -0.28632 | -0.29263 | -0.30105 | -0.30842 | -0.31474 | -0.32211 | -0.32842 | -1.8916 | -1.9137 | -1.9284 | -0.28 | -0.28632 | -0.29158 | -0.29789 | -0.30421 | -0.30947 | -0.31579 | -0.32105 | -0.32632 | -0.33158 | -2.3326 | -2.3516 | -2.3632
|  | ROUSAY | HT |  |  |  |  | -0.20842 | -0.21053 | -0.21158 | -0.21474 | -0.21684 | -0.21895 | -0.22421 | -0.22947 | -0.23684 | -0.24421 | -1.8379 | -1.8589 | -1.8716 | -0.26632 | -0.27158 | -0.27579 | -0.28211 | -0.28737 | -0.29263 | -0.30105 | -0.30632 | -0.31579 | -0.32316 | -1.5726 | -1.5947 | -1.6137 | -0.28 | -0.28421 | -0.28737 | -0.29368 | -0.29895 | -0.30421 | -0.31053 | -0.31579 | -0.32211 | -0.32842 | -1.9337 | -1.9526 | -1.9674
|  | ROUSAY | HE |  |  |  |  | -0.20737 | -0.20947 | -0.21158 | -0.21263 | -0.21474 | -0.21789 | -0.22105 | -0.22316 | -0.22526 | -0.22526 | -1.0179 | -1.0263 | -1.0337 | -0.26211 | -0.26632 | -0.27053 | -0.27263 | -0.27684 | -0.28105 | -0.28526 | -0.28947 | -0.29368 | -0.29474 | -0.90737 | -0.91895 | -0.92842 | -0.27579 | -0.28 | -0.28316 | -0.28526 | -0.28947 | -0.29368 | -0.29789 | -0.30211 | -0.30526 | -0.30632 | -1.1095 | -1.1189 | -1.1263
|  | ROUSAY | FB |  |  |  |  | -0.20632 | -0.20737 | -0.20842 | -0.20842 | -0.20947 | -0.21053 | -0.21158 | -0.21263 | -0.21368 | -0.21474 | -0.22 | -0.23263 | -0.24211 | -0.26105 | -0.26316 | -0.26526 | -0.26737 | -0.26947 | -0.27263 | -0.27474 | -0.27684 | -0.28 | -0.28316 | -0.29579 | -0.31053 | -0.32316 | -0.27368 | -0.27579 | -0.27895 | -0.28 | -0.28211 | -0.28526 | -0.28737 | -0.28947 | -0.29263 | -0.29474 | -0.30632 | -0.31789 | -0.32632
| CRAIGIEBUCKLER | RUTHRIESTON | MINIMUM HEADROOM | NJ 92574 04060 | NO | YES | 0.38776 | 24.2705 | 24.2105 | 24.16 | 24.1011 | 24.0305 | 23.9463 | 23.8611 | 23.7905 | 23.7221 | 23.6547 | 23.4042 | 23.2484 | 23.0905 | 23.7516 | 23.7021 | 23.6642 | 23.6147 | 23.5063 | 23.3537 | 23.2063 | 23.0653 | 22.94 | 22.7768 | 22.2779 | 21.9853 | 21.4863 | 24.3789 | 24.2653 | 24.1632 | 24.0505 | 23.8916 | 23.7295 | 23.5747 | 23.4242 | 23.2916 | 23.1158 | 22.5863 | 22.2853 | 21.7484
|  | RUTHRIESTON | EE |  |  |  |  | 24.2705 | 24.2105 | 24.16 | 24.1011 | 24.0305 | 23.9463 | 23.8611 | 23.7905 | 23.7221 | 23.6547 | 23.4042 | 23.3137 | 23.1684 | 23.7516 | 23.7021 | 23.6642 | 23.6168 | 23.5063 | 23.3537 | 23.2063 | 23.0653 | 22.94 | 22.7768 | 22.2779 | 21.9884 | 21.58 | 24.3789 | 24.2653 | 24.1632 | 24.0505 | 23.8916 | 23.7295 | 23.5747 | 23.4242 | 23.2916 | 23.1158 | 22.5863 | 22.2853 | 21.8442
|  | RUTHRIESTON | HT |  |  |  |  | 24.2842 | 24.2295 | 24.1705 | 24.1074 | 24.0326 | 23.9642 | 23.8958 | 23.8221 | 23.7495 | 23.6568 | 23.4579 | 23.2484 | 23.0905 | 23.76 | 23.7158 | 23.6674 | 23.6147 | 23.5526 | 23.4326 | 23.3074 | 23.1811 | 23.0516 | 22.8432 | 22.5211 | 21.9853 | 21.4863 | 24.4116 | 24.3084 | 24.2053 | 24.0968 | 23.9505 | 23.8158 | 23.6832 | 23.5495 | 23.4126 | 23.1895 | 22.8611 | 22.2853 | 21.7484
|  | RUTHRIESTON | HE |  |  |  |  | 24.3095 | 24.2589 | 24.2189 | 24.1684 | 24.1032 | 24.0253 | 23.9432 | 23.8916 | 23.84 | 23.8021 | 23.6695 | 23.5737 | 23.4979 | 23.7768 | 23.7326 | 23.6989 | 23.6537 | 23.5979 | 23.5274 | 23.4537 | 23.4074 | 23.3611 | 23.2611 | 22.9684 | 22.7463 | 22.5274 | 24.4579 | 24.3989 | 24.3316 | 24.2547 | 24.1453 | 24.0379 | 23.9189 | 23.8389 | 23.7621 | 23.6432 | 23.3305 | 23.0916 | 22.8547
|  | RUTHRIESTON | FB |  |  |  |  | 24.3337 | 24.3084 | 24.2811 | 24.2537 | 24.2211 | 24.1895 | 24.1579 | 24.1232 | 24.0895 | 24.0495 | 23.9147 | 23.7947 | 23.7168 | 23.7979 | 23.7779 | 23.7558 | 23.7337 | 23.7084 | 23.6821 | 23.6558 | 23.6284 | 23.6 | 23.5695 | 23.2979 | 23.0189 | 22.7853 | 24.4779 | 24.46 | 24.4158 | 24.3642 | 24.3011 | 24.2421 | 24.1884 | 24.1221 | 24.06 | 23.9821 | 23.6705 | 23.3716 | 23.1179
| TAYNUILT | SALEN | MINIMUM HEADROOM | NM 57252 42849 | NO | YES | 0 | 6.2189 | 6.1842 | 6.1568 | 6.0768 | 6.04 | 5.9021 | 5.8253 | 5.7705 | 5.7095 | 5.6758 | 5.5168 | 5.3905 | 5.2947 | 6.6295 | 6.62 | 6.6116 | 6.5242 | 6.4832 | 6.3263 | 6.2411 | 6.18 | 6.1126 | 6.0747 | 5.9 | 5.7611 | 5.6568 | 6.4389 | 6.4095 | 6.3853 | 6.3211 | 6.2895 | 6.1789 | 6.1158 | 6.0705 | 6.0221 | 5.9916 | 5.86 | 5.7537 | 5.6747
|  | SALEN | EE |  |  |  |  | 6.2189 | 6.1842 | 6.1568 | 6.0768 | 6.04 | 5.9021 | 5.8253 | 5.7705 | 5.7095 | 5.6758 | 5.5168 | 5.3905 | 5.2947 | 6.6295 | 6.62 | 6.6116 | 6.5242 | 6.4832 | 6.3263 | 6.2411 | 6.18 | 6.1126 | 6.0747 | 5.9 | 5.7611 | 5.6568 | 6.4389 | 6.4095 | 6.3853 | 6.3211 | 6.2895 | 6.1789 | 6.1158 | 6.0705 | 6.0221 | 5.9916 | 5.86 | 5.7537 | 5.6747
|  | SALEN | HT |  |  |  |  | 6.2274 | 6.1968 | 6.1726 | 6.0989 | 6.0611 | 5.9558 | 5.8737 | 5.7937 | 5.72 | 5.6832 | 5.5284 | 5.4105 | 5.3295 | 6.6316 | 6.6242 | 6.6158 | 6.5474 | 6.5053 | 6.3863 | 6.2926 | 6.2011 | 6.1179 | 6.0779 | 5.9358 | 5.7989 | 5.6853 | 6.4463 | 6.4211 | 6.4 | 6.34 | 6.3084 | 6.2242 | 6.1579 | 6.0937 | 6.0337 | 6.0011 | 5.8937 | 5.7916 | 5.7053
|  | SALEN | HE |  |  |  |  | 6.2453 | 6.2189 | 6.2063 | 6.1516 | 6.1347 | 6.0589 | 5.9874 | 5.9295 | 5.8811 | 5.8642 | 5.7632 | 5.6979 | 5.6484 | 6.6347 | 6.6263 | 6.6221 | 6.6074 | 6.5895 | 6.5053 | 6.4232 | 6.3558 | 6.3032 | 6.2832 | 6.1705 | 6.0979 | 6.0442 | 6.46 | 6.4379 | 6.4274 | 6.3832 | 6.3684 | 6.3063 | 6.2474 | 6.2 | 6.1621 | 6.1474 | 6.0642 | 6.0105 | 5.9695
|  | SALEN | FB |  |  |  |  | 6.2663 | 6.2537 | 6.2432 | 6.2158 | 6.2053 | 6.1632 | 6.1284 | 6.1063 | 6.0768 | 6.0579 | 5.9642 | 5.8737 | 5.8095 | 6.6379 | 6.6358 | 6.6326 | 6.6284 | 6.6253 | 6.62 | 6.58 | 6.5547 | 6.5211 | 6.4989 | 6.3926 | 6.2916 | 6.2179 | 6.4779 | 6.4674 | 6.4579 | 6.4368 | 6.4274 | 6.3947 | 6.3663 | 6.3484 | 6.3242 | 6.3084 | 6.2316 | 6.1589 | 6.1074
| FORT WILLIAM | SALEN 2 | MINIMUM HEADROOM | NM 69002 65519 | YES | NO | 0 | 2.3989 | 2.3737 | 3.4995 | 3.4689 | 3.4374 | 3.4037 | 3.3721 | 3.3468 | 3.3205 | 3.2963 | 3.2153 | 3.13 | 3.0732 | 2.4842 | 2.4568 | 3.5795 | 3.5468 | 3.5132 | 3.4763 | 3.4437 | 3.4153 | 3.3868 | 3.3605 | 3.2995 | 3.2047 | 3.1342 | 2.4874 | 2.4779 | 3.6184 | 3.5847 | 3.55 | 3.5121 | 3.4784 | 3.4489 | 3.4195 | 3.3932 | 3.3353 | 3.2363 | 3.1647
|  | SALEN 2 | EE |  |  |  |  | 2.3989 | 2.3737 | 3.4995 | 3.4689 | 3.4374 | 3.4037 | 3.3721 | 3.3468 | 3.3205 | 3.2963 | 3.2268 | 3.1405 | 3.0795 | 2.4842 | 2.4568 | 3.5795 | 3.5468 | 3.5132 | 3.4763 | 3.4437 | 3.4153 | 3.3868 | 3.3605 | 3.2995 | 3.2047 | 3.1384 | 2.4874 | 2.4779 | 3.6184 | 3.5847 | 3.55 | 3.5121 | 3.4784 | 3.4489 | 3.4195 | 3.3932 | 3.3353 | 3.2363 | 3.1679
|  | SALEN 2 | HT |  |  |  |  | 2.4053 | 2.3832 | 3.51 | 3.4868 | 3.4542 | 3.4258 | 3.3984 | 3.37 | 3.3416 | 3.3416 | 3.2153 | 3.13 | 3.0732 | 2.4905 | 2.4674 | 3.5921 | 3.5668 | 3.5321 | 3.5016 | 3.4721 | 3.4416 | 3.4111 | 3.4258 | 3.3121 | 3.2111 | 3.1342 | 2.4874 | 2.48 | 3.6195 | 3.6058 | 3.57 | 3.5384 | 3.5079 | 3.4774 | 3.4447 | 3.4658 | 3.3489 | 3.2447 | 3.1647
|  | SALEN 2 | HE |  |  |  |  | 2.4221 | 2.4053 | 3.5437 | 3.5279 | 3.5079 | 3.4921 | 3.4732 | 3.4553 | 3.4384 | 3.4258 | 3.3995 | 3.3489 | 3.3195 | 2.5095 | 2.4916 | 3.6289 | 3.6121 | 3.5911 | 3.5742 | 3.5542 | 3.5363 | 3.5174 | 3.5037 | 3.4889 | 3.4342 | 3.4016 | 2.4916 | 2.4832 | 3.6289 | 3.6195 | 3.61 | 3.5995 | 3.5858 | 3.5753 | 3.5563 | 3.5426 | 3.5311 | 3.4742 | 3.4405
|  | SALEN 2 | FB |  |  |  |  | 2.4316 | 2.4211 | 3.5616 | 3.5511 | 3.5395 | 3.5289 | 3.5184 | 3.5079 | 3.4963 | 3.4795 | 3.4195 | 3.3626 | 3.3195 | 2.5189 | 2.5084 | 3.6468 | 3.6363 | 3.6237 | 3.6121 | 3.6005 | 3.59 | 3.5774 | 3.5584 | 3.4932 | 3.4311 | 3.3837 | 2.4958 | 2.4926 | 3.6395 | 3.6363 | 3.6332 | 3.63 | 3.6258 | 3.6216 | 3.6163 | 3.5963 | 3.5289 | 3.4647 | 3.4153
| THURSO | SANDAY | MINIMUM HEADROOM | HY 61184 35797 | YES | YES | 0 | 0.89895 | 0.89579 | 0.89158 | 0.88842 | 0.88211 | 0.87789 | 0.87158 | 0.86737 | 0.86316 | 0.85789 | -1.1179 | -1.1432 | -1.1611 | 0.78526 | 0.77263 | 0.76 | 0.74526 | 0.73158 | 0.71263 | 0.69684 | 0.68421 | 0.67053 | 0.65895 | -0.92421 | -0.96211 | -0.98947 | 0.78947 | 0.78632 | 0.78211 | 0.77895 | 0.77263 | 0.76842 | 0.76211 | 0.75789 | 0.75368 | 0.74842 | -1.2358 | -1.2747 | -1.3042
|  | SANDAY | EE |  |  |  |  | 0.89895 | 0.89579 | 0.89158 | 0.88842 | 0.88421 | 0.87789 | 0.87158 | 0.86737 | 0.86316 | 0.85895 | -1.1179 | -1.1432 | -1.1611 | 0.78526 | 0.77263 | 0.76 | 0.74526 | 0.73158 | 0.71263 | 0.69684 | 0.68421 | 0.67053 | 0.65895 | -0.92421 | -0.96211 | -0.98947 | 0.78947 | 0.78632 | 0.78211 | 0.77895 | 0.77474 | 0.76842 | 0.76211 | 0.75789 | 0.75368 | 0.74947 | -1.2358 | -1.2747 | -1.3042
|  | SANDAY | HT |  |  |  |  | 0.9 | 0.89579 | 0.89263 | 0.88842 | 0.88211 | 0.87789 | 0.87368 | 0.86842 | 0.86316 | 0.85789 | -0.73053 | -0.75579 | -0.77579 | 0.78947 | 0.77789 | 0.76737 | 0.75474 | 0.73895 | 0.72211 | 0.70842 | 0.69579 | 0.68211 | 0.66526 | -0.60737 | -0.65053 | -0.68316 | 0.79053 | 0.78632 | 0.78316 | 0.77895 | 0.77263 | 0.76842 | 0.76421 | 0.75895 | 0.75368 | 0.74842 | -0.84211 | -0.88632 | -0.92105
|  | SANDAY | HE |  |  |  |  | 0.90105 | 0.89789 | 0.89474 | 0.89053 | 0.88737 | 0.88211 | 0.87579 | 0.87263 | 0.86947 | 0.86632 | 0.11368 | 0.1 | 0.091579 | 0.79789 | 0.79053 | 0.78316 | 0.77368 | 0.76842 | 0.75579 | 0.74526 | 0.73895 | 0.73053 | 0.72211 | 0.097895 | 0.076842 | 0.063158 | 0.79158 | 0.78842 | 0.78526 | 0.78105 | 0.77789 | 0.77263 | 0.76632 | 0.76316 | 0.76 | 0.75684 | 0.018947 | -0.0031579 | -0.015789
|  | SANDAY | FB |  |  |  |  | 0.90316 | 0.90105 | 0.9 | 0.89789 | 0.89684 | 0.89474 | 0.89263 | 0.89158 | 0.88947 | 0.88737 | 0.88 | 0.87368 | 0.87053 | 0.80211 | 0.79579 | 0.79158 | 0.78632 | 0.78 | 0.77474 | 0.76842 | 0.76421 | 0.75789 | 0.75053 | 0.72316 | 0.69474 | 0.67053 | 0.79368 | 0.79158 | 0.79053 | 0.78842 | 0.78737 | 0.78526 | 0.78316 | 0.78211 | 0.78 | 0.77789 | 0.77053 | 0.76421 | 0.76105
| DUNOON | SANDBANK | MINIMUM HEADROOM | NS 15274 81386 | NO | YES | 0.19388 | 7.4632 | 7.4137 | 7.3642 | 7.3021 | 7.2463 | 7.1842 | 7.1179 | 7.0558 | 6.9968 | 6.9484 | 6.7158 | 6.54 | 6.4105 | 6.9074 | 6.8811 | 6.8263 | 6.7589 | 6.6979 | 6.6305 | 6.56 | 6.4926 | 6.4284 | 6.3716 | 6.1211 | 5.9284 | 5.7853 | 7.0168 | 6.9705 | 6.9221 | 6.8642 | 6.8105 | 6.7505 | 6.6884 | 6.6295 | 6.5726 | 6.5263 | 6.3053 | 6.1379 | 6.0147
|  | SANDBANK | EE |  |  |  |  | 7.4632 | 7.4137 | 7.3642 | 7.3021 | 7.2463 | 7.1842 | 7.1179 | 7.0558 | 6.9968 | 6.9484 | 6.7158 | 6.54 | 6.4105 | 6.9074 | 6.8811 | 6.8263 | 6.7589 | 6.6979 | 6.6305 | 6.56 | 6.4926 | 6.4284 | 6.3747 | 6.1211 | 5.9284 | 5.7853 | 7.0168 | 6.9705 | 6.9221 | 6.8642 | 6.8105 | 6.7505 | 6.6884 | 6.6295 | 6.5726 | 6.5263 | 6.3053 | 6.1379 | 6.0147
|  | SANDBANK | HT |  |  |  |  | 7.4789 | 7.4358 | 7.3895 | 7.3326 | 7.2758 | 7.2084 | 7.1474 | 7.0842 | 7.0042 | 6.9484 | 6.7168 | 6.5505 | 6.4358 | 6.9116 | 6.8947 | 6.8537 | 6.7926 | 6.7305 | 6.6558 | 6.5905 | 6.52 | 6.4316 | 6.3716 | 6.1642 | 5.9716 | 5.8074 | 7.0326 | 6.9905 | 6.9463 | 6.8926 | 6.8389 | 6.7747 | 6.7168 | 6.6558 | 6.5811 | 6.5274 | 6.3453 | 6.18 | 6.0411
|  | SANDBANK | HE |  |  |  |  | 7.5126 | 7.48 | 7.4516 | 7.4189 | 7.3874 | 7.3505 | 7.3011 | 7.2621 | 7.2221 | 7.1958 | 7.0589 | 6.9684 | 6.9053 | 6.9179 | 6.9011 | 6.8916 | 6.8758 | 6.8547 | 6.8168 | 6.7642 | 6.7221 | 6.6779 | 6.6484 | 6.4979 | 6.3979 | 6.3295 | 7.0632 | 7.0316 | 7.0053 | 6.9737 | 6.9432 | 6.9074 | 6.8589 | 6.8221 | 6.7842 | 6.7589 | 6.6295 | 6.5442 | 6.4853
|  | SANDBANK | FB |  |  |  |  | 7.5295 | 7.5095 | 7.4884 | 7.4674 | 7.4463 | 7.4242 | 7.4032 | 7.3811 | 7.3516 | 7.3221 | 7.1863 | 7.0579 | 6.9705 | 6.9253 | 6.9189 | 6.9126 | 6.9063 | 6.8989 | 6.8905 | 6.8705 | 6.8453 | 6.8126 | 6.78 | 6.6295 | 6.4874 | 6.3874 | 7.08 | 7.0611 | 7.04 | 7.0211 | 7.0011 | 6.98 | 6.96 | 6.9379 | 6.9105 | 6.8832 | 6.7558 | 6.6347 | 6.5537
| SHETLAND | SANDWICK | MINIMUM HEADROOM | HU4308625957 | YES | YES | 0 | 2.9211 | 2.8779 | 7.6 | 7.5621 | 7.5253 | 7.4832 | 7.4432 | 7.4074 | 7.3716 | 7.3389 | 7.2 | 7.1 | 7.0295 | 3.44 | 3.4042 | 7.7211 | 7.6779 | 7.6379 | 7.5916 | 7.5484 | 7.5084 | 7.4695 | 7.4337 | 7.2989 | 7.1832 | 7.0874 | 2.9221 | 2.8716 | 7.3874 | 7.3421 | 7.3011 | 7.2537 | 7.2095 | 7.1684 | 7.1284 | 7.0916 | 6.9537 | 6.8368 | 6.74
|  | SANDWICK | EE |  |  |  |  | 2.9211 | 2.8779 | 7.6 | 7.5621 | 7.5253 | 7.4832 | 7.4432 | 7.4074 | 7.3716 | 7.3389 | 7.2168 | 7.1158 | 7.0453 | 3.44 | 3.4042 | 7.7211 | 7.6779 | 7.6379 | 7.5916 | 7.5484 | 7.5084 | 7.4695 | 7.4337 | 7.2989 | 7.1832 | 7.1 | 2.9221 | 2.8716 | 7.3874 | 7.3421 | 7.3011 | 7.2537 | 7.2095 | 7.1684 | 7.1284 | 7.0916 | 6.9537 | 6.8368 | 6.7516
|  | SANDWICK | HT |  |  |  |  | 2.9326 | 2.8958 | 7.6189 | 7.5789 | 7.5379 | 7.5021 | 7.4642 | 7.4284 | 7.3905 | 7.3516 | 7.2 | 7.1 | 7.0295 | 3.4432 | 3.4253 | 7.7432 | 7.6989 | 7.6537 | 7.6147 | 7.5726 | 7.5326 | 7.4916 | 7.4495 | 7.3105 | 7.1884 | 7.0874 | 2.9358 | 2.8926 | 7.4105 | 7.3642 | 7.3179 | 7.2779 | 7.2347 | 7.1937 | 7.1526 | 7.1095 | 6.9653 | 6.8421 | 6.74
|  | SANDWICK | HE |  |  |  |  | 2.96 | 2.9305 | 7.6684 | 7.6421 | 7.6126 | 7.5821 | 7.5495 | 7.5242 | 7.4989 | 7.4842 | 7.4137 | 7.3632 | 7.3284 | 3.4474 | 3.4326 | 7.7832 | 7.7684 | 7.7411 | 7.7074 | 7.6726 | 7.6463 | 7.6189 | 7.6021 | 7.5232 | 7.4663 | 7.4263 | 2.9695 | 2.9358 | 7.4695 | 7.44 | 7.4084 | 7.3747 | 7.34 | 7.3126 | 7.2842 | 7.2674 | 7.1853 | 7.1263 | 7.0863
|  | SANDWICK | FB |  |  |  |  | 2.9758 | 2.9589 | 7.7021 | 7.6842 | 7.6663 | 7.6495 | 7.6316 | 7.6137 | 7.5947 | 7.5768 | 7.5032 | 7.4316 | 7.3821 | 3.4558 | 3.4505 | 7.8053 | 7.7989 | 7.7926 | 7.7779 | 7.7568 | 7.7379 | 7.7168 | 7.6947 | 7.6137 | 7.5326 | 7.4747 | 2.9874 | 2.9674 | 7.5074 | 7.4863 | 7.4653 | 7.4453 | 7.4242 | 7.4042 | 7.3821 | 7.36 | 7.2768 | 7.1926 | 7.1326
| SHETLAND | SCALLOWAY | MINIMUM HEADROOM | HU4139939639 | YES | YES | 0 | 0.89263 | 0.82737 | 0.74 | 7.4021 | 7.3463 | 7.2537 | 7.1853 | 7.1326 | 7.0832 | 7.0389 | 6.8611 | 6.7179 | 6.6147 | 0.86842 | 0.78947 | 0.68526 | 6.9284 | 6.8632 | 6.7547 | 6.6747 | 6.6158 | 6.56 | 6.5095 | 6.3063 | 6.1389 | 6.0189 | 0.86947 | 0.79053 | 0.68632 | 7.1295 | 7.0642 | 6.9558 | 6.8768 | 6.8179 | 6.7611 | 6.7116 | 6.5084 | 6.3411 | 6.22
|  | SCALLOWAY | EE |  |  |  |  | 0.89263 | 0.83368 | 0.74421 | 7.4053 | 7.3526 | 7.2537 | 7.1853 | 7.1326 | 7.0832 | 7.0389 | 6.8611 | 6.7179 | 6.6147 | 0.86842 | 0.79895 | 0.69053 | 6.9305 | 6.8705 | 6.7547 | 6.6747 | 6.6158 | 6.56 | 6.5095 | 6.3063 | 6.1389 | 6.0189 | 0.86947 | 0.8 | 0.69158 | 7.1316 | 7.0716 | 6.9558 | 6.8768 | 6.8179 | 6.7611 | 6.7116 | 6.5084 | 6.3411 | 6.22
|  | SCALLOWAY | HT |  |  |  |  | 0.90632 | 0.82737 | 0.74 | 7.4021 | 7.3463 | 7.2937 | 7.2421 | 7.1895 | 7.1368 | 7.0832 | 6.8716 | 6.7263 | 6.6274 | 0.88526 | 0.78947 | 0.68526 | 6.9284 | 6.8632 | 6.8042 | 6.7463 | 6.6874 | 6.6274 | 6.5674 | 6.3705 | 6.1905 | 6.0442 | 0.88632 | 0.79053 | 0.68632 | 7.1295 | 7.0642 | 7.0053 | 6.9474 | 6.8884 | 6.8284 | 6.7695 | 6.5716 | 6.3937 | 6.2463
|  | SCALLOWAY | HE |  |  |  |  | 0.94316 | 0.90526 | 0.84632 | 7.5368 | 7.4989 | 7.3758 | 7.3305 | 7.2968 | 7.2611 | 7.2389 | 7.1463 | 7.0705 | 7.0211 | 0.93053 | 0.88737 | 0.81579 | 7.0937 | 7.0526 | 6.9032 | 6.8558 | 6.8168 | 6.7779 | 6.7526 | 6.6453 | 6.5558 | 6.4979 | 0.93158 | 0.88737 | 0.81684 | 7.2947 | 7.2526 | 7.1042 | 7.0568 | 7.0179 | 6.9789 | 6.9537 | 6.8463 | 6.7568 | 6.6989
|  | SCALLOWAY | FB |  |  |  |  | 0.96632 | 0.94316 | 0.91895 | 7.6432 | 7.6189 | 7.5747 | 7.5126 | 7.4895 | 7.4642 | 7.4347 | 7.3305 | 7.2316 | 7.1568 | 0.95684 | 0.92947 | 0.90105 | 7.2168 | 7.1884 | 7.1347 | 7.06 | 7.0316 | 7.0021 | 6.9684 | 6.8474 | 6.7295 | 6.64 | 0.95684 | 0.92947 | 0.90105 | 7.4168 | 7.3884 | 7.3358 | 7.26 | 7.2326 | 7.2032 | 7.1695 | 7.0484 | 6.9316 | 6.8421
| TAYNUILT | SCAMMADALE | MINIMUM HEADROOM | NM 84207 19638 | YES | YES | 0 | 0.12105 | 0.12105 | 0.12 | 0.12 | 0.11789 | 0.11789 | 0.11684 | 0.11684 | 0.11579 | 0.11474 | 0.11263 | 0.11053 | 0.10842 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.11053 | 0.10947 | 0.10947 | 0.10947 | 0.10842 | 0.10632 | 0.10421 | 0.10211 | 0.11474 | 0.11368 | 0.11368 | 0.11368 | 0.11158 | 0.11158 | 0.11053 | 0.10947 | 0.10842 | 0.10737 | 0.10421 | 0.10211 | 0.1
|  | SCAMMADALE | EE |  |  |  |  | 0.12105 | 0.12105 | 0.12 | 0.12 | 0.11789 | 0.11789 | 0.11789 | 0.11684 | 0.11579 | 0.11579 | 0.11263 | 0.11053 | 0.10842 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.11053 | 0.11053 | 0.10947 | 0.10947 | 0.10947 | 0.10632 | 0.10421 | 0.10316 | 0.11474 | 0.11368 | 0.11368 | 0.11368 | 0.11158 | 0.11158 | 0.11053 | 0.10947 | 0.10842 | 0.10842 | 0.10421 | 0.10211 | 0.10105
|  | SCAMMADALE | HT |  |  |  |  | 0.12211 | 0.12105 | 0.12105 | 0.12 | 0.11895 | 0.11789 | 0.11684 | 0.11684 | 0.11684 | 0.11474 | 0.11263 | 0.11053 | 0.10842 | 0.11263 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.11053 | 0.10947 | 0.10947 | 0.10947 | 0.10842 | 0.10737 | 0.10421 | 0.10211 | 0.11579 | 0.11368 | 0.11368 | 0.11368 | 0.11263 | 0.11158 | 0.11053 | 0.10947 | 0.10947 | 0.10737 | 0.10526 | 0.10211 | 0.1
|  | SCAMMADALE | HE |  |  |  |  | 0.12211 | 0.12211 | 0.12105 | 0.12105 | 0.12105 | 0.12 | 0.11895 | 0.11789 | 0.11895 | 0.11684 | 0.11684 | 0.11579 | 0.11474 | 0.11263 | 0.11263 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.10947 | 0.10947 | 0.11053 | 0.10842 | 0.10947 | 0.10842 | 0.10842 | 0.11579 | 0.11579 | 0.11474 | 0.11474 | 0.11368 | 0.11263 | 0.11158 | 0.11158 | 0.11263 | 0.11053 | 0.11053 | 0.10842 | 0.10737
|  | SCAMMADALE | FB |  |  |  |  | 0.12211 | 0.12211 | 0.12211 | 0.12105 | 0.12105 | 0.12105 | 0.12105 | 0.12105 | 0.12 | 0.12 | 0.11789 | 0.11684 | 0.11579 | 0.11263 | 0.11263 | 0.11263 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.10947 | 0.10947 | 0.11579 | 0.11579 | 0.11579 | 0.11474 | 0.11474 | 0.11368 | 0.11368 | 0.11368 | 0.11368 | 0.11368 | 0.11158 | 0.10947 | 0.10842
| ABERNETHY | SCONE | MINIMUM HEADROOM | NO 14401 25495 | NO | YES | 1.6143 | 13.8679 | 13.7258 | 13.5795 | 13.4079 | 13.2384 | 12.4205 | 12.2184 | 12.0468 | 11.8753 | 11.7153 | 10.9047 | 10.6205 | 10.4237 | 13.7558 | 13.5463 | 13.3242 | 13.0621 | 12.8168 | 11.5 | 11.2074 | 10.9516 | 10.6979 | 10.4611 | 9.5095 | 8.9653 | 8.6168 | 14.1245 | 13.9118 | 13.6866 | 13.4213 | 13.1718 | 11.8318 | 11.535 | 11.2771 | 11.0192 | 10.7792 | 9.8087 | 9.2529 | 8.8961
|  | SCONE | EE |  |  |  |  | 13.8679 | 13.7258 | 13.5795 | 13.4079 | 13.2426 | 12.4205 | 12.2184 | 12.0468 | 11.8753 | 11.7184 | 11.0858 | 10.7437 | 10.5458 | 13.7558 | 13.5463 | 13.3242 | 13.0621 | 12.8168 | 11.5 | 11.2074 | 10.9516 | 10.6979 | 10.4611 | 9.5095 | 9.0126 | 8.7274 | 14.1245 | 13.9118 | 13.6866 | 13.4213 | 13.1718 | 11.8318 | 11.535 | 11.2771 | 11.0192 | 10.7792 | 9.8087 | 9.2982 | 9.0066
|  | SCONE | HT |  |  |  |  | 13.8889 | 13.7511 | 13.6005 | 13.4279 | 13.2384 | 12.4426 | 12.2647 | 12.0868 | 11.9026 | 11.7153 | 10.9047 | 10.6205 | 10.4237 | 13.7884 | 13.5874 | 13.3642 | 13.1084 | 12.8284 | 11.5495 | 11.2895 | 11.0305 | 10.7632 | 10.4916 | 9.5116 | 8.9653 | 8.6168 | 14.1582 | 13.9529 | 13.7276 | 13.4676 | 13.1845 | 11.8834 | 11.6203 | 11.3571 | 11.0866 | 10.8108 | 9.8118 | 9.2529 | 8.8961
|  | SCONE | HE |  |  |  |  | 13.9426 | 13.8279 | 13.7079 | 13.5637 | 13.4195 | 12.6226 | 12.4426 | 12.2974 | 12.1521 | 12.0258 | 11.5216 | 11.2921 | 11.1784 | 13.8663 | 13.6989 | 13.5168 | 13.3011 | 13.0895 | 11.8137 | 11.5526 | 11.3347 | 11.1158 | 10.9189 | 10.1316 | 9.7853 | 9.6179 | 14.2371 | 14.0676 | 13.8824 | 13.6634 | 13.4487 | 12.1508 | 11.8866 | 11.6666 | 11.4445 | 11.2434 | 10.4434 | 10.0887 | 9.9182
|  | SCONE | FB |  |  |  |  | 13.9953 | 13.9374 | 13.8742 | 13.8058 | 13.7405 | 13.6584 | 13.5711 | 13.4826 | 13.39 | 13.2911 | 12.9016 | 12.6689 | 12.5374 | 13.9411 | 13.8547 | 13.7589 | 13.6558 | 13.5589 | 13.4347 | 13.3 | 13.1653 | 13.0242 | 12.8737 | 12.2789 | 11.9347 | 11.7358 | 14.3129 | 14.2245 | 14.1276 | 14.0234 | 13.9245 | 13.7982 | 13.6613 | 13.5255 | 13.3813 | 13.2287 | 12.6245 | 12.2761 | 12.0739
| THURSO | SHAPINSAY | MINIMUM HEADROOM | HY 48313 17148 | YES | YES | 0 | 0.98947 | 0.98632 | 0.98105 | 0.97368 | 0.96947 | 0.96316 | 0.95684 | 0.95263 | 0.94632 | 0.94211 | -1.0189 | -1.0316 | -1.04 | 0.96947 | 0.96526 | 0.95895 | 0.95053 | 0.94421 | 0.93684 | 0.92947 | 0.92316 | 0.91684 | 0.91053 | -0.67789 | -0.69895 | -0.71158 | 0.97684 | 0.97263 | 0.96737 | 0.96 | 0.95579 | 0.94947 | 0.94211 | 0.93789 | 0.93158 | 0.92632 | -1.0684 | -1.0863 | -1.0979
|  | SHAPINSAY | EE |  |  |  |  | 0.98947 | 0.98632 | 0.98105 | 0.97368 | 0.96947 | 0.96316 | 0.95684 | 0.95263 | 0.94632 | 0.94211 | -1.0189 | -1.0316 | -1.04 | 0.96947 | 0.96526 | 0.95895 | 0.95053 | 0.94421 | 0.93684 | 0.92947 | 0.92316 | 0.91684 | 0.91053 | -0.67789 | -0.69895 | -0.71158 | 0.97684 | 0.97263 | 0.96737 | 0.96 | 0.95579 | 0.94947 | 0.94211 | 0.93789 | 0.93158 | 0.92632 | -1.0684 | -1.0863 | -1.0979
|  | SHAPINSAY | HT |  |  |  |  | 0.99158 | 0.98737 | 0.98211 | 0.97789 | 0.97263 | 0.96737 | 0.96211 | 0.95684 | 0.95158 | 0.94632 | -0.62632 | -0.63895 | -0.64632 | 0.97263 | 0.96737 | 0.96105 | 0.95579 | 0.94842 | 0.94211 | 0.93684 | 0.92947 | 0.92316 | 0.91579 | -0.36 | -0.38211 | -0.39579 | 0.97895 | 0.97368 | 0.96947 | 0.96421 | 0.95895 | 0.95368 | 0.94842 | 0.94316 | 0.93684 | 0.93158 | -0.66947 | -0.68947 | -0.70211
|  | SHAPINSAY | HE |  |  |  |  | 0.99474 | 0.99158 | 0.98842 | 0.98632 | 0.98211 | 0.98 | 0.97474 | 0.97263 | 0.96842 | 0.96632 | 0.18737 | 0.18105 | 0.17684 | 0.97684 | 0.97263 | 0.96842 | 0.96632 | 0.96211 | 0.95895 | 0.95368 | 0.95053 | 0.94632 | 0.94211 | 0.30421 | 0.29474 | 0.28737 | 0.98211 | 0.97789 | 0.97474 | 0.97263 | 0.96947 | 0.96632 | 0.96211 | 0.95895 | 0.95474 | 0.95158 | 0.15263 | 0.14316 | 0.13684
|  | SHAPINSAY | FB |  |  |  |  | 0.99684 | 0.99368 | 0.99263 | 0.99053 | 0.98842 | 0.98526 | 0.98421 | 0.98211 | 0.98 | 0.97684 | 0.96632 | 0.95579 | 0.94632 | 0.97895 | 0.97579 | 0.97368 | 0.97053 | 0.96842 | 0.96526 | 0.96316 | 0.96 | 0.95789 | 0.95368 | 0.94 | 0.92632 | 0.91474 | 0.98316 | 0.98105 | 0.98 | 0.97684 | 0.97474 | 0.97263 | 0.97053 | 0.96842 | 0.96632 | 0.96316 | 0.95263 | 0.94105 | 0.92947
| BROADFORD | SHIELDAIG | MINIMUM HEADROOM | NG 81637 52250 | YES | YES | 0 | -1.4811 | -1.4937 | -1.5084 | -1.5221 | -1.5368 | -1.5526 | -1.5663 | -1.58 | -1.5947 | -1.6095 | -1.6811 | -1.7505 | -1.8074 | -1.36 | -1.3726 | -1.3874 | -1.4011 | -1.4168 | -1.4326 | -1.4484 | -1.4621 | -1.4779 | -1.4926 | -1.5526 | -1.6221 | -1.6937 | -1.5021 | -1.5158 | -1.5305 | -1.5442 | -1.5589 | -1.5758 | -1.5905 | -1.6042 | -1.62 | -1.6347 | -1.6958 | -1.7653 | -1.8379
|  | SHIELDAIG | EE |  |  |  |  | 0.95789 | 0.91368 | 0.86947 | 0.82316 | 0.77579 | 0.73368 | 0.69053 | 0.64737 | 0.60211 | 0.55684 | 0.39895 | 0.22842 | 0.055789 | 0.95684 | 0.91579 | 0.87263 | 0.82737 | 0.78 | 0.73895 | 0.69579 | 0.65368 | 0.61053 | 0.56632 | 0.41053 | 0.24421 | 0.076842 | 0.95368 | 0.90947 | 0.86632 | 0.81789 | 0.76947 | 0.72632 | 0.68105 | 0.63789 | 0.59158 | 0.54526 | 0.38421 | 0.20947 | 0.034737
|  | SHIELDAIG | HT |  |  |  |  | -1.4811 | -1.4937 | -1.5084 | -1.5221 | -1.5368 | -1.5526 | -1.5663 | -1.58 | -1.5947 | -1.6095 | -1.6811 | -1.7505 | -1.8074 | -1.36 | -1.3726 | -1.3874 | -1.4011 | -1.4168 | -1.4326 | -1.4484 | -1.4621 | -1.4779 | -1.4926 | -1.5526 | -1.6221 | -1.6937 | -1.5021 | -1.5158 | -1.5305 | -1.5442 | -1.5589 | -1.5758 | -1.5905 | -1.6042 | -1.62 | -1.6347 | -1.6958 | -1.7653 | -1.8379
|  | SHIELDAIG | HE |  |  |  |  | -1.48 | -1.4937 | -1.5074 | -1.5211 | -1.5358 | -1.5505 | -1.5653 | -1.5779 | -1.5916 | -1.6053 | -1.6579 | -1.7263 | -1.7937 | -1.3579 | -1.3716 | -1.3853 | -1.3989 | -1.4137 | -1.4274 | -1.4421 | -1.4547 | -1.4684 | -1.4821 | -1.5358 | -1.6032 | -1.6684 | -1.5011 | -1.5158 | -1.5295 | -1.5432 | -1.5568 | -1.5716 | -1.5874 | -1.6011 | -1.6147 | -1.6284 | -1.6832 | -1.7526 | -1.82
|  | SHIELDAIG | FB |  |  |  |  | -1.4705 | -1.4737 | -1.4779 | -1.4811 | -1.4842 | -1.4884 | -1.4916 | -1.4958 | -1.4979 | -1.5011 | -1.5137 | -1.5263 | -1.5368 | -1.3495 | -1.3526 | -1.3558 | -1.36 | -1.3632 | -1.3684 | -1.3705 | -1.3747 | -1.3779 | -1.3832 | -1.3979 | -1.4126 | -1.4253 | -1.4916 | -1.4947 | -1.4989 | -1.5021 | -1.5063 | -1.5105 | -1.5126 | -1.5168 | -1.52 | -1.5232 | -1.5379 | -1.5505 | -1.5632
| SHIN | SHIN | MINIMUM HEADROOM | NH 57246 97463 | YES | NO | 0 | 2.1326 | 1.6379 | 1.1147 | 0.57684 | 0.025263 | -0.46105 | -0.96 | -1.4684 | -1.9884 | -2.5232 | -4.3589 | -6.3832 | -8.4389 | 2.0916 | 1.6053 | 1.1021 | 0.58842 | 0.06 | -0.40526 | -0.88 | -1.3663 | -1.8621 | -2.3716 | -4.1221 | -6.0516 | -8.0095 | 2.0442 | 1.5589 | 1.0337 | 0.49368 | -0.058947 | -0.55158 | -1.0537 | -1.5663 | -2.0916 | -2.6305 | -4.4832 | -6.5253 | -8.5979
|  | SHIN | EE |  |  |  |  | 2.1326 | 1.6379 | 1.1147 | 0.57684 | 0.025263 | -0.46105 | -0.96 | -1.4684 | -1.9884 | -2.5232 | -4.3589 | -6.3832 | -8.4389 | 2.0916 | 1.6053 | 1.1021 | 0.58842 | 0.06 | -0.40526 | -0.88 | -1.3663 | -1.8621 | -2.3716 | -4.1221 | -6.0516 | -8.0095 | 2.0442 | 1.5589 | 1.0337 | 0.49368 | -0.058947 | -0.55158 | -1.0537 | -1.5663 | -2.0916 | -2.6305 | -4.4832 | -6.5253 | -8.5979
|  | SHIN | HT |  |  |  |  | 2.4474 | 2.3147 | 2.1716 | 2.0232 | 1.8747 | 1.7242 | 1.5758 | 1.4242 | 1.2705 | 1.1147 | 0.33789 | -0.45368 | -1.1011 | 2.4147 | 2.2726 | 2.1274 | 1.9821 | 1.8358 | 1.6874 | 1.54 | 1.3916 | 1.2432 | 1.0926 | 0.49579 | -0.25895 | -1.0316 | 2.3695 | 2.2242 | 2.0789 | 1.9337 | 1.7863 | 1.64 | 1.4905 | 1.3368 | 1.1821 | 1.0263 | 0.40105 | -0.38947 | -1.2011
|  | SHIN | HE |  |  |  |  | 2.4484 | 2.3158 | 2.1716 | 2.0242 | 1.8789 | 1.7316 | 1.5768 | 1.4263 | 1.2747 | 1.1189 | 0.50526 | -0.27368 | -1.0768 | 2.4179 | 2.2747 | 2.1305 | 1.9842 | 1.8411 | 1.6968 | 1.5442 | 1.3989 | 1.2537 | 1.1053 | 0.51684 | -0.22947 | -0.99579 | 2.3705 | 2.2274 | 2.0821 | 1.9379 | 1.7968 | 1.6516 | 1.4968 | 1.3453 | 1.1926 | 1.0368 | 0.42 | -0.36211 | -1.1726
|  | SHIN | FB |  |  |  |  | 2.5337 | 2.5053 | 2.4768 | 2.4453 | 2.4147 | 2.3853 | 2.3568 | 2.3274 | 2.2958 | 2.2674 | 2.1537 | 2.0253 | 1.9105 | 2.4895 | 2.4705 | 2.4432 | 2.4137 | 2.3832 | 2.3495 | 2.3168 | 2.2842 | 2.2537 | 2.2232 | 2.1074 | 1.9789 | 1.8642 | 2.4737 | 2.4389 | 2.4042 | 2.3684 | 2.3337 | 2.3 | 2.2663 | 2.2347 | 2.2032 | 2.1716 | 2.0547 | 1.9253 | 1.8095
| FORT WILLIAM | SHONA BEG | MINIMUM HEADROOM | NM 67173 74363 | YES | NO | 0 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.1 | 0.1
|  | SHONA BEG | EE |  |  |  |  | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.1 | 0.1
|  | SHONA BEG | HT |  |  |  |  | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.1 | 0.1
|  | SHONA BEG | HE |  |  |  |  | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211
|  | SHONA BEG | FB |  |  |  |  | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10211 | 0.10211 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10211 | 0.10211
| KINTORE | SKENE | MINIMUM HEADROOM | NJ 82203 06495 | NO | YES | 0.041837 | 33.6263 | 33.5663 | 33.5105 | 33.4411 | 33.3368 | 33.1589 | 32.98 | 32.8221 | 32.6684 | 32.5242 | 31.0095 | 30.4116 | 29.9811 | 32.2958 | 32.2337 | 32.02 | 31.8284 | 31.6389 | 31.44 | 31.2411 | 31.0632 | 30.8895 | 30.7221 | 29.3579 | 28.7126 | 28.0726 | 29.7432 | 29.6442 | 29.5516 | 29.46 | 29.3589 | 29.2411 | 29.1211 | 29.02 | 28.9211 | 28.8295 | 27.5832 | 27.32 | 27.1221
|  | SKENE | EE |  |  |  |  | 33.6263 | 33.5663 | 33.5126 | 33.4547 | 33.3368 | 33.1589 | 32.98 | 32.8221 | 32.6684 | 32.5242 | 31.0095 | 30.4811 | 30.0495 | 32.2958 | 32.2337 | 32.02 | 31.8284 | 31.6389 | 31.44 | 31.2411 | 31.0632 | 30.8895 | 30.7221 | 29.3579 | 28.7358 | 28.2211 | 29.7432 | 29.6442 | 29.5516 | 29.46 | 29.3589 | 29.2411 | 29.1211 | 29.02 | 28.9211 | 28.8411 | 27.5832 | 27.32 | 27.1221
|  | SKENE | HT |  |  |  |  | 33.6326 | 33.5747 | 33.5105 | 33.4411 | 33.3621 | 33.2263 | 33.0621 | 32.8968 | 32.7305 | 32.5589 | 31.02 | 30.4116 | 29.9811 | 32.3021 | 32.2442 | 32.0905 | 31.9116 | 31.7063 | 31.5253 | 31.34 | 31.1547 | 30.9684 | 30.7747 | 29.4832 | 28.7126 | 28.0726 | 29.76 | 29.6674 | 29.5674 | 29.4705 | 29.36 | 29.2589 | 29.1547 | 29.0453 | 28.9368 | 28.8295 | 27.7295 | 27.4105 | 27.1411
|  | SKENE | HE |  |  |  |  | 33.6537 | 33.5968 | 33.5526 | 33.4937 | 33.4263 | 33.34 | 33.2495 | 33.1905 | 33.1316 | 33.1053 | 32.4147 | 32.1453 | 31.8832 | 32.3232 | 32.2663 | 32.2221 | 32.1632 | 32.0526 | 31.9116 | 31.7684 | 31.6442 | 31.5232 | 31.4179 | 30.7684 | 30.4505 | 30.1347 | 29.8063 | 29.7274 | 29.6589 | 29.5768 | 29.4947 | 29.3947 | 29.2905 | 29.2158 | 29.1411 | 29.1 | 28.5642 | 28.4326 | 28.3232
|  | SKENE | FB |  |  |  |  | 33.6937 | 33.6758 | 33.6558 | 33.6358 | 33.6137 | 33.5905 | 33.5663 | 33.5411 | 33.5168 | 33.4895 | 33.3895 | 33.2768 | 33.0263 | 32.3632 | 32.3453 | 32.3253 | 32.3053 | 32.2832 | 32.26 | 32.2358 | 32.2105 | 32.1863 | 32.1589 | 31.9253 | 31.5832 | 31.2811 | 29.9337 | 29.9 | 29.8642 | 29.8274 | 29.7905 | 29.7547 | 29.7168 | 29.6789 | 29.64 | 29.5937 | 29.4347 | 29.2874 | 29.1821
| BROADFORD | SKULAMUS | MINIMUM HEADROOM | NG 65881 22438 | YES | YES | 0 | 1.2874 | 6.5337 | 6.4726 | 6.3105 | 6.2621 | 5.0368 | 3.5947 | 1.8579 | 0.48632 | -0.12211 | -1.4779 | -1.6253 | -1.7295 | 0.64526 | 5.8853 | 5.8137 | 5.6263 | 5.5716 | 4.1326 | 2.4379 | 0.39474 | -1.2168 | -1.9295 | -3.4695 | -3.6537 | -3.7979 | 0.97579 | 6.2589 | 6.2442 | 6.2179 | 6.1968 | 4.7947 | 3.1053 | 1.0684 | -0.53895 | -1.2495 | -2.7842 | -2.9684 | -3.1126
|  | SKULAMUS | EE |  |  |  |  | 1.2874 | 6.5337 | 6.4726 | 6.3105 | 6.2621 | 6.2042 | 6.1063 | 4.9095 | 3.4505 | 1.7253 | -1.1632 | -1.5989 | -1.7116 | 0.64526 | 5.8853 | 5.8137 | 5.6263 | 5.5716 | 5.5084 | 5.3968 | 3.9895 | 2.2747 | 0.24421 | -3.1474 | -3.6537 | -3.7832 | 0.97579 | 6.2589 | 6.2442 | 6.2189 | 6.2011 | 6.1663 | 6.0547 | 4.6516 | 2.9421 | 0.91789 | -2.4642 | -2.9684 | -3.0979
|  | SKULAMUS | HT |  |  |  |  | 1.2989 | 6.5505 | 6.4916 | 6.3368 | 6.2842 | 5.0368 | 3.5947 | 1.8579 | 0.48632 | -0.12211 | -1.4779 | -1.6253 | -1.7295 | 0.65895 | 5.9042 | 5.8368 | 5.6579 | 5.5989 | 4.1326 | 2.4379 | 0.39474 | -1.2168 | -1.9295 | -3.4695 | -3.6484 | -3.7979 | 0.97789 | 6.2621 | 6.2442 | 6.2179 | 6.1968 | 4.7947 | 3.1053 | 1.0684 | -0.53895 | -1.2495 | -2.7842 | -2.9632 | -3.1126
|  | SKULAMUS | HE |  |  |  |  | 1.3274 | 6.5895 | 6.5432 | 6.4074 | 6.3758 | 6.3274 | 6.2516 | 4.9474 | 3.3463 | 1.3916 | -0.88316 | -1.2579 | -1.32 | 0.69158 | 5.9484 | 5.8968 | 5.7379 | 5.7042 | 5.6505 | 5.5663 | 4.0305 | 2.1474 | -0.15474 | -2.8295 | -3.2663 | -3.3389 | 0.98421 | 6.2705 | 6.2579 | 6.2368 | 6.2189 | 6.1979 | 6.1726 | 4.6937 | 2.8158 | 0.52105 | -2.1463 | -2.5821 | -2.6537
|  | SKULAMUS | FB |  |  |  |  | 1.3474 | 6.6263 | 6.6011 | 6.4874 | 6.4674 | 6.4474 | 6.4053 | 6.3621 | 5.7979 | 5.1042 | 2.1242 | 1.6568 | 1.5779 | 0.71368 | 5.9895 | 5.96 | 5.8274 | 5.8053 | 5.7832 | 5.7337 | 5.6842 | 5.0211 | 4.2042 | 0.69895 | 0.15263 | 0.061053 | 0.99368 | 6.2874 | 6.2821 | 6.2695 | 6.2621 | 6.2547 | 6.2463 | 6.2379 | 5.6811 | 4.8663 | 1.3716 | 0.82632 | 0.73579
| WOODHILL | SPRINGHILL | MINIMUM HEADROOM | NJ 89850 06421 | NO | NO | 0.14796 | 24.9942 | 42.4253 | 42.2274 | 41.9158 | 41.5632 | 41.2084 | 40.7389 | 40.0884 | 39.2947 | 38.8505 | 35.3768 | 33.9684 | 33.2653 | 23.5232 | 40.9042 | 40.8832 | 40.7842 | 40.6211 | 40.3474 | 39.8337 | 39.0905 | 38.1684 | 37.6632 | 34.3958 | 32.1926 | 31.1832 | 19.1587 | 36.8368 | 36.7442 | 36.4568 | 36.1316 | 35.7989 | 35.3695 | 34.7758 | 34.0547 | 33.6442 | 31.1 | 29.3779 | 28.5579
|  | SPRINGHILL | EE |  |  |  |  | 24.9942 | 42.4253 | 42.2274 | 41.9158 | 41.5632 | 41.2084 | 40.86 | 40.3958 | 39.9116 | 39.5432 | 37.0326 | 34.1705 | 33.4716 | 23.5232 | 40.9042 | 40.8832 | 40.7842 | 40.6211 | 40.3474 | 39.9726 | 39.4621 | 38.9063 | 38.4842 | 35.5632 | 32.2021 | 31.3989 | 19.1587 | 36.8368 | 36.7442 | 36.4568 | 36.1316 | 35.7989 | 35.4726 | 35.0463 | 34.6032 | 34.2653 | 31.9832 | 29.3989 | 28.7579
|  | SPRINGHILL | HT |  |  |  |  | 25.07 | 42.6105 | 42.3284 | 42.0305 | 41.6432 | 41.3316 | 40.7389 | 40.0884 | 39.2947 | 38.8505 | 35.3768 | 33.9684 | 33.2653 | 23.5421 | 40.9874 | 40.8895 | 40.7853 | 40.6263 | 40.4674 | 39.8337 | 39.0905 | 38.1684 | 37.6632 | 34.3958 | 32.1926 | 31.1832 | 19.2282 | 37.0947 | 36.8337 | 36.5579 | 36.2011 | 35.9105 | 35.3695 | 34.7758 | 34.0547 | 33.6442 | 31.1 | 29.3779 | 28.5579
|  | SPRINGHILL | HE |  |  |  |  | 25.2321 | 42.7495 | 42.6379 | 42.4105 | 42.1168 | 41.7411 | 41.4137 | 41.0032 | 40.5253 | 40.2632 | 37.8979 | 35.7442 | 35.3663 | 23.5779 | 40.9705 | 40.9611 | 40.8716 | 40.7632 | 40.5337 | 40.3495 | 40.1032 | 39.5758 | 39.2789 | 36.4968 | 33.9537 | 33.52 | 19.3755 | 37.1326 | 37.1168 | 36.9042 | 36.6316 | 36.1926 | 35.8853 | 35.5105 | 35.0747 | 34.8358 | 32.7042 | 30.7674 | 30.4221
|  | SPRINGHILL | FB |  |  |  |  | 25.2974 | 42.9421 | 42.8074 | 42.6695 | 42.5105 | 42.3505 | 42.1989 | 42.0179 | 41.7916 | 41.5758 | 40.4168 | 38.0979 | 37.6947 | 23.62 | 41.0632 | 41.0221 | 40.9789 | 40.9305 | 40.8821 | 40.8316 | 40.7579 | 40.6674 | 40.5737 | 39.4105 | 36.6789 | 36.2126 | 19.4755 | 37.3137 | 37.1895 | 37.0621 | 36.9158 | 36.7684 | 36.6284 | 36.4611 | 36.2547 | 36.0558 | 35.0011 | 32.9147 | 32.5453
| BRIDGE OF DUN | ST CYRUS | MINIMUM HEADROOM | NO 74889 65577 | NO | YES | 0.013265 | 3.1495 | 3.0263 | 2.9042 | 2.7579 | 2.6947 | 2.62 | 2.5811 | 2.5421 | 2.5084 | 2.4747 | 0.68737 | -2.8632 | -2.9558 | 2.8516 | 2.7126 | 2.5737 | 2.4084 | 2.3379 | 2.2558 | 2.2126 | 2.1705 | 2.1337 | 2.0968 | 1.4368 | -2.2632 | -2.3653 | 2.8126 | 2.7274 | 2.5958 | 2.4379 | 2.3705 | 2.2916 | 2.2495 | 2.2095 | 2.1737 | 2.1379 | 1.3895 | -3.2116 | -3.3147
|  | ST CYRUS | EE |  |  |  |  | 3.1495 | 3.0263 | 2.9042 | 2.7579 | 2.6947 | 2.62 | 2.5811 | 2.5421 | 2.5084 | 2.4747 | 1.7126 | -2.8632 | -2.9558 | 2.8516 | 2.7126 | 2.5737 | 2.4084 | 2.3379 | 2.2558 | 2.2126 | 2.1705 | 2.1337 | 2.0968 | 1.4368 | -2.2632 | -2.3653 | 2.8126 | 2.7274 | 2.5958 | 2.4379 | 2.3705 | 2.2916 | 2.2495 | 2.2095 | 2.1737 | 2.1379 | 1.3895 | -3.2116 | -3.3147
|  | ST CYRUS | HT |  |  |  |  | 3.1568 | 3.0474 | 2.9211 | 2.78 | 2.7063 | 2.64 | 2.6 | 2.5621 | 2.5221 | 2.4832 | 0.68737 | -1.8895 | -1.9884 | 2.86 | 2.7368 | 2.5937 | 2.4326 | 2.3516 | 2.2779 | 2.2347 | 2.1926 | 2.1505 | 2.1074 | 1.5442 | -1.4716 | -1.6095 | 2.8179 | 2.7505 | 2.6137 | 2.4611 | 2.3832 | 2.3126 | 2.2716 | 2.2305 | 2.1895 | 2.1484 | 1.5137 | -2.1884 | -2.3263
|  | ST CYRUS | HE |  |  |  |  | 3.1768 | 3.0811 | 2.9737 | 2.8421 | 2.7937 | 2.7337 | 2.7084 | 2.6842 | 2.6632 | 2.6411 | 2.3147 | 0.48316 | 0.42947 | 2.8821 | 2.7747 | 2.6516 | 2.5032 | 2.4484 | 2.3832 | 2.3568 | 2.3305 | 2.3074 | 2.2842 | 1.9947 | 0.49368 | 0.43368 | 2.8316 | 2.7716 | 2.6695 | 2.5284 | 2.4758 | 2.4137 | 2.3874 | 2.3621 | 2.34 | 2.3168 | 1.9937 | 0.23158 | 0.17158
|  | ST CYRUS | FB |  |  |  |  | 3.2474 | 3.2095 | 3.1589 | 3.1158 | 3.0716 | 3.0284 | 3.0063 | 2.9874 | 2.9705 | 2.9484 | 2.8737 | 2.7989 | 2.7379 | 2.9611 | 2.9189 | 2.8621 | 2.8126 | 2.7632 | 2.7147 | 2.6905 | 2.6684 | 2.6505 | 2.6263 | 2.5442 | 2.4621 | 2.3926 | 2.8737 | 2.8505 | 2.82 | 2.7926 | 2.7653 | 2.7295 | 2.7063 | 2.6853 | 2.6674 | 2.6453 | 2.5653 | 2.4863 | 2.42
| ST FERGUS GAS | ST FERGUS GAS TERM | MINIMUM HEADROOM | NK 0916 5377 | NO | YES | 0 | 20.8211 | 20.8116 | 20.8042 | 20.7947 | 20.7821 | 20.7705 | 20.7568 | 20.7453 | 20.7337 | 20.7211 | 20.6189 | 18.2284 | 18.1863 | 16.3389 | 16.3053 | 16.2705 | 16.2263 | 16.1979 | 16.1421 | 16.0905 | 16.0211 | 15.9421 | 15.9105 | 15.7811 | 13.7874 | 13.7442 | 13.7758 | 13.7495 | 13.7221 | 13.6916 | 13.6716 | 13.6358 | 13.6042 | 13.5632 | 13.5168 | 13.4947 | 13.4095 | 10.9905 | 10.9642
|  | ST FERGUS GAS TERM | EE |  |  |  |  | 20.8211 | 20.8116 | 20.8042 | 20.7958 | 20.7853 | 20.7705 | 20.7568 | 20.7453 | 20.7337 | 20.7242 | 20.6642 | 20.5684 | 20.4979 | 16.3389 | 16.3053 | 16.2705 | 16.2263 | 16.1979 | 16.1421 | 16.0979 | 16.0474 | 15.9937 | 15.9621 | 15.7979 | 15.7 | 15.6284 | 13.7758 | 13.7495 | 13.7221 | 13.6916 | 13.6716 | 13.6358 | 13.6074 | 13.5758 | 13.5432 | 13.5221 | 13.4211 | 13.3589 | 13.3147
|  | ST FERGUS GAS TERM | HT |  |  |  |  | 20.8221 | 20.8137 | 20.8042 | 20.7947 | 20.7821 | 20.7705 | 20.7589 | 20.7463 | 20.7337 | 20.7211 | 20.6189 | 20.5168 | 20.4411 | 16.3442 | 16.3116 | 16.2758 | 16.2337 | 16.2042 | 16.1579 | 16.0905 | 16.0211 | 15.9421 | 15.9105 | 15.7811 | 15.6674 | 15.5705 | 13.78 | 13.7547 | 13.7263 | 13.6947 | 13.6726 | 13.6442 | 13.6042 | 13.5632 | 13.5168 | 13.4947 | 13.4095 | 13.3368 | 13.2768
|  | ST FERGUS GAS TERM | HE |  |  |  |  | 20.8263 | 20.8189 | 20.8126 | 20.8042 | 20.7937 | 20.7811 | 20.7695 | 20.7589 | 20.7505 | 20.7453 | 20.7263 | 18.2284 | 18.1863 | 16.3579 | 16.3316 | 16.3042 | 16.2716 | 16.2547 | 16.2232 | 16.1863 | 16.1337 | 16.0758 | 16.0579 | 15.9379 | 13.7874 | 13.7442 | 13.7916 | 13.7705 | 13.7484 | 13.7232 | 13.7074 | 13.6821 | 13.6579 | 13.6263 | 13.5926 | 13.5811 | 13.5105 | 10.9905 | 10.9642
|  | ST FERGUS GAS TERM | FB |  |  |  |  | 20.8295 | 20.8274 | 20.8242 | 20.8211 | 20.8179 | 20.8137 | 20.8105 | 20.8063 | 20.8021 | 20.7979 | 20.7821 | 20.7695 | 20.7632 | 16.3663 | 16.3537 | 16.3389 | 16.3232 | 16.3137 | 16.2989 | 16.2842 | 16.2684 | 16.2484 | 16.2326 | 16.1484 | 16.0789 | 16.0368 | 13.7979 | 13.7884 | 13.7768 | 13.7642 | 13.7568 | 13.7453 | 13.7337 | 13.7211 | 13.7053 | 13.6958 | 13.6453 | 13.6042 | 13.5789
| PERSLEY | ST MACHAR | MINIMUM HEADROOM | NJ 93584 08102 | NO | NO | 0.19388 | 23.5442 | 23.5126 | 23.4821 | 23.4432 | 23.4126 | 23.3547 | 23.2968 | 23.2589 | 23.2232 | 23.1084 | 22.4811 | 22.0189 | 21.6737 | 22.0811 | 21.9737 | 21.8747 | 21.7568 | 21.6189 | 21.4884 | 21.6316 | 21.4853 | 21.2611 | 21.0737 | 20.4295 | 19.9084 | 19.3968 | 21.3484 | 21.3116 | 21.2789 | 21.2358 | 21.1989 | 21.1421 | 21.0874 | 21.0442 | 21.0021 | 20.9779 | 20.3316 | 19.8011 | 19.2842
|  | ST MACHAR | EE |  |  |  |  | 23.5442 | 23.5126 | 23.4884 | 23.4558 | 23.4179 | 23.3663 | 23.4137 | 23.3705 | 23.3253 | 23.2284 | 22.5568 | 22.1547 | 21.8084 | 22.0811 | 21.9737 | 21.8747 | 21.7568 | 21.6189 | 21.4884 | 21.6737 | 21.5189 | 21.3632 | 21.2126 | 20.4295 | 19.9589 | 19.5411 | 21.3484 | 21.3116 | 21.2821 | 21.2442 | 21.1989 | 21.1421 | 21.3147 | 21.2632 | 21.2105 | 21.1442 | 20.3316 | 19.8516 | 19.4295
|  | ST MACHAR | HT |  |  |  |  | 23.5474 | 23.5158 | 23.4821 | 23.4432 | 23.5032 | 23.4589 | 23.4126 | 23.3621 | 23.2726 | 23.1084 | 22.4811 | 22.0189 | 21.6737 | 22.1084 | 22.0084 | 21.9126 | 21.8042 | 21.9663 | 21.8516 | 21.6779 | 21.4853 | 21.2611 | 21.0737 | 20.4463 | 19.9084 | 19.3968 | 21.3526 | 21.3168 | 21.2789 | 21.2358 | 21.4189 | 21.3695 | 21.3147 | 21.2547 | 21.1916 | 21.0021 | 20.3516 | 19.8011 | 19.2842
|  | ST MACHAR | HE |  |  |  |  | 23.5537 | 23.5189 | 23.4916 | 23.4558 | 23.4126 | 23.3547 | 23.2968 | 23.2589 | 23.2232 | 23.2042 | 22.8537 | 22.6526 | 22.4632 | 22.1726 | 22.0968 | 22.0295 | 21.9558 | 21.8484 | 21.7463 | 21.6316 | 21.5147 | 21.3874 | 21.2874 | 20.6663 | 20.4347 | 20.2137 | 21.3632 | 21.3253 | 21.2958 | 21.2568 | 21.2095 | 21.1495 | 21.0874 | 21.0442 | 21.0021 | 20.9779 | 20.5958 | 20.3558 | 20.1253
|  | ST MACHAR | FB |  |  |  |  | 23.5663 | 23.5495 | 23.5305 | 23.5105 | 23.4895 | 23.4663 | 23.4442 | 23.42 | 23.3958 | 23.3695 | 23.2726 | 22.96 | 22.7505 | 22.2 | 22.1474 | 22.0937 | 22.0368 | 21.9705 | 21.9063 | 21.8495 | 21.7768 | 21.6979 | 21.6074 | 21.1611 | 20.78 | 20.5326 | 21.3768 | 21.3579 | 21.3358 | 21.3137 | 21.2895 | 21.2642 | 21.2389 | 21.2116 | 21.1842 | 21.1537 | 21.0326 | 20.7116 | 20.4537
| THURSO | ST MARYS | MINIMUM HEADROOM | HY 46965 01396 | YES | YES | 0 | -3.0421 | -3.0568 | -3.0684 | -3.0853 | -3.1032 | -3.1211 | -3.1453 | -3.1611 | -3.1789 | -3.1989 | -8.3137 | -8.3874 | -8.5053 | -2.2589 | -2.2737 | -2.2853 | -2.3021 | -2.32 | -2.3379 | -2.3621 | -2.3779 | -2.3958 | -2.4158 | -5.8779 | -6.0579 | -6.2189 | -1.1442 | -1.1589 | -1.1705 | -1.1874 | -1.2053 | -1.2274 | -1.4042 | -1.66 | -1.9947 | -2.06 | -7.5211 | -7.72 | -7.9
|  | ST MARYS | EE |  |  |  |  | -3.0421 | -3.0568 | -3.0684 | -3.0821 | -3.0979 | -3.1211 | -3.1453 | -3.1611 | -3.1789 | -3.1926 | -6.0547 | -6.0947 | -6.1337 | -2.2589 | -2.2737 | -2.2853 | -2.2989 | -2.3147 | -2.3379 | -2.3621 | -2.3779 | -2.3958 | -2.4095 | -4.0358 | -4.1011 | -4.2442 | -1.1442 | -1.1589 | -1.1705 | -1.1842 | -1.2 | -1.2274 | -1.2884 | -1.4116 | -1.5789 | -1.6347 | -5.1263 | -5.3474 | -5.4905
|  | ST MARYS | HT |  |  |  |  | -3.0411 | -3.0537 | -3.0674 | -3.0853 | -3.1032 | -3.12 | -3.1389 | -3.1579 | -3.1779 | -3.1989 | -8.3137 | -8.3874 | -8.5053 | -2.2579 | -2.2705 | -2.2842 | -2.3021 | -2.32 | -2.3368 | -2.3558 | -2.3747 | -2.3947 | -2.4158 | -5.8779 | -6.0579 | -6.2189 | -1.1432 | -1.1558 | -1.1695 | -1.1874 | -1.2053 | -1.2221 | -1.4042 | -1.66 | -1.9947 | -2.06 | -7.5211 | -7.72 | -7.9
|  | ST MARYS | HE |  |  |  |  | -3.0358 | -3.0474 | -3.0568 | -3.0705 | -3.0863 | -3.1074 | -3.1295 | -3.1421 | -3.1547 | -3.1621 | -7.8705 | -7.8905 | -7.9032 | -2.2526 | -2.2642 | -2.2737 | -2.2874 | -2.3032 | -2.3242 | -2.3463 | -2.3589 | -2.3716 | -2.3789 | -5.3126 | -5.4126 | -5.4926 | -1.1379 | -1.1495 | -1.1589 | -1.1726 | -1.1884 | -1.2095 | -1.2316 | -1.2442 | -1.3716 | -1.4095 | -6.8663 | -6.9789 | -7.0684
|  | ST MARYS | FB |  |  |  |  | -3.0284 | -3.0326 | -3.0389 | -3.0442 | -3.0505 | -3.0579 | -3.0642 | -3.0716 | -3.0779 | -3.0863 | -3.1147 | -3.1379 | -3.1505 | -2.2453 | -2.2495 | -2.2558 | -2.2611 | -2.2674 | -2.2747 | -2.2811 | -2.2884 | -2.2947 | -2.3032 | -2.3316 | -2.3547 | -2.3674 | -1.1305 | -1.1347 | -1.1411 | -1.1463 | -1.1526 | -1.16 | -1.1663 | -1.1737 | -1.18 | -1.1884 | -1.4916 | -1.7516 | -1.8516
| WILLOWDALE | ST NICHOLAS | MINIMUM HEADROOM | NJ 93737 06782 | NO | YES | 0 | 17.6179 | 17.5684 | 17.3021 | 16.8905 | 16.7747 | 16.2537 | 16.0116 | 15.9179 | 15.8337 | 15.7284 | 15.3874 | 15.0642 | 14.7705 | 17.7284 | 17.6979 | 17.5358 | 17.2653 | 17.1832 | 16.6979 | 16.4421 | 16.3453 | 16.2568 | 16.1463 | 15.7895 | 15.4316 | 15.0989 | 17.5326 | 17.4263 | 17.0579 | 16.6421 | 16.5263 | 15.9979 | 15.7537 | 15.6611 | 15.5758 | 15.4705 | 15.1263 | 14.8 | 14.5032
|  | ST NICHOLAS | EE |  |  |  |  | 17.6179 | 17.5937 | 17.5189 | 17.0589 | 16.9568 | 16.2537 | 16.0116 | 15.9179 | 15.8337 | 15.7284 | 15.3874 | 15.0642 | 14.7705 | 17.7284 | 17.7074 | 17.6432 | 17.3758 | 17.3021 | 16.6979 | 16.4421 | 16.3453 | 16.2568 | 16.1463 | 15.7895 | 15.4316 | 15.0989 | 17.5326 | 17.5021 | 17.2779 | 16.8126 | 16.7105 | 15.9979 | 15.7537 | 15.6611 | 15.5758 | 15.4705 | 15.1263 | 14.8 | 14.5032
|  | ST NICHOLAS | HT |  |  |  |  | 17.6232 | 17.5684 | 17.3021 | 16.8905 | 16.7747 | 16.3453 | 16.2579 | 16.1737 | 16.0863 | 15.9579 | 15.5684 | 15.1863 | 14.8989 | 17.7337 | 17.6979 | 17.5358 | 17.2653 | 17.1832 | 16.7958 | 16.7053 | 16.6179 | 16.5263 | 16.3926 | 16.0579 | 15.66 | 15.2579 | 17.54 | 17.4263 | 17.0579 | 16.6421 | 16.5263 | 16.0916 | 16.0042 | 15.9189 | 15.8316 | 15.7021 | 15.38 | 14.9968 | 14.6337
|  | ST NICHOLAS | HE |  |  |  |  | 17.6295 | 17.6063 | 17.5747 | 17.5358 | 17.5042 | 17.3989 | 17.2516 | 17.1242 | 16.9926 | 16.8505 | 16.3495 | 15.8042 | 15.4074 | 17.7368 | 17.7147 | 17.6916 | 17.6621 | 17.6326 | 17.5474 | 17.4611 | 17.3726 | 17.2811 | 17.1863 | 16.8084 | 16.2326 | 15.8105 | 17.5505 | 17.5242 | 17.4758 | 17.4168 | 17.3579 | 17.1568 | 17.0084 | 16.88 | 16.7474 | 16.6032 | 16.0979 | 15.5474 | 15.1463
|  | ST NICHOLAS | FB |  |  |  |  | 17.6411 | 17.6284 | 17.6137 | 17.5947 | 17.5779 | 17.5526 | 17.5284 | 17.5053 | 17.4811 | 17.3863 | 16.9853 | 16.5284 | 16.1568 | 17.7463 | 17.7347 | 17.7221 | 17.7074 | 17.6926 | 17.6737 | 17.6547 | 17.6358 | 17.5947 | 17.5484 | 17.2874 | 16.9716 | 16.6042 | 17.5663 | 17.5505 | 17.5337 | 17.5042 | 17.4832 | 17.4453 | 17.4084 | 17.3274 | 17.24 | 17.1442 | 16.7389 | 16.2779 | 15.9032
| ARDMORE / HARRIS GRID | STOCKINISH | MINIMUM HEADROOM | NG 13447 94222 | YES | YES | 0 | 0.84316 | 0.83158 | 0.82 | 0.80526 | 0.79053 | 0.77579 | 0.76 | 0.74737 | 0.73368 | 0.72105 | 0.67368 | 0.63263 | 0.60421 | 0.90211 | 0.89789 | 0.89368 | 0.88842 | 0.88105 | 0.86842 | 0.85368 | 0.84316 | 0.83158 | 0.82105 | 0.78211 | 0.73263 | 0.69895 | -5.0905 | -5.1042 | -5.1168 | -5.1337 | -5.1495 | -5.1653 | -5.1832 | -5.1979 | -5.2126 | -5.2263 | -5.2758 | -5.3232 | -5.3558
|  | STOCKINISH | EE |  |  |  |  | 0.84316 | 0.83158 | 0.82 | 0.80526 | 0.79053 | 0.77579 | 0.76 | 0.74737 | 0.73368 | 0.72105 | 0.67579 | 0.63263 | 0.60421 | 0.90211 | 0.89789 | 0.89368 | 0.88947 | 0.88105 | 0.86842 | 0.85368 | 0.84316 | 0.83158 | 0.82105 | 0.78211 | 0.73263 | 0.69895 | -5.0905 | -5.1042 | -5.1168 | -5.1337 | -5.1495 | -5.1653 | -5.1832 | -5.1979 | -5.2126 | -5.2263 | -5.2758 | -5.3232 | -5.3558
|  | STOCKINISH | HT |  |  |  |  | 0.84737 | 0.83789 | 0.82526 | 0.81263 | 0.79895 | 0.78632 | 0.77158 | 0.75789 | 0.74421 | 0.73053 | 0.67368 | 0.63263 | 0.60526 | 0.90316 | 0.9 | 0.89368 | 0.88842 | 0.88316 | 0.87684 | 0.86421 | 0.85263 | 0.84 | 0.82737 | 0.78842 | 0.74211 | 0.70105 | -5.0863 | -5.0968 | -5.1105 | -5.1242 | -5.1389 | -5.1537 | -5.1705 | -5.1853 | -5.2 | -5.2147 | -5.2653 | -5.3147 | -5.3537
|  | STOCKINISH | HE |  |  |  |  | 0.85579 | 0.84737 | 0.84105 | 0.83158 | 0.82421 | 0.81579 | 0.80632 | 0.79579 | 0.78842 | 0.78211 | 0.75789 | 0.73684 | 0.72105 | 0.90526 | 0.9 | 0.89789 | 0.89263 | 0.88842 | 0.88211 | 0.87474 | 0.86947 | 0.86632 | 0.86526 | 0.84947 | 0.83263 | 0.82 | -5.0768 | -5.0863 | -5.0937 | -5.1032 | -5.1105 | -5.12 | -5.1305 | -5.1411 | -5.1495 | -5.1568 | -5.1832 | -5.2074 | -5.2242
|  | STOCKINISH | FB |  |  |  |  | 0.86 | 0.85474 | 0.85053 | 0.84526 | 0.83895 | 0.83368 | 0.82842 | 0.82316 | 0.81684 | 0.80947 | 0.78105 | 0.75368 | 0.73263 | 0.90737 | 0.90632 | 0.90316 | 0.90211 | 0.9 | 0.89789 | 0.89579 | 0.89263 | 0.89053 | 0.88842 | 0.87263 | 0.85053 | 0.83263 | -5.0726 | -5.0779 | -5.0832 | -5.0895 | -5.0958 | -5.1011 | -5.1074 | -5.1137 | -5.12 | -5.1284 | -5.16 | -5.1905 | -5.2147
| PORT ANN | STONEFIELD | MINIMUM HEADROOM | NR 86244 73400 | YES | YES | 0 | 0.31395 | 0.31395 | 0.31395 | 0.31184 | 0.31079 | 0.30974 | 0.30974 | 0.30868 | 0.19816 | -0.030263 | -0.47026 | -0.47658 | -0.47974 | 0.31711 | 0.31711 | 0.31711 | 0.31395 | 0.31395 | 0.31289 | 0.31184 | 0.31079 | 0.18132 | -0.088158 | -0.60605 | -0.61132 | -0.61658 | 0.31605 | 0.31605 | 0.31605 | 0.31289 | 0.31289 | 0.31184 | 0.31079 | 0.30974 | 0.18026 | -0.087105 | -0.60395 | -0.60921 | -0.61553
|  | STONEFIELD | EE |  |  |  |  | 0.31395 | 0.31395 | 0.31395 | 0.31184 | 0.31079 | 0.30974 | 0.30974 | 0.30868 | 0.30658 | 0.30658 | -0.46816 | -0.47237 | -0.47763 | 0.31711 | 0.31711 | 0.31711 | 0.31395 | 0.31395 | 0.31289 | 0.31184 | 0.31079 | 0.30868 | 0.30763 | -0.60395 | -0.60921 | -0.61447 | 0.31605 | 0.31605 | 0.31605 | 0.31289 | 0.31289 | 0.31184 | 0.31079 | 0.30974 | 0.30763 | 0.30658 | -0.60184 | -0.60816 | -0.61342
|  | STONEFIELD | HT |  |  |  |  | 0.31395 | 0.31395 | 0.31395 | 0.31289 | 0.31079 | 0.30974 | 0.30974 | 0.30868 | 0.19816 | -0.030263 | -0.47026 | -0.47658 | -0.47974 | 0.31711 | 0.31711 | 0.31711 | 0.315 | 0.31395 | 0.31289 | 0.31184 | 0.31079 | 0.18132 | -0.088158 | -0.60605 | -0.61132 | -0.61658 | 0.31605 | 0.31605 | 0.31605 | 0.31395 | 0.31289 | 0.31184 | 0.31079 | 0.30974 | 0.18026 | -0.087105 | -0.60395 | -0.60921 | -0.61553
|  | STONEFIELD | HE |  |  |  |  | 0.315 | 0.31395 | 0.31395 | 0.31395 | 0.31395 | 0.31289 | 0.31289 | 0.31289 | 0.31289 | 0.31079 | -0.46289 | -0.46605 | -0.46605 | 0.31711 | 0.31711 | 0.31711 | 0.31711 | 0.31711 | 0.31605 | 0.31605 | 0.31605 | 0.315 | 0.31395 | -0.59868 | -0.60079 | -0.60079 | 0.31711 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.315 | 0.315 | 0.315 | 0.31395 | 0.31289 | -0.59658 | -0.59974 | -0.59974
|  | STONEFIELD | FB |  |  |  |  | 0.315 | 0.315 | 0.31395 | 0.31395 | 0.31395 | 0.31395 | 0.31395 | 0.31395 | 0.31395 | 0.31289 | 0.10974 | -0.17658 | -0.17974 | 0.31711 | 0.31711 | 0.31711 | 0.31711 | 0.31711 | 0.31711 | 0.31711 | 0.31711 | 0.31711 | 0.315 | 0.077105 | -0.26079 | -0.265 | 0.31711 | 0.31711 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.31605 | 0.31395 | 0.076053 | -0.26079 | -0.26395
| FIDDES | STONEHAVEN | MINIMUM HEADROOM | NO 85903 85641 | NO | YES | 0.20408 | 18.3116 | 17.1653 | 15.9768 | 14.3284 | 14.1053 | 13.8063 | 13.5558 | 13.3863 | 13.22 | 13.0495 | 4.5495 | -0.61158 | -2.48 | 17.4147 | 16.0463 | 14.6284 | 12.7011 | 12.4505 | 12.1137 | 11.8337 | 11.6463 | 11.4621 | 11.2716 | 4.3642 | -2.0821 | -4.8074 | 17.5253 | 16.2074 | 14.8253 | 12.9463 | 12.7011 | 12.3705 | 12.0968 | 11.9126 | 11.7305 | 11.5442 | 4.0432 | -2.9189 | -5.6453
|  | STONEHAVEN | EE |  |  |  |  | 18.3253 | 17.1653 | 15.9768 | 14.3284 | 14.1053 | 13.8063 | 13.5558 | 13.3863 | 13.22 | 13.0495 | 8.04 | 4.1463 | 2.6642 | 17.4326 | 16.0463 | 14.6284 | 12.7011 | 12.4505 | 12.1137 | 11.8337 | 11.6463 | 11.4621 | 11.2716 | 6.8074 | 3.4358 | 1.7126 | 17.5421 | 16.2074 | 14.8253 | 12.9463 | 12.7011 | 12.3705 | 12.0968 | 11.9126 | 11.7305 | 11.5442 | 6.2495 | 2.2316 | 0.55053
|  | STONEHAVEN | HT |  |  |  |  | 18.3116 | 17.2853 | 16.0611 | 14.4316 | 14.1968 | 13.9737 | 13.7968 | 13.6211 | 13.4189 | 13.1747 | 4.5495 | -0.61158 | -2.48 | 17.4147 | 16.1884 | 14.7274 | 12.8253 | 12.5611 | 12.3095 | 12.1147 | 11.92 | 11.6958 | 11.4232 | 4.3642 | -2.0821 | -4.8074 | 17.5253 | 16.3474 | 14.9221 | 13.0674 | 12.8074 | 12.5611 | 12.3695 | 12.1779 | 11.9579 | 11.6895 | 4.0432 | -2.9189 | -5.6453
|  | STONEHAVEN | HE |  |  |  |  | 18.38 | 17.4611 | 16.3495 | 14.8042 | 14.5853 | 14.3232 | 14.1505 | 14.04 | 13.9263 | 13.8179 | 11.0916 | 8.9979 | 7.7253 | 17.4926 | 16.3958 | 15.0642 | 13.2516 | 13.0063 | 12.7116 | 12.5242 | 12.4021 | 12.2779 | 12.1547 | 9.5232 | 7.5284 | 6.0411 | 17.6 | 16.5495 | 15.2516 | 13.4853 | 13.2442 | 12.9547 | 12.7695 | 12.6505 | 12.5274 | 12.4074 | 9.4663 | 7.2147 | 5.7474
|  | STONEHAVEN | FB |  |  |  |  | 18.6189 | 18.5989 | 18.3432 | 17.7863 | 17.4337 | 17.1484 | 16.9274 | 16.7695 | 16.6874 | 16.5821 | 11.6726 | 5.9874 | 2.1863 | 18.3326 | 17.9621 | 17.4526 | 16.7863 | 16.3663 | 16.0274 | 15.7663 | 15.5821 | 15.4884 | 15.3674 | 9.6063 | 2.9474 | -1.5063 | 18.2726 | 18.0347 | 17.5611 | 16.9295 | 16.52 | 16.1895 | 15.9337 | 15.7537 | 15.6632 | 15.5432 | 9.8884 | 3.2274 | -1.2274
| STRICHEN | STONEYHILL | MINIMUM HEADROOM | NK 6773 4109 | YES | YES | 0 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -0.057895 | -8.1853 | -17.5937 | -23.9 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -0.47368 | -10.0916 | -21.3337 | -28.7611 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -0.56947 | -9.5989 | -20.8063 | -28.2116
|  | STONEYHILL | EE |  |  |  |  | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -0.057895 | -1.5411 | -2.7568 | -4.4905 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -0.47368 | -2.4242 | -3.8547 | -5.8968 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -0.56947 | -2.0463 | -3.3811 | -5.4168
|  | STONEYHILL | HT |  |  |  |  | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -0.057895 | -8.1853 | -13.1821 | -15.6453 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -0.47368 | -8.3147 | -15.4095 | -19.0368 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -0.56947 | -7.8274 | -14.9011 | -18.5168
|  | STONEYHILL | HE |  |  |  |  | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -0.057895 | -1.5411 | -2.7568 | -4.4905 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -0.47368 | -2.4242 | -3.8547 | -5.8968 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -0.56947 | -2.0463 | -3.3811 | -5.4168
|  | STONEYHILL | FB |  |  |  |  | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -2.36 | -0.057895 | -8.0505 | -17.5937 | -23.9 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -2.6674 | -0.47368 | -10.0916 | -21.3337 | -28.7611 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -2.9453 | -0.56947 | -9.5989 | -20.8063 | -28.2116
| PERSLEY | STONEYWOOD T1&T2 | MINIMUM HEADROOM | NJ 89285 11082 | NO | NO | 0 | 24.7421 | 24.2316 | 23.4674 | 22.8526 | 20.9632 | 20.7526 | 20.4758 | 19.9937 | 19.3821 | 19.2684 | 17.2653 | 16.66 | 16.3811 | 23.6242 | 23.0189 | 22.1084 | 21.3779 | 19.1011 | 18.8674 | 18.5253 | 17.9484 | 17.2158 | 17.0853 | 15.8474 | 14.1926 | 13.9 | 20.3726 | 19.7863 | 18.8926 | 18.1611 | 15.8853 | 15.6484 | 15.3105 | 14.7358 | 14.0042 | 13.8737 | 12.8516 | 10.9979 | 10.7053
|  | STONEYWOOD T1&T2 | EE |  |  |  |  | 24.7421 | 24.2316 | 23.4674 | 22.8526 | 21.1863 | 20.7526 | 20.6326 | 20.3505 | 20.0379 | 19.9295 | 18.7705 | 16.66 | 16.3811 | 23.6242 | 23.0189 | 22.1084 | 21.3779 | 19.38 | 18.8674 | 18.7358 | 18.4074 | 18.0411 | 17.9179 | 16.9021 | 14.4063 | 14.0884 | 20.3726 | 19.7863 | 18.8926 | 18.1611 | 16.1611 | 15.6484 | 15.5158 | 15.1863 | 14.8189 | 14.6958 | 13.8811 | 11.3926 | 11.0726
|  | STONEYWOOD T1&T2 | HT |  |  |  |  | 24.7705 | 24.2842 | 23.5347 | 22.9368 | 20.9632 | 20.8895 | 20.4758 | 19.9937 | 19.3821 | 19.2684 | 17.2653 | 16.94 | 16.6979 | 23.6547 | 23.0768 | 22.1832 | 21.4737 | 19.1011 | 19.0189 | 18.5253 | 17.9484 | 17.2158 | 17.0853 | 15.8474 | 14.7663 | 14.4158 | 20.4042 | 19.8442 | 18.9695 | 18.2579 | 15.8853 | 15.8032 | 15.3105 | 14.7358 | 14.0042 | 13.8737 | 12.8516 | 11.7684 | 11.4158
|  | STONEYWOOD T1&T2 | HE |  |  |  |  | 24.8389 | 24.4063 | 23.7105 | 23.1674 | 21.5674 | 21.1853 | 21.12 | 20.9179 | 20.6484 | 20.5926 | 19.0137 | 16.8947 | 16.6495 | 23.7295 | 23.2116 | 22.3758 | 21.7253 | 19.8021 | 19.3484 | 19.2758 | 19.0358 | 18.7147 | 18.6484 | 16.7484 | 14.1926 | 13.9 | 20.48 | 19.98 | 19.1674 | 18.5158 | 16.5926 | 16.1379 | 16.0663 | 15.8274 | 15.5063 | 15.44 | 13.5463 | 10.9979 | 10.7053
|  | STONEYWOOD T1&T2 | FB |  |  |  |  | 25.1221 | 24.9084 | 24.6263 | 24.3768 | 23.8084 | 23.5221 | 23.4874 | 23.4474 | 23.3611 | 23.3105 | 22.8211 | 20.7958 | 20.48 | 23.8516 | 23.8126 | 23.4737 | 23.1758 | 22.4926 | 22.1484 | 22.1095 | 22.0642 | 21.9621 | 21.9042 | 21.3232 | 18.8884 | 18.5105 | 20.8074 | 20.56 | 20.2337 | 19.9453 | 19.2832 | 18.94 | 18.9 | 18.8547 | 18.7526 | 18.6947 | 18.1137 | 15.68 | 15.3032
| DYCE | STONEYWOOD T3 | MINIMUM HEADROOM | NJ 89285 11082 | NO | YES | 0 | 22.9789 | 22.9674 | 22.9568 | 22.9442 | 22.9316 | 22.9168 | 22.9042 | 22.8905 | 22.8789 | 22.8674 | 22.8232 | 22.7811 | 22.7495 | 22.8621 | 22.8558 | 22.8516 | 22.8453 | 22.8389 | 22.8305 | 22.8221 | 22.8147 | 22.8074 | 22.8011 | 22.7411 | 22.6874 | 22.6232 | 23.4295 | 23.4242 | 23.42 | 23.4147 | 23.4084 | 23.4011 | 23.3937 | 23.3863 | 23.38 | 23.3737 | 23.3337 | 23.2842 | 23.2221
|  | STONEYWOOD T3 | EE |  |  |  |  | 22.9789 | 22.9674 | 22.9568 | 22.9442 | 22.9316 | 22.9168 | 22.9042 | 22.8905 | 22.8789 | 22.8674 | 22.8253 | 22.7916 | 22.7663 | 22.8621 | 22.8558 | 22.8516 | 22.8453 | 22.8389 | 22.8305 | 22.8221 | 22.8147 | 22.8074 | 22.8021 | 22.7411 | 22.6884 | 22.6474 | 23.4295 | 23.4242 | 23.42 | 23.4147 | 23.4095 | 23.4011 | 23.3937 | 23.3863 | 23.38 | 23.3747 | 23.3337 | 23.2863 | 23.2463
|  | STONEYWOOD T3 | HT |  |  |  |  | 22.9821 | 22.9726 | 22.9611 | 22.9505 | 22.9368 | 22.9242 | 22.9116 | 22.8989 | 22.8874 | 22.8737 | 22.8232 | 22.7811 | 22.7495 | 22.8632 | 22.8589 | 22.8516 | 22.8463 | 22.8389 | 22.8316 | 22.8242 | 22.8158 | 22.8095 | 22.8011 | 22.7568 | 22.6874 | 22.6232 | 23.4305 | 23.4263 | 23.42 | 23.4147 | 23.4084 | 23.4021 | 23.3947 | 23.3874 | 23.3811 | 23.3737 | 23.3474 | 23.2842 | 23.2221
|  | STONEYWOOD T3 | HE |  |  |  |  | 22.9874 | 22.98 | 22.9747 | 22.9674 | 22.9568 | 22.9474 | 22.9358 | 22.9274 | 22.9189 | 22.9126 | 22.8895 | 22.8716 | 22.8589 | 22.8642 | 22.86 | 22.8568 | 22.8526 | 22.8453 | 22.8379 | 22.8305 | 22.8242 | 22.8189 | 22.8168 | 22.8053 | 22.7968 | 22.7916 | 23.4316 | 23.4274 | 23.4242 | 23.42 | 23.4137 | 23.4063 | 23.3989 | 23.3937 | 23.3884 | 23.3863 | 23.3758 | 23.3684 | 23.3642
|  | STONEYWOOD T3 | FB |  |  |  |  | 22.9926 | 22.9884 | 22.9832 | 22.9789 | 22.9726 | 22.9684 | 22.9642 | 22.9579 | 22.9526 | 22.9453 | 22.9211 | 22.8979 | 22.8811 | 22.8684 | 22.8653 | 22.8632 | 22.8611 | 22.8589 | 22.8558 | 22.8537 | 22.8505 | 22.8484 | 22.8442 | 22.8337 | 22.8232 | 22.8158 | 23.4347 | 23.4326 | 23.4305 | 23.4284 | 23.4263 | 23.4242 | 23.4221 | 23.4189 | 23.4168 | 23.4137 | 23.4042 | 23.3947 | 23.3905
| CLACHAN | STRACHUR | MINIMUM HEADROOM | NN 08672 01180 | YES | YES | 0 | 0.97053 | 0.95158 | 0.93263 | 0.91368 | 0.89263 | 0.87474 | 0.85053 | 0.81579 | 0.78526 | 0.76842 | 0.67895 | 0.61263 | 0.55684 | 0.96947 | 0.95158 | 0.93158 | 0.91263 | 0.89158 | 0.87368 | 0.84947 | 0.81474 | 0.78421 | 0.76737 | 0.67895 | 0.61158 | 0.55684 | 0.96632 | 0.94421 | 0.92421 | 0.90211 | 0.87895 | 0.85789 | 0.83263 | 0.79158 | 0.75684 | 0.73895 | 0.63789 | 0.56421 | 0.50211
|  | STRACHUR | EE |  |  |  |  | 0.97053 | 0.95158 | 0.93263 | 0.91368 | 0.89263 | 0.87474 | 0.85053 | 0.81579 | 0.78526 | 0.76842 | 0.67895 | 0.61263 | 0.55684 | 0.96947 | 0.95158 | 0.93158 | 0.91263 | 0.89158 | 0.87368 | 0.84947 | 0.81474 | 0.78421 | 0.76737 | 0.67895 | 0.61158 | 0.55684 | 0.96632 | 0.94421 | 0.92421 | 0.90211 | 0.87895 | 0.85789 | 0.83263 | 0.79158 | 0.75684 | 0.73895 | 0.63789 | 0.56421 | 0.50211
|  | STRACHUR | HT |  |  |  |  | 0.97789 | 0.96632 | 0.95158 | 0.93368 | 0.91895 | 0.90211 | 0.87053 | 0.83789 | 0.81579 | 0.80211 | 0.74421 | 0.70211 | 0.66842 | 0.97579 | 0.96421 | 0.94842 | 0.92947 | 0.91474 | 0.89579 | 0.86105 | 0.82526 | 0.80105 | 0.78842 | 0.74211 | 0.69579 | 0.65474 | 0.97474 | 0.96211 | 0.94526 | 0.92421 | 0.90842 | 0.88947 | 0.85263 | 0.81579 | 0.79053 | 0.77684 | 0.72526 | 0.67263 | 0.62632
|  | STRACHUR | HE |  |  |  |  | 0.98632 | 0.97684 | 0.96842 | 0.95579 | 0.94737 | 0.93895 | 0.91474 | 0.88842 | 0.86105 | 0.85368 | 0.81789 | 0.78842 | 0.76526 | 0.98526 | 0.97579 | 0.96737 | 0.95474 | 0.94632 | 0.93684 | 0.91263 | 0.88316 | 0.85368 | 0.84737 | 0.81053 | 0.78316 | 0.76105 | 0.98421 | 0.97368 | 0.96526 | 0.95053 | 0.94105 | 0.93158 | 0.90421 | 0.87368 | 0.84421 | 0.83579 | 0.79368 | 0.76105 | 0.73474
|  | STRACHUR | FB |  |  |  |  | 0.99053 | 0.98632 | 0.98105 | 0.97579 | 0.97053 | 0.96526 | 0.96 | 0.95158 | 0.93789 | 0.93158 | 0.89263 | 0.85895 | 0.84105 | 0.99053 | 0.98421 | 0.98 | 0.97368 | 0.96737 | 0.96211 | 0.95684 | 0.94737 | 0.93158 | 0.92421 | 0.88 | 0.84316 | 0.82421 | 0.98947 | 0.98421 | 0.97895 | 0.97263 | 0.96632 | 0.96 | 0.95474 | 0.94526 | 0.92842 | 0.92211 | 0.87684 | 0.84 | 0.81895
| TARLAND | STRATHDON | MINIMUM HEADROOM | NJ 37343 11904 | YES | YES | 0 | 1.0284 | 1.0168 | 1.0063 | 0.98947 | 0.97474 | 0.95789 | 0.94211 | 0.92737 | 0.91263 | 0.89895 | 0.67579 | 0.62421 | 0.58737 | 0.97579 | 0.96316 | 0.95053 | 0.93158 | 0.91368 | 0.89368 | 0.87579 | 0.86 | 0.84316 | 0.82737 | 0.63895 | 0.57895 | 0.53263 | 0.97579 | 0.96316 | 0.95053 | 0.93158 | 0.91368 | 0.89474 | 0.87684 | 0.86 | 0.84316 | 0.82842 | 0.6 | 0.54 | 0.49684
|  | STRATHDON | EE |  |  |  |  | 1.0284 | 1.0168 | 1.0063 | 0.98947 | 0.97474 | 0.95789 | 0.94211 | 0.92737 | 0.91263 | 0.89895 | 0.67579 | 0.62421 | 0.58737 | 0.97579 | 0.96316 | 0.95053 | 0.93158 | 0.91368 | 0.89368 | 0.87579 | 0.86 | 0.84316 | 0.82737 | 0.63895 | 0.57895 | 0.53684 | 0.97579 | 0.96316 | 0.95053 | 0.93158 | 0.91368 | 0.89474 | 0.87684 | 0.86 | 0.84316 | 0.82842 | 0.6 | 0.54 | 0.49684
|  | STRATHDON | HT |  |  |  |  | 1.0316 | 1.0221 | 1.0126 | 1 | 0.98316 | 0.96947 | 0.95474 | 0.94 | 0.92526 | 0.90947 | 0.70211 | 0.64105 | 0.59684 | 0.97895 | 0.96842 | 0.95789 | 0.94421 | 0.92526 | 0.90842 | 0.89158 | 0.87474 | 0.85895 | 0.84 | 0.67263 | 0.59789 | 0.53263 | 0.97895 | 0.96842 | 0.95789 | 0.94421 | 0.92526 | 0.90947 | 0.89158 | 0.87474 | 0.85895 | 0.84105 | 0.64211 | 0.56632 | 0.50105
|  | STRATHDON | HE |  |  |  |  | 1.04 | 1.0316 | 1.0263 | 1.0189 | 1.0126 | 1.0042 | 0.99579 | 0.98842 | 0.98 | 0.97263 | 0.87579 | 0.84947 | 0.83053 | 0.98842 | 0.98 | 0.97368 | 0.96632 | 0.95895 | 0.95053 | 0.94105 | 0.93263 | 0.92316 | 0.91368 | 0.83053 | 0.8 | 0.77789 | 0.98842 | 0.98 | 0.97368 | 0.96632 | 0.96 | 0.95053 | 0.94105 | 0.93263 | 0.92316 | 0.91368 | 0.81474 | 0.78421 | 0.76211
|  | STRATHDON | FB |  |  |  |  | 1.0421 | 1.0389 | 1.0337 | 1.0295 | 1.0253 | 1.02 | 1.0147 | 1.0116 | 1.0053 | 0.99684 | 0.96526 | 0.93263 | 0.90842 | 0.99263 | 0.98737 | 0.98211 | 0.97684 | 0.97263 | 0.96632 | 0.96105 | 0.95579 | 0.94947 | 0.93895 | 0.90316 | 0.86526 | 0.83579 | 0.99263 | 0.98737 | 0.98211 | 0.97684 | 0.97263 | 0.96737 | 0.96105 | 0.95684 | 0.94947 | 0.93895 | 0.90316 | 0.86526 | 0.83684
| STRICHEN | STRICHEN | MINIMUM HEADROOM | NJ 95900 55137 | NO | YES | 0.66327 | -0.49579 | -0.62421 | -0.78105 | -1.1116 | -1.1642 | -1.2211 | -1.3147 | -1.4579 | -1.6063 | -1.6642 | -10.1495 | -14.1189 | -14.2442 | -0.17158 | -0.63158 | -1.2116 | -1.9263 | -1.9842 | -2.0474 | -2.1537 | -2.3179 | -2.4832 | -2.5474 | -8.0979 | -12.4674 | -12.6126 | 0.097895 | -0.36 | -0.94 | -1.6526 | -1.7105 | -1.7747 | -1.88 | -2.0442 | -2.2084 | -2.2716 | -9.3074 | -14.6558 | -14.8074
|  | STRICHEN | EE |  |  |  |  | -0.49579 | -0.62421 | -0.78105 | -1.1116 | -1.1642 | -1.2211 | -1.2789 | -1.3642 | -1.4663 | -1.5168 | -8.7063 | -14.1189 | -14.2442 | -0.17158 | -0.63158 | -1.2116 | -1.9263 | -1.9842 | -2.0474 | -2.1105 | -2.2074 | -2.3253 | -2.3811 | -8.0979 | -12.4674 | -12.6126 | 0.097895 | -0.36 | -0.94 | -1.6526 | -1.7105 | -1.7747 | -1.8368 | -1.9337 | -2.0516 | -2.1063 | -9.3074 | -14.6558 | -14.8074
|  | STRICHEN | HT |  |  |  |  | -0.48947 | -0.61579 | -0.77368 | -1.0832 | -1.14 | -1.1937 | -1.3147 | -1.4579 | -1.6063 | -1.6642 | -10.1495 | -11.7295 | -11.8568 | -0.15474 | -0.60947 | -1.1863 | -1.8926 | -1.9558 | -2.0147 | -2.1537 | -2.3179 | -2.4832 | -2.5474 | -6.9937 | -10.5474 | -10.7316 | 0.11474 | -0.33895 | -0.91474 | -1.6189 | -1.6821 | -1.7411 | -1.88 | -2.0442 | -2.2084 | -2.2716 | -7.9653 | -12.2653 | -12.4558
|  | STRICHEN | HE |  |  |  |  | -0.47579 | -0.59579 | -0.74632 | -1.0053 | -1.0389 | -1.0779 | -1.1158 | -1.1863 | -1.2821 | -1.3126 | -4.2779 | -8.5084 | -8.5832 | -0.12 | -0.55895 | -1.1179 | -1.8032 | -1.8389 | -1.8811 | -1.9221 | -2.0021 | -2.1126 | -2.1463 | -4.5116 | -7.8916 | -7.9779 | 0.14947 | -0.28842 | -0.84632 | -1.5305 | -1.5663 | -1.6084 | -1.6484 | -1.7295 | -1.8389 | -1.8726 | -4.9516 | -9.0895 | -9.18
|  | STRICHEN | FB |  |  |  |  | -0.38526 | -0.42737 | -0.48105 | -0.54632 | -0.55789 | -0.56842 | -0.58 | -0.59053 | -0.60737 | -0.62 | -0.70316 | -0.76842 | -0.80211 | 0.21368 | 0.061053 | -0.13684 | -0.37895 | -0.40211 | -0.42526 | -0.44842 | -0.47158 | -0.51368 | -0.54526 | -0.78737 | -0.97579 | -1.0726 | 0.48211 | 0.33053 | 0.13263 | -0.10842 | -0.13158 | -0.15474 | -0.17789 | -0.20105 | -0.24316 | -0.27474 | -0.51684 | -0.70421 | -0.80105
| THURSO | STROMNESS | MINIMUM HEADROOM | HY 25978 10409 | NO | YES | 0 | 8.5126 | 8.0242 | 7.5579 | 7.4653 | 7.2937 | 6.8979 | 6.7979 | 6.6874 | 6.5484 | 6.4621 | 4.4537 | 3.8368 | 3.6105 | 8.0695 | 7.5095 | 6.9632 | 6.8579 | 6.6621 | 6.2032 | 6.0926 | 5.9674 | 5.8095 | 5.7126 | 5.1547 | 3.3832 | 3.1242 | 8.1653 | 7.6726 | 7.1379 | 7.0326 | 6.8358 | 6.3768 | 6.2663 | 6.1411 | 5.9821 | 5.8853 | 5.3284 | 3.1105 | 2.8516
|  | STROMNESS | EE |  |  |  |  | 8.5126 | 8.0242 | 7.5579 | 7.4653 | 7.2937 | 6.8979 | 6.7979 | 6.6874 | 6.5484 | 6.4621 | 5.9726 | 3.8368 | 3.6105 | 8.0695 | 7.5095 | 6.9632 | 6.8579 | 6.6621 | 6.2032 | 6.0926 | 5.9674 | 5.8095 | 5.7126 | 5.1547 | 3.3832 | 3.1242 | 8.1653 | 7.6726 | 7.1379 | 7.0326 | 6.8358 | 6.3768 | 6.2663 | 6.1411 | 5.9821 | 5.8853 | 5.3284 | 3.1105 | 2.8516
|  | STROMNESS | HT |  |  |  |  | 8.5158 | 8.0853 | 7.6074 | 7.5253 | 7.3516 | 7.2505 | 7.1042 | 6.92 | 6.7358 | 6.5221 | 4.4537 | 4.16 | 3.9463 | 8.0737 | 7.5811 | 7.0221 | 6.9295 | 6.7316 | 6.6168 | 6.4516 | 6.2411 | 6.0305 | 5.7853 | 5.1979 | 3.6916 | 3.3832 | 8.1684 | 7.7347 | 7.1958 | 7.1042 | 6.9063 | 6.7916 | 6.6253 | 6.4147 | 6.2042 | 5.9589 | 5.3716 | 3.5084 | 3.2
|  | STROMNESS | HE |  |  |  |  | 8.5526 | 8.16 | 7.7253 | 7.6716 | 7.5326 | 7.1674 | 7.0968 | 7.0242 | 6.9295 | 6.8768 | 6.4726 | 5.5611 | 5.4263 | 8.1095 | 7.6674 | 7.1568 | 7.0979 | 6.9389 | 6.5158 | 6.44 | 6.3589 | 6.2516 | 6.1905 | 5.7232 | 4.9484 | 4.7947 | 8.2063 | 7.8095 | 7.3316 | 7.2716 | 7.1137 | 6.6895 | 6.6137 | 6.5326 | 6.4253 | 6.3642 | 5.8979 | 4.9432 | 4.7895
|  | STROMNESS | FB |  |  |  |  | 8.8632 | 8.7232 | 8.5484 | 8.4747 | 8.3874 | 8.2547 | 8.1558 | 8.0842 | 8.0389 | 7.9874 | 7.7 | 7.4326 | 7.2853 | 8.3505 | 8.2705 | 8.1053 | 8.0337 | 7.9358 | 7.7811 | 7.6674 | 7.5842 | 7.5337 | 7.4758 | 7.1463 | 6.8389 | 6.6684 | 8.4684 | 8.3779 | 8.2021 | 8.1274 | 8.04 | 7.9053 | 7.8063 | 7.7326 | 7.6874 | 7.6358 | 7.3211 | 7.0126 | 6.8432
| DUNOON | STRONDAVON | MINIMUM HEADROOM | NS 04281 90471 | YES | YES | 0 | -0.14053 | -0.14421 | -0.14684 | -0.14947 | -0.15211 | -0.15579 | -0.15842 | -0.16105 | -0.16474 | -0.16737 | -0.18211 | -0.19632 | -0.20737 | -0.14632 | -0.14947 | -0.15211 | -0.15474 | -0.15789 | -0.16211 | -0.16526 | -0.16842 | -0.17211 | -0.17526 | -0.18842 | -0.20421 | -0.21895 | -0.15 | -0.15421 | -0.15632 | -0.16 | -0.16316 | -0.16684 | -0.17 | -0.17316 | -0.17737 | -0.18053 | -0.19421 | -0.21 | -0.22579
|  | STRONDAVON | EE |  |  |  |  | 0.017368 | 0.012632 | 0.0073684 | -0.0010526 | -0.01 | -0.017895 | -0.026842 | -0.034737 | -0.043158 | -0.052105 | -0.082632 | -0.11632 | -0.15105 | 0.0078947 | 0.0026316 | -0.0052632 | -0.013684 | -0.022632 | -0.03 | -0.039474 | -0.047368 | -0.056842 | -0.065789 | -0.096842 | -0.13105 | -0.16632 | 0.01 | 0.0031579 | -0.0042105 | -0.012632 | -0.022632 | -0.031053 | -0.040526 | -0.049474 | -0.058947 | -0.067895 | -0.10105 | -0.13684 | -0.17263
|  | STRONDAVON | HT |  |  |  |  | -0.14053 | -0.14421 | -0.14632 | -0.14947 | -0.15211 | -0.15526 | -0.15842 | -0.16105 | -0.16474 | -0.16737 | -0.18211 | -0.19632 | -0.20737 | -0.14632 | -0.14947 | -0.15158 | -0.15474 | -0.15789 | -0.16211 | -0.16526 | -0.16842 | -0.17211 | -0.17526 | -0.18842 | -0.20421 | -0.21895 | -0.15 | -0.15421 | -0.15632 | -0.16 | -0.16316 | -0.16684 | -0.17 | -0.17316 | -0.17737 | -0.18053 | -0.19421 | -0.21 | -0.22579
|  | STRONDAVON | HE |  |  |  |  | -0.14053 | -0.14421 | -0.14684 | -0.14947 | -0.15211 | -0.15579 | -0.15842 | -0.16105 | -0.16421 | -0.16684 | -0.17737 | -0.19053 | -0.20421 | -0.14579 | -0.14895 | -0.15211 | -0.15421 | -0.15684 | -0.16105 | -0.16316 | -0.16632 | -0.16895 | -0.17211 | -0.18316 | -0.19737 | -0.21053 | -0.15 | -0.15368 | -0.15632 | -0.15947 | -0.16211 | -0.16579 | -0.16842 | -0.17158 | -0.17474 | -0.17789 | -0.18947 | -0.20316 | -0.21789
|  | STRONDAVON | FB |  |  |  |  | 0.021579 | 0.021053 | 0.020526 | 0.020526 | 0.019474 | 0.019474 | 0.018947 | 0.017895 | 0.017895 | 0.017895 | 0.014737 | 0.0073684 | 0.0031579 | 0.011053 | 0.0094737 | 0.0094737 | 0.0094737 | 0.0084211 | 0.0084211 | 0.0084211 | 0.0078947 | 0.0073684 | 0.0073684 | 0.0031579 | -0.0042105 | -0.0084211 | 0.016316 | 0.015263 | 0.014737 | 0.014737 | 0.013684 | 0.013158 | 0.012632 | 0.011579 | 0.011579 | 0.011053 | 0.0042105 | -0.0042105 | -0.0089474
| THURSO | STRONSAY | MINIMUM HEADROOM | HY 64548 27016 | YES | YES | 0 | 0.99053 | 0.98526 | 0.98105 | 0.97474 | 0.96947 | 0.96316 | 0.95684 | 0.95263 | 0.94737 | 0.94105 | 0.92105 | 0.90421 | 0.89474 | 0.98737 | 0.98105 | 0.97579 | 0.96737 | 0.96105 | 0.95368 | 0.94526 | 0.94105 | 0.93474 | 0.92737 | 0.90632 | 0.88632 | 0.87053 | 0.98737 | 0.98105 | 0.97579 | 0.96842 | 0.96105 | 0.95368 | 0.94632 | 0.94105 | 0.93474 | 0.92737 | 0.90632 | 0.88632 | 0.87053
|  | STRONSAY | EE |  |  |  |  | 0.99053 | 0.98526 | 0.98105 | 0.97474 | 0.96947 | 0.96316 | 0.95684 | 0.95263 | 0.94737 | 0.94316 | 0.92737 | 0.91053 | 0.9 | 0.98737 | 0.98105 | 0.97579 | 0.96737 | 0.96105 | 0.95368 | 0.94526 | 0.94105 | 0.93474 | 0.92947 | 0.91053 | 0.89053 | 0.87579 | 0.98737 | 0.98105 | 0.97579 | 0.96842 | 0.96105 | 0.95368 | 0.94632 | 0.94105 | 0.93474 | 0.92947 | 0.91053 | 0.89053 | 0.87579
|  | STRONSAY | HT |  |  |  |  | 0.99158 | 0.98737 | 0.98211 | 0.97789 | 0.97263 | 0.96526 | 0.95895 | 0.95474 | 0.95053 | 0.94105 | 0.92105 | 0.90421 | 0.89474 | 0.98947 | 0.98421 | 0.97789 | 0.97263 | 0.96526 | 0.95579 | 0.94947 | 0.94421 | 0.93789 | 0.92737 | 0.90632 | 0.88632 | 0.87053 | 0.98947 | 0.98421 | 0.97789 | 0.97263 | 0.96632 | 0.95684 | 0.94947 | 0.94421 | 0.93789 | 0.92737 | 0.90632 | 0.88632 | 0.87053
|  | STRONSAY | HE |  |  |  |  | 0.99579 | 0.99158 | 0.98842 | 0.98526 | 0.98316 | 0.97895 | 0.97263 | 0.97158 | 0.96632 | 0.96526 | 0.95368 | 0.94526 | 0.94 | 0.99474 | 0.98947 | 0.98632 | 0.98211 | 0.98 | 0.97474 | 0.96842 | 0.96632 | 0.96105 | 0.95789 | 0.94526 | 0.93368 | 0.92737 | 0.99474 | 0.98947 | 0.98632 | 0.98211 | 0.98 | 0.97474 | 0.96842 | 0.96632 | 0.96105 | 0.95789 | 0.94526 | 0.93368 | 0.92737
|  | STRONSAY | FB |  |  |  |  | 0.99684 | 0.99474 | 0.99368 | 0.99053 | 0.98842 | 0.98526 | 0.98316 | 0.98105 | 0.98 | 0.97684 | 0.96632 | 0.95474 | 0.94526 | 0.99579 | 0.99368 | 0.99158 | 0.98842 | 0.98526 | 0.98211 | 0.97895 | 0.97579 | 0.97474 | 0.97158 | 0.95684 | 0.94211 | 0.93053 | 0.99579 | 0.99368 | 0.99158 | 0.98842 | 0.98526 | 0.98211 | 0.97895 | 0.97579 | 0.97474 | 0.97158 | 0.95684 | 0.94211 | 0.93053
| FORT WILLIAM | STRONTIAN | MINIMUM HEADROOM | NM 81521 61955 | YES | NO | 0 | 0.97895 | 0.96737 | 0.95789 | 0.94526 | 0.93368 | 0.68316 | 0.52316 | 0.42211 | 0.37684 | 0.36737 | 0.31684 | 0.28421 | 0.25684 | 1.0295 | 1.0179 | 1.0084 | 0.99579 | 0.98316 | 0.69053 | 0.5 | 0.38 | 0.32842 | 0.31789 | 0.27158 | 0.23789 | 0.21053 | 0.97263 | 0.95895 | 0.94737 | 0.93368 | 0.92105 | 0.62 | 0.42737 | 0.30632 | 0.25368 | 0.24211 | 0.18526 | 0.14842 | 0.11684
|  | STRONTIAN | EE |  |  |  |  | 0.97895 | 0.96737 | 0.95789 | 0.94526 | 0.93368 | 0.92316 | 0.87895 | 0.64526 | 0.49474 | 0.39263 | 0.31684 | 0.28421 | 0.25684 | 1.0295 | 1.0179 | 1.0084 | 0.99579 | 0.98316 | 0.97263 | 0.92526 | 0.65263 | 0.47579 | 0.35368 | 0.27158 | 0.23789 | 0.21053 | 0.97263 | 0.95895 | 0.94737 | 0.93368 | 0.92105 | 0.90737 | 0.85684 | 0.57684 | 0.39684 | 0.27263 | 0.18526 | 0.14842 | 0.11684
|  | STRONTIAN | HT |  |  |  |  | 0.98316 | 0.97474 | 0.96526 | 0.95579 | 0.94211 | 0.68316 | 0.52316 | 0.42211 | 0.37684 | 0.36737 | 0.32105 | 0.29053 | 0.26842 | 1.0337 | 1.0232 | 1.0137 | 1.0042 | 0.98947 | 0.69053 | 0.5 | 0.38 | 0.32842 | 0.31789 | 0.27474 | 0.24 | 0.21053 | 0.97684 | 0.96737 | 0.95684 | 0.94632 | 0.93053 | 0.62 | 0.42737 | 0.30632 | 0.25368 | 0.24211 | 0.19684 | 0.16211 | 0.13053
|  | STRONTIAN | HE |  |  |  |  | 0.98947 | 0.98316 | 0.97789 | 0.97053 | 0.96526 | 0.95053 | 0.91895 | 0.66632 | 0.51053 | 0.41474 | 0.38947 | 0.37368 | 0.36105 | 1.04 | 1.0326 | 1.0274 | 1.0211 | 1.0158 | 1.0011 | 0.96526 | 0.66947 | 0.48632 | 0.37158 | 0.34526 | 0.32842 | 0.31474 | 0.98421 | 0.97684 | 0.97158 | 0.96316 | 0.95789 | 0.94105 | 0.90316 | 0.59895 | 0.41368 | 0.29684 | 0.26842 | 0.25053 | 0.23684
|  | STRONTIAN | FB |  |  |  |  | 0.99368 | 0.98947 | 0.98526 | 0.98 | 0.97684 | 0.97263 | 0.96211 | 0.95053 | 0.84211 | 0.76316 | 0.62211 | 0.60316 | 0.58947 | 1.0411 | 1.04 | 1.0358 | 1.0305 | 1.0274 | 1.0232 | 1.0105 | 0.99789 | 0.87474 | 0.78105 | 0.61368 | 0.59368 | 0.57789 | 0.98842 | 0.98421 | 0.97895 | 0.97368 | 0.96947 | 0.96526 | 0.95263 | 0.93789 | 0.80842 | 0.71368 | 0.54421 | 0.52316 | 0.50737
| SHETLAND | SUMBURGH | MINIMUM HEADROOM | HU3900512755 | YES | YES | 0 | 0.96316 | 0.94316 | 0.92526 | 0.90632 | 0.88947 | 0.86947 | 0.85158 | 0.83368 | 0.81684 | 0.80211 | 0.73895 | 0.69158 | 0.65895 | 0.96947 | 0.95263 | 0.93684 | 0.92105 | 0.90632 | 0.88842 | 0.87263 | 0.85579 | 0.84211 | 0.82842 | 0.77789 | 0.73579 | 0.70211 | 0.95684 | 0.93474 | 0.91474 | 0.89263 | 0.87368 | 0.85263 | 0.83263 | 0.81263 | 0.79368 | 0.77684 | 0.71368 | 0.65789 | 0.61895
|  | SUMBURGH | EE |  |  |  |  | 0.96316 | 0.94316 | 0.92526 | 0.90632 | 0.88947 | 0.86947 | 0.85158 | 0.83368 | 0.81684 | 0.80211 | 0.74421 | 0.69474 | 0.66421 | 0.96947 | 0.95263 | 0.93684 | 0.92105 | 0.90632 | 0.88842 | 0.87263 | 0.85579 | 0.84211 | 0.82842 | 0.77789 | 0.73579 | 0.70842 | 0.95684 | 0.93474 | 0.91474 | 0.89263 | 0.87368 | 0.85263 | 0.83263 | 0.81263 | 0.79368 | 0.77684 | 0.71368 | 0.65789 | 0.62211
|  | SUMBURGH | HT |  |  |  |  | 0.96737 | 0.95053 | 0.93368 | 0.91684 | 0.89789 | 0.88211 | 0.86316 | 0.84526 | 0.82947 | 0.81053 | 0.73895 | 0.69158 | 0.65895 | 0.97263 | 0.95789 | 0.94316 | 0.92842 | 0.91158 | 0.89789 | 0.88211 | 0.86526 | 0.85053 | 0.83474 | 0.78211 | 0.73895 | 0.70211 | 0.96316 | 0.94316 | 0.92421 | 0.90526 | 0.88421 | 0.86632 | 0.84632 | 0.82632 | 0.80842 | 0.78842 | 0.72316 | 0.66632 | 0.61895
|  | SUMBURGH | HE |  |  |  |  | 0.97789 | 0.96737 | 0.95579 | 0.94421 | 0.93053 | 0.91684 | 0.90211 | 0.89053 | 0.87895 | 0.87053 | 0.84105 | 0.81684 | 0.79895 | 0.98105 | 0.97158 | 0.96105 | 0.95053 | 0.93895 | 0.92632 | 0.91158 | 0.90211 | 0.89158 | 0.88421 | 0.85789 | 0.83789 | 0.82316 | 0.97579 | 0.96316 | 0.95053 | 0.93789 | 0.92316 | 0.90842 | 0.89263 | 0.88 | 0.86737 | 0.85789 | 0.82421 | 0.79684 | 0.77684
|  | SUMBURGH | FB |  |  |  |  | 0.98737 | 0.98 | 0.97053 | 0.96421 | 0.95579 | 0.94632 | 0.93895 | 0.93053 | 0.92211 | 0.91263 | 0.88 | 0.84632 | 0.82105 | 0.98947 | 0.98316 | 0.97579 | 0.96947 | 0.96211 | 0.95474 | 0.94842 | 0.94105 | 0.93368 | 0.92526 | 0.89789 | 0.86947 | 0.84842 | 0.98526 | 0.97684 | 0.96632 | 0.95895 | 0.94947 | 0.93895 | 0.93053 | 0.92105 | 0.91158 | 0.90105 | 0.86316 | 0.82526 | 0.79474
| ALNESS | TAIN | MINIMUM HEADROOM | NH 77578 81489 | NO | YES | 0.069388 | 16.2679 | 16.2426 | 16.2216 | 24.9253 | 24.8926 | 23.5516 | 22.1221 | 20.5726 | 19.58 | 19.0684 | 18.2347 | 17.9853 | 17.8063 | 13.4547 | 13.3358 | 13.2158 | 21.3 | 21.2179 | 19.7758 | 18.3758 | 16.8568 | 15.8853 | 15.3832 | 14.6063 | 14.3653 | 14.1421 | 15.3097 | 15.2845 | 15.2634 | 23.6758 | 23.5874 | 21.9074 | 20.2705 | 18.4832 | 17.3189 | 16.7211 | 15.8021 | 15.5284 | 15.2747
|  | TAIN | EE |  |  |  |  | 16.2679 | 16.2426 | 16.2216 | 24.9274 | 24.8989 | 24.8316 | 24.4716 | 23.2695 | 21.7905 | 20.2716 | 18.2768 | 18.0337 | 17.8537 | 13.4547 | 13.3358 | 13.2158 | 21.3 | 21.2179 | 21.1305 | 20.7189 | 19.4979 | 18.0495 | 16.5621 | 14.6063 | 14.3674 | 14.1895 | 15.3097 | 15.2845 | 15.2634 | 23.6758 | 23.5874 | 23.4926 | 23.0221 | 21.5937 | 19.8989 | 18.1389 | 15.8021 | 15.5284 | 15.3221
|  | TAIN | HT |  |  |  |  | 16.2711 | 16.2479 | 16.2237 | 24.9253 | 24.8926 | 23.5516 | 22.1221 | 20.5726 | 19.58 | 19.0684 | 18.2347 | 17.9853 | 17.8063 | 13.4747 | 13.3642 | 13.2484 | 21.3411 | 21.2537 | 19.7758 | 18.3758 | 16.8568 | 15.8853 | 15.3832 | 14.6253 | 14.3653 | 14.1421 | 15.3129 | 15.2897 | 15.2655 | 23.7221 | 23.6274 | 21.9074 | 20.2705 | 18.4832 | 17.3189 | 16.7211 | 15.8284 | 15.5305 | 15.2747
|  | TAIN | HE |  |  |  |  | 16.2784 | 16.2553 | 16.2374 | 24.9432 | 24.9147 | 24.8716 | 24.6368 | 23.3737 | 21.7789 | 20.1042 | 18.6916 | 18.5453 | 18.4411 | 13.5189 | 13.4242 | 13.3295 | 21.4453 | 21.3874 | 21.1737 | 20.9084 | 19.6011 | 18.0379 | 16.3989 | 15.0147 | 14.8705 | 14.7674 | 15.3203 | 15.2971 | 15.2792 | 23.76 | 23.7316 | 23.54 | 23.24 | 21.7105 | 19.8811 | 17.9337 | 16.2747 | 16.1084 | 15.9884
|  | TAIN | FB |  |  |  |  | 16.2921 | 16.2837 | 16.2742 | 24.9947 | 24.9832 | 24.9726 | 24.9611 | 24.9495 | 24.4674 | 23.8242 | 21.3768 | 21.2137 | 21.0853 | 13.56 | 13.5105 | 13.4568 | 21.6589 | 21.6242 | 21.5895 | 21.4305 | 21.2884 | 20.6958 | 20.0442 | 17.6474 | 17.4863 | 17.36 | 15.3339 | 15.3255 | 15.3161 | 23.8116 | 23.8 | 23.7895 | 23.7779 | 23.66 | 22.9747 | 22.2126 | 19.4074 | 19.2253 | 19.0811
| ARDMORE / HARRIS GRID | TARBERT | MINIMUM HEADROOM | NB 15289 00157 | NO | YES | 0 | 0.94632 | 0.89053 | 0.84316 | 0.81474 | 0.77684 | 0.72316 | 0.69368 | 0.66632 | 0.64 | 0.61684 | 0.52632 | 0.44737 | 0.39368 | 1.1432 | 1.1053 | 1.0537 | 1.0232 | 0.98211 | 0.92 | 0.88842 | 0.85895 | 0.83053 | 0.80421 | 0.70632 | 0.61895 | 0.55789 | 0.98316 | 0.97053 | 0.95579 | 0.94316 | 0.92526 | 0.90526 | 0.87368 | 0.84421 | 0.81474 | 0.78947 | 0.69053 | 0.60211 | 0.54105
|  | TARBERT | EE |  |  |  |  | 0.94632 | 0.91789 | 0.84316 | 0.81474 | 0.78737 | 0.72316 | 0.69368 | 0.66632 | 0.64 | 0.61684 | 0.52632 | 0.44737 | 0.39368 | 1.1432 | 1.1326 | 1.0537 | 1.0232 | 0.99368 | 0.92 | 0.88842 | 0.85895 | 0.83053 | 0.80421 | 0.70632 | 0.61895 | 0.55789 | 0.98316 | 0.97263 | 0.95579 | 0.94316 | 0.92947 | 0.90526 | 0.87368 | 0.84421 | 0.81474 | 0.78947 | 0.69053 | 0.60211 | 0.54105
|  | TARBERT | HT |  |  |  |  | 0.95368 | 0.89053 | 0.86526 | 0.84 | 0.77684 | 0.74947 | 0.72316 | 0.69579 | 0.66737 | 0.64 | 0.53053 | 0.45263 | 0.39789 | 1.1442 | 1.1053 | 1.0789 | 1.0516 | 0.98211 | 0.95158 | 0.92211 | 0.89263 | 0.86316 | 0.83263 | 0.73368 | 0.64105 | 0.56632 | 0.98526 | 0.97053 | 0.95789 | 0.94632 | 0.92526 | 0.91158 | 0.89684 | 0.87789 | 0.84842 | 0.81789 | 0.71789 | 0.62526 | 0.54947
|  | TARBERT | HE |  |  |  |  | 0.97158 | 0.95474 | 0.88842 | 0.87158 | 0.85368 | 0.79789 | 0.77579 | 0.75789 | 0.74 | 0.72842 | 0.68105 | 0.64105 | 0.61368 | 1.1474 | 1.14 | 1.1032 | 1.0853 | 1.0663 | 1.0074 | 0.98421 | 0.96526 | 0.94526 | 0.93263 | 0.88 | 0.83474 | 0.80421 | 0.98842 | 0.98 | 0.96737 | 0.95684 | 0.94421 | 0.92421 | 0.90842 | 0.89789 | 0.88737 | 0.88316 | 0.85895 | 0.82 | 0.78947
|  | TARBERT | FB |  |  |  |  | 0.98316 | 0.97158 | 0.95895 | 0.92737 | 0.91474 | 0.90211 | 0.87474 | 0.86211 | 0.84947 | 0.83368 | 0.78 | 0.72632 | 0.68526 | 1.1537 | 1.1505 | 1.1463 | 1.14 | 1.1316 | 1.1179 | 1.0874 | 1.0747 | 1.0611 | 1.0453 | 0.98632 | 0.92632 | 0.88 | 0.99474 | 0.99158 | 0.98632 | 0.98 | 0.97579 | 0.97053 | 0.96316 | 0.95789 | 0.95158 | 0.94421 | 0.92 | 0.89895 | 0.86526
| PORT ANN | TARBERT JURA | MINIMUM HEADROOM | NR 60552 82166 | YES | YES | 0 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19789 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.19895
|  | TARBERT JURA | EE |  |  |  |  | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2
|  | TARBERT JURA | HT |  |  |  |  | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.19789 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.19895
|  | TARBERT JURA | HE |  |  |  |  | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211
|  | TARBERT JURA | FB |  |  |  |  | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20105
| PORT ANN | TARBERT LOCH FYNE | MINIMUM HEADROOM | NR 86003 68479 | NO | YES | 0 | 3.2053 | 3.1937 | 3.1863 | 3.1768 | 3.1632 | 3.1463 | 3.1295 | 3.1147 | 3.0747 | 3.0411 | 2.8758 | 2.7516 | 2.6579 | 2.7947 | 2.7842 | 2.7674 | 2.7242 | 2.6853 | 2.6358 | 2.5737 | 2.5242 | 2.4789 | 2.4432 | 2.2747 | 2.1453 | 2.0495 | 3.0526 | 3.0084 | 2.9789 | 2.9347 | 2.8968 | 2.8495 | 2.7884 | 2.7358 | 2.6821 | 2.6442 | 2.4621 | 2.3253 | 2.2189
|  | TARBERT LOCH FYNE | EE |  |  |  |  | 3.2053 | 3.1937 | 3.1863 | 3.1768 | 3.1632 | 3.1463 | 3.1295 | 3.1147 | 3.0747 | 3.0411 | 2.8758 | 2.7516 | 2.6579 | 2.7947 | 2.7842 | 2.7674 | 2.7242 | 2.6853 | 2.6432 | 2.5947 | 2.5326 | 2.4789 | 2.4442 | 2.2747 | 2.1453 | 2.0495 | 3.0526 | 3.0084 | 2.9789 | 2.9347 | 2.8968 | 2.8547 | 2.8053 | 2.7411 | 2.6821 | 2.6442 | 2.4621 | 2.3253 | 2.2189
|  | TARBERT LOCH FYNE | HT |  |  |  |  | 3.2084 | 3.1979 | 3.1874 | 3.1768 | 3.1642 | 3.1526 | 3.1389 | 3.1242 | 3.0821 | 3.0442 | 2.8916 | 2.7758 | 2.6947 | 2.7979 | 2.7884 | 2.7726 | 2.7358 | 2.7 | 2.6358 | 2.5737 | 2.5242 | 2.4821 | 2.4432 | 2.3147 | 2.1853 | 2.0768 | 3.0589 | 3.0168 | 2.9874 | 2.9495 | 2.9137 | 2.8495 | 2.7884 | 2.7358 | 2.6905 | 2.6484 | 2.5116 | 2.3768 | 2.2642
|  | TARBERT LOCH FYNE | HE |  |  |  |  | 3.2116 | 3.2011 | 3.1947 | 3.1863 | 3.1737 | 3.1589 | 3.1432 | 3.1347 | 3.1253 | 3.12 | 3.0979 | 3.0442 | 2.9989 | 2.8011 | 2.7916 | 2.7853 | 2.7758 | 2.7642 | 2.7495 | 2.7 | 2.6558 | 2.6147 | 2.5968 | 2.5105 | 2.4453 | 2.4011 | 3.0789 | 3.0495 | 3.0316 | 3.0095 | 2.9895 | 2.9663 | 2.9137 | 2.8695 | 2.8284 | 2.8095 | 2.7221 | 2.6505 | 2.6
|  | TARBERT LOCH FYNE | FB |  |  |  |  | 3.2158 | 3.2116 | 3.2074 | 3.2032 | 3.1979 | 3.1926 | 3.1874 | 3.1821 | 3.1758 | 3.1695 | 3.1484 | 3.1095 | 3.0474 | 2.8053 | 2.8011 | 2.7968 | 2.7926 | 2.7874 | 2.7821 | 2.7768 | 2.7716 | 2.7516 | 2.7305 | 2.6137 | 2.5084 | 2.4453 | 3.1032 | 3.0916 | 3.0779 | 3.0642 | 3.0516 | 3.0379 | 3.0242 | 3.0011 | 2.9663 | 2.9453 | 2.8305 | 2.7189 | 2.6495
| TAYNUILT | TAYNUILT | MINIMUM HEADROOM | NN 01856 31079 | NO | YES | 0 | 1.8211 | 1.7432 | 1.6632 | 1.58 | 1.4937 | 1.4147 | 1.3347 | 1.2537 | 1.1737 | 1.0905 | 0.75579 | 0.18316 | -0.40316 | 2.4684 | 2.3221 | 2.1411 | 1.9853 | 1.8295 | 1.6811 | 1.5368 | 1.3905 | 1.2432 | 1.0916 | 0.56632 | -0.0031579 | -0.57368 | 2.4347 | 2.2968 | 2.0726 | 1.9137 | 1.7684 | 1.6168 | 1.4768 | 1.3411 | 1.1968 | 1.0389 | 0.49053 | -0.10526 | -0.70105
|  | TAYNUILT | EE |  |  |  |  | 1.8211 | 1.7432 | 1.6632 | 1.58 | 1.4937 | 1.4147 | 1.3347 | 1.2537 | 1.1737 | 1.0905 | 0.75579 | 0.18316 | -0.40316 | 2.4684 | 2.3221 | 2.1411 | 1.9853 | 1.8295 | 1.6811 | 1.5368 | 1.3905 | 1.2432 | 1.0916 | 0.56632 | -0.0031579 | -0.57368 | 2.4347 | 2.2968 | 2.0726 | 1.9137 | 1.7684 | 1.6168 | 1.4768 | 1.3411 | 1.1968 | 1.0389 | 0.49053 | -0.10526 | -0.70105
|  | TAYNUILT | HT |  |  |  |  | 1.8726 | 1.8453 | 1.8179 | 1.7916 | 1.7621 | 1.7337 | 1.7042 | 1.6768 | 1.6474 | 1.6168 | 1.4768 | 1.3484 | 1.2432 | 2.5453 | 2.44 | 2.3895 | 2.3316 | 2.2842 | 2.2126 | 2.1674 | 2.1242 | 2.0758 | 2.0232 | 1.8274 | 1.5979 | 1.3705 | 2.52 | 2.4063 | 2.3484 | 2.2811 | 2.2274 | 2.1484 | 2.0947 | 2.0432 | 1.9916 | 1.9379 | 1.7379 | 1.5011 | 1.2695
|  | TAYNUILT | HE |  |  |  |  | 1.8747 | 1.8474 | 1.8232 | 1.7958 | 1.7695 | 1.7389 | 1.7095 | 1.6821 | 1.6547 | 1.6305 | 1.5316 | 1.4116 | 1.2905 | 2.5568 | 2.5147 | 2.3937 | 2.3389 | 2.3021 | 2.2368 | 2.1968 | 2.1558 | 2.1095 | 2.0663 | 1.8979 | 1.6916 | 1.4716 | 2.5326 | 2.4811 | 2.3516 | 2.2895 | 2.2463 | 2.1716 | 2.1242 | 2.08 | 2.0316 | 1.9895 | 1.8168 | 1.6084 | 1.4042
|  | TAYNUILT | FB |  |  |  |  | 1.8926 | 1.8853 | 1.8779 | 1.8705 | 1.8632 | 1.8558 | 1.8474 | 1.8411 | 1.8337 | 1.8274 | 1.7989 | 1.7726 | 1.7516 | 2.5811 | 2.5674 | 2.5484 | 2.4968 | 2.4821 | 2.4632 | 2.4432 | 2.4295 | 2.4168 | 2.4021 | 2.3453 | 2.2863 | 2.2379 | 2.5621 | 2.5463 | 2.5263 | 2.4716 | 2.4558 | 2.4326 | 2.4126 | 2.3979 | 2.3821 | 2.3663 | 2.3021 | 2.2368 | 2.1832
| BURGHMUIR | THIMBLEROW | MINIMUM HEADROOM | NO 11356 23764 | NO | YES | 0 | 26.3484 | 26.3074 | 26.26 | 26.2095 | 26.1495 | 26.0916 | 26.0295 | 25.9642 | 25.8968 | 25.8242 | 25.56 | 25.4021 | 25.1874 | 26.4453 | 26.3242 | 26.2221 | 26.0705 | 25.9347 | 25.7789 | 25.62 | 25.4716 | 25.3221 | 25.2 | 24.6832 | 24.12 | 23.6074 | 25.8 | 25.7432 | 25.6874 | 25.6189 | 25.5421 | 25.4663 | 25.3874 | 25.3053 | 25.2211 | 25.1326 | 24.5495 | 23.84 | 23.1411
|  | THIMBLEROW | EE |  |  |  |  | 26.3484 | 26.3074 | 26.2758 | 26.2379 | 26.1895 | 26.1232 | 26.0526 | 25.9989 | 25.9442 | 25.9021 | 25.7105 | 25.5716 | 25.3263 | 26.4453 | 26.3242 | 26.2221 | 26.0705 | 25.9347 | 25.7789 | 25.62 | 25.4716 | 25.3221 | 25.2 | 24.6842 | 24.1684 | 23.7432 | 25.8 | 25.7432 | 25.6968 | 25.6368 | 25.5705 | 25.4863 | 25.3979 | 25.3253 | 25.2516 | 25.1916 | 24.5495 | 23.8432 | 23.2484
|  | THIMBLEROW | HT |  |  |  |  | 26.3495 | 26.3074 | 26.26 | 26.2095 | 26.1495 | 26.0916 | 26.0295 | 25.9642 | 25.8968 | 25.8242 | 25.56 | 25.4021 | 25.1874 | 26.4632 | 26.3484 | 26.2347 | 26.1021 | 25.9589 | 25.8126 | 25.6642 | 25.5137 | 25.3611 | 25.2116 | 24.6832 | 24.12 | 23.6074 | 25.8042 | 25.7474 | 25.6874 | 25.6189 | 25.5421 | 25.4663 | 25.3874 | 25.3053 | 25.2211 | 25.1326 | 24.6032 | 23.84 | 23.1411
|  | THIMBLEROW | HE |  |  |  |  | 26.3642 | 26.3211 | 26.2905 | 26.2474 | 26.1937 | 26.1253 | 26.0516 | 26.0095 | 25.9663 | 25.9495 | 25.8526 | 25.78 | 25.7316 | 26.5274 | 26.4326 | 26.3621 | 26.2758 | 26.1958 | 26.0989 | 25.9884 | 25.8979 | 25.7968 | 25.7326 | 25.44 | 25.14 | 24.8884 | 25.8295 | 25.7758 | 25.7368 | 25.6853 | 25.6263 | 25.5526 | 25.4716 | 25.4189 | 25.3642 | 25.3379 | 25.2021 | 25.0832 | 24.8474
|  | THIMBLEROW | FB |  |  |  |  | 26.3821 | 26.3632 | 26.3432 | 26.3221 | 26.2979 | 26.2737 | 26.2484 | 26.2221 | 26.1958 | 26.1663 | 26.0611 | 25.9716 | 25.9232 | 26.5842 | 26.5358 | 26.4863 | 26.4347 | 26.3832 | 26.3305 | 26.2768 | 26.2137 | 26.1316 | 26.0484 | 25.7032 | 25.34 | 25.0558 | 25.8547 | 25.8305 | 25.8042 | 25.7768 | 25.7474 | 25.7179 | 25.6863 | 25.6526 | 25.6147 | 25.5747 | 25.4211 | 25.2768 | 25.0011
| TAYNUILT | TIRORAN BRIDGE | MINIMUM HEADROOM | NM 48666 28729 | YES | YES | 0 | 0.20421 | 0.20316 | 0.20316 | 0.20105 | 0.2 | 0.2 | 0.19684 | 0.19684 | 0.19579 | 0.19368 | 0.19053 | 0.18842 | 0.18737 | 0.20526 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.2 | 0.19684 | 0.19579 | 0.19474 | 0.19368 | 0.18842 | 0.18632 | 0.18526 | 0.20526 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.2 | 0.19684 | 0.19579 | 0.19474 | 0.19368 | 0.18842 | 0.18632 | 0.18526
|  | TIRORAN BRIDGE | EE |  |  |  |  | 0.20421 | 0.20316 | 0.20316 | 0.20105 | 0.2 | 0.2 | 0.19684 | 0.19684 | 0.19579 | 0.19368 | 0.19053 | 0.18842 | 0.18737 | 0.20526 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.2 | 0.19684 | 0.19579 | 0.19474 | 0.19368 | 0.18842 | 0.18632 | 0.18526 | 0.20526 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.2 | 0.19684 | 0.19579 | 0.19474 | 0.19368 | 0.18842 | 0.18632 | 0.18526
|  | TIRORAN BRIDGE | HT |  |  |  |  | 0.20421 | 0.20421 | 0.20316 | 0.20316 | 0.20105 | 0.2 | 0.19895 | 0.19684 | 0.19684 | 0.19474 | 0.19053 | 0.18947 | 0.18842 | 0.20526 | 0.20526 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.19895 | 0.19684 | 0.19579 | 0.19368 | 0.19158 | 0.18947 | 0.18737 | 0.20526 | 0.20526 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.19895 | 0.19684 | 0.19579 | 0.19368 | 0.19158 | 0.18947 | 0.18737
|  | TIRORAN BRIDGE | HE |  |  |  |  | 0.20421 | 0.20421 | 0.20421 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.20526 | 0.20526 | 0.20526 | 0.20421 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.20526 | 0.20526 | 0.20526 | 0.20421 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.20105 | 0.2 | 0.2
|  | TIRORAN BRIDGE | FB |  |  |  |  | 0.20526 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.2 | 0.19895 | 0.20632 | 0.20526 | 0.20526 | 0.20526 | 0.20526 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.2 | 0.20632 | 0.20526 | 0.20526 | 0.20526 | 0.20526 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.2
| BOAT OF GARTEN | TOMATIN | MINIMUM HEADROOM | NH 79106 29734 | YES | YES | 0 | 1.1611 | 1.1505 | 1.1421 | 1.1337 | 1.1253 | 0.84 | 0.52 | 0.29263 | 0.21263 | 0.20421 | 0.16947 | 0.14632 | 0.12842 | 1.0421 | 1.0305 | 1.0211 | 1.0116 | 1.0021 | 0.66526 | 0.28737 | 0.018947 | -0.074737 | -0.084211 | -0.11895 | -0.14526 | -0.16737 | 0.92632 | 0.91474 | 0.90526 | 0.89579 | 0.88632 | 0.55053 | 0.17368 | -0.093684 | -0.18737 | -0.19579 | -0.23158 | -0.25684 | -0.28
|  | TOMATIN | EE |  |  |  |  | 1.1611 | 1.1505 | 1.1421 | 1.1337 | 1.1253 | 1.1147 | 1.0516 | 0.75368 | 0.46737 | 0.27263 | 0.17263 | 0.14947 | 0.13263 | 1.0421 | 1.0305 | 1.0211 | 1.0116 | 1.0021 | 0.99053 | 0.91684 | 0.56421 | 0.22632 | -0.0031579 | -0.11895 | -0.14526 | -0.16421 | 0.92632 | 0.91474 | 0.90526 | 0.89579 | 0.88632 | 0.87474 | 0.80105 | 0.44947 | 0.11368 | -0.11579 | -0.23158 | -0.25684 | -0.27684
|  | TOMATIN | HT |  |  |  |  | 1.1621 | 1.1537 | 1.1474 | 1.1368 | 1.1284 | 0.84 | 0.52 | 0.29263 | 0.21263 | 0.20421 | 0.16947 | 0.14632 | 0.12842 | 1.0442 | 1.0347 | 1.0263 | 1.0147 | 1.0053 | 0.66526 | 0.28737 | 0.018947 | -0.074737 | -0.084211 | -0.11579 | -0.14316 | -0.16737 | 0.92842 | 0.91895 | 0.91158 | 0.9 | 0.88947 | 0.55053 | 0.17368 | -0.093684 | -0.18737 | -0.19579 | -0.22842 | -0.25579 | -0.28
|  | TOMATIN | HE |  |  |  |  | 1.1695 | 1.1632 | 1.1579 | 1.1537 | 1.1474 | 1.1221 | 1.0716 | 0.76421 | 0.44211 | 0.24842 | 0.22 | 0.20737 | 0.19895 | 1.0516 | 1.0442 | 1.0389 | 1.0337 | 1.0274 | 0.99789 | 0.93895 | 0.57684 | 0.19579 | -0.033684 | -0.065263 | -0.08 | -0.089474 | 0.93579 | 0.92947 | 0.92316 | 0.91895 | 0.91158 | 0.88316 | 0.82316 | 0.46211 | 0.083158 | -0.14526 | -0.17789 | -0.19263 | -0.20211
|  | TOMATIN | FB |  |  |  |  | 1.1726 | 1.1695 | 1.1663 | 1.1621 | 1.1579 | 1.1547 | 1.1274 | 1.0895 | 0.97789 | 0.83895 | 0.59368 | 0.57789 | 0.56316 | 1.0558 | 1.0516 | 1.0474 | 1.0432 | 1.0379 | 1.0347 | 1.0021 | 0.95789 | 0.82632 | 0.66211 | 0.37368 | 0.35474 | 0.33789 | 0.94 | 0.93579 | 0.93263 | 0.92737 | 0.92316 | 0.91895 | 0.88632 | 0.84316 | 0.71158 | 0.54737 | 0.26 | 0.24105 | 0.22421
| LAIRG | TORBOLL | MINIMUM HEADROOM | NC 75779 00296 | YES | YES | 0 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947
|  | TORBOLL | EE |  |  |  |  | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947
|  | TORBOLL | HT |  |  |  |  | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947
|  | TORBOLL | HE |  |  |  |  | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1
|  | TORBOLL | FB |  |  |  |  | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1
| KINTORE | TORRYBURN | MINIMUM HEADROOM | NJ 79129 15653 | NO | YES | 0.82857 | 23.5095 | 22.9463 | 22.3768 | 21.3474 | 20.6874 | 19.7095 | 18.7221 | 18.0779 | 17.4705 | 15.7979 | 13.1737 | 11.6305 | 11.26 | 20.1947 | 19.4926 | 18.7811 | 17.5516 | 16.7958 | 15.6684 | 14.5337 | 13.7947 | 13.1 | 11.1684 | 8.5021 | 7.1253 | 6.7074 | 21.3768 | 20.6842 | 19.9832 | 18.7684 | 18.0042 | 16.8642 | 15.7158 | 14.9695 | 14.2663 | 12.3137 | 9.4221 | 7.8137 | 7.3916
|  | TORRYBURN | EE |  |  |  |  | 23.5095 | 22.9463 | 22.3905 | 21.4463 | 20.8063 | 19.7095 | 18.7221 | 18.0779 | 17.4705 | 15.8737 | 13.1737 | 11.6305 | 11.26 | 20.1947 | 19.4926 | 18.7979 | 17.6663 | 16.9305 | 15.6684 | 14.5337 | 13.7947 | 13.1 | 11.2526 | 8.5021 | 7.1253 | 6.7074 | 21.3768 | 20.6842 | 19.9989 | 18.8832 | 18.1411 | 16.8642 | 15.7158 | 14.9695 | 14.2663 | 12.3989 | 9.4221 | 7.8137 | 7.3916
|  | TORRYBURN | HT |  |  |  |  | 23.5221 | 23.0116 | 22.3768 | 21.3474 | 20.6874 | 20.1579 | 19.5695 | 18.8832 | 18.0495 | 15.7979 | 13.2632 | 11.8937 | 11.5253 | 20.2084 | 19.5737 | 18.7811 | 17.5516 | 16.7958 | 16.1905 | 15.5168 | 14.7305 | 13.7726 | 11.1684 | 8.6958 | 7.4021 | 6.8789 | 21.3905 | 20.7642 | 19.9832 | 18.7684 | 18.0042 | 17.3926 | 16.7105 | 15.9168 | 14.9484 | 12.3137 | 9.6589 | 8.1779 | 7.6484
|  | TORRYBURN | HE |  |  |  |  | 23.5821 | 23.1263 | 22.5832 | 21.6737 | 21.0832 | 20.1589 | 19.0926 | 18.4547 | 17.8621 | 16.2632 | 14.4968 | 13.8411 | 13.6179 | 20.2811 | 19.7137 | 19.0337 | 17.9242 | 17.2474 | 16.1853 | 14.9579 | 14.2242 | 13.5432 | 11.6916 | 9.7947 | 9.2 | 8.9463 | 21.4621 | 20.9032 | 20.2326 | 19.1389 | 18.46 | 17.3863 | 16.1453 | 15.4032 | 14.7158 | 12.8411 | 10.8453 | 10.1558 | 9.9
|  | TORRYBURN | FB |  |  |  |  | 24.2295 | 24.0558 | 23.8368 | 23.5432 | 23.3442 | 22.9768 | 22.54 | 21.9779 | 21.6305 | 20.9221 | 19.9347 | 19.2663 | 19.0389 | 21.0937 | 20.8768 | 20.6042 | 20.2358 | 19.9874 | 19.5263 | 18.9768 | 18.2716 | 17.8716 | 17.0526 | 15.9189 | 15.1526 | 14.8937 | 22.2632 | 22.0495 | 21.78 | 21.4168 | 21.1726 | 20.7179 | 20.1758 | 19.4811 | 19.0874 | 18.2621 | 17.1168 | 16.3421 | 16.08
| LAIRG | TRESSADY | MINIMUM HEADROOM | NC 70537 03678 | YES | YES | 0 | 0.58526 | 0.57684 | 0.57053 | 0.56316 | 0.55579 | 0.54947 | 0.54 | 0.53474 | 0.52737 | 0.52316 | 0.49579 | 0.47474 | 0.46 | 0.52316 | 0.51368 | 0.50632 | 0.49789 | 0.48842 | 0.48105 | 0.47158 | 0.46421 | 0.45684 | 0.45158 | 0.42421 | 0.40105 | 0.38 | 0.52632 | 0.51895 | 0.51368 | 0.50737 | 0.5 | 0.49368 | 0.48421 | 0.47789 | 0.47053 | 0.46526 | 0.44 | 0.41684 | 0.39579
|  | TRESSADY | EE |  |  |  |  | 0.58526 | 0.57684 | 0.57053 | 0.56316 | 0.55579 | 0.54947 | 0.54 | 0.53474 | 0.52737 | 0.52316 | 0.49895 | 0.48105 | 0.46526 | 0.52316 | 0.51368 | 0.50632 | 0.49789 | 0.48842 | 0.48105 | 0.47158 | 0.46421 | 0.45684 | 0.45158 | 0.42421 | 0.40211 | 0.38421 | 0.52632 | 0.51895 | 0.51368 | 0.50737 | 0.5 | 0.49368 | 0.48421 | 0.47789 | 0.47053 | 0.46526 | 0.44 | 0.41789 | 0.4
|  | TRESSADY | HT |  |  |  |  | 0.58526 | 0.58 | 0.57263 | 0.56632 | 0.55789 | 0.55053 | 0.54421 | 0.53684 | 0.53053 | 0.52316 | 0.49579 | 0.47474 | 0.46 | 0.52526 | 0.51684 | 0.50842 | 0.50105 | 0.49263 | 0.48316 | 0.47579 | 0.46842 | 0.46 | 0.45263 | 0.42632 | 0.40105 | 0.38 | 0.52842 | 0.52211 | 0.51474 | 0.50947 | 0.50211 | 0.49474 | 0.48842 | 0.48105 | 0.47368 | 0.46632 | 0.44211 | 0.41684 | 0.39579
|  | TRESSADY | HE |  |  |  |  | 0.58842 | 0.58526 | 0.58105 | 0.57789 | 0.57263 | 0.56737 | 0.56211 | 0.55789 | 0.55263 | 0.54947 | 0.53579 | 0.52842 | 0.52316 | 0.53263 | 0.52526 | 0.52 | 0.51474 | 0.51053 | 0.50421 | 0.49789 | 0.49368 | 0.48737 | 0.48316 | 0.46842 | 0.45895 | 0.45368 | 0.53368 | 0.52842 | 0.52316 | 0.51895 | 0.51474 | 0.50947 | 0.50421 | 0.50105 | 0.49579 | 0.49263 | 0.48 | 0.47158 | 0.46632
|  | TRESSADY | FB |  |  |  |  | 0.58947 | 0.58842 | 0.58737 | 0.58526 | 0.58316 | 0.58 | 0.57684 | 0.57368 | 0.57053 | 0.56632 | 0.55158 | 0.53789 | 0.53053 | 0.53474 | 0.53158 | 0.52737 | 0.52421 | 0.52 | 0.51789 | 0.51368 | 0.50947 | 0.50632 | 0.50105 | 0.48421 | 0.46737 | 0.45789 | 0.53474 | 0.53263 | 0.53053 | 0.52737 | 0.52421 | 0.52211 | 0.51895 | 0.51684 | 0.51368 | 0.50947 | 0.49579 | 0.48105 | 0.47263
| SHETLAND | TUMBLIN | MINIMUM HEADROOM | HU3334053363 | YES | YES | 0 | 5.9347 | 5.9011 | 5.8705 | 5.8389 | 5.8095 | 5.7737 | 5.7411 | 5.7116 | 5.6832 | 5.6568 | 5.5484 | 5.4653 | 5.4074 | 5.9305 | 5.8937 | 5.8621 | 5.8284 | 5.7968 | 5.76 | 5.7253 | 5.6947 | 5.6653 | 5.6368 | 5.5337 | 5.4463 | 5.3747 | 5.9232 | 5.8832 | 5.8474 | 5.8105 | 5.7768 | 5.7379 | 5.7011 | 5.6674 | 5.6358 | 5.6053 | 5.4947 | 5.3989 | 5.3232
|  | TUMBLIN | EE |  |  |  |  | 5.9347 | 5.9011 | 5.8705 | 5.8389 | 5.8095 | 5.7737 | 5.7411 | 5.7116 | 5.6832 | 5.6568 | 5.5589 | 5.4768 | 5.4179 | 5.9305 | 5.8937 | 5.8621 | 5.8284 | 5.7968 | 5.76 | 5.7253 | 5.6947 | 5.6653 | 5.6368 | 5.5337 | 5.4463 | 5.3842 | 5.9232 | 5.8832 | 5.8474 | 5.8105 | 5.7768 | 5.7379 | 5.7011 | 5.6674 | 5.6358 | 5.6053 | 5.4947 | 5.3989 | 5.3305
|  | TUMBLIN | HT |  |  |  |  | 5.9442 | 5.9137 | 5.8832 | 5.8526 | 5.8232 | 5.7926 | 5.7621 | 5.7326 | 5.7011 | 5.6705 | 5.5484 | 5.4653 | 5.4074 | 5.94 | 5.9074 | 5.8758 | 5.8432 | 5.8116 | 5.78 | 5.7484 | 5.7168 | 5.6842 | 5.6526 | 5.5474 | 5.4526 | 5.3747 | 5.9337 | 5.8989 | 5.8642 | 5.8284 | 5.7947 | 5.7611 | 5.7263 | 5.6926 | 5.6579 | 5.6232 | 5.5105 | 5.4074 | 5.3232
|  | TUMBLIN | HE |  |  |  |  | 5.9642 | 5.9432 | 5.9232 | 5.9032 | 5.88 | 5.8547 | 5.8274 | 5.8095 | 5.7874 | 5.7758 | 5.7242 | 5.6821 | 5.6547 | 5.9621 | 5.94 | 5.9179 | 5.8979 | 5.8737 | 5.8474 | 5.82 | 5.8011 | 5.7779 | 5.7653 | 5.7105 | 5.6663 | 5.6368 | 5.9589 | 5.9347 | 5.9116 | 5.8895 | 5.8642 | 5.8368 | 5.8074 | 5.7874 | 5.7621 | 5.7495 | 5.6895 | 5.6411 | 5.6084
|  | TUMBLIN | FB |  |  |  |  | 5.9779 | 5.9642 | 5.9505 | 5.9368 | 5.9232 | 5.9074 | 5.8937 | 5.8789 | 5.8642 | 5.8474 | 5.7895 | 5.7305 | 5.6895 | 5.9758 | 5.9621 | 5.9474 | 5.9316 | 5.9179 | 5.9011 | 5.8863 | 5.8716 | 5.8558 | 5.8379 | 5.7758 | 5.7137 | 5.6684 | 5.9737 | 5.9579 | 5.9421 | 5.9253 | 5.9095 | 5.8905 | 5.8747 | 5.8589 | 5.8411 | 5.8221 | 5.7547 | 5.6853 | 5.6358
| TUMMEL BRIDGE | TUMMEL BRIDGE | MINIMUM HEADROOM | NN 75906 59080 | YES | YES | 0 | 0.95684 | 0.93895 | 0.92 | 0.89895 | 0.87684 | 0.85368 | 0.83158 | 0.80947 | 0.79158 | 0.77053 | 0.69684 | 0.62421 | 0.56 | 1.0358 | 1.0295 | 1.0211 | 1.0032 | 0.98421 | 0.96526 | 0.94526 | 0.92737 | 0.91158 | 0.89579 | 0.82737 | 0.76211 | 0.69789 | 1 | 0.98632 | 0.97368 | 0.96211 | 0.94842 | 0.92842 | 0.90421 | 0.88 | 0.85895 | 0.83684 | 0.75368 | 0.67158 | 0.59789
|  | TUMMEL BRIDGE | EE |  |  |  |  | 0.95684 | 0.93895 | 0.92 | 0.89895 | 0.87684 | 0.85368 | 0.83158 | 0.80947 | 0.79158 | 0.77053 | 0.69684 | 0.62421 | 0.56 | 1.0358 | 1.0295 | 1.0211 | 1.0032 | 0.98421 | 0.96526 | 0.94526 | 0.92737 | 0.91158 | 0.89579 | 0.82737 | 0.76211 | 0.69789 | 1 | 0.98632 | 0.97368 | 0.96211 | 0.94842 | 0.92842 | 0.90421 | 0.88 | 0.85895 | 0.83684 | 0.75368 | 0.67158 | 0.59789
|  | TUMMEL BRIDGE | HT |  |  |  |  | 0.96421 | 0.95474 | 0.94316 | 0.93158 | 0.91579 | 0.90105 | 0.88421 | 0.86947 | 0.85579 | 0.84105 | 0.77789 | 0.72526 | 0.68737 | 1.0379 | 1.0337 | 1.0295 | 1.0232 | 1.0084 | 0.99368 | 0.97684 | 0.96316 | 0.94947 | 0.93474 | 0.88211 | 0.83158 | 0.78737 | 1.0063 | 1.0011 | 0.99368 | 0.98737 | 0.98 | 0.97474 | 0.96421 | 0.94737 | 0.93263 | 0.91579 | 0.85684 | 0.79579 | 0.74211
|  | TUMMEL BRIDGE | HE |  |  |  |  | 0.97053 | 0.96211 | 0.95684 | 0.94842 | 0.94105 | 0.93158 | 0.92316 | 0.91158 | 0.90316 | 0.89579 | 0.86211 | 0.82842 | 0.8 | 1.0389 | 1.0347 | 1.0347 | 1.0295 | 1.0263 | 1.0211 | 1.0158 | 1.0105 | 1.0021 | 0.99474 | 0.96421 | 0.93474 | 0.91263 | 1.0074 | 1.0021 | 0.99895 | 0.99158 | 0.98737 | 0.98 | 0.97263 | 0.96526 | 0.96105 | 0.95789 | 0.93895 | 0.90105 | 0.86947
|  | TUMMEL BRIDGE | FB |  |  |  |  | 0.97579 | 0.97263 | 0.96842 | 0.96421 | 0.96105 | 0.95579 | 0.95263 | 0.94737 | 0.94211 | 0.93579 | 0.90842 | 0.88105 | 0.86 | 1.0421 | 1.0411 | 1.0389 | 1.0379 | 1.0368 | 1.0358 | 1.0347 | 1.0316 | 1.0305 | 1.0253 | 0.99579 | 0.96737 | 0.94421 | 1.0116 | 1.0105 | 1.0084 | 1.0063 | 1.0053 | 1.0032 | 1.0011 | 0.99895 | 0.99684 | 0.99579 | 0.98842 | 0.95895 | 0.93368
| MACDUFF | TURRIFF | MINIMUM HEADROOM | NJ 72407 50271 | NO | YES | 0.11327 | 4.7953 | 4.5311 | 4.1805 | 3.7468 | 2.4784 | 1.0542 | -0.32579 | -0.62263 | -0.82789 | -0.95316 | -7.7932 | -10.2395 | -10.6111 | 6.5947 | 6.1768 | 5.7684 | 5.2642 | 3.7726 | 2.1 | 0.48 | 0.13684 | -0.096842 | -0.23789 | -6.6368 | -8.6747 | -9.1032 | 6.0592 | 5.8897 | 5.7297 | 5.4161 | 4.0329 | 2.4097 | 0.81395 | 0.47711 | 0.24658 | 0.10763 | -7.1797 | -9.6829 | -10.105
|  | TURRIFF | EE |  |  |  |  | 4.7953 | 4.5311 | 4.1805 | 3.7468 | 2.4784 | 1.0542 | -0.32579 | -0.62263 | -0.82789 | -0.95316 | -7.7932 | -10.2395 | -10.6111 | 6.5947 | 6.1768 | 5.7684 | 5.2642 | 3.7726 | 2.1 | 0.48 | 0.13684 | -0.096842 | -0.23789 | -6.6368 | -8.6747 | -9.1032 | 6.0592 | 5.8897 | 5.7297 | 5.4161 | 4.0329 | 2.4097 | 0.81395 | 0.47711 | 0.24658 | 0.10763 | -7.1797 | -9.6829 | -10.105
|  | TURRIFF | HT |  |  |  |  | 4.8026 | 4.5921 | 4.2384 | 3.8258 | 2.5458 | 2.2974 | 1.9563 | 1.5479 | 0.65421 | -0.80684 | -7.1563 | -9.2374 | -9.6037 | 6.62 | 6.2484 | 5.8379 | 5.3579 | 3.8547 | 3.5705 | 3.1768 | 2.7042 | 1.6568 | -0.061053 | -6.0558 | -7.8663 | -8.3968 | 6.0718 | 5.9203 | 5.7508 | 5.5024 | 4.1076 | 3.8413 | 3.4708 | 3.0045 | 1.9729 | 0.28026 | -6.4113 | -8.5913 | -9.1155
|  | TURRIFF | HE |  |  |  |  | 4.8216 | 4.7016 | 4.3974 | 4.0321 | 2.8184 | 1.4795 | 0.13842 | -0.12474 | -0.28474 | -0.35947 | -6.7879 | -9.9868 | -10.2058 | 6.6989 | 6.3747 | 6.02 | 5.5947 | 4.1695 | 2.5958 | 1.0211 | 0.71789 | 0.53579 | 0.44947 | -5.5853 | -8.0947 | -8.3484 | 6.1076 | 5.9729 | 5.8339 | 5.6645 | 4.4024 | 2.9003 | 1.3487 | 1.0497 | 0.86974 | 0.78553 | -6.0776 | -9.3397 | -9.5766
|  | TURRIFF | FB |  |  |  |  | 4.8605 | 4.8374 | 4.8111 | 4.7847 | 4.5132 | 4.0321 | 3.3805 | 2.5468 | 2.47 | 2.39 | 1.5268 | 0.52579 | 0.29105 | 6.8768 | 6.7884 | 6.6453 | 6.4895 | 6.1526 | 5.5874 | 4.82 | 3.8379 | 3.7516 | 3.66 | 2.6537 | 1.4821 | 1.2095 | 6.2034 | 6.1487 | 6.0855 | 6.0213 | 5.895 | 5.6897 | 5.0097 | 4.1003 | 4.0182 | 3.9318 | 2.9571 | 1.8024 | 1.5339
| RANNOCH | TYNDRUM | MINIMUM HEADROOM | NN 32894 30860 | YES | YES | 0 | 0.67579 | 0.67368 | 0.67053 | 0.66737 | 0.66316 | 0.65895 | 0.65474 | 0.65158 | 0.64737 | 0.64526 | 0.62632 | 0.57368 | 0.52632 | 0.88316 | 0.88105 | 0.87895 | 0.87579 | 0.87263 | 0.86842 | 0.86526 | 0.86211 | 0.85895 | 0.85789 | 0.84842 | 0.84105 | 0.79895 | 0.94316 | 0.94 | 0.93684 | 0.93368 | 0.92947 | 0.92421 | 0.92 | 0.91684 | 0.91158 | 0.90947 | 0.89684 | 0.85263 | 0.79263
|  | TYNDRUM | EE |  |  |  |  | 0.67579 | 0.67368 | 0.67053 | 0.66737 | 0.66316 | 0.65895 | 0.65474 | 0.65158 | 0.64737 | 0.64526 | 0.63368 | 0.57789 | 0.52632 | 0.88316 | 0.88105 | 0.87895 | 0.87579 | 0.87263 | 0.86842 | 0.86526 | 0.86211 | 0.85895 | 0.85789 | 0.84842 | 0.84105 | 0.79895 | 0.94316 | 0.94 | 0.93684 | 0.93368 | 0.92947 | 0.92421 | 0.92 | 0.91684 | 0.91158 | 0.90947 | 0.89684 | 0.85263 | 0.79263
|  | TYNDRUM | HT |  |  |  |  | 0.67684 | 0.67579 | 0.67263 | 0.67053 | 0.66632 | 0.66421 | 0.66211 | 0.65789 | 0.65579 | 0.65368 | 0.62632 | 0.57368 | 0.53368 | 0.88316 | 0.88211 | 0.88 | 0.87684 | 0.87368 | 0.87158 | 0.86947 | 0.86632 | 0.86421 | 0.86211 | 0.85263 | 0.84421 | 0.80842 | 0.94316 | 0.94211 | 0.94 | 0.93684 | 0.93368 | 0.93158 | 0.92842 | 0.92526 | 0.92316 | 0.92 | 0.91053 | 0.85789 | 0.80105
|  | TYNDRUM | HE |  |  |  |  | 0.67789 | 0.67579 | 0.67368 | 0.67158 | 0.66842 | 0.66526 | 0.66211 | 0.66 | 0.65684 | 0.65684 | 0.65263 | 0.64526 | 0.60421 | 0.88421 | 0.88211 | 0.88105 | 0.87789 | 0.87579 | 0.87263 | 0.86947 | 0.86842 | 0.86526 | 0.86526 | 0.86105 | 0.85684 | 0.85579 | 0.94421 | 0.94211 | 0.94105 | 0.93789 | 0.93579 | 0.93263 | 0.92842 | 0.92737 | 0.92421 | 0.92316 | 0.91895 | 0.91263 | 0.88
|  | TYNDRUM | FB |  |  |  |  | 0.67895 | 0.67789 | 0.67684 | 0.67684 | 0.67579 | 0.67474 | 0.67368 | 0.67263 | 0.67263 | 0.67053 | 0.66526 | 0.66211 | 0.66105 | 0.88526 | 0.88421 | 0.88316 | 0.88316 | 0.88211 | 0.88105 | 0.88 | 0.87895 | 0.87895 | 0.87789 | 0.87263 | 0.86842 | 0.86737 | 0.94632 | 0.94526 | 0.94316 | 0.94316 | 0.94211 | 0.94105 | 0.94 | 0.93895 | 0.93895 | 0.93789 | 0.93263 | 0.92842 | 0.92737
| DUNVEGAN | UIG | MINIMUM HEADROOM | NG 39131 64412 | YES | YES | 0 | 2.6411 | 2.6116 | 2.5853 | 2.5505 | 2.5158 | 2.2716 | 1.9305 | 1.6968 | 1.5853 | 1.5221 | 1.3126 | 1.2084 | 1.1316 | 2.6926 | 2.66 | 2.6305 | 2.5905 | 2.5505 | 2.2537 | 1.8568 | 1.5821 | 1.4537 | 1.3832 | 1.1516 | 1.0389 | 0.94316 | 2.4147 | 2.3811 | 2.3505 | 2.3095 | 2.2684 | 1.9768 | 1.5789 | 1.3053 | 1.1779 | 1.1063 | 0.86737 | 0.75158 | 0.66421
|  | UIG | EE |  |  |  |  | 2.6411 | 2.6116 | 2.5853 | 2.5505 | 2.5158 | 2.48 | 2.4442 | 2.1842 | 1.8442 | 1.5989 | 1.3126 | 1.2116 | 1.1379 | 2.6926 | 2.66 | 2.6305 | 2.5905 | 2.5505 | 2.5095 | 2.4674 | 2.1621 | 1.7642 | 1.4779 | 1.1516 | 1.0389 | 0.95895 | 2.4147 | 2.3811 | 2.3505 | 2.3095 | 2.2684 | 2.2263 | 2.1853 | 1.8789 | 1.4821 | 1.1968 | 0.86737 | 0.75158 | 0.66947
|  | UIG | HT |  |  |  |  | 2.6474 | 2.6242 | 2.5989 | 2.5716 | 2.5358 | 2.2716 | 1.9305 | 1.6968 | 1.5853 | 1.5221 | 1.3147 | 1.2084 | 1.1316 | 2.7021 | 2.6747 | 2.6442 | 2.6137 | 2.5726 | 2.2537 | 1.8568 | 1.5821 | 1.4537 | 1.3832 | 1.18 | 1.0505 | 0.94316 | 2.4232 | 2.3958 | 2.3674 | 2.3358 | 2.2947 | 1.9768 | 1.5789 | 1.3053 | 1.1779 | 1.1063 | 0.90316 | 0.77263 | 0.66421
|  | UIG | HE |  |  |  |  | 2.6653 | 2.6484 | 2.6337 | 2.6158 | 2.5947 | 2.5758 | 2.5547 | 2.2884 | 1.9211 | 1.6811 | 1.5211 | 1.4653 | 1.4305 | 2.7232 | 2.7042 | 2.6863 | 2.6674 | 2.6442 | 2.6232 | 2.6011 | 2.2758 | 1.8453 | 1.5642 | 1.3789 | 1.3179 | 1.28 | 2.4442 | 2.4253 | 2.4084 | 2.3884 | 2.3653 | 2.3442 | 2.3211 | 1.9979 | 1.5684 | 1.2884 | 1.1021 | 1.0389 | 1
|  | UIG | FB |  |  |  |  | 2.6768 | 2.6663 | 2.6547 | 2.6442 | 2.6305 | 2.6189 | 2.6074 | 2.5968 | 2.4832 | 2.3168 | 1.94 | 1.8726 | 1.8253 | 2.7347 | 2.7232 | 2.7105 | 2.6979 | 2.6821 | 2.6684 | 2.6547 | 2.6421 | 2.4989 | 2.3011 | 1.8611 | 1.7863 | 1.7316 | 2.4579 | 2.4453 | 2.4316 | 2.4189 | 2.4032 | 2.3895 | 2.3758 | 2.3632 | 2.2211 | 2.0242 | 1.5853 | 1.5095 | 1.4547
| GRUDIE BRIDGE | ULLAPOOL | MINIMUM HEADROOM | NH 13018 94588 | NO | NO | 0 | 1.6042 | 1.5947 | 4.5863 | 4.5768 | 4.5463 | 3.86 | 3.1074 | 2.4084 | 2.0379 | 2.0084 | 1.8663 | 1.7621 | 1.6895 | 0.93579 | 0.91684 | 3.8589 | 3.8137 | 3.7905 | 3.3695 | 2.5905 | 1.7674 | 1.3337 | 1.3011 | 1.16 | 1.0411 | 0.94105 | 0.93053 | 0.90947 | 3.8474 | 3.7979 | 3.7737 | 3.3063 | 2.6147 | 1.7916 | 1.3579 | 1.3253 | 1.1842 | 1.0653 | 0.96526
|  | ULLAPOOL | EE |  |  |  |  | 1.6042 | 1.5947 | 4.5863 | 4.5768 | 4.5463 | 4.5116 | 4.4779 | 3.8105 | 3.0516 | 2.3379 | 1.8842 | 1.7789 | 1.6968 | 0.93579 | 0.91684 | 3.8589 | 3.8137 | 3.7905 | 3.7632 | 3.7368 | 3.3295 | 2.5295 | 1.6884 | 1.16 | 1.0411 | 0.94737 | 0.93053 | 0.90947 | 3.8474 | 3.7979 | 3.7737 | 3.7442 | 3.7158 | 3.2653 | 2.5537 | 1.7126 | 1.1842 | 1.0653 | 0.97158
|  | ULLAPOOL | HT |  |  |  |  | 1.6063 | 1.5968 | 4.5884 | 4.5779 | 4.56 | 3.86 | 3.1074 | 2.4084 | 2.0379 | 2.0084 | 1.8663 | 1.7621 | 1.6895 | 0.94211 | 0.92316 | 3.8684 | 3.8253 | 3.7989 | 3.3695 | 2.5905 | 1.7674 | 1.3337 | 1.3011 | 1.1684 | 1.0463 | 0.94105 | 0.93684 | 0.91789 | 3.8579 | 3.8105 | 3.7821 | 3.3063 | 2.6147 | 1.7916 | 1.3579 | 1.3253 | 1.1926 | 1.0705 | 0.96526
|  | ULLAPOOL | HE |  |  |  |  | 1.6084 | 1.6 | 4.5937 | 4.5842 | 4.5726 | 4.56 | 4.5453 | 3.8474 | 3.0168 | 2.2505 | 2.0642 | 2.0021 | 1.9547 | 0.95263 | 0.93895 | 3.8895 | 3.8526 | 3.8347 | 3.8179 | 3.8 | 3.3537 | 2.4863 | 1.5832 | 1.3663 | 1.2958 | 1.24 | 0.94842 | 0.93368 | 3.88 | 3.84 | 3.8221 | 3.8042 | 3.7863 | 3.2916 | 2.5116 | 1.6074 | 1.3905 | 1.32 | 1.2642
|  | ULLAPOOL | FB |  |  |  |  | 1.6137 | 1.6105 | 4.6074 | 4.6032 | 4.6 | 4.5958 | 4.5905 | 4.5863 | 4.3663 | 4 | 3.1158 | 3.0453 | 2.9884 | 0.96 | 0.95263 | 3.9284 | 3.9105 | 3.9021 | 3.8937 | 3.8821 | 3.8737 | 3.6821 | 3.46 | 2.5968 | 2.5158 | 2.4505 | 0.95684 | 0.94842 | 3.9221 | 3.9021 | 3.8937 | 3.8842 | 3.8726 | 3.8632 | 3.6516 | 3.4053 | 2.6211 | 2.5411 | 2.4747
| SHETLAND | UNST | MINIMUM HEADROOM | HP6398113411 | YES | YES | 0 | 1.5505 | 1.5358 | 1.5232 | 1.5095 | 1.4968 | 1.48 | 1.4642 | 1.4516 | 1.4379 | 1.4274 | 1.3758 | 1.34 | 1.3137 | 1.3116 | 1.2905 | 1.2726 | 1.2537 | 1.2368 | 1.2158 | 1.1947 | 1.1779 | 1.1589 | 1.1442 | 1.0821 | 1.0284 | 0.98842 | 0.96421 | 0.94526 | 0.92842 | 0.91053 | 0.89579 | 0.87579 | 0.85684 | 0.84211 | 0.82526 | 0.81263 | 0.75895 | 0.71368 | 0.67684
|  | UNST | EE |  |  |  |  | 1.5505 | 1.5358 | 1.5232 | 1.5095 | 1.4968 | 1.48 | 1.4642 | 1.4516 | 1.4379 | 1.4274 | 1.3821 | 1.3463 | 1.3221 | 1.3116 | 1.2905 | 1.2726 | 1.2537 | 1.2368 | 1.2158 | 1.1947 | 1.1779 | 1.1589 | 1.1442 | 1.0821 | 1.0284 | 0.99158 | 0.96421 | 0.94526 | 0.92842 | 0.91053 | 0.89579 | 0.87579 | 0.85684 | 0.84211 | 0.82526 | 0.81263 | 0.75895 | 0.71368 | 0.68211
|  | UNST | HT |  |  |  |  | 1.5537 | 1.5411 | 1.5274 | 1.5137 | 1.5 | 1.4863 | 1.4726 | 1.4589 | 1.4442 | 1.4305 | 1.3758 | 1.34 | 1.3137 | 1.3158 | 1.2979 | 1.28 | 1.2621 | 1.2442 | 1.2263 | 1.2084 | 1.1916 | 1.1716 | 1.1537 | 1.0916 | 1.0358 | 0.98842 | 0.96842 | 0.95158 | 0.93579 | 0.91895 | 0.90105 | 0.88526 | 0.86842 | 0.85263 | 0.83474 | 0.81895 | 0.76526 | 0.71684 | 0.67684
|  | UNST | HE |  |  |  |  | 1.5632 | 1.5516 | 1.5432 | 1.5326 | 1.5232 | 1.5095 | 1.4968 | 1.4863 | 1.4779 | 1.4726 | 1.4484 | 1.4305 | 1.4189 | 1.3305 | 1.3158 | 1.3042 | 1.2916 | 1.28 | 1.2632 | 1.2495 | 1.2358 | 1.2253 | 1.2179 | 1.1863 | 1.16 | 1.1411 | 0.98105 | 0.96737 | 0.95684 | 0.94526 | 0.93368 | 0.91789 | 0.90421 | 0.89263 | 0.88211 | 0.87474 | 0.84632 | 0.82211 | 0.80632
|  | UNST | FB |  |  |  |  | 1.5684 | 1.5632 | 1.5568 | 1.5505 | 1.5442 | 1.5379 | 1.5316 | 1.5253 | 1.52 | 1.5126 | 1.4874 | 1.4621 | 1.4453 | 1.3368 | 1.3295 | 1.32 | 1.3116 | 1.3032 | 1.2947 | 1.2853 | 1.2768 | 1.2695 | 1.26 | 1.2242 | 1.1874 | 1.1579 | 0.98737 | 0.98 | 0.97263 | 0.96526 | 0.95684 | 0.94842 | 0.94105 | 0.93263 | 0.92526 | 0.91684 | 0.88421 | 0.85158 | 0.82842
| SHETLAND | VOE | MINIMUM HEADROOM | HU4117663079 | YES | YES | 0 | 8.9863 | 8.9695 | 8.9537 | 8.9347 | 8.9116 | 8.8716 | 8.8189 | 8.7653 | 8.7074 | 8.6621 | 8.4716 | 8.3484 | 8.2621 | 8.4137 | 8.3937 | 8.3758 | 8.3558 | 8.3316 | 8.3074 | 8.2789 | 8.2347 | 8.1726 | 8.1253 | 7.9379 | 7.8032 | 7.6968 | 7.9716 | 7.9516 | 7.9337 | 7.9137 | 7.8884 | 7.8642 | 7.8347 | 7.8116 | 7.7874 | 7.7621 | 7.6832 | 7.6042 | 7.4989
|  | VOE | EE |  |  |  |  | 8.9863 | 8.9695 | 8.9537 | 8.9368 | 8.9158 | 8.8716 | 8.8189 | 8.7653 | 8.7074 | 8.6695 | 8.4884 | 8.3642 | 8.2747 | 8.4137 | 8.3937 | 8.3758 | 8.3568 | 8.3347 | 8.3074 | 8.2789 | 8.2358 | 8.1726 | 8.1326 | 7.9379 | 7.8032 | 7.7074 | 7.9716 | 7.9516 | 7.9337 | 7.9147 | 7.8916 | 7.8642 | 7.8347 | 7.8116 | 7.7874 | 7.7684 | 7.6884 | 7.6042 | 7.5084
|  | VOE | HT |  |  |  |  | 8.9884 | 8.9726 | 8.9547 | 8.9347 | 8.9116 | 8.8832 | 8.8263 | 8.7653 | 8.7074 | 8.6621 | 8.4716 | 8.3484 | 8.2621 | 8.4158 | 8.3979 | 8.3789 | 8.3558 | 8.3316 | 8.3084 | 8.2842 | 8.2347 | 8.1737 | 8.1253 | 7.9568 | 7.8137 | 7.6968 | 7.9747 | 7.9568 | 7.9368 | 7.9137 | 7.8884 | 7.8653 | 7.8411 | 7.8137 | 7.7884 | 7.7621 | 7.6832 | 7.6137 | 7.4989
|  | VOE | HE |  |  |  |  | 8.9937 | 8.9779 | 8.9642 | 8.9484 | 8.9274 | 8.9032 | 8.8779 | 8.86 | 8.8432 | 8.8274 | 8.7337 | 8.6684 | 8.6253 | 8.4232 | 8.4063 | 8.3916 | 8.3747 | 8.3526 | 8.3274 | 8.3 | 8.28 | 8.2621 | 8.2547 | 8.2042 | 8.1337 | 8.0874 | 7.9821 | 7.9642 | 7.9495 | 7.9326 | 7.9105 | 7.8853 | 7.8579 | 7.8379 | 7.8189 | 7.8116 | 7.7747 | 7.7484 | 7.7326
|  | VOE | FB |  |  |  |  | 9.0032 | 8.9979 | 8.9916 | 8.9842 | 8.9768 | 8.9695 | 8.9621 | 8.9537 | 8.9453 | 8.9358 | 8.8705 | 8.7747 | 8.7105 | 8.4337 | 8.4274 | 8.42 | 8.4116 | 8.4032 | 8.3947 | 8.3863 | 8.3768 | 8.3674 | 8.3568 | 8.3189 | 8.2421 | 8.1716 | 7.9916 | 7.9853 | 7.9779 | 7.9695 | 7.9611 | 7.9526 | 7.9442 | 7.9347 | 7.9253 | 7.9137 | 7.8758 | 7.8432 | 7.8263
| DUDHOPE | WALTON | MINIMUM HEADROOM | NO 38995 30333 | NO | YES | 0 | 24.74 | 24.5063 | 24.3611 | 24.1916 | 24.0126 | 23.8284 | 23.6474 | 23.4705 | 23.2884 | 23.1074 | 22.7305 | 22.0495 | 21.4474 | 22.8968 | 22.6463 | 22.4916 | 22.3074 | 22.1137 | 21.9137 | 21.7189 | 21.5284 | 21.3316 | 21.1347 | 20.9095 | 20.1979 | 19.58 | 23.7137 | 23.4874 | 23.3379 | 23.1537 | 22.94 | 22.7179 | 22.5053 | 22.2958 | 22.0779 | 21.86 | 21.5253 | 20.74 | 20.0705
|  | WALTON | EE |  |  |  |  | 24.74 | 24.5063 | 24.3611 | 24.1916 | 24.0126 | 23.8284 | 23.6474 | 23.4705 | 23.2884 | 23.1074 | 22.7305 | 22.0495 | 21.4474 | 22.8968 | 22.6463 | 22.4916 | 22.3074 | 22.1137 | 21.9137 | 21.7189 | 21.5284 | 21.3316 | 21.1347 | 20.9095 | 20.1979 | 19.58 | 23.7137 | 23.4874 | 23.3379 | 23.1537 | 22.94 | 22.7179 | 22.5053 | 22.2958 | 22.0779 | 21.86 | 21.5253 | 20.74 | 20.0705
|  | WALTON | HT |  |  |  |  | 24.7779 | 24.6621 | 24.5811 | 24.4895 | 24.3716 | 24.2663 | 24.1379 | 24.0063 | 23.8421 | 24.0232 | 23.3379 | 22.8295 | 22.4579 | 22.9611 | 22.8063 | 22.7232 | 22.6221 | 22.4916 | 22.3758 | 22.2326 | 22.0842 | 21.8989 | 22.2453 | 21.6589 | 21.1274 | 20.6611 | 23.7842 | 23.6526 | 23.5747 | 23.4821 | 23.3274 | 23.1937 | 23.0263 | 22.8505 | 22.6274 | 22.9579 | 22.3126 | 21.7084 | 21.1916
|  | WALTON | HE |  |  |  |  | 24.7832 | 24.7074 | 24.6453 | 24.5789 | 24.4968 | 24.4 | 24.3137 | 24.2284 | 24.1305 | 24.0474 | 23.6695 | 23.3505 | 23.0937 | 22.98 | 22.8526 | 22.7905 | 22.7232 | 22.6379 | 22.5368 | 22.4474 | 22.3537 | 22.2463 | 22.1526 | 21.7295 | 21.3768 | 21.0979 | 23.8063 | 23.6874 | 23.6263 | 23.5589 | 23.48 | 23.3853 | 23.2989 | 23.2063 | 23.0811 | 22.9716 | 22.4716 | 22.0705 | 21.7632
|  | WALTON | FB |  |  |  |  | 24.8042 | 24.7874 | 24.7695 | 24.7505 | 24.7316 | 24.7116 | 24.6916 | 24.6611 | 24.6126 | 24.5474 | 24.2947 | 24.0516 | 23.8779 | 23.0663 | 23.0337 | 23.0042 | 22.9758 | 22.94 | 22.9 | 22.8495 | 22.8084 | 22.7589 | 22.6926 | 22.4095 | 22.1316 | 21.9168 | 23.8737 | 23.8463 | 23.8179 | 23.7905 | 23.7621 | 23.7211 | 23.6737 | 23.6368 | 23.5926 | 23.5358 | 23.2326 | 22.8926 | 22.6463
| INVERNESS | WATERLOO PLACE | MINIMUM HEADROOM | NH 66301 45800 | NO | YES | 0 | 39.4296 | 39.4014 | 39.3696 | 39.2902 | 39.2397 | 39.1851 | 39.0894 | 38.9842 | 38.8964 | 38.819 | 38.4599 | 38.459 | 38.3394 | 38.4443 | 38.426 | 38.4061 | 38.362 | 38.3307 | 38.296 | 38.2405 | 38.1819 | 38.1323 | 38.0872 | 37.8809 | 37.9736 | 37.8228 | 39.4209 | 39.3896 | 39.3539 | 39.2622 | 39.2046 | 39.1431 | 39.0335 | 38.9125 | 38.8108 | 38.722 | 38.3069 | 38.4155 | 38.2712
|  | WATERLOO PLACE | EE |  |  |  |  | 39.4296 | 39.4014 | 39.3696 | 39.2902 | 39.2397 | 39.1851 | 39.0894 | 38.9842 | 38.8964 | 38.8364 | 38.4599 | 38.4649 | 38.3394 | 38.4443 | 38.426 | 38.4061 | 38.362 | 38.3307 | 38.296 | 38.2405 | 38.1819 | 38.1323 | 38.0976 | 37.8809 | 37.9736 | 37.8283 | 39.4209 | 39.3896 | 39.3539 | 39.2622 | 39.2046 | 39.1431 | 39.0335 | 38.9125 | 38.8108 | 38.7424 | 38.3069 | 38.4155 | 38.2712
|  | WATERLOO PLACE | HT |  |  |  |  | 39.4346 | 39.4093 | 39.3835 | 39.3215 | 39.2694 | 39.1871 | 39.1047 | 39.0095 | 38.9386 | 38.819 | 38.6197 | 38.459 | 38.3454 | 38.4483 | 38.4309 | 38.4131 | 38.3764 | 38.3446 | 38.2975 | 38.2504 | 38.1963 | 38.1541 | 38.0872 | 38.1913 | 38.0068 | 37.8412 | 39.4263 | 39.3981 | 39.3698 | 39.2984 | 39.2398 | 39.1451 | 39.0509 | 38.9413 | 38.8599 | 38.722 | 38.6392 | 38.4462 | 38.2806
|  | WATERLOO PLACE | HE |  |  |  |  | 39.444 | 39.4247 | 39.4088 | 39.3646 | 39.3443 | 39.3046 | 39.2436 | 39.1662 | 39.1087 | 39.0656 | 38.7521 | 38.826 | 38.5105 | 38.4537 | 38.4393 | 38.4289 | 38.4017 | 38.3863 | 38.359 | 38.3213 | 38.2781 | 38.2449 | 38.2216 | 38.0559 | 38.2901 | 37.8228 | 39.4368 | 39.4154 | 39.3986 | 39.348 | 39.3262 | 39.2815 | 39.2126 | 39.1238 | 39.0578 | 39.0077 | 38.6427 | 38.8302 | 38.3128
|  | WATERLOO PLACE | FB |  |  |  |  | 39.4485 | 39.4376 | 39.4257 | 39.4038 | 39.3909 | 39.3775 | 39.3428 | 39.3002 | 39.258 | 39.2312 | 38.9852 | 38.8776 | 38.7913 | 38.4572 | 38.4498 | 38.4423 | 38.4299 | 38.4215 | 38.4126 | 38.3932 | 38.3694 | 38.3461 | 38.3307 | 38.1988 | 38.1378 | 38.0907 | 39.4417 | 39.4293 | 39.4159 | 39.3911 | 39.3767 | 39.3619 | 39.3217 | 39.2721 | 39.2235 | 39.1927 | 38.907 | 38.7835 | 38.6833
| LYNDHURST | WEST KIRKTON | MINIMUM HEADROOM | NO 39194 33796 | NO | YES | 0 | 24.3163 | 24.1774 | 24.0521 | 23.8858 | 23.7795 | 23.6658 | 23.5489 | 23.4416 | 23.3237 | 23.2268 | 22.7511 | 22.4658 | 22.2711 | 21.7747 | 21.5832 | 21.4074 | 21.1779 | 21.0421 | 20.8937 | 20.7453 | 20.6137 | 20.4621 | 20.3389 | 19.8389 | 19.4232 | 19.1095 | 23.2655 | 23.0434 | 22.8392 | 22.5739 | 22.4224 | 22.255 | 22.0866 | 21.9434 | 21.7708 | 21.6318 | 21.0718 | 20.5992 | 20.2466
|  | WEST KIRKTON | EE |  |  |  |  | 24.3163 | 24.1774 | 24.0553 | 23.9121 | 23.8142 | 23.6953 | 23.5647 | 23.4416 | 23.3237 | 23.2289 | 22.8647 | 22.5837 | 22.3963 | 21.7747 | 21.5832 | 21.4126 | 21.2137 | 21.0884 | 20.9411 | 20.7768 | 20.6137 | 20.4621 | 20.3389 | 19.8758 | 19.5084 | 19.2589 | 23.2655 | 23.0434 | 22.8466 | 22.615 | 22.4739 | 22.3097 | 22.1266 | 21.9434 | 21.7708 | 21.6318 | 21.1118 | 20.6961 | 20.4129
|  | WEST KIRKTON | HT |  |  |  |  | 24.3374 | 24.2037 | 24.0521 | 23.8858 | 23.7795 | 23.6658 | 23.5489 | 23.4489 | 23.35 | 23.2268 | 22.7511 | 22.4658 | 22.2711 | 21.8032 | 21.6189 | 21.4074 | 21.1779 | 21.0421 | 20.8937 | 20.7453 | 20.62 | 20.4989 | 20.3432 | 19.8389 | 19.4232 | 19.1095 | 23.2982 | 23.0845 | 22.8392 | 22.5739 | 22.4224 | 22.255 | 22.0866 | 21.9476 | 21.815 | 21.6403 | 21.0718 | 20.5992 | 20.2466
|  | WEST KIRKTON | HE |  |  |  |  | 24.3942 | 24.2774 | 24.1711 | 24.0384 | 23.9605 | 23.8605 | 23.7437 | 23.6521 | 23.5668 | 23.5079 | 23.3026 | 23.1363 | 23.0363 | 21.8811 | 21.7232 | 21.5726 | 21.3916 | 21.2958 | 21.1768 | 21.0316 | 20.9126 | 20.8021 | 20.7221 | 20.4537 | 20.2295 | 20.0947 | 23.3887 | 23.2066 | 23.0318 | 22.8224 | 22.7171 | 22.5866 | 22.4255 | 22.2918 | 22.1655 | 22.0739 | 21.7708 | 21.5139 | 21.3592
|  | WEST KIRKTON | FB |  |  |  |  | 24.4816 | 24.4311 | 24.3721 | 24.3111 | 24.2658 | 24.2195 | 24.17 | 24.1132 | 24.0437 | 23.9858 | 23.7437 | 23.5332 | 23.4068 | 22.0074 | 21.9368 | 21.8547 | 21.7705 | 21.7126 | 21.6516 | 21.5863 | 21.5105 | 21.4147 | 21.3389 | 21.0126 | 20.7305 | 20.5547 | 23.4771 | 23.4445 | 23.3603 | 23.2624 | 23.1961 | 23.1276 | 23.0529 | 22.9666 | 22.8571 | 22.7697 | 22.3971 | 22.0729 | 21.8697
| KILLIN | WESTER DRUMMOND | MINIMUM HEADROOM | NN 72155 44784 | YES | YES | 0 | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.094737 | 0.093684 | 0.10105 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.095789 | 0.094737 | 0.093684 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.095789 | 0.094737
|  | WESTER DRUMMOND | EE |  |  |  |  | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.095789 | 0.095789 | 0.094737 | 0.093684 | 0.10105 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.094737 | 0.093684 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.095789 | 0.094737
|  | WESTER DRUMMOND | HT |  |  |  |  | 0.1 | 0.1 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.094737 | 0.094737 | 0.094737 | 0.10105 | 0.10105 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.095789 | 0.094737 | 0.094737 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.095789 | 0.095789
|  | WESTER DRUMMOND | HE |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.096842 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.097895 | 0.097895 | 0.097895
|  | WESTER DRUMMOND | FB |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.097895 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947
| THURSO | WESTRAY | MINIMUM HEADROOM | HY 50213 39413 | YES | YES | 0.05102 | -0.89684 | -0.9 | -0.90421 | -0.90842 | -0.91368 | -0.91895 | -0.92526 | -0.92947 | -0.93474 | -0.94 | -5.7379 | -5.7726 | -5.8 | -2.0632 | -2.0747 | -2.0884 | -2.1063 | -2.1221 | -2.1421 | -2.1621 | -2.1758 | -2.1916 | -2.2074 | -6.1337 | -6.1947 | -6.2526 | -2.0284 | -2.0326 | -2.0368 | -2.0421 | -2.0474 | -2.0537 | -2.0632 | -2.0737 | -2.0863 | -2.1 | -7.0558 | -7.1084 | -7.1579
|  | WESTRAY | EE |  |  |  |  | -0.89684 | -0.9 | -0.90421 | -0.90842 | -0.91263 | -0.91895 | -0.92526 | -0.92947 | -0.93474 | -0.93789 | -3.0158 | -3.0505 | -3.0716 | -2.0632 | -2.0747 | -2.0884 | -2.1063 | -2.1221 | -2.1421 | -2.1621 | -2.1758 | -2.1916 | -2.2074 | -3.9968 | -4.0526 | -4.0884 | -2.0284 | -2.0326 | -2.0368 | -2.0421 | -2.0474 | -2.0537 | -2.0632 | -2.0737 | -2.0863 | -2.1 | -4.3442 | -4.3916 | -4.4221
|  | WESTRAY | HT |  |  |  |  | -0.89579 | -0.9 | -0.90316 | -0.90842 | -0.91368 | -0.91895 | -0.92316 | -0.92842 | -0.93368 | -0.94 | -5.7379 | -5.7726 | -5.8 | -2.0589 | -2.0705 | -2.08 | -2.0947 | -2.1105 | -2.1295 | -2.1432 | -2.1589 | -2.1779 | -2.1968 | -6.1337 | -6.1947 | -6.2526 | -2.0274 | -2.0316 | -2.0358 | -2.0411 | -2.0474 | -2.0537 | -2.0579 | -2.0642 | -2.0768 | -2.0916 | -7.0558 | -7.1084 | -7.1579
|  | WESTRAY | HE |  |  |  |  | -0.89474 | -0.89789 | -0.90105 | -0.90526 | -0.90842 | -0.91579 | -0.92105 | -0.92421 | -0.92737 | -0.93053 | -3.2242 | -3.2453 | -3.2547 | -2.0505 | -2.0579 | -2.0653 | -2.0737 | -2.08 | -2.0937 | -2.1053 | -2.1137 | -2.1232 | -2.1347 | -4.1105 | -4.1474 | -4.1642 | -2.0253 | -2.0295 | -2.0326 | -2.0368 | -2.04 | -2.0484 | -2.0537 | -2.0568 | -2.0611 | -2.0642 | -4.5263 | -4.5579 | -4.5726
|  | WESTRAY | FB |  |  |  |  | -0.89263 | -0.89474 | -0.89579 | -0.89789 | -0.89895 | -0.90105 | -0.90316 | -0.90526 | -0.90737 | -0.90947 | -0.91684 | -0.92316 | -0.92632 | -2.0463 | -2.0516 | -2.0568 | -2.0621 | -2.0674 | -2.0747 | -2.08 | -2.0853 | -2.0926 | -2.1032 | -2.1379 | -2.1695 | -2.1968 | -2.0232 | -2.0263 | -2.0274 | -2.0295 | -2.0305 | -2.0337 | -2.0358 | -2.0379 | -2.04 | -2.0432 | -2.0516 | -2.0674 | -2.0895
| TARLAND | WHITEHOUSE | MINIMUM HEADROOM | NJ 61658 15058 | NO | YES | 2.45 | 6.0421 | 5.8463 | 5.6158 | 5.3347 | 5.2421 | 5.0411 | 4.9189 | 4.8347 | 4.7516 | 4.6674 | 4.3084 | 3.9768 | 3.7495 | 5.3611 | 5.1326 | 4.8621 | 4.5337 | 4.4305 | 4.1989 | 4.0642 | 3.9695 | 3.8779 | 3.7821 | 3.4379 | 3.0747 | 2.7453 | 5.0884 | 4.8726 | 4.6179 | 4.3063 | 4.2084 | 3.9874 | 3.8579 | 3.7653 | 3.6758 | 3.5853 | 3.2537 | 2.9095 | 2.5895
|  | WHITEHOUSE | EE |  |  |  |  | 6.0421 | 5.8463 | 5.6158 | 5.3347 | 5.2421 | 5.0411 | 4.9189 | 4.8347 | 4.7516 | 4.6674 | 4.3579 | 4.0568 | 3.8168 | 5.3611 | 5.1326 | 4.8621 | 4.5337 | 4.4305 | 4.1989 | 4.0642 | 3.9695 | 3.8779 | 3.7821 | 3.4379 | 3.0968 | 2.8211 | 5.0884 | 4.8726 | 4.6179 | 4.3063 | 4.2084 | 3.9874 | 3.8579 | 3.7653 | 3.6758 | 3.5853 | 3.2537 | 2.9274 | 2.6589
|  | WHITEHOUSE | HT |  |  |  |  | 6.0621 | 5.8537 | 5.6168 | 5.3453 | 5.2484 | 5.0968 | 5.0063 | 4.9168 | 4.8263 | 4.7284 | 4.3084 | 3.9768 | 3.7495 | 5.3821 | 5.14 | 4.8642 | 4.5463 | 4.4368 | 4.2632 | 4.1632 | 4.0642 | 3.9632 | 3.8558 | 3.4779 | 3.0747 | 2.7453 | 5.1095 | 4.88 | 4.6189 | 4.32 | 4.2147 | 4.0495 | 3.9526 | 3.8579 | 3.7611 | 3.6579 | 3.2947 | 2.9095 | 2.5895
|  | WHITEHOUSE | HE |  |  |  |  | 6.1105 | 5.9663 | 5.7663 | 5.5284 | 5.4695 | 5.2758 | 5.2105 | 5.1526 | 5.0979 | 5.0463 | 4.8716 | 4.7168 | 4.5779 | 5.4379 | 5.2716 | 5.0368 | 4.7568 | 4.6926 | 4.4705 | 4.4011 | 4.3379 | 4.2768 | 4.2189 | 4.0211 | 3.8442 | 3.6832 | 5.1632 | 5.0042 | 4.7832 | 4.52 | 4.4579 | 4.2463 | 4.1779 | 4.1168 | 4.0589 | 4.0032 | 3.8126 | 3.6442 | 3.4916
|  | WHITEHOUSE | FB |  |  |  |  | 8.3832 | 6.1611 | 6.0884 | 6.0011 | 5.9305 | 5.84 | 5.7305 | 5.6874 | 5.6474 | 5.5947 | 5.4211 | 5.2463 | 5.0979 | 7.2011 | 5.4968 | 5.4126 | 5.3105 | 5.2295 | 5.1253 | 4.9968 | 4.9484 | 4.9021 | 4.8421 | 4.6463 | 4.4453 | 4.2726 | 7.4779 | 5.2179 | 5.1389 | 5.0421 | 4.9653 | 4.8653 | 4.7442 | 4.6979 | 4.6537 | 4.5968 | 4.4105 | 4.22 | 4.0568
| PERSLEY | WHITESTRIPES | MINIMUM HEADROOM | NJ 92850 11054 | NO | NO | 0 | 16.2216 | 16.1068 | 13.93 | 13.47 | 15.9279 | 15.07 | 14.9405 | 14.7995 | 14.6647 | 14.5089 | 13.9742 | 13.39 | 12.8511 | 14.9947 | 14.8653 | 11.5484 | 11.0253 | 14.6895 | 12.9232 | 12.7874 | 12.6358 | 12.4937 | 12.3274 | 11.76 | 11.1463 | 10.5768 | 15.4739 | 15.3413 | 12.0108 | 11.4929 | 15.1655 | 13.3645 | 13.2297 | 13.0792 | 12.9371 | 12.7718 | 12.2076 | 11.5961 | 11.0297
|  | WHITESTRIPES | EE |  |  |  |  | 16.2237 | 16.1121 | 13.93 | 13.47 | 23.4511 | 21.2511 | 21.0405 | 20.8416 | 20.6584 | 20.4395 | 19.7216 | 19.0258 | 18.2868 | 14.9947 | 14.8684 | 11.5484 | 11.0253 | 21.0042 | 18.4347 | 18.2105 | 17.9979 | 17.8032 | 17.5653 | 16.7968 | 16.0705 | 15.2842 | 15.4739 | 15.3434 | 12.0108 | 11.4929 | 21.4708 | 18.9339 | 18.7118 | 18.5003 | 18.3066 | 18.0708 | 17.3066 | 16.5918 | 15.8097
|  | WHITESTRIPES | HT |  |  |  |  | 16.2216 | 16.1068 | 13.9647 | 13.5026 | 23.4732 | 23.2763 | 23.0826 | 22.89 | 22.6921 | 22.4237 | 21.5784 | 20.7121 | 20.0153 | 14.9947 | 14.8653 | 11.5937 | 11.0705 | 21.0389 | 20.8295 | 20.6242 | 20.42 | 20.2116 | 19.92 | 19.2042 | 18.2926 | 17.3632 | 15.4739 | 15.3413 | 12.0539 | 11.5371 | 21.5055 | 21.2971 | 21.0929 | 20.8897 | 20.6824 | 20.3929 | 19.6887 | 18.7824 | 17.8592
|  | WHITESTRIPES | HE |  |  |  |  | 16.3163 | 16.2405 | 14.2963 | 13.9121 | 23.9321 | 21.7679 | 21.6016 | 21.4858 | 21.3721 | 21.2416 | 20.8521 | 20.5289 | 20.2374 | 15.0937 | 15.0053 | 11.9505 | 11.5105 | 21.5305 | 18.9947 | 18.8168 | 18.6926 | 18.5726 | 18.4274 | 18.0063 | 17.6579 | 17.34 | 15.5729 | 15.4824 | 12.4097 | 11.9739 | 21.9939 | 19.4918 | 19.3139 | 19.1908 | 19.0708 | 18.9266 | 18.5087 | 18.1634 | 17.8466
|  | WHITESTRIPES | FB |  |  |  |  | 16.27 | 16.1858 | 16.1016 | 16.0153 | 15.9279 | 15.07 | 14.9405 | 14.7995 | 14.6647 | 14.5089 | 13.9742 | 13.39 | 12.8511 | 15.0547 | 14.9632 | 14.8716 | 14.7768 | 14.6895 | 12.9232 | 12.7874 | 12.6358 | 12.4937 | 12.3274 | 11.76 | 11.1463 | 10.5768 | 15.5266 | 15.4424 | 15.3497 | 15.2529 | 15.1655 | 13.3645 | 13.2297 | 13.0792 | 12.9371 | 12.7718 | 12.2076 | 11.5961 | 11.0297
| CARRADALE 1 | WHITING BAY | MINIMUM HEADROOM | NS 04169 26277 | YES | YES | 0 | 6.6926 | 6.6516 | 6.6179 | 6.5747 | 6.5368 | 6.4937 | 6.4505 | 6.4126 | 6.3758 | 6.3432 | 6.2126 | 6.1011 | 6.0179 | 6.6421 | 6.5979 | 6.5589 | 6.5126 | 6.4705 | 6.4242 | 6.3779 | 6.3379 | 6.2979 | 6.2621 | 6.1253 | 6.0011 | 5.9105 | 6.6537 | 6.6105 | 6.5716 | 6.5253 | 6.4842 | 6.4379 | 6.3916 | 6.3516 | 6.3116 | 6.2758 | 6.1389 | 6.0147 | 5.9232
|  | WHITING BAY | EE |  |  |  |  | 6.6926 | 6.6516 | 6.6179 | 6.5747 | 6.5368 | 6.4937 | 6.4505 | 6.4126 | 6.3758 | 6.3432 | 6.2158 | 6.1011 | 6.0179 | 6.6421 | 6.5979 | 6.5589 | 6.5126 | 6.4705 | 6.4242 | 6.3779 | 6.3379 | 6.2979 | 6.2621 | 6.1253 | 6.0011 | 5.9105 | 6.6537 | 6.6105 | 6.5716 | 6.5253 | 6.4842 | 6.4379 | 6.3916 | 6.3516 | 6.3116 | 6.2758 | 6.1389 | 6.0147 | 5.9232
|  | WHITING BAY | HT |  |  |  |  | 6.7042 | 6.6705 | 6.6358 | 6.5979 | 6.5611 | 6.5211 | 6.4842 | 6.4453 | 6.4063 | 6.3695 | 6.2126 | 6.1032 | 6.0295 | 6.6558 | 6.6168 | 6.5789 | 6.5379 | 6.4968 | 6.4537 | 6.4126 | 6.3695 | 6.3284 | 6.2884 | 6.1474 | 6.0179 | 5.9147 | 6.6674 | 6.6305 | 6.5937 | 6.5526 | 6.5126 | 6.4705 | 6.4295 | 6.3874 | 6.3474 | 6.3063 | 6.1674 | 6.0411 | 5.9389
|  | WHITING BAY | HE |  |  |  |  | 6.7316 | 6.7063 | 6.6874 | 6.6642 | 6.64 | 6.6095 | 6.5811 | 6.5589 | 6.5358 | 6.5179 | 6.4505 | 6.3916 | 6.3516 | 6.6874 | 6.6589 | 6.6368 | 6.6126 | 6.5874 | 6.5558 | 6.5242 | 6.5011 | 6.4758 | 6.4568 | 6.3832 | 6.3168 | 6.2737 | 6.6979 | 6.6716 | 6.6495 | 6.6253 | 6.6 | 6.5684 | 6.5368 | 6.5137 | 6.4895 | 6.4695 | 6.3968 | 6.3326 | 6.2895
|  | WHITING BAY | FB |  |  |  |  | 6.7453 | 6.7305 | 6.7137 | 6.6979 | 6.6811 | 6.6632 | 6.6484 | 6.6305 | 6.6137 | 6.5937 | 6.5189 | 6.4442 | 6.3884 | 6.7011 | 6.6842 | 6.6663 | 6.6484 | 6.6295 | 6.6105 | 6.5937 | 6.5737 | 6.5537 | 6.5316 | 6.4484 | 6.3642 | 6.3011 | 6.7126 | 6.6958 | 6.6779 | 6.66 | 6.6421 | 6.6232 | 6.6063 | 6.5884 | 6.5695 | 6.5474 | 6.4663 | 6.3842 | 6.3232
| MYBSTER 1 | WICK | MINIMUM HEADROOM | ND 35583 50947 | NO | YES | 0.15306 | 16.7011 | 16.6505 | 16.6095 | 16.56 | 16.5032 | 15.0432 | 13.3021 | 11.6232 | 10.3558 | 9.6811 | 6.1947 | 5.8895 | 5.6674 | 15.7274 | 15.6789 | 15.5958 | 15.4063 | 15.2263 | 13.0316 | 10.9074 | 8.96 | 7.4947 | 6.7189 | 3.8221 | 3.4853 | 3.2389 | 16.16 | 16.0926 | 15.9937 | 15.8074 | 15.6295 | 13.5842 | 11.5874 | 9.7558 | 8.3758 | 7.6179 | 3.9347 | 3.5947 | 3.3442
|  | WICK | EE |  |  |  |  | 16.7011 | 16.6505 | 16.6095 | 16.56 | 16.5032 | 16.4284 | 16.3526 | 14.6768 | 12.9011 | 11.1674 | 8.5032 | 7.9874 | 7.5947 | 15.7274 | 15.6789 | 15.5958 | 15.4063 | 15.2263 | 15.0284 | 14.8242 | 12.6347 | 10.4968 | 8.4874 | 5.4284 | 4.8695 | 4.4442 | 16.16 | 16.0926 | 15.9937 | 15.8074 | 15.6295 | 15.4347 | 15.2347 | 13.1726 | 11.1589 | 9.2663 | 6.2663 | 5.6842 | 5.2368
|  | WICK | HT |  |  |  |  | 16.7105 | 16.6695 | 16.62 | 16.5705 | 16.5126 | 15.0432 | 13.3021 | 11.6232 | 10.3558 | 9.6811 | 8.4958 | 7.9926 | 7.6389 | 15.7347 | 15.6947 | 15.6463 | 15.5147 | 15.3253 | 13.0316 | 10.9074 | 8.96 | 7.4947 | 6.7189 | 5.5242 | 4.9263 | 4.4337 | 16.1737 | 16.1179 | 16.0632 | 15.9211 | 15.74 | 13.5842 | 11.5874 | 9.7558 | 8.3758 | 7.6179 | 6.4095 | 5.7979 | 5.2947
|  | WICK | HE |  |  |  |  | 16.7232 | 16.6811 | 16.6484 | 16.6042 | 16.5505 | 16.4842 | 16.4126 | 14.9947 | 13.1221 | 11.3147 | 6.1947 | 5.8895 | 5.6674 | 15.7474 | 15.7063 | 15.6747 | 15.6305 | 15.5779 | 15.5063 | 15.3663 | 12.9968 | 10.7116 | 8.6095 | 3.8221 | 3.4853 | 3.2389 | 16.1905 | 16.1368 | 16.1 | 16.0505 | 15.9937 | 15.9063 | 15.7684 | 13.5432 | 11.3958 | 9.4221 | 3.9347 | 3.5947 | 3.3442
|  | WICK | FB |  |  |  |  | 16.7495 | 16.7326 | 16.7158 | 16.6958 | 16.6758 | 16.6558 | 16.6337 | 16.6116 | 16.2937 | 15.4379 | 12.5074 | 12.1842 | 11.9368 | 15.7726 | 15.7568 | 15.7389 | 15.72 | 15.7 | 15.68 | 15.6589 | 15.6021 | 14.5779 | 13.5 | 9.9621 | 9.6 | 9.3189 | 16.2179 | 16.1937 | 16.1726 | 16.1505 | 16.1263 | 16.1032 | 16.0779 | 16.0105 | 15.0474 | 14.0347 | 10.7105 | 10.3653 | 10.0989
| WOODHILL | WOODHILL | MINIMUM HEADROOM | NJ 91259 07053 | NO | NO | 0 | 24.1821 | 24.12 | 24.1063 | 24.0432 | 23.9663 | 23.8737 | 23.7737 | 23.7032 | 23.6232 | 23.56 | 23.4768 | 23.3789 | 23.2516 | 22.7463 | 22.6768 | 22.66 | 22.5958 | 22.5105 | 22.4168 | 22.3095 | 22.2263 | 22.1411 | 22.0684 | 21.9979 | 21.8884 | 21.7347 | 24.9053 | 24.8432 | 24.8379 | 24.7747 | 24.6979 | 24.5968 | 24.4968 | 24.4337 | 24.3558 | 24.2916 | 24.2 | 24.1021 | 23.3779
|  | WOODHILL | EE |  |  |  |  | 24.1821 | 24.12 | 24.1063 | 24.0495 | 23.9779 | 23.8821 | 23.78 | 23.7032 | 23.6232 | 23.56 | 23.6179 | 23.4726 | 23.3453 | 22.7463 | 22.6768 | 22.66 | 22.5979 | 22.5189 | 22.4168 | 22.3095 | 22.2263 | 22.1411 | 22.0684 | 22.1453 | 21.9811 | 21.8316 | 24.9053 | 24.8432 | 24.8379 | 24.7821 | 24.7105 | 24.6147 | 24.5126 | 24.4358 | 24.3558 | 24.2916 | 24.4389 | 24.18 | 23.5463
|  | WOODHILL | HT |  |  |  |  | 24.1926 | 24.1716 | 24.1105 | 24.0432 | 23.9663 | 23.8916 | 23.8116 | 23.7284 | 23.8116 | 23.7179 | 23.5989 | 23.4032 | 23.2516 | 22.7589 | 22.7358 | 22.6695 | 22.5958 | 22.5105 | 22.4305 | 22.3453 | 22.2579 | 22.3558 | 22.2516 | 22.1926 | 21.9516 | 21.7347 | 24.9158 | 24.9042 | 24.8432 | 24.7747 | 24.6979 | 24.6232 | 24.5432 | 24.4611 | 24.5884 | 24.4947 | 24.4853 | 24.1695 | 23.3779
|  | WOODHILL | HE |  |  |  |  | 24.2084 | 24.1484 | 24.1389 | 24.0768 | 24.0032 | 23.8737 | 23.7737 | 23.7105 | 23.6495 | 23.6189 | 23.4768 | 23.3789 | 23.3147 | 22.7789 | 22.7158 | 22.7074 | 22.6421 | 22.5632 | 22.4253 | 22.3211 | 22.2547 | 22.1905 | 22.1537 | 21.9979 | 21.8884 | 21.8116 | 24.9316 | 24.8716 | 24.8716 | 24.8095 | 24.7358 | 24.5968 | 24.4968 | 24.4337 | 24.3726 | 24.3421 | 24.2 | 24.1021 | 23.9463
|  | WOODHILL | FB |  |  |  |  | 24.2347 | 24.2084 | 24.18 | 24.1505 | 24.1179 | 24.0832 | 24.0484 | 24.0126 | 23.9758 | 23.9358 | 23.7895 | 23.6653 | 23.6011 | 22.8074 | 22.7779 | 22.7463 | 22.7147 | 22.6779 | 22.64 | 22.6021 | 22.5621 | 22.5221 | 22.4779 | 22.3179 | 22.1789 | 22.1011 | 24.9579 | 24.9316 | 24.9032 | 24.8737 | 24.8411 | 24.8063 | 24.7716 | 24.7358 | 24.6989 | 24.6589 | 24.5126 | 24.3884 | 24.3063

## Local Authority Reference
#VALUE! | Local Authority | Grid Supply Point | Primary Substation
| Aberdeen City | CLAYHILLS | BALNAGASK
| Aberdeen City | PERSLEY | BRIDGE OF DON
| Aberdeen City | CLAYHILLS | CLAYHILLS
| Aberdeen City | CLAYHILLS | COMMERCE STREET
| Aberdeen City | CRAIGIEBUCKLER | CRAIGIEBUCKLER
| Aberdeen City | REDMOSS | CRAIGINCHES
| Aberdeen City | CRAIGIEBUCKLER | CRAIGTON
| Aberdeen City | CRAIGIEBUCKLER | CULTER
| Aberdeen City | WILLOWDALE | DENBURN
| Aberdeen City | DYCE | DYCE NORTH
| Aberdeen City | WILLOWDALE | GREYFRIARS
| Aberdeen City | DYCE | HARVEST AVENUE
| Aberdeen City | PERSLEY | HAUDAGAIN
| Aberdeen City | WILLOWDALE | HAYTON
| Aberdeen City | REDMOSS | KINCORTH
| Aberdeen City | PERSLEY | NORTHFIELD
| Aberdeen City | KINTORE | PARK
| Aberdeen City | WOODHILL | QUEENS LANE NORTH
| Aberdeen City | REDMOSS | REDMOSS
| Aberdeen City | CRAIGIEBUCKLER | RUTHRIESTON
| Aberdeen City | KINTORE | SKENE
| Aberdeen City | WOODHILL | SPRINGHILL
| Aberdeen City | PERSLEY | ST MACHAR
| Aberdeen City | WILLOWDALE | ST NICHOLAS
| Aberdeen City | PERSLEY | STONEYWOOD T1&T2
| Aberdeen City | PERSLEY | STONEYWOOD T3
| Aberdeen City | KINTORE | TORRYBURN
| Aberdeen City | PERSLEY | WHITESTRIPES
| Aberdeen City | WOODHILL | WOODHILL
| Aberdeenshire | TARLAND | ABOYNE
| Aberdeenshire | BOAT OF GARTEN | AVIEMORE
| Aberdeenshire | TARLAND | BALLATER
| Aberdeenshire | BOAT OF GARTEN | BALLINDALLOCH
| Aberdeenshire | DYCE | BALMEDIE
| Aberdeenshire | KINTORE | BANCHORY
| Aberdeenshire | PETERHEAD SHELL | BODDAM
| Aberdeenshire | TUMMEL BRIDGE | BONSKEID
| Aberdeenshire | PERSLEY | BRIDGE OF DON
| Aberdeenshire | CRAIGIEBUCKLER | CRAIGTON
| Aberdeenshire | KEITH | CULLEN
| Aberdeenshire | CRAIGIEBUCKLER | CULTER
| Aberdeenshire | COUPAR ANGUS | DALRULZION
| Aberdeenshire | KEITH | DUFFTOWN
| Aberdeenshire | DYCE | DYCE NORTH
| Aberdeenshire | FIDDES | EDZELL
| Aberdeenshire | DYCE | ELLON
| Aberdeenshire | FRASERBURGH | FRASERBURGH
| Aberdeenshire | KINTORE | FYVIE
| Aberdeenshire | STRICHEN | HATTON
| Aberdeenshire | KEITH | HUNTLY
| Aberdeenshire | BRIDGE OF DUN | INCHBARE
| Aberdeenshire | KEITH | INSCH
| Aberdeenshire | FIDDES | INVERBERVIE
| Aberdeenshire | KINTORE | INVERURIE
| Aberdeenshire | KEITH | KEITH
| Aberdeenshire | KINTORE | KEMNAY
| Aberdeenshire | REDMOSS | KINCORTH
| Aberdeenshire | DYCE | KINGSEAT
| Aberdeenshire | FIDDES | LAURENCEKIRK
| Aberdeenshire | KEITH | LIMEHILLOCKS
| Aberdeenshire | BRIDGE OF DUN | LOGIE PERT
| Aberdeenshire | MACDUFF | MACDUFF
| Aberdeenshire | KEITH | MARNOCH
| Aberdeenshire | LUNANHEAD | MARYTON
| Aberdeenshire | STRICHEN | MAUD
| Aberdeenshire | KINTORE | METHLICK
| Aberdeenshire | KINTORE | MIDMAR
| Aberdeenshire | STRICHEN | MINTLAW
| Aberdeenshire | BRIDGE OF DUN | MONTROSE NORTH
| Aberdeenshire | TARLAND | MOSSAT
| Aberdeenshire | STRICHEN | NEW PITSLIGO
| Aberdeenshire | REDMOSS | NEWTONHILL
| Aberdeenshire | KINTORE | OLDMELDRUM
| Aberdeenshire | KINTORE | PARK
| Aberdeenshire | PETERHEAD GRANGE | PETERHEAD GRANGE
| Aberdeenshire | PETERHEAD GRANGE | PETERHEAD NORTH STREET
| Aberdeenshire | MACDUFF | PORTSOY
| Aberdeenshire | REDMOSS | REDMOSS
| Aberdeenshire | CRAIGIEBUCKLER | RUTHRIESTON
| Aberdeenshire | KINTORE | SKENE
| Aberdeenshire | WOODHILL | SPRINGHILL
| Aberdeenshire | BRIDGE OF DUN | ST CYRUS
| Aberdeenshire | ST FERGUS GAS | ST FERGUS GAS TERM
| Aberdeenshire | FIDDES | STONEHAVEN
| Aberdeenshire | STRICHEN | STONEYHILL
| Aberdeenshire | TARLAND | STRATHDON
| Aberdeenshire | STRICHEN | STRICHEN
| Aberdeenshire | KINTORE | TORRYBURN
| Aberdeenshire | MACDUFF | TURRIFF
| Aberdeenshire | TARLAND | WHITEHOUSE
| Aberdeenshire | PERSLEY | WHITESTRIPES
| Angus | COUPAR ANGUS | ALYTH
| Angus | MILTON OF CRAIGIE | ASHLUDIE
| Angus | ABERNETHY | BALBEGGIE
| Angus | MILTON OF CRAIGIE | BALDOVIE
| Angus | TARLAND | BALLATER
| Angus | KINTORE | BANCHORY
| Angus | BRIDGE OF DUN | BRECHIN
| Angus | BRIDGE OF DUN | BRIDGE OF DUN
| Angus | MILTON OF CRAIGIE | BROUGHTY FERRY
| Angus | ARBROATH | CARNOUSTIE
| Angus | ARBROATH | CHARLES AVENUE
| Angus | COUPAR ANGUS | COUPAR ANGUS
| Angus | COUPAR ANGUS | DALRULZION
| Angus | FIDDES | EDZELL
| Angus | MILTON OF CRAIGIE | EDZELL STREET
| Angus | ARBROATH | ELLIOT DEPOT
| Angus | LUNANHEAD | FRIOCKHEIM
| Angus | CHARLESTON | GOURDIE
| Angus | ARBROATH | HUME STREET
| Angus | BRIDGE OF DUN | INCHBARE
| Angus | LUNANHEAD | INVERARITY
| Angus | FIDDES | LAURENCEKIRK
| Angus | COUPAR ANGUS | LEOCH
| Angus | LUNANHEAD | LOCHSIDE
| Angus | BRIDGE OF DUN | LOGIE PERT
| Angus | MILTON OF CRAIGIE | LONGHAUGH
| Angus | LUNANHEAD | LUNANHEAD
| Angus | LYNDHURST | MACALPINE ROAD
| Angus | LUNANHEAD | MARYTON
| Angus | BRIDGE OF DUN | MILL ROAD MONTROSE
| Angus | BRIDGE OF DUN | MONTROSE NORTH
| Angus | ARBROATH | REDFORD
| Angus | BRIDGE OF DUN | ST CYRUS
| Angus | LYNDHURST | WEST KIRKTON
| Argyll and Bute | PORT ANN | AIRIGH-NA-BRODAIG
| Argyll and Bute | CARRADALE | BALLURE
| Argyll and Bute | TAYNUILT | BARCALDINE
| Argyll and Bute | RANNOCH | BLACKMOUNT
| Argyll and Bute | PORT ANN | BOWMORE
| Argyll and Bute | DUNOON | BRUCHAG
| Argyll and Bute | CLACHAN | BUTTERBRIDGE
| Argyll and Bute | CARRADALE | CAMPBELTOWN
| Argyll and Bute | KILLIN | CASHLIE
| Argyll and Bute | KILLIN | CHAORACH
| Argyll and Bute | CARRADALE | CLAONAIG
| Argyll and Bute | DUNOON | COLINTRAIVE
| Argyll and Bute | TAYNUILT | CONNEL
| Argyll and Bute | PORT ANN | CRINAN
| Argyll and Bute | PORT ANN | CROMALT
| Argyll and Bute | TAYNUILT | DALMALLY
| Argyll and Bute | TAYNUILT | DERVAIG
| Argyll and Bute | CARRADALE | DIPPEN
| Argyll and Bute | CLACHAN | DOUGLAS PIER
| Argyll and Bute | STRATHLEVEN | DRYMEN
| Argyll and Bute | DUNOON | DUNOON
| Argyll and Bute | TAYNUILT | EREDINE
| Argyll and Bute | DUNOON | GLENDARUEL
| Argyll and Bute | RANNOCH | GLENETIVE
| Argyll and Bute | DUNOON | INNELLAN
| Argyll and Bute | CLACHAN | INVERARAY
| Argyll and Bute | PORT ANN | INVERNEIL
| Argyll and Bute | DUNOON | KAMES
| Argyll and Bute | TAYNUILT | KENMORE
| Argyll and Bute | TAYNUILT | KERRERA
| Argyll and Bute | TAYNUILT | KILCHRENAN
| Argyll and Bute | TAYNUILT | KILMELFORD
| Argyll and Bute | TAYNUILT | KILNINVER
| Argyll and Bute | TAYNUILT | KINLOCH
| Argyll and Bute | TUMMEL BRIDGE | KINLOCH RANNOCH
| Argyll and Bute | TAYNUILT | LOCHDONHEAD
| Argyll and Bute | PORT ANN | LOCHGILPHEAD
| Argyll and Bute | CLACHAN | LOCHGOILHEAD
| Argyll and Bute | PORT ANN | LUSSAGIVEN
| Argyll and Bute | DUNOON | NEWTON
| Argyll and Bute | TAYNUILT | OBAN
| Argyll and Bute | DUNOON | OTTER FERRY
| Argyll and Bute | PORT ANN | PORT ASKAIG
| Argyll and Bute | PORT ANN | PORT ELLEN
| Argyll and Bute | DUNOON | ROTHESAY
| Argyll and Bute | FORT WILLIAM | SALEN 2
| Argyll and Bute | DUNOON | SANDBANK
| Argyll and Bute | TAYNUILT | SCAMMADALE
| Argyll and Bute | PORT ANN | STONEFIELD
| Argyll and Bute | CLACHAN | STRACHUR
| Argyll and Bute | DUNOON | STRONDAVON
| Argyll and Bute | PORT ANN | TARBERT JURA
| Argyll and Bute | PORT ANN | TARBERT LOCH FYNE
| Argyll and Bute | TAYNUILT | TAYNUILT
| Argyll and Bute | TAYNUILT | TIRORAN BRIDGE
| Argyll and Bute | RANNOCH | TYNDRUM
| Argyll and Bute | CARRADALE | WESTPARK FERGUS
| Clackmannanshire | ABERNETHY | GLENDEVON
| Clackmannanshire | BRACO | GLENEAGLES
| Clackmannanshire | ABERNETHY | MILNATHORT
| Dundee City | MILTON OF CRAIGIE | ASHLUDIE
| Dundee City | MILTON OF CRAIGIE | BALDOVIE
| Dundee City | MILTON OF CRAIGIE | BROUGHTY FERRY
| Dundee City | CHARLESTON | CHARLESTON
| Dundee City | DUDHOPE | CONSTABLE STREET
| Dundee City | MILTON OF CRAIGIE | EDZELL STREET
| Dundee City | CHARLESTON | GOURDIE
| Dundee City | COUPAR ANGUS | LEOCH
| Dundee City | LYNDHURST | LOCHEE
| Dundee City | MILTON OF CRAIGIE | LONGHAUGH
| Dundee City | LYNDHURST | LYNDHURST
| Dundee City | LYNDHURST | MACALPINE ROAD
| Dundee City | CHARLESTON | MENZIESHILL
| Dundee City | MILTON OF CRAIGIE | MILTON OF CRAIGIE
| Dundee City | CHARLESTON | NINEWELLS
| Dundee City | MILTON OF CRAIGIE | OLD CRAIGIE ROAD
| Dundee City | GLENAGNES | OVERGATE
| Dundee City | DUDHOPE | ROSEBANK STREET
| Dundee City | GLENAGNES | WALTON
| Dundee City | LYNDHURST | WEST KIRKTON
| East Dunbartonshire | STRATHLEVEN | KEPCULLOCH
| East Dunbartonshire | STRATHLEVEN | KILLEARN
| East Dunbartonshire | BRACO | KIPPEN
| Eilean Siar | ARDMORE | AIRD
| Eilean Siar | STORNOWAY | ARNISH
| Eilean Siar | STORNOWAY | BARVAS
| Eilean Siar | STORNOWAY | BATTERY POINT
| Eilean Siar | STORNOWAY | CALLANISH
| Eilean Siar | ARDMORE | CLACHAN
| Eilean Siar | STORNOWAY | COLL
| Eilean Siar | ARDMORE | DRIMORE
| Eilean Siar | STORNOWAY | GISLA
| Eilean Siar | ARDMORE | HARRIS GRID
| Eilean Siar | STORNOWAY | LAXAY
| Eilean Siar | ARDMORE | LOCH CARNAN
| Eilean Siar | STORNOWAY | MAARUIG
| Eilean Siar | ARDMORE | POLLACHAR
| Eilean Siar | ARDMORE / HARRIS GRID | STOCKINISH
| Eilean Siar | ARDMORE / HARRIS GRID | TARBERT
| Fife | ABERNETHY | ABERNETHY
| Fife | ABERNETHY | BRIDGE OF EARN
| Fife | ABERNETHY | GLENDEVON
| Fife | ABERNETHY | MILNATHORT
| Highland | FORT AUGUSTUS | ABERCHALDER
| Highland | KEITH | ABERLOUR
| Highland | GRUDIE BRIDGE | ACHILTIBUIE
| Highland | BROADFORD | ACHINTEE
| Highland | BEAULY | AIGAS
| Highland | FORT WILLIAM | ANNAT
| Highland | NAIRN | ARDERSIER
| Highland | FORT AUGUSTUS | ARDOCHY
| Highland | FORT WILLIAM | ARISAIG
| Highland | GRUDIE BRIDGE | AULTBEA
| Highland | BOAT OF GARTEN | AVIEMORE
| Highland | ALNESS | BALALDIE
| Highland | BOAT OF GARTEN | BALLINDALLOCH
| Highland | TAYNUILT | BARCALDINE
| Highland | DOUNREAY | BETTYHILL
| Highland | GRUDIE BRIDGE | BIDEN CLAN RAONAILD
| Highland | RANNOCH | BLACKMOUNT
| Highland | BEAULY | BLACKSTAND
| Highland | BOAT OF GARTEN | BOAT OF GARTEN
| Highland | TUMMEL BRIDGE | BONSKEID
| Highland | RANNOCH | BRIDGE OF GAUR
| Highland | BROADFORD | BROADFORD
| Highland | FORT AUGUSTUS | BUNOICH
| Highland | TUMMEL BRIDGE | CALVINE
| Highland | DOUNREAY | COLDBACKIE
| Highland | ST FILLANS | COMRIE
| Highland | BEAULY | CONON BRIDGE
| Highland | BEAULY | CONON FALLS
| Highland | ALNESS | CONTULLICH
| Highland | FORT WILLIAM | CORRAN
| Highland | ALNESS | CROSSHILLS
| Highland | INVERNESS | CULLODEN
| Highland | NAIRN | DALCROSS
| Highland | INVERNESS | DALNEIGH
| Highland | BOAT OF GARTEN | DALWHINNIE
| Highland | BEAULY | DINGWALL
| Highland | BRORA | DORNOCH
| Highland | DOUNREAY | DOUNREAY
| Highland | CEANNACROC | DRUMNADROCHIT
| Highland | GRUDIE BRIDGE | DRUMRUNIE
| Highland | DUNVEGAN | DRYNOCH
| Highland | DUNOON | DUNOON
| Highland | DUNVEGAN | DUNVEGAN GRID
| Highland | INVERNESS | ERROGIE
| Highland | FORT WILLIAM | FISHNISH
| Highland | NAIRN | FORRES
| Highland | DOUNREAY | FORSS
| Highland | INVERNESS | FOYERS
| Highland | GRUDIE BRIDGE | GARBAT FOREST
| Highland | ALNESS | GLASTULLICH
| Highland | SHIN | GLEDFIELD
| Highland | FORT AUGUSTUS | GLEN LAOGH
| Highland | KINLOCHLEVEN | GLENCOE
| Highland | FORT AUGUSTUS | GLENDOE PRIMARY
| Highland | RANNOCH | GLENETIVE
| Highland | FORT WILLIAM | GLENUIG
| Highland | BRORA | GOLSPIE
| Highland | BOAT OF GARTEN | GRANTOWN
| Highland | GRUDIE BRIDGE | GRUDIE BRIDGE
| Highland | THURSO | HALKIRK
| Highland | THURSO | HASTIGROW
| Highland | BRORA | HELMSDALE
| Highland | INVERNESS | HILTON
| Highland | INVERNESS | INVERARNIE
| Highland | GRUDIE BRIDGE | INVERBROOM
| Highland | FORT AUGUSTUS | INVERGARRY
| Highland | ALNESS | INVERGORDON
| Highland | FORT WILLIAM | INVERLOCHY
| Highland | INVERNESS | INVERNESS
| Highland | BROADFORD | KALNAKIL
| Highland | GRUDIE BRIDGE | KERRY FALLS
| Highland | BEAULY | KILTARLITY
| Highland | FORT WILLIAM | KINGAIRLOCH
| Highland | BOAT OF GARTEN | KINGUSSIE
| Highland | TUMMEL BRIDGE | KINLOCH RANNOCH
| Highland | GRUDIE BRIDGE | KINLOCHEWE
| Highland | KINLOCHLEVEN | KINLOCHLEVEN
| Highland | FORT WILLIAM | KINLOCHMOIDART
| Highland | BROADFORD | KISHORNHILL
| Highland | BROADFORD | KYLE
| Highland | LAIRG | LAIRG GRID
| Highland | MYBSTER | LATHERON
| Highland | NAIRN | LETHEN
| Highland | GRUDIE BRIDGE | LETTEREWE
| Highland | FORT WILLIAM | LIDDESDALE
| Highland | GRUDIE BRIDGE | LOCH GLASCARNOCH
| Highland | FORT WILLIAM | LOCHALINE
| Highland | GRUDIE BRIDGE | LOCHINVER
| Highland | BROADFORD | LOWER OLLACH
| Highland | FORT WILLIAM | MALLAIG
| Highland | BEAULY | MARYBANK
| Highland | MYBSTER | MELVICH
| Highland | THURSO | MOUNT PLEASANT
| Highland | BEAULY | MUIR OF ORD
| Highland | BEAULY | MUIREND
| Highland | NAIRN | NAIRN CENTRAL
| Highland | ALNESS | NIGG
| Highland | BROADFORD | NOSTIE BRIDGE
| Highland | THURSO | ORMLIE
| Highland | CASSLEY | OVERSCAIG
| Highland | ALNESS | PEDDIESTON
| Highland | FORT WILLIAM | PINEGROVE
| Highland | FORT WILLIAM | POOR HOUSE
| Highland | DUNVEGAN | PORTREE
| Highland | QUOICH | QUOICH PRIMARY
| Highland | FORT WILLIAM | RAHOY
| Highland | INVERNESS | RAIGMORE
| Highland | INVERNESS | LONGMAN DRIVE
| Highland | CASSLEY | RHICONICH
| Highland | TAYNUILT | SALEN
| Highland | BROADFORD | SHIELDAIG
| Highland | SHIN | SHIN
| Highland | FORT WILLIAM | SHONA BEAG
| Highland | BROADFORD | SKULAMUS
| Highland | FORT WILLIAM | STRONTIAN
| Highland | ALNESS | TAIN
| Highland | BOAT OF GARTEN | TOMATIN
| Highland | LAIRG | TORBOLL
| Highland | LAIRG | TRESSADY
| Highland | DUNVEGAN | UIG
| Highland | GRUDIE BRIDGE | ULLAPOOL
| Highland | INVERNESS | WATERLOO PLACE
| Highland | KILLIN | WESTER DRUMMOND
| Highland | MYBSTER | WICK
| Moray | KEITH | ABERLOUR
| Moray | ELGIN | ASHGROVE
| Moray | BOAT OF GARTEN | AVIEMORE
| Moray | TARLAND | BALLATER
| Moray | BOAT OF GARTEN | BALLINDALLOCH
| Moray | ELGIN | BILBOHALL
| Moray | KEITH | BUCKIE
| Moray | ELGIN | BURGHEAD
| Moray | KEITH | CULLEN
| Moray | ELGIN | CUMMING STREET
| Moray | KEITH | DUFFTOWN
| Moray | ELGIN | ELGIN
| Moray | ELGIN | FOCHABERS
| Moray | NAIRN | FORRES
| Moray | BOAT OF GARTEN | GRANTOWN
| Moray | KEITH | HUNTLY
| Moray | KEITH | KEITH
| Moray | ELGIN | KINLOSS
| Moray | NAIRN | LETHEN
| Moray | ELGIN | LHANBRYDE
| Moray | KEITH | LIMEHILLOCKS
| Moray | ELGIN | LOSSIEMOUTH
| Moray | KEITH | MARNOCH
| Moray | TARLAND | MOSSAT
| Moray | NAIRN | NAIRN CENTRAL
| Moray | MACDUFF | PORTSOY
| Moray | KEITH | ROTHES
| Moray | TARLAND | STRATHDON
| North Ayrshire | CARRADALE | BALLIEKINE
| North Ayrshire | CARRADALE | BRODICK
| North Ayrshire | DUNOON | BRUCHAG
| North Ayrshire | CARRADALE | MACHRIE
| North Ayrshire | CARRADALE | WHITING BAY
| North Lanarkshire | BRACO | KIPPEN
| Orkney Islands | THURSO | BURGARHILL
| Orkney Islands | THURSO | EDAY
| Orkney Islands | THURSO | EDAY TIDAL
| Orkney Islands | THURSO | FLOTTA
| Orkney Islands | THURSO | KIRKWALL
| Orkney Islands | THURSO | LYNESS
| Orkney Islands | THURSO | NORTH HOY
| Orkney Islands | THURSO | RACKWICK
| Orkney Islands | THURSO | ROUSAY
| Orkney Islands | THURSO | SANDAY
| Orkney Islands | THURSO | SHAPINSAY
| Orkney Islands | THURSO | ST MARYS
| Orkney Islands | THURSO | STROMNESS
| Orkney Islands | THURSO | STRONSAY
| Orkney Islands | THURSO | WESTRAY
| Perth and Kinross | TUMMEL BRIDGE | ABERFELDY
| Perth and Kinross | ABERNETHY | ABERNETHY
| Perth and Kinross | COUPAR ANGUS | ALYTH
| Perth and Kinross | BOAT OF GARTEN | AVIEMORE
| Perth and Kinross | ABERNETHY | BALBEGGIE
| Perth and Kinross | TARLAND | BALLATER
| Perth and Kinross | RANNOCH | BLACKMOUNT
| Perth and Kinross | COUPAR ANGUS | BLAIRGOWRIE
| Perth and Kinross | TUMMEL BRIDGE | BONSKEID
| Perth and Kinross | ABERNETHY | BRIDGE OF EARN
| Perth and Kinross | RANNOCH | BRIDGE OF GAUR
| Perth and Kinross | BURGHMUIR | BURGHMUIR
| Perth and Kinross | BRACO | CALLANDER
| Perth and Kinross | TUMMEL BRIDGE | CALVINE
| Perth and Kinross | COUPAR ANGUS | CAPUTH
| Perth and Kinross | KILLIN | CASHLIE
| Perth and Kinross | KILLIN | CHAORACH
| Perth and Kinross | KILLIN | COSHIEVILLE
| Perth and Kinross | COUPAR ANGUS | COUPAR ANGUS
| Perth and Kinross | BRACO | CRIEFF
| Perth and Kinross | ST FILLANS | DALCHONZIE
| Perth and Kinross | COUPAR ANGUS | DALRULZION
| Perth and Kinross | BOAT OF GARTEN | DALWHINNIE
| Perth and Kinross | BRACO | DUNBLANE
| Perth and Kinross | ABERNETHY | ERROL
| Perth and Kinross | TUMMEL BRIDGE | FINCASTLE
| Perth and Kinross | BRACO | FORTEVIOT
| Perth and Kinross | ABERNETHY | GLENDEVON
| Perth and Kinross | BRACO | GLENEAGLES
| Perth and Kinross | RANNOCH | GLENETIVE
| Perth and Kinross | BURGHMUIR | GOODLYBURN
| Perth and Kinross | CHARLESTON | GOURDIE
| Perth and Kinross | ABERNETHY | HARBOUR
| Perth and Kinross | BURGHMUIR | INVERALMOND
| Perth and Kinross | FORT WILLIAM | INVERLOCHY
| Perth and Kinross | KILLIN | KILLIN TOWN
| Perth and Kinross | BOAT OF GARTEN | KINGUSSIE
| Perth and Kinross | TUMMEL BRIDGE | KINLOCH RANNOCH
| Perth and Kinross | COUPAR ANGUS | LEOCH
| Perth and Kinross | KILLIN | LOCHEARNHEAD
| Perth and Kinross | LUNANHEAD | MARYTON
| Perth and Kinross | ABERNETHY | MILNATHORT
| Perth and Kinross | CHARLESTON | NINEWELLS
| Perth and Kinross | TUMMEL BRIDGE | PITLOCHRY
| Perth and Kinross | BURGHMUIR | REDGORTON
| Perth and Kinross | ABERNETHY | SCONE
| Perth and Kinross | ST FILLANS | ST FILLANS
| Perth and Kinross | BURGHMUIR | THIMBLEROW
| Perth and Kinross | RANNOCH | TYNDRUM
| Shetland Islands | WOODHILL | BRAE
| Shetland Islands | SHETLAND | FIRTH
| Shetland Islands | SHETLAND | GUTCHER
| Shetland Islands | SHETLAND | MID YELL
| Shetland Islands | SHETLAND | SANDWICK
| Shetland Islands | SHETLAND | SCALLOWAY
| Shetland Islands | SHETLAND | SUMBURGH
| Shetland Islands | SHETLAND | TUMBLIN
| Shetland Islands | SHETLAND | UNST
| Shetland Islands | SHETLAND | VOE
| Stirling | STRATHLEVEN | ABERFOYLE
| Stirling | KILLIN | ARCHYLE
| Stirling | BRACO | CALLANDER
| Stirling | KILLIN | CASHLIE
| Stirling | KILLIN | CHAORACH
| Stirling | KILLIN | COSHIEVILLE
| Stirling | ST FILLANS | DALCHONZIE
| Stirling | TAYNUILT | DALMALLY
| Stirling | STRATHLEVEN | DRYMEN
| Stirling | BRACO | DUNBLANE
| Stirling | BRACO | GLENEAGLES
| Stirling | STRATHLEVEN | KEPCULLOCH
| Stirling | STRATHLEVEN | KILLEARN
| Stirling | KILLIN | KILLIN TOWN
| Stirling | BRACO | KIPPEN
| Stirling | KILLIN | LOCHEARNHEAD
| Stirling | KILLIN | LUBNAIG
| Stirling | ST FILLANS | ST FILLANS
| Stirling | RANNOCH | TYNDRUM
| West Dunbartonshire | STRATHLEVEN | BLAIRLINNANS
| West Dunbartonshire | STRATHLEVEN | DRYMEN
| West Dunbartonshire | STRATHLEVEN | KILLEARN

## EISD
#VALUE! | GSPs in November 2025 LTDS | Demand |  | Generation |  | Comments (optional)
|  | EISD | Under review at freeze date? | EISD | Under review at freeze date?
| Abernethy | 2028 | Under active review | 2028 | Under active review
| Braco | 2025 | Under active review | 2035 | Under active review
| Burghmuir | 2028 | Under active review | 2028 | Under active review
| Coupar Angus | NA |  | 2029 | Under active review
| Killin | 2025 | Under active review | 2030 | Under active review
| Rannoch | 2025 | Under active review | 2025 | Under active review
| St Fillans | 2025 | Under active review | 2028 | Under active review
| Tummel Bridge | 2025 | Under active review | 2026 | Under active review
| Redmoss | NA |  | 2031
| Woodhill | NA |  | NA
| Ardkinglas | 2025 | Under active review | 2030 | Under active review
| Ardmore | 2028 | Under active review | 2028 | Under active review
| Cassley | NA | Under active review | 2028 | Under active review
| Charleston | 2030 | Under active review | 2028 | Under active review
| Clayhills | NA |  | 2025 | Under active review
| Lyndhurst | 2032 | Under active review | 2035 | Under active review
| Peterhead Grange | 2033 | Under active review | 2033 | Under active review
| Dunbeath | NA |  | NA | Under active review
| Alness | NA |  | 2030 | Under active review
| Beauly | NA |  | 2030 | Under active review
| Broadford | 2028 | Under active review | 2028 | Under active review
| Brora | NA |  | 2034 | Under active review
| Dunvegan | NA |  | 2028 | Under active review
| Fasnakyle | 2025 | Under active review | 2035 | Under active review
| Grudie Bridge | NA |  | NA
| Lairg | NA |  | 2033 | Under active review
| Shin | NA |  | NA | Under active review
| Orrin | NA |  | NA
| Dounreay | NA |  | 2033 | Under active review
| Fraserburgh | 2033 | Under active review | 2033 | Under active review
| Dallas | 2025 | Under active review | N/A
| Kinlochleven | 2025 | Under active review | N/A
| Glenfarclas | 2025 | Under active review | N/A
| Berryburn | 2024 | Under active review | 2030 | Under active review
| Fetteresso | NA |  | 2029 | Under active review
| Craigiebuckler | NA |  | 2032
| Kintore | 2032 | Under active review | 2032 | Under active review
| Tarland | NA |  | 2032 | Under active review
| Willowdale | NA |  | 2030
| Dyce | 2025 | Under active review | 2025 | Under active review
| Persley | NA |  | NA
| Peterhead Shell | NA |  | NA
| Strichen | 2033 | Under active review | 2033 | Under active review
| Arbroath | 2026 | Under active review | 2032 | Under active review
| Bridge of Dun | NA |  | 2032 | Under active review
| Fiddes | NA |  | 2032 | Under active review
| Lunanhead | 2028 | Under active review | 2028 | Under active review
| Milton of Craigie | NA |  | 2033 | Under active review
| Ceannacroc | NA |  | NA
| Fort Augustus | 2035 | Under active review | 2035 | Under active review
| Quoich | 2028 |  | 2028
| Boat of Garten | 2025 | Under active review | 2030 | Under active review
| Inverness | NA |  | 2030 | Under active review
| Nairn | 2027 | Under active review | 2027 | Under active review
| Rothienorman | 2033 | Under active review | 2033 | Under active review
| Cairnford | NA |  | NA
| Elgin | 2025 | Under active review | 2027 | Under active review
| Keith 1 | 2028 | Under active review | 2028 | Under active review
| Keith 2 | 2028 | Under active review | 2028 | Under active review
| MacDuff | NA |  | 2029 | Under active review
| Carradale 1 | 2025 | Under active review | 2034 | Under active review
| Carradale 2 | 2025 | Under active review | 2034 | Under active review
| Clachan | 2025 | Under active review | 2030 | Under active review
| Dunoon | 2025 | Under active review | 2028 | Under active review
| Fort William | NA | Under active review | NA | Under active review
| Port Ann | 2029 | Under active review | 2034 | Under active review
| Taynuilt | 2025 | Under active review | 2034 | Under active review
| Dudhope | NA |  | 2028 | Under active review
| Mybster 1 | NA |  | 2035
| Mybster 2 | NA |  | NA
| Thurso | NA |  | 2033
| Sloy | 2025 | Under active review | 2030 | Under active review
| St Fergus Gas | NA |  | 2033 | Under active review
Links to additional public-domain information related to the EISDs, provided by the Transmission Owner
https://www.ssen-transmission.co.uk/customer-connections/transmission-owner-reinforcement-instruction-tori-quarterly-update-reports/
2025-04-11 | Transmission Owner's freeze date
SHEPD | DNO Licence area
SSEN Transmisson | Transmision Owner providing
V1.1 11/04/2025 | Last update (version, date)
Notes
1 Earliest in service dates (EISDs) represent a snapshot of the Transmission Owner's view at the 'freeze date' of the earliest date for connection for NEW applications for demand and generation of significant size (>1MW)
For customers which already have accepted connections with a DNO, DNOs may already have agreed with transmission for earlier connection dates for demand and generation customers
2 Approved by Ofgem in April 2025, connections reform aim to remove unviable projects from the queue and prioritise projects meeting specific readiness and strategic alignment criteria. A revised timeline has been published on 13 February 2026 to illustrate the issue of modification offers by NESO.
https://www.neso.energy/industry-information/connections-reform/connections-reform-timeline
3 Connections Network Design Methodology (CNDM) defines the queue formation process undertaken during application windows, including allocation of new capacity and reallocation of released capacity when projects exit the queue.
https://www.neso.energy/industry-information/connections-reform/connections-reform-design-documents-and-methodologies
4 Where the transmission owner is actively reviewing projects as part of the connection reform process, this is shown as "under active review". Projects that have not yet entered the review process are shown as “Pending review”.
5 Where an EISD has not been established for a GSP, this is shown as N/A.
There is likely to be some headroom for connection because there is no constraint yet defined with defined construction works affecting connnection, this is shown as "no date restriction identified".
6 Where the transmission owner is actively reviewing construction works and earliest in service dates for new applications may be revised e.g. due to an application for capacity affecting that GSP, this is shown as "under active review"
7 The EISDs reflect both works at a Grid Supply Point and in wider tranmission network.
8 Unlike the rest of the DNO Network Scenario Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output.
9 The list of GSPs includes at a minimum the GSPs associated with the primary substations and Bulk Supply Points in the DNO's last Long Term Development Statement Table 3. Future new GSPs may not be included.