## Contents
SHEPD Network Scenario Headroom Report 2025 Summary
Our Network Scenario Headroom Report (NSHR) is published to enable customers, developers, generators, local authorities and other interested third parties to view the possible headroom capacity at our Primary Substations up to 2050. SHEPD have used the latest Distribution Future Energy Scenarios (DFES) data to inform four scenarios of demand and generation forecasts. SSEN's best view of the future demand and generation needs on our network is aligned to the Holistic Transition scenario, moving from Consumer Transformation which was our best view in the 2024 NSHR. Although the NSHR provides a view of the future in terms of our potential available capacity and constraints on our network, we would encourage any party using this information in their decision-making process to engage with us ahead of making an application to connect or offer flexible services.
Network Headroom Report Contents
Tab | Description
Key Information | This tab provides some additional detail to assist users with how to read the data presented within this report.
Primary Headroom Dem | This tab provides the demand headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Primary Headroom Gen | This tab provides the generation headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Local Authority Reference | This tab provides information on the local authorities and the Primaries that support those areas
EISD | To indicate potential transmission constraints by 'Earliest in Service Date' per Grid Supply Point (GSP)
May 2025
Version 1.1

## Key Information
SHEPD Network Scenario Headroom Report 2025 Key Information
Our Network Scenario Headroom Report (NSHR) has been developed to be used in conjunction with our others documents that combine to make the full Network Development Plan; the other documents to reference are the Network Development Plan Methodology & Assumptions and Network Development Report. The capacity that demand and generation growth is measured against is the firm capacity of the primary substation or BSP as per our Load Indices submission to Ofgem and as indicated by our Long Term Development Statement. Firm capacity means the available capacity on the network with a single feed on outage; for instance a twin transformer sites firm capacity would be the lowest capacity available on a single transformer. For single transformer sites, the firm capacity is based on the backfeed supply available to restore supplies; this may be limited by the backfeed circuit capacity rather than the transformer providing the backfeed. In order to identify future overloaded network assets, forecasts are created which combine our long term DFES projections with the estimated contribution from our connections pipeline after appropriate diversity factors have been applied. When reviewing the headroom reports for demand and generation the following applies: GREEN and POSTIVE VALUES = Capacity is forecast to be available RED and NEGATIVE VALUES = There are constraints forecast It must be noted that forecasts in RED do not mean that connections cannot be made; there are opportunities through flexible services that can enable connections without triggering network reinforcement. We would encourage any developer, generator or customer to contact us to discuss their connection and available opportuinites to connect. The data shown within this NSHR is used by us to identify long term investment opportunities where there are constraints highlighted. As the forecast is scenario based, these constraints are subject to change and will be reviewed and published annually by SHEPD. Please note that our DFES scenario naming convention has been updated since 2024 to more closely align with the updated NESO Future Energy Scenario (FES) pathways framework. Published annually, the FES framework outlines different scenarios for the future of the whole energy system. SSEN's DFES builds on the FES scenarios by engaging a diverse and expert range of stakeholders, undertaking detailed investigations into the pipeline of projects seeking to connect, and reflecting extensive industry and local area insight to forecast future load on SSEN’s network.
New DFES Scenario | Previous DFES Scenario | FES Pathway Description
Electric Engagement (EE) | Consumer Transformation (CT) | Net zero met through mainly electrified demand. Consumers are highly engaged in the energy transition through smart technologies that reduce energy demands, utilising technologies such as electric heat pumps and electric vehicles.
Holistic Transition (HT) | Leading the Way (LW) | Net zero met through a mix of electrification and hydrogen, with hydrogen mainly around industrial clusters. Consumer engagement in the transition is very strong with demand shifting, with smart homes and electric vehicles providing flexibility to the grid.
Hydrogen Evolution (HE) | System Transformation (ST) | Net zero met through fast progress for hydrogen in industry and heat. Many consumers will have hydrogen boilers, though energy efficiency will be key to reducing cost. There are low levels of consumer engagement. Hydrogen will be prevalent for heavy goods vehicles but electric car uptake is strong.
Counterfactual (CF) | Falling Short (FS) | Net zero missed, though some progress is made for decarbonisation compared to today. While home insulation improves, there is still a heavy reliance on gas across all sectors, particularly power and space heating. Electric vehicle uptake is slower than the net zero pathways, but still displaces petrol and diesel.
`
May 2025
Version 1.1

## Primary Headroom Dem
#VALUE! | Grid Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Demand (MVA) | Demand Headroom Winter (MVA) | [12 empty] | Demand Headroom Summer (MVA) | [12 empty] | Demand Headroom Spring/Autumn (MVA)
[8 empty] | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
| FORT AUGUSTUS | ABERCHALDER | MINIMUM HEADROOM | NH 33843 03575 | YES | YES | 0 | 0.19518 | 0.19212 | 0.1911 | 0.18192 | 0.17988 | 0.17069 | 0.17069 | 0.16865 | 0.16661 | 0.16763 | 0.16253 | 0.15743 | 0.15743 | 0.19351 | 0.19249 | 0.19147 | 0.18229 | 0.18127 | 0.1731 | 0.17718 | 0.17208 | 0.16902 | 0.1731 | 0.17514 | 0.17106 | 0.16494 | 0.19639 | 0.19333 | 0.19231 | 0.18312 | 0.1821 | 0.17292 | 0.1719 | 0.17088 | 0.16884 | 0.16986 | 0.16476 | 0.16067 | 0.16067
|  | ABERCHALDER | EE |  |  |  |  | 0.19518 | 0.19212 | 0.1911 | 0.18192 | 0.17988 | 0.17069 | 0.17069 | 0.17376 | 0.16967 | 0.16763 | 0.16253 | 0.15845 | 0.15845 | 0.19351 | 0.19249 | 0.19147 | 0.18229 | 0.18127 | 0.1731 | 0.17718 | 0.18127 | 0.17718 | 0.17514 | 0.17514 | 0.17106 | 0.168 | 0.19639 | 0.19333 | 0.19231 | 0.18312 | 0.1821 | 0.17292 | 0.1719 | 0.17598 | 0.1719 | 0.16986 | 0.16476 | 0.16169 | 0.16169
|  | ABERCHALDER | HT |  |  |  |  | 0.20233 | 0.20131 | 0.1911 | 0.19008 | 0.19008 | 0.1809 | 0.17886 | 0.16865 | 0.16865 | 0.16763 | 0.16355 | 0.15743 | 0.15743 | 0.20065 | 0.20065 | 0.19249 | 0.19045 | 0.19045 | 0.18229 | 0.18127 | 0.1731 | 0.17616 | 0.17616 | 0.17514 | 0.17106 | 0.17106 | 0.20353 | 0.20251 | 0.19333 | 0.19129 | 0.19129 | 0.1821 | 0.18108 | 0.17088 | 0.17088 | 0.16986 | 0.16578 | 0.16067 | 0.16067
|  | ABERCHALDER | HE |  |  |  |  | 0.20233 | 0.20233 | 0.19212 | 0.1911 | 0.19008 | 0.17988 | 0.17886 | 0.16967 | 0.16661 | 0.16967 | 0.16559 | 0.16253 | 0.15947 | 0.20065 | 0.20065 | 0.19249 | 0.19147 | 0.19045 | 0.18127 | 0.18024 | 0.17208 | 0.16902 | 0.17616 | 0.17514 | 0.1731 | 0.17004 | 0.20353 | 0.20353 | 0.19333 | 0.19231 | 0.19129 | 0.1821 | 0.18006 | 0.1719 | 0.16884 | 0.1719 | 0.16782 | 0.16476 | 0.16169
|  | ABERCHALDER | CF |  |  |  |  | 0.20233 | 0.20233 | 0.19416 | 0.19212 | 0.19212 | 0.1911 | 0.18294 | 0.17988 | 0.17273 | 0.17069 | 0.17478 | 0.16763 | 0.16151 | 0.20065 | 0.20065 | 0.19351 | 0.19249 | 0.19249 | 0.19045 | 0.18229 | 0.18127 | 0.17412 | 0.1731 | 0.18127 | 0.17412 | 0.16494 | 0.20353 | 0.20353 | 0.19537 | 0.19333 | 0.19333 | 0.19129 | 0.18312 | 0.1821 | 0.17496 | 0.1719 | 0.17598 | 0.16884 | 0.16373
| TUMMEL BRIDGE | ABERFELDY | MINIMUM HEADROOM | NN 84889 48876 | NO | YES | 0.211 | 3.6528 | 3.4712 | 3.2926 | 3.0763 | 2.8089 | 2.5222 | 2.1763 | 1.8375 | 1.5569 | 1.2161 | 0.18752 | -0.22473 | -0.3033 | 4.6089 | 4.4865 | 4.3712 | 4.2243 | 4.0477 | 3.8794 | 3.6447 | 3.4161 | 3.2498 | 3.0487 | 2.4671 | 2.2089 | 1.9028 | 4.2528 | 4.0906 | 3.9294 | 3.7334 | 3.4936 | 3.2355 | 2.9079 | 2.5947 | 2.3447 | 2.0406 | 1.1334 | 0.76303 | 0.69364
|  | ABERFELDY | EE |  |  |  |  | 3.6528 | 3.4712 | 3.2987 | 3.0794 | 2.8181 | 2.56 | 2.1763 | 1.8375 | 1.5569 | 1.2161 | 0.18752 | -0.20636 | -0.29718 | 4.6089 | 4.4865 | 4.3712 | 4.2243 | 4.0477 | 3.8794 | 3.6447 | 3.4161 | 3.2498 | 3.0487 | 2.4671 | 2.2089 | 1.9559 | 4.2528 | 4.0906 | 3.9345 | 3.7334 | 3.4967 | 3.2498 | 2.9079 | 2.5947 | 2.3447 | 2.0406 | 1.1334 | 0.78242 | 0.69874
|  | ABERFELDY | HT |  |  |  |  | 3.6692 | 3.4987 | 3.2926 | 3.0763 | 2.8089 | 2.5222 | 2.2263 | 1.9232 | 1.6018 | 1.2447 | 0.26813 | -0.22473 | -0.3033 | 4.6263 | 4.5222 | 4.3987 | 4.2671 | 4.0998 | 3.9294 | 3.7508 | 3.5824 | 3.3987 | 3.2049 | 2.6436 | 2.4028 | 2.3671 | 4.2651 | 4.11 | 3.9294 | 3.7345 | 3.4936 | 3.2355 | 2.9702 | 2.6998 | 2.412 | 2.0998 | 1.21 | 0.76303 | 0.69364
|  | ABERFELDY | HE |  |  |  |  | 3.6896 | 3.5681 | 3.4304 | 3.2753 | 3.0651 | 2.813 | 2.4957 | 2.2334 | 1.9477 | 1.61 | 0.74364 | 0.30691 | 0.14772 | 4.6385 | 4.5508 | 4.4579 | 4.3528 | 4.21 | 4.0518 | 3.8559 | 3.6998 | 3.5212 | 3.3232 | 2.7457 | 2.4467 | 2.1875 | 4.2855 | 4.1722 | 4.0487 | 3.9059 | 3.7151 | 3.4916 | 3.212 | 2.9794 | 2.7273 | 2.4334 | 1.6355 | 1.2426 | 1.1049
|  | ABERFELDY | CF |  |  |  |  | 3.7518 | 3.6875 | 3.6059 | 3.51 | 3.41 | 3.2773 | 3.1304 | 2.9447 | 2.8212 | 2.6375 | 1.664 | 0.98242 | 0.52425 | 4.6865 | 4.6355 | 4.5743 | 4.5049 | 4.4283 | 4.3273 | 4.2202 | 4.0845 | 3.9947 | 3.8651 | 3.1763 | 2.5253 | 1.9028 | 4.3457 | 4.2855 | 4.21 | 4.1202 | 4.0334 | 3.9089 | 3.7773 | 3.61 | 3.4957 | 3.3334 | 2.4743 | 1.8406 | 1.4294
| STRATHLEVEN | ABERFOYLE | MINIMUM HEADROOM | NS 53215 99705 | YES | YES | 0.384 | 3.3282 | 3.2873 | 3.2373 | 3.17 | 3.1251 | 3.0577 | 2.973 | 2.8741 | 2.7996 | 2.6904 | 2.3802 | 2.2118 | 2.1292 | 3.9996 | 3.9588 | 3.9139 | 3.8577 | 3.8118 | 3.7506 | 3.6741 | 3.5833 | 3.5333 | 3.4639 | 3.2424 | 3.1312 | 2.8649 | 3.8134 | 3.7552 | 3.6899 | 3.6062 | 3.5409 | 3.4593 | 3.3491 | 3.2215 | 3.146 | 3.047 | 2.7756 | 2.6378 | 2.5725
|  | ABERFOYLE | EE |  |  |  |  | 3.3282 | 3.2873 | 3.2373 | 3.17 | 3.1251 | 3.0577 | 2.973 | 2.8741 | 2.7996 | 2.6904 | 2.3802 | 2.2812 | 2.2077 | 3.9996 | 3.9588 | 3.9139 | 3.8577 | 3.8118 | 3.7506 | 3.6741 | 3.5833 | 3.5333 | 3.4639 | 3.2424 | 3.1312 | 2.9751 | 3.8134 | 3.7552 | 3.6899 | 3.6062 | 3.5409 | 3.4593 | 3.3491 | 3.2215 | 3.146 | 3.047 | 2.7756 | 2.697 | 2.6368
|  | ABERFOYLE | HT |  |  |  |  | 3.3618 | 3.3282 | 3.2914 | 3.2424 | 3.2006 | 3.1445 | 3.1037 | 3.0322 | 2.9445 | 2.8414 | 2.4322 | 2.2118 | 2.1292 | 4.0271 | 3.9945 | 3.9608 | 3.9159 | 3.872 | 3.822 | 3.7802 | 3.7149 | 3.6577 | 3.5935 | 3.3333 | 3.1986 | 3.1526 | 3.8419 | 3.7909 | 3.7368 | 3.6674 | 3.6093 | 3.5338 | 3.4664 | 3.3736 | 3.294 | 3.1991 | 2.8317 | 2.6378 | 2.5725
|  | ABERFOYLE | HE |  |  |  |  | 3.3618 | 3.3333 | 3.3026 | 3.2618 | 3.2271 | 3.1802 | 3.1424 | 3.0782 | 3.019 | 2.9547 | 2.5251 | 2.373 | 2.3077 | 4.023 | 3.9965 | 3.9679 | 3.9292 | 3.8955 | 3.8486 | 3.8108 | 3.7506 | 3.6965 | 3.6384 | 3.3424 | 3.1996 | 3.0526 | 3.8419 | 3.8021 | 3.7613 | 3.7103 | 3.6634 | 3.6011 | 3.546 | 3.4664 | 3.396 | 3.3144 | 2.9185 | 2.7889 | 2.7389
|  | ABERFOYLE | CF |  |  |  |  | 3.371 | 3.3506 | 3.319 | 3.2986 | 3.2628 | 3.2373 | 3.1996 | 3.1516 | 3.1322 | 3.0904 | 2.8037 | 2.5455 | 2.3659 | 4.0312 | 4.0098 | 3.9802 | 3.9547 | 3.92 | 3.8924 | 3.8516 | 3.8026 | 3.7782 | 3.7322 | 3.4659 | 3.1914 | 2.8649 | 3.8532 | 3.8185 | 3.7787 | 3.7429 | 3.6991 | 3.6613 | 3.6103 | 3.547 | 3.5144 | 3.4583 | 3.1491 | 2.9215 | 2.7817
| KEITH 2 | ABERLOUR | MINIMUM HEADROOM | NJ 24809 40878 | NO | YES | 1.931 | 0.61642 | 0.52357 | 0.44296 | 0.3654 | 0.24193 | 0.14398 | 0.047037 | -0.11113 | -0.33358 | -0.53051 | -1.0948 | -1.3254 | -1.405 | 1.4511 | 1.3797 | 1.3174 | 1.2623 | 1.1664 | 1.0879 | 1.0164 | 0.91642 | 0.74193 | 0.59704 | 0.2103 | 0.078669 | 0.0052 | 1.043 | 0.97357 | 0.91949 | 0.86949 | 0.7552 | 0.63989 | 0.52969 | 0.38377 | 0.16949 | -0.017249 | -0.53868 | -0.72745 | -0.80807
|  | ABERLOUR | EE |  |  |  |  | 0.61642 | 0.52357 | 0.44296 | 0.3654 | 0.24193 | 0.14398 | 0.047037 | -0.11113 | -0.33358 | -0.53051 | -1.0948 | -1.2713 | -1.2999 | 1.4511 | 1.3797 | 1.3174 | 1.2623 | 1.1664 | 1.0879 | 1.0164 | 0.91642 | 0.74193 | 0.59704 | 0.21642 | 0.14398 | 0.12867 | 1.043 | 0.97357 | 0.91949 | 0.86949 | 0.7552 | 0.63989 | 0.52969 | 0.38377 | 0.16949 | -0.017249 | -0.53868 | -0.67337 | -0.69684
|  | ABERLOUR | HT |  |  |  |  | 0.64193 | 0.55622 | 0.49193 | 0.42867 | 0.31847 | 0.23989 | 0.14193 | 0.012343 | -0.25092 | -0.44684 | -1.0611 | -1.3254 | -1.405 | 1.4736 | 1.4123 | 1.3644 | 1.3154 | 1.2307 | 1.1756 | 1.1062 | 1.0215 | 0.79806 | 0.64398 | 0.24193 | 0.10418 | 0.048057 | 1.0613 | 0.99908 | 0.9552 | 0.91336 | 0.83479 | 0.74296 | 0.64091 | 0.5154 | 0.25826 | 0.070506 | -0.50398 | -0.72745 | -0.80807
|  | ABERLOUR | HE |  |  |  |  | 0.63989 | 0.56234 | 0.50622 | 0.44602 | 0.34193 | 0.26949 | 0.18581 | 0.081731 | -0.10296 | -0.27031 | -1.0172 | -1.2489 | -1.3621 | 1.4705 | 1.4144 | 1.3695 | 1.3215 | 1.244 | 1.1879 | 1.1205 | 1.0338 | 0.87459 | 0.73989 | 0.2103 | 0.078669 | 0.0052 | 1.0603 | 1.0021 | 0.9654 | 0.92765 | 0.85418 | 0.79296 | 0.69704 | 0.57867 | 0.38683 | 0.22357 | -0.48766 | -0.69684 | -0.80296
|  | ABERLOUR | CF |  |  |  |  | 0.65622 | 0.59908 | 0.56132 | 0.52459 | 0.44908 | 0.39806 | 0.35622 | 0.29806 | 0.2103 | 0.12255 | -0.39072 | -0.8897 | -1.1999 | 1.4848 | 1.4389 | 1.4123 | 1.3807 | 1.3225 | 1.2817 | 1.2491 | 1.1991 | 1.1236 | 1.046 | 0.62561 | 0.27357 | 0.090914 | 1.0685 | 1.0236 | 1.0001 | 0.97663 | 0.91949 | 0.88479 | 0.8603 | 0.81949 | 0.72561 | 0.62969 | 0.10418 | -0.36623 | -0.65194
| ABERNETHY | ABERNETHY | MINIMUM HEADROOM | NO 20094 17132 | YES | YES | 0.074 | 1.6158 | 1.5689 | 1.5148 | 1.4464 | 1.3944 | 1.2964 | 1.176 | 1.0638 | 0.99131 | 0.8607 | 0.58417 | 0.52601 | 0.50968 | 2.2689 | 2.2505 | 2.224 | 2.1872 | 2.1566 | 2.0954 | 2.026 | 1.9576 | 1.9168 | 1.8454 | 1.678 | 1.6015 | 1.3729 | 2.0954 | 2.0566 | 2.0076 | 1.9474 | 1.8964 | 1.8087 | 1.6995 | 1.5964 | 1.5311 | 1.4189 | 1.1832 | 1.1342 | 1.1209
|  | ABERNETHY | EE |  |  |  |  | 1.6158 | 1.5689 | 1.5148 | 1.4464 | 1.3944 | 1.2964 | 1.176 | 1.0638 | 0.99131 | 0.8607 | 0.58417 | 0.55152 | 0.53927 | 2.2689 | 2.2505 | 2.224 | 2.1872 | 2.1566 | 2.0954 | 2.026 | 1.9576 | 1.9168 | 1.8454 | 1.678 | 1.6168 | 1.5209 | 2.0954 | 2.0566 | 2.0076 | 1.9474 | 1.8964 | 1.8087 | 1.6995 | 1.5964 | 1.5311 | 1.4189 | 1.1832 | 1.1566 | 1.1444
|  | ABERNETHY | HT |  |  |  |  | 1.6423 | 1.5985 | 1.5576 | 1.5046 | 1.4485 | 1.3556 | 1.2821 | 1.1811 | 1.0699 | 0.88417 | 0.64233 | 0.52601 | 0.50968 | 2.2903 | 2.274 | 2.2525 | 2.225 | 2.1985 | 2.1485 | 2.1158 | 2.0627 | 2.0036 | 1.9107 | 1.7515 | 1.6893 | 1.678 | 2.1148 | 2.076 | 2.0372 | 1.9903 | 1.9403 | 1.8627 | 1.8015 | 1.7127 | 1.6189 | 1.4658 | 1.2362 | 1.1342 | 1.1209
|  | ABERNETHY | HE |  |  |  |  | 1.6434 | 1.6087 | 1.577 | 1.528 | 1.4872 | 1.4005 | 1.3127 | 1.2138 | 1.1117 | 0.98519 | 0.65764 | 0.57805 | 0.56989 | 2.2913 | 2.274 | 2.2566 | 2.2301 | 2.2087 | 2.1617 | 2.1138 | 2.0607 | 2.0025 | 1.9321 | 1.7229 | 1.6332 | 1.5423 | 2.1148 | 2.0872 | 2.0576 | 2.0199 | 1.9821 | 1.9036 | 1.8321 | 1.7434 | 1.6566 | 1.5474 | 1.2515 | 1.1811 | 1.1729
|  | ABERNETHY | CF |  |  |  |  | 1.6474 | 1.6178 | 1.576 | 1.5525 | 1.5209 | 1.4699 | 1.4107 | 1.3607 | 1.2995 | 1.2066 | 0.89642 | 0.68621 | 0.57805 | 2.2944 | 2.2801 | 2.2556 | 2.2444 | 2.224 | 2.1985 | 2.1648 | 2.1332 | 2.0903 | 2.0372 | 1.8219 | 1.6015 | 1.3729 | 2.1199 | 2.0944 | 2.0607 | 2.0393 | 2.0087 | 1.9699 | 1.9178 | 1.875 | 1.8178 | 1.7352 | 1.4587 | 1.2617 | 1.174
| TARLAND | ABOYNE | MINIMUM HEADROOM | NO 52048 98716 | NO | NO | 1.669 | 7.1534 | 6.9922 | 6.7208 | 6.4003 | 6.0708 | 5.6881 | 5.2595 | 4.8003 | 4.584 | 4.2361 | 3.3279 | 3.0401 | 2.9187 | 8.7871 | 8.6626 | 8.5218 | 8.3554 | 8.184 | 7.983 | 7.7524 | 7.4963 | 7.3687 | 7.1656 | 6.585 | 6.3544 | 5.4871 | 8.4141 | 8.1978 | 7.9509 | 7.659 | 7.3662 | 7.0233 | 6.6366 | 6.2192 | 6.0447 | 5.7243 | 4.8968 | 4.6335 | 4.5274
|  | ABOYNE | EE |  |  |  |  | 7.1534 | 6.9922 | 6.7208 | 6.4003 | 6.0708 | 5.6881 | 5.2595 | 4.8003 | 4.584 | 4.2361 | 3.3279 | 3.1605 | 3.1034 | 8.7871 | 8.6626 | 8.5218 | 8.3554 | 8.184 | 7.983 | 7.7524 | 7.4963 | 7.3687 | 7.1656 | 6.6136 | 6.432 | 6.0463 | 8.4141 | 8.1978 | 7.9509 | 7.659 | 7.3662 | 7.0233 | 6.6366 | 6.2192 | 6.0447 | 5.7243 | 4.8968 | 4.7458 | 4.6958
|  | ABOYNE | HT |  |  |  |  | 7.1901 | 7.032 | 6.782 | 6.4799 | 6.1993 | 5.8463 | 5.483 | 5.1238 | 4.7391 | 4.3901 | 3.5616 | 3.0401 | 2.9187 | 8.8279 | 8.7116 | 8.5922 | 8.4412 | 8.3034 | 8.1146 | 7.9197 | 7.7054 | 7.4789 | 7.2565 | 6.7065 | 6.4381 | 6.3228 | 8.459 | 8.2488 | 8.0253 | 7.7519 | 7.4988 | 7.1764 | 6.8519 | 6.5315 | 6.1804 | 5.86 | 5.107 | 4.6335 | 4.5274
|  | ABOYNE | HE |  |  |  |  | 7.1963 | 7.0922 | 6.9197 | 6.685 | 6.4514 | 6.1473 | 5.7993 | 5.484 | 5.1401 | 4.8452 | 3.6269 | 3.2789 | 3.1544 | 8.8289 | 8.734 | 8.6228 | 8.4912 | 8.3585 | 8.183 | 7.983 | 7.7728 | 7.5534 | 7.3422 | 6.585 | 6.3544 | 6.1167 | 8.4611 | 8.3121 | 8.1386 | 7.9304 | 7.7202 | 7.4447 | 7.1355 | 6.8529 | 6.5427 | 6.2662 | 5.0886 | 4.7447 | 4.6284
|  | ABOYNE | CF |  |  |  |  | 7.1993 | 7.1003 | 6.9912 | 6.7983 | 6.5861 | 6.3616 | 6.1177 | 5.8463 | 5.631 | 5.432 | 4.4616 | 3.9156 | 3.3126 | 8.8514 | 8.782 | 8.7105 | 8.6146 | 8.5116 | 8.4034 | 8.2748 | 8.1238 | 7.9952 | 7.8636 | 7.135 | 6.485 | 5.4871 | 8.4794 | 8.3488 | 8.21 | 8.0376 | 7.8458 | 7.6478 | 7.4315 | 7.1906 | 7.0039 | 6.8213 | 5.909 | 5.3662 | 4.7713
| GRUDIE BRIDGE | ACHILTIBUIE | MINIMUM HEADROOM | NC 01618 09557 | YES | NO | 0.082 | 0.12636 | 0.1131 | 0.088608 | 0.06922 | 0.04269 | 0.026363 | -0.0052694 | -0.043024 | -0.067514 | -0.097106 | -0.1716 | -0.19813 | -0.20323 | 0.28351 | 0.27636 | 0.26208 | 0.25085 | 0.23249 | 0.22126 | 0.20289 | 0.1784 | 0.1631 | 0.14575 | 0.096771 | 0.080445 | 0.04371 | 0.0039143 | -0.0083306 | -0.029759 | -0.048127 | -0.072616 | -0.088943 | -0.11956 | -0.15629 | -0.17976 | -0.20629 | -0.27568 | -0.30221 | -0.30833
|  | ACHILTIBUIE | EE |  |  |  |  | 0.12636 | 0.1131 | 0.088608 | 0.06922 | 0.04269 | 0.026363 | -0.0052694 | -0.043024 | -0.067514 | -0.097106 | -0.1716 | -0.18078 | -0.18792 | 0.28351 | 0.27636 | 0.26208 | 0.25085 | 0.23249 | 0.22126 | 0.20289 | 0.1784 | 0.1631 | 0.14575 | 0.096771 | 0.080445 | 0.055955 | 0.0039143 | -0.0083306 | -0.029759 | -0.048127 | -0.072616 | -0.088943 | -0.11956 | -0.15629 | -0.17976 | -0.20629 | -0.27568 | -0.28486 | -0.29302
|  | ACHILTIBUIE | HT |  |  |  |  | 0.13147 | 0.12126 | 0.10596 | 0.087588 | 0.0682 | 0.053914 | 0.026363 | -0.0011878 | -0.015473 | -0.046086 | -0.14915 | -0.19813 | -0.20323 | 0.28759 | 0.28249 | 0.2733 | 0.26412 | 0.25289 | 0.24371 | 0.22738 | 0.21106 | 0.20187 | 0.18453 | 0.11718 | 0.086567 | 0.084527 | 0.0090163 | -0.00016735 | -0.014453 | -0.029759 | -0.048127 | -0.062412 | -0.087922 | -0.11445 | -0.12976 | -0.15629 | -0.25629 | -0.30221 | -0.30833
|  | ACHILTIBUIE | HE |  |  |  |  | 0.13147 | 0.1233 | 0.11208 | 0.10085 | 0.081465 | 0.070241 | 0.048812 | 0.022282 | 0.013098 | -0.0083306 | -0.12364 | -0.15221 | -0.15833 | 0.28759 | 0.28351 | 0.27636 | 0.27024 | 0.25493 | 0.24779 | 0.23453 | 0.21922 | 0.2131 | 0.19983 | 0.12942 | 0.098812 | 0.078404 | 0.0090163 | 0.0018735 | -0.0073102 | -0.018535 | -0.033841 | -0.046086 | -0.068535 | -0.092004 | -0.10221 | -0.12466 | -0.2318 | -0.25935 | -0.26343
|  | ACHILTIBUIE | CF |  |  |  |  | 0.13249 | 0.12942 | 0.12126 | 0.11004 | 0.097792 | 0.083506 | 0.073302 | 0.055955 | 0.04269 | 0.036567 | -0.040984 | -0.11649 | -0.15425 | 0.28759 | 0.28861 | 0.28147 | 0.27228 | 0.26514 | 0.25698 | 0.25187 | 0.24065 | 0.22738 | 0.22432 | 0.16922 | 0.10187 | 0.04371 | 0.011057 | 0.0090163 | 0.00085306 | -0.010371 | -0.022616 | -0.03282 | -0.043024 | -0.060371 | -0.074657 | -0.079759 | -0.15323 | -0.22466 | -0.26037
| BEAULY | AIGAS | MINIMUM HEADROOM | NH 45362 40529 | YES | NO | 0 | 0.45122 | 0.44918 | 0.44714 | 0.44 | 0.43592 | 0.42673 | 0.41653 | 0.40224 | 0.4002 | 0.38898 | 0.36959 | 0.36653 | 0.36551 | 0.44806 | 0.44806 | 0.45316 | 0.44806 | 0.26514 | 0.43888 | 0.43378 | 0.42357 | 0.42153 | 0.41439 | 0.39806 | 0.39194 | 0.36847 | 0.45423 | 0.45321 | 0.45321 | 0.44811 | 0.44301 | 0.43383 | 0.42566 | 0.4124 | 0.4073 | 0.39709 | 0.37872 | 0.37668 | 0.37566
|  | AIGAS | EE |  |  |  |  | 0.45122 | 0.45531 | 0.44714 | 0.44 | 0.43592 | 0.42673 | 0.41653 | 0.40224 | 0.4002 | 0.38898 | 0.36959 | 0.36959 | 0.36551 | 0.44806 | 0.45827 | 0.45316 | 0.44806 | 0.445 | 0.43888 | 0.43378 | 0.42357 | 0.42153 | 0.41439 | 0.39806 | 0.39398 | 0.38378 | 0.45423 | 0.46036 | 0.45321 | 0.44811 | 0.44301 | 0.43383 | 0.42566 | 0.4124 | 0.4073 | 0.39709 | 0.37872 | 0.37872 | 0.37566
|  | AIGAS | HT |  |  |  |  | 0.46755 | 0.44918 | 0.44714 | 0.4451 | 0.44204 | 0.43898 | 0.42776 | 0.42469 | 0.41755 | 0.41041 | 0.37878 | 0.36653 | 0.36551 | 0.46235 | 0.44806 | 0.45316 | 0.45214 | 0.4501 | 0.4501 | 0.44194 | 0.43888 | 0.43582 | 0.42969 | 0.40929 | 0.40112 | 0.4001 | 0.47056 | 0.45321 | 0.45321 | 0.45219 | 0.44913 | 0.44607 | 0.43587 | 0.43179 | 0.42566 | 0.41852 | 0.38893 | 0.37668 | 0.37668
|  | AIGAS | HE |  |  |  |  | 0.46755 | 0.44918 | 0.4502 | 0.44918 | 0.4451 | 0.44204 | 0.4349 | 0.43082 | 0.42265 | 0.41551 | 0.38184 | 0.37265 | 0.37061 | 0.46235 | 0.44806 | 0.4552 | 0.45418 | 0.45214 | 0.4501 | 0.44398 | 0.44296 | 0.43786 | 0.43173 | 0.40724 | 0.39704 | 0.38684 | 0.47056 | 0.45321 | 0.45628 | 0.45526 | 0.45219 | 0.45015 | 0.44097 | 0.43791 | 0.43179 | 0.4226 | 0.38893 | 0.38077 | 0.38179
|  | AIGAS | CF |  |  |  |  | 0.46755 | 0.46041 | 0.45122 | 0.45327 | 0.44918 | 0.44408 | 0.44102 | 0.43388 | 0.43082 | 0.42367 | 0.40224 | 0.37469 | 0.36959 | 0.46235 | 0.4552 | 0.4552 | 0.45724 | 0.4552 | 0.45316 | 0.45112 | 0.445 | 0.44092 | 0.43582 | 0.41847 | 0.39194 | 0.36847 | 0.47056 | 0.46342 | 0.4573 | 0.46036 | 0.45628 | 0.45219 | 0.44913 | 0.43995 | 0.43893 | 0.43179 | 0.40934 | 0.38281 | 0.3777
| ARDMORE | AIRD | MINIMUM HEADROOM | NF 79163 53853 | NO | YES | 0.812 | 4.191 | 4.14 | 4.0828 | 4.0287 | 3.9369 | 3.8002 | 3.6971 | 3.6165 | 3.5083 | 3.4175 | 3.1971 | 3.1226 | 3.1022 | 5.1571 | 5.1255 | 5.0836 | 5.0438 | 4.9551 | 4.8469 | 4.7867 | 4.7214 | 4.6591 | 4.603 | 4.3938 | 4.2867 | 4.0949 | 4.7377 | 4.6959 | 4.6347 | 4.5806 | 4.4887 | 4.3306 | 4.2285 | 4.1489 | 4.0428 | 3.954 | 3.7449 | 3.6745 | 3.6581
|  | AIRD | EE |  |  |  |  | 4.191 | 4.14 | 4.0828 | 4.0287 | 3.9553 | 3.8002 | 3.6971 | 3.6165 | 3.5083 | 3.4175 | 3.1971 | 3.1665 | 3.1461 | 5.1571 | 5.1255 | 5.0836 | 5.0438 | 4.9938 | 4.8469 | 4.7867 | 4.7214 | 4.6591 | 4.603 | 4.4398 | 4.3877 | 4.2714 | 4.7377 | 4.6959 | 4.6347 | 4.5806 | 4.4979 | 4.3306 | 4.2285 | 4.1489 | 4.0428 | 3.954 | 3.7449 | 3.7153 | 3.6938
|  | AIRD | HT |  |  |  |  | 4.2185 | 4.1675 | 4.1247 | 4.0777 | 3.9369 | 3.8757 | 3.8236 | 3.7512 | 3.6767 | 3.5951 | 3.2665 | 3.1226 | 3.1042 | 5.1826 | 5.153 | 5.1255 | 5.0898 | 4.9551 | 4.9122 | 4.8755 | 4.8183 | 4.7642 | 4.7081 | 4.4745 | 4.3796 | 4.3438 | 4.7581 | 4.7163 | 4.6785 | 4.6387 | 4.4887 | 4.4306 | 4.3847 | 4.304 | 4.2234 | 4.1387 | 3.8132 | 3.6745 | 3.6581
|  | AIRD | HE |  |  |  |  | 4.2175 | 4.1767 | 4.1461 | 4.1083 | 4.0624 | 3.9328 | 3.8879 | 3.8226 | 3.7563 | 3.6798 | 3.3134 | 3.1634 | 3.1022 | 5.1806 | 5.152 | 5.1234 | 5.0887 | 5.053 | 4.9132 | 4.8694 | 4.8081 | 4.752 | 4.6877 | 4.3938 | 4.2867 | 4.2398 | 4.7561 | 4.7234 | 4.6969 | 4.6642 | 4.6234 | 4.4714 | 4.4347 | 4.3632 | 4.2898 | 4.2142 | 3.8632 | 3.7673 | 3.7122
|  | AIRD | CF |  |  |  |  | 4.2226 | 4.193 | 4.1553 | 4.1287 | 4.0981 | 4.0604 | 3.9369 | 3.9012 | 3.8604 | 3.8185 | 3.5747 | 3.3298 | 3.1491 | 5.1847 | 5.1694 | 5.1418 | 5.1224 | 5.104 | 5.0734 | 4.95 | 4.9194 | 4.8796 | 4.8438 | 4.6183 | 4.3867 | 4.0949 | 4.7602 | 4.7357 | 4.7061 | 4.6816 | 4.6571 | 4.6234 | 4.4816 | 4.451 | 4.401 | 4.3571 | 4.1071 | 3.8653 | 3.7398
| PORT ANN | AIRIGH-NA-BRODAIG | MINIMUM HEADROOM | NR 85849 74792 | YES | YES | 0 | 0.31966 | 0.31864 | 0.3166 | 0.30843 | 0.29925 | 0.29721 | 0.29517 | 0.29619 | 0.29415 | 0.29109 | 0.28599 | 0.28497 | 0.28292 | 0.3107 | 0.30968 | 0.30866 | 0.30151 | 0.29437 | 0.29233 | 0.29437 | 0.29131 | 0.29335 | 0.29233 | 0.28927 | 0.28723 | 0.28315 | 0.31773 | 0.31671 | 0.31569 | 0.30752 | 0.29834 | 0.2963 | 0.29528 | 0.29528 | 0.29426 | 0.29222 | 0.28712 | 0.28508 | 0.28304
|  | AIRIGH-NA-BRODAIG | EE |  |  |  |  | 0.31966 | 0.31864 | 0.3166 | 0.30843 | 0.29925 | 0.29721 | 0.29517 | 0.30027 | 0.29415 | 0.29211 | 0.28599 | 0.28599 | 0.28497 | 0.3107 | 0.30968 | 0.30866 | 0.30151 | 0.29437 | 0.29233 | 0.29437 | 0.29845 | 0.29539 | 0.29335 | 0.28927 | 0.28723 | 0.28621 | 0.31773 | 0.31671 | 0.31569 | 0.30752 | 0.29834 | 0.2963 | 0.29528 | 0.30038 | 0.29426 | 0.29222 | 0.28712 | 0.2861 | 0.28508
|  | AIRIGH-NA-BRODAIG | HT |  |  |  |  | 0.3268 | 0.32374 | 0.3166 | 0.31558 | 0.31354 | 0.30639 | 0.30435 | 0.29619 | 0.29415 | 0.29109 | 0.29007 | 0.28497 | 0.28292 | 0.31784 | 0.3158 | 0.30866 | 0.30866 | 0.30866 | 0.30151 | 0.29947 | 0.29131 | 0.29335 | 0.29233 | 0.29131 | 0.28825 | 0.28825 | 0.32487 | 0.32283 | 0.31569 | 0.31467 | 0.31365 | 0.30548 | 0.30344 | 0.29528 | 0.29426 | 0.29222 | 0.29018 | 0.28508 | 0.28304
|  | AIRIGH-NA-BRODAIG | HE |  |  |  |  | 0.3268 | 0.32374 | 0.31864 | 0.3166 | 0.3166 | 0.30843 | 0.30639 | 0.29823 | 0.29517 | 0.29619 | 0.29211 | 0.28701 | 0.28701 | 0.31784 | 0.3158 | 0.30968 | 0.30866 | 0.30866 | 0.30151 | 0.30151 | 0.29233 | 0.29335 | 0.29437 | 0.29233 | 0.28825 | 0.28825 | 0.32487 | 0.32283 | 0.31671 | 0.31569 | 0.31569 | 0.3065 | 0.30548 | 0.29732 | 0.2963 | 0.29528 | 0.29222 | 0.28916 | 0.28814
|  | AIRIGH-NA-BRODAIG | CF |  |  |  |  | 0.3268 | 0.32476 | 0.3166 | 0.3166 | 0.3166 | 0.30843 | 0.30843 | 0.30741 | 0.29823 | 0.29823 | 0.29415 | 0.29007 | 0.28701 | 0.31784 | 0.31682 | 0.30866 | 0.30866 | 0.30866 | 0.30151 | 0.30151 | 0.30151 | 0.29335 | 0.29335 | 0.29539 | 0.28927 | 0.28315 | 0.32487 | 0.32385 | 0.31569 | 0.31569 | 0.31569 | 0.30752 | 0.30752 | 0.3065 | 0.29834 | 0.29834 | 0.29528 | 0.2912 | 0.28814
| COUPAR ANGUS | ALYTH | MINIMUM HEADROOM | NO 23579 48311 | NO | NO | 2.103 | 1.726 | 1.4576 | 1.1576 | 0.8382 | 0.42698 | -0.0077184 | -0.4669 | -0.76486 | -1.0914 | -1.4159 | -2.574 | -3.1842 | -3.2945 | 2.7984 | 2.6555 | 2.4882 | 2.3025 | 2.1188 | 1.879 | 1.6341 | 1.4678 | 1.276 | 1.0933 | 0.49738 | 0.16983 | -0.10976 | 2.229 | 2.0076 | 1.7535 | 1.4566 | 1.1351 | 0.7331 | 0.33208 | 0.064731 | -0.23527 | -0.52302 | -1.5271 | -2.0516 | -2.1485
|  | ALYTH | EE |  |  |  |  | 1.7494 | 1.476 | 1.178 | 0.8382 | 0.46065 | -0.0077184 | -0.4669 | -0.76486 | -1.0914 | -1.4159 | -2.574 | -3.1424 | -3.2608 | 2.8045 | 2.6555 | 2.4882 | 2.3025 | 2.1188 | 1.879 | 1.6341 | 1.4678 | 1.276 | 1.0933 | 0.49738 | 0.16983 | -0.10976 | 2.2413 | 2.0086 | 1.7535 | 1.4566 | 1.1351 | 0.7331 | 0.33208 | 0.064731 | -0.23527 | -0.52302 | -1.5271 | -2.0108 | -2.1169
|  | ALYTH | HT |  |  |  |  | 1.726 | 1.4576 | 1.1576 | 0.8382 | 0.42698 | -0.0046571 | -0.32915 | -0.64853 | -0.99649 | -1.324 | -2.5302 | -3.1842 | -3.2945 | 2.7984 | 2.6678 | 2.5188 | 2.3719 | 2.178 | 1.9688 | 1.826 | 1.6586 | 1.479 | 1.326 | 0.66677 | 0.37596 | 0.32902 | 2.229 | 2.0076 | 1.7535 | 1.4882 | 1.1443 | 0.77698 | 0.50044 | 0.21473 | -0.094453 | -0.36996 | -1.4791 | -2.0516 | -2.1485
|  | ALYTH | HE |  |  |  |  | 1.7923 | 1.5668 | 1.326 | 1.0586 | 0.70963 | 0.28922 | -0.045473 | -0.29751 | -0.55874 | -0.78629 | -1.8485 | -2.4679 | -2.7067 | 2.8494 | 2.7239 | 2.5841 | 2.4484 | 2.2739 | 2.0678 | 1.9055 | 1.7566 | 1.6076 | 1.479 | 0.828 | 0.45453 | 0.14738 | 2.2882 | 2.1004 | 1.8943 | 1.6749 | 1.38 | 1.028 | 0.74636 | 0.51779 | 0.28718 | 0.094322 | -0.88323 | -1.42 | -1.622
|  | ALYTH | CF |  |  |  |  | 2.0147 | 1.8362 | 1.6402 | 1.4504 | 1.2096 | 0.94024 | 0.73106 | 0.56575 | 0.39432 | 0.17085 | -0.69343 | -1.4679 | -2.1006 | 3.0209 | 2.9055 | 2.7902 | 2.6841 | 2.5525 | 2.4025 | 2.2729 | 2.1709 | 2.0555 | 1.9158 | 1.3045 | 0.62698 | -0.092412 | 2.4933 | 2.3413 | 2.1739 | 2.0158 | 1.8127 | 1.5841 | 1.4035 | 1.2606 | 1.1096 | 0.91575 | 0.13922 | -0.57813 | -1.1149
| FORT WILLIAM | ANNAT | MINIMUM HEADROOM | NN 08452 76751 | YES | NO | 0.142 | 3.754 | 3.6713 | 3.5887 | 3.4877 | 3.3754 | 3.2897 | 3.1468 | 2.9795 | 2.8213 | 2.7366 | 2.404 | 2.2836 | 2.2499 | 4.7254 | 4.6795 | 4.6366 | 4.5815 | 4.5224 | 4.4764 | 4.3907 | 4.2846 | 4.1815 | 4.1356 | 3.9315 | 3.8264 | 3.4132 | 4.3836 | 4.3019 | 4.2234 | 4.1254 | 4.0193 | 3.9366 | 3.804 | 3.6458 | 3.4979 | 3.4142 | 3.0999 | 2.9907 | 2.9611
|  | ANNAT | EE |  |  |  |  | 3.754 | 3.6713 | 3.5887 | 3.4877 | 3.3754 | 3.2897 | 3.1468 | 2.9795 | 2.8213 | 2.7366 | 2.404 | 2.3346 | 2.303 | 4.7254 | 4.6795 | 4.6366 | 4.5815 | 4.5224 | 4.4764 | 4.3907 | 4.2846 | 4.1815 | 4.1356 | 3.9315 | 3.8264 | 3.6468 | 4.3836 | 4.3019 | 4.2234 | 4.1254 | 4.0193 | 3.9366 | 3.804 | 3.6458 | 3.4979 | 3.4142 | 3.0999 | 3.0366 | 3.007
|  | ANNAT | HT |  |  |  |  | 3.7917 | 3.7244 | 3.653 | 3.5672 | 3.4989 | 3.403 | 3.2958 | 3.1662 | 3.0805 | 2.9601 | 2.4928 | 2.2836 | 2.2499 | 4.7448 | 4.7101 | 4.6744 | 4.6295 | 4.5938 | 4.5458 | 4.4887 | 4.4213 | 4.3815 | 4.3101 | 4.0193 | 3.906 | 3.8887 | 4.4193 | 4.354 | 4.2836 | 4.2009 | 4.1315 | 4.0397 | 3.9397 | 3.8162 | 3.7407 | 3.6254 | 3.1856 | 2.9907 | 2.9611
|  | ANNAT | HE |  |  |  |  | 3.7917 | 3.7397 | 3.6856 | 3.6142 | 3.5601 | 3.4836 | 3.3928 | 3.2805 | 3.2111 | 3.104 | 2.5734 | 2.4397 | 2.4203 | 4.7458 | 4.7152 | 4.6856 | 4.6458 | 4.6152 | 4.5713 | 4.5172 | 4.456 | 4.4142 | 4.356 | 4.0295 | 3.8785 | 3.705 | 4.4193 | 4.3703 | 4.3152 | 4.2458 | 4.1938 | 4.1193 | 4.0346 | 3.9244 | 3.8611 | 3.7581 | 3.2611 | 3.1336 | 3.1172
|  | ANNAT | CF |  |  |  |  | 3.803 | 3.7601 | 3.703 | 3.654 | 3.5887 | 3.5519 | 3.4836 | 3.4121 | 3.3326 | 3.255 | 2.8968 | 2.606 | 2.4417 | 4.753 | 4.7264 | 4.6948 | 4.6672 | 4.6326 | 4.606 | 4.5662 | 4.5193 | 4.4703 | 4.4224 | 4.1672 | 3.8387 | 3.4132 | 4.4305 | 4.3897 | 4.3377 | 4.2907 | 4.2315 | 4.1917 | 4.1275 | 4.0611 | 3.9897 | 3.9183 | 3.5805 | 3.2979 | 3.1336
| KILLIN | ARDCHYLE | MINIMUM HEADROOM | NN 52734 29223 | YES | YES | 0 | 0.10678 | 0.10576 | 0.10576 | 0.098612 | 0.098612 | 0.098612 | 0.098612 | 0.091469 | 0.090449 | 0.090449 | 0.083306 | 0.081265 | 0.081265 | 0.10288 | 0.10288 | 0.10288 | 0.095735 | 0.095735 | 0.095735 | 0.095735 | 0.088592 | 0.087571 | 0.087571 | 0.080429 | 0.079408 | 0.079408 | 0.021663 | 0.021663 | 0.021663 | 0.01452 | 0.01452 | 0.01452 | 0.01452 | 0.0073776 | 0.0063571 | 0.0063571 | -0.00078571 | -0.00078571 | -0.00078571
|  | ARDCHYLE | EE |  |  |  |  | 0.10678 | 0.10576 | 0.10576 | 0.098612 | 0.098612 | 0.098612 | 0.098612 | 0.091469 | 0.090449 | 0.090449 | 0.083306 | 0.081265 | 0.081265 | 0.10288 | 0.10288 | 0.10288 | 0.095735 | 0.095735 | 0.095735 | 0.095735 | 0.088592 | 0.087571 | 0.087571 | 0.080429 | 0.079408 | 0.079408 | 0.021663 | 0.021663 | 0.021663 | 0.01452 | 0.01452 | 0.01452 | 0.01452 | 0.0073776 | 0.0063571 | 0.0063571 | -0.00078571 | -0.00078571 | -0.00078571
|  | ARDCHYLE | HT |  |  |  |  | 0.10678 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.098612 | 0.098612 | 0.098612 | 0.097592 | 0.097592 | 0.083306 | 0.081265 | 0.081265 | 0.10288 | 0.10288 | 0.10288 | 0.10288 | 0.10288 | 0.095735 | 0.095735 | 0.095735 | 0.094714 | 0.094714 | 0.080429 | 0.079408 | 0.079408 | 0.021663 | 0.021663 | 0.021663 | 0.021663 | 0.021663 | 0.01452 | 0.01452 | 0.01452 | 0.0135 | 0.0135 | -0.00078571 | -0.00078571 | -0.00078571
|  | ARDCHYLE | HE |  |  |  |  | 0.10678 | 0.10678 | 0.10576 | 0.10576 | 0.10576 | 0.098612 | 0.098612 | 0.098612 | 0.098612 | 0.098612 | 0.090449 | 0.083306 | 0.081265 | 0.10288 | 0.10288 | 0.10288 | 0.10288 | 0.10288 | 0.095735 | 0.095735 | 0.095735 | 0.095735 | 0.095735 | 0.087571 | 0.080429 | 0.079408 | 0.021663 | 0.021663 | 0.021663 | 0.021663 | 0.021663 | 0.01452 | 0.01452 | 0.01452 | 0.01452 | 0.01452 | 0.0063571 | -0.00078571 | -0.00078571
|  | ARDCHYLE | CF |  |  |  |  | 0.10678 | 0.10678 | 0.10576 | 0.10576 | 0.10576 | 0.10576 | 0.098612 | 0.098612 | 0.098612 | 0.098612 | 0.090449 | 0.083306 | 0.081265 | 0.10288 | 0.10288 | 0.10288 | 0.10288 | 0.10288 | 0.10288 | 0.095735 | 0.095735 | 0.095735 | 0.095735 | 0.087571 | 0.080429 | 0.079408 | 0.021663 | 0.021663 | 0.021663 | 0.021663 | 0.021663 | 0.021663 | 0.01452 | 0.01452 | 0.01452 | 0.01452 | 0.0063571 | -0.00078571 | -0.00078571
| NAIRN | ARDERSIER | MINIMUM HEADROOM | NH 80475 55905 | NO | YES | 0.076 | 4.2579 | 4.1875 | 4.0946 | 4.0273 | 3.9415 | 3.6834 | 3.3089 | 2.9242 | 2.564 | 2.1834 | 1.7599 | 1.6722 | 1.6364 | 5.2395 | 5.2058 | 5.1517 | 5.114 | 5.062 | 4.9558 | 4.7752 | 4.5824 | 4.412 | 4.2232 | 3.9028 | 3.8109 | 3.4558 | 4.8956 | 4.8283 | 4.7497 | 4.6813 | 4.6038 | 4.412 | 4.1048 | 3.7875 | 3.4966 | 3.1834 | 2.7905 | 2.712 | 2.6793
|  | ARDERSIER | EE |  |  |  |  | 4.2579 | 4.1875 | 4.0946 | 4.0273 | 3.9415 | 3.8375 | 3.7528 | 3.3609 | 2.9538 | 2.564 | 1.7599 | 1.714 | 1.6946 | 5.2395 | 5.2058 | 5.1517 | 5.114 | 5.062 | 5.0007 | 4.9507 | 4.7364 | 4.5232 | 4.3262 | 3.9028 | 3.8109 | 3.663 | 4.8956 | 4.8283 | 4.7497 | 4.6813 | 4.6038 | 4.513 | 4.4262 | 4.0885 | 3.7477 | 3.4262 | 2.7905 | 2.7497 | 2.7293
|  | ARDERSIER | HT |  |  |  |  | 4.2854 | 4.2283 | 4.165 | 4.1017 | 4.0354 | 3.6834 | 3.3089 | 2.9242 | 2.564 | 2.1834 | 1.7987 | 1.6722 | 1.6364 | 5.2548 | 5.2364 | 5.1997 | 5.166 | 5.1324 | 4.9558 | 4.7752 | 4.5824 | 4.412 | 4.2232 | 3.9803 | 3.9171 | 3.8987 | 4.9232 | 4.8691 | 4.8089 | 4.7507 | 4.6905 | 4.412 | 4.1048 | 3.7875 | 3.4966 | 3.1834 | 2.8181 | 2.712 | 2.6793
|  | ARDERSIER | HE |  |  |  |  | 4.2834 | 4.2303 | 4.1742 | 4.116 | 4.0517 | 3.9864 | 3.9017 | 3.7456 | 3.5956 | 3.4609 | 2.5834 | 2.0671 | 1.7324 | 5.2528 | 5.2354 | 5.2038 | 5.1762 | 5.1354 | 5.1099 | 5.063 | 4.966 | 4.865 | 4.7905 | 4.2813 | 3.9742 | 3.6854 | 4.9211 | 4.8711 | 4.8181 | 4.764 | 4.7028 | 4.6415 | 4.5599 | 4.4181 | 4.2803 | 4.1558 | 3.4232 | 3.0293 | 2.763
|  | ARDERSIER | CF |  |  |  |  | 4.2905 | 4.2538 | 4.215 | 4.1773 | 4.1232 | 4.0926 | 4.0344 | 3.9732 | 3.8405 | 3.7038 | 3.0242 | 2.3558 | 1.7875 | 5.2558 | 5.2415 | 5.2211 | 5.1956 | 5.164 | 5.1405 | 5.1038 | 5.063 | 4.9844 | 4.9048 | 4.4762 | 3.9915 | 3.4558 | 4.9242 | 4.8895 | 4.8568 | 4.8232 | 4.7793 | 4.7466 | 4.6966 | 4.6354 | 4.5242 | 4.4028 | 3.8171 | 3.2579 | 2.8109
| FORT AUGUSTUS | ARDOCHY | MINIMUM HEADROOM | NH 47714 12561 | YES | YES | 0 | 0.118 | 0.11086 | 0.10882 | 0.10882 | 0.10167 | 0.10167 | 0.09351 | 0.09351 | 0.091469 | 0.091469 | 0.091469 | 0.094531 | 0.094531 | 0.109 | 0.10186 | 0.10084 | 0.10084 | 0.093694 | 0.093694 | 0.085531 | 0.085531 | 0.086551 | 0.085531 | 0.086551 | 0.090633 | 0.089612 | 0.1135 | 0.10636 | 0.10534 | 0.10534 | 0.098194 | 0.098194 | 0.08901 | 0.08901 | 0.086969 | 0.086969 | 0.086969 | 0.091051 | 0.091051
|  | ARDOCHY | EE |  |  |  |  | 0.118 | 0.11086 | 0.10984 | 0.10984 | 0.10167 | 0.10167 | 0.09351 | 0.09351 | 0.091469 | 0.091469 | 0.095551 | 0.095551 | 0.094531 | 0.109 | 0.10186 | 0.10186 | 0.10186 | 0.093694 | 0.093694 | 0.085531 | 0.085531 | 0.086551 | 0.086551 | 0.091653 | 0.091653 | 0.090633 | 0.1135 | 0.10636 | 0.10534 | 0.10534 | 0.098194 | 0.098194 | 0.08901 | 0.08901 | 0.086969 | 0.086969 | 0.092071 | 0.092071 | 0.091051
|  | ARDOCHY | HT |  |  |  |  | 0.118 | 0.118 | 0.10882 | 0.10984 | 0.10984 | 0.10984 | 0.10167 | 0.10065 | 0.10065 | 0.09351 | 0.095551 | 0.094531 | 0.094531 | 0.109 | 0.109 | 0.10084 | 0.10186 | 0.10186 | 0.10186 | 0.093694 | 0.092673 | 0.092673 | 0.085531 | 0.091653 | 0.090633 | 0.090633 | 0.1135 | 0.1135 | 0.10534 | 0.10534 | 0.10534 | 0.10534 | 0.098194 | 0.096153 | 0.096153 | 0.08901 | 0.092071 | 0.091051 | 0.091051
|  | ARDOCHY | HE |  |  |  |  | 0.118 | 0.118 | 0.11086 | 0.10882 | 0.10984 | 0.10984 | 0.10269 | 0.10167 | 0.10167 | 0.09351 | 0.095551 | 0.095551 | 0.095551 | 0.109 | 0.109 | 0.10186 | 0.10084 | 0.10186 | 0.10186 | 0.094714 | 0.093694 | 0.093694 | 0.085531 | 0.091653 | 0.091653 | 0.091653 | 0.1135 | 0.1135 | 0.10636 | 0.10534 | 0.10534 | 0.10534 | 0.098194 | 0.098194 | 0.098194 | 0.08901 | 0.092071 | 0.092071 | 0.092071
|  | ARDOCHY | CF |  |  |  |  | 0.118 | 0.118 | 0.118 | 0.11086 | 0.11086 | 0.10882 | 0.10882 | 0.10882 | 0.10167 | 0.10065 | 0.091469 | 0.095551 | 0.095551 | 0.109 | 0.109 | 0.109 | 0.10186 | 0.10186 | 0.10084 | 0.10084 | 0.10084 | 0.093694 | 0.092673 | 0.086551 | 0.091653 | 0.089612 | 0.1135 | 0.1135 | 0.1135 | 0.10636 | 0.10636 | 0.10534 | 0.10534 | 0.10534 | 0.098194 | 0.097173 | 0.086969 | 0.092071 | 0.092071
| FORT WILLIAM | ARISAIG | MINIMUM HEADROOM | NM 66564 86619 | YES | NO | 0.04 | 2.3152 | 2.2877 | 2.2612 | 2.2428 | 2.2061 | 2.1826 | 2.1367 | 2.0857 | 2.0683 | 2.0295 | 1.9469 | 1.9183 | 1.9112 | 2.1729 | 2.1525 | 2.1341 | 2.1229 | 2.0974 | 2.079 | 2.0515 | 2.0117 | 2.0005 | 1.9719 | 1.9086 | 1.8831 | 1.7688 | 2.2538 | 2.2283 | 2.2048 | 2.1834 | 2.1507 | 2.1272 | 2.0854 | 2.0354 | 2.017 | 1.9813 | 1.9027 | 1.8783 | 1.8721
|  | ARISAIG | EE |  |  |  |  | 2.3152 | 2.2877 | 2.2612 | 2.2428 | 2.2061 | 2.1826 | 2.1367 | 2.0857 | 2.0683 | 2.0295 | 1.9469 | 1.9346 | 1.9255 | 2.1729 | 2.1525 | 2.1341 | 2.1229 | 2.0974 | 2.079 | 2.0515 | 2.0117 | 2.0005 | 1.9719 | 1.9086 | 1.8831 | 1.8362 | 2.2538 | 2.2283 | 2.2048 | 2.1834 | 2.1507 | 2.1272 | 2.0854 | 2.0354 | 2.017 | 1.9813 | 1.9027 | 1.8925 | 1.8844
|  | ARISAIG | HT |  |  |  |  | 2.3295 | 2.3091 | 2.2897 | 2.2673 | 2.2408 | 2.2255 | 2.1948 | 2.155 | 2.1336 | 2.0959 | 1.9734 | 1.9183 | 1.9112 | 2.1851 | 2.1688 | 2.1576 | 2.1454 | 2.126 | 2.1168 | 2.0974 | 2.0709 | 2.0545 | 2.029 | 1.9423 | 1.9076 | 1.9045 | 2.2681 | 2.2497 | 2.2323 | 2.2109 | 2.1864 | 2.1721 | 2.1415 | 2.1038 | 2.0823 | 2.0476 | 1.9293 | 1.8783 | 1.8721
|  | ARISAIG | HE |  |  |  |  | 2.3255 | 2.3142 | 2.2948 | 2.2785 | 2.253 | 2.2448 | 2.2173 | 2.1806 | 2.1612 | 2.1275 | 1.9928 | 1.9581 | 1.951 | 2.1831 | 2.1739 | 2.1607 | 2.1484 | 2.13 | 2.1239 | 2.1045 | 2.077 | 2.0637 | 2.0402 | 1.9433 | 1.8994 | 1.8576 | 2.266 | 2.2558 | 2.2354 | 2.2211 | 2.1976 | 2.1874 | 2.1599 | 2.1272 | 2.1079 | 2.0762 | 1.9497 | 1.916 | 1.9099
|  | ARISAIG | CF |  |  |  |  | 2.3306 | 2.3163 | 2.303 | 2.2857 | 2.2724 | 2.251 | 2.2438 | 2.2193 | 2.1969 | 2.1857 | 2.0897 | 1.9908 | 1.953 | 2.1851 | 2.1749 | 2.1658 | 2.1515 | 2.1433 | 2.126 | 2.1219 | 2.1035 | 2.0851 | 2.076 | 1.9943 | 1.8872 | 1.7688 | 2.2701 | 2.2558 | 2.2436 | 2.2272 | 2.213 | 2.1946 | 2.1864 | 2.1619 | 2.1405 | 2.1313 | 2.0385 | 1.9456 | 1.9119
| ELGIN | ASHGROVE | MINIMUM HEADROOM | NJ 22458 62130 | YES | YES | 3.228 | 1.2125 | 0.082931 | 25.1268 | 24.038 | 23.1421 | 22.0758 | 20.9503 | 19.6421 | 18.3584 | 17.3044 | 13.3595 | 11.8146 | 11.4799 | 2.8635 | 2.0186 | 26.9819 | 26.288 | 25.7625 | 25.1207 | 24.4421 | 23.5135 | 22.6207 | 21.8911 | 19.3411 | 18.2778 | 17.3799 | 2.1656 | 1.1166 | 26.4095 | 25.4278 | 24.6442 | 23.7248 | 22.7564 | 21.585 | 20.4493 | 19.5135 | 16.2523 | 15.0217 | 14.7595
|  | ASHGROVE | EE |  |  |  |  | 1.2125 | 0.087012 | 25.1493 | 24.1186 | 23.2319 | 22.2074 | 21.6258 | 20.6472 | 19.6737 | 18.6493 | 13.8197 | 12.0737 | 11.5309 | 2.8635 | 2.0227 | 27.0023 | 26.3044 | 25.7931 | 25.1758 | 24.8635 | 24.2044 | 23.5329 | 22.8044 | 19.3411 | 18.2778 | 17.4472 | 2.1656 | 1.1166 | 26.4197 | 25.4921 | 24.7411 | 23.8615 | 23.3635 | 22.4962 | 21.634 | 20.7237 | 16.6074 | 15.2176 | 14.7993
|  | ASHGROVE | HT |  |  |  |  | 1.234 | 0.082931 | 25.1268 | 24.038 | 23.1421 | 22.0758 | 20.9503 | 19.6421 | 18.3584 | 17.3044 | 13.3595 | 11.8146 | 11.4799 | 2.8686 | 2.0186 | 26.9819 | 26.288 | 25.7625 | 25.1207 | 24.4421 | 23.5135 | 22.6207 | 21.8911 | 19.4462 | 18.7391 | 18.5819 | 2.1891 | 1.1217 | 26.4095 | 25.4278 | 24.6442 | 23.7248 | 22.7564 | 21.585 | 20.4493 | 19.5135 | 16.2523 | 15.0217 | 14.7595
|  | ASHGROVE | HE |  |  |  |  | 1.2686 | 0.26456 | 25.4615 | 24.5666 | 23.8544 | 23.0135 | 22.3625 | 21.4972 | 20.6156 | 19.9523 | 15.4156 | 13.6421 | 12.8533 | 2.8911 | 2.0686 | 27.0952 | 26.4727 | 26.0891 | 25.5676 | 25.1584 | 24.5391 | 23.8962 | 23.3788 | 19.9717 | 18.8778 | 17.9697 | 2.2217 | 1.285 | 26.7074 | 25.9003 | 25.2778 | 24.5615 | 24.0125 | 23.2554 | 22.4829 | 21.8931 | 18.0105 | 16.5819 | 15.9309
|  | ASHGROVE | CF |  |  |  |  | 1.3737 | 0.50028 | 25.8503 | 25.136 | 24.637 | 24.0421 | 23.6605 | 23.2942 | 22.886 | 22.4084 | 18.6666 | 15.3584 | 14.2023 | 2.9431 | 2.184 | 27.2921 | 26.7931 | 26.5625 | 26.2054 | 25.9401 | 25.6462 | 25.3258 | 24.9452 | 22.0503 | 19.0972 | 17.3799 | 2.3197 | 1.5013 | 27.0625 | 26.4248 | 25.9993 | 25.4891 | 25.1799 | 24.8676 | 24.5186 | 24.1115 | 20.9197 | 18.0554 | 17.1166
| MILTON OF CRAIGIE | ASHLUDIE | MINIMUM HEADROOM | NO 49222 33584 | NO | NO | 0.954 | 3.7787 | 3.3929 | 2.9756 | 18.6215 | 18.1878 | 17.7419 | 17.5021 | 16.9001 | 16.3144 | 15.7542 | 13.7858 | 13.2287 | 13.1205 | 7.0338 | 6.8205 | 6.5725 | 20.898 | 20.6215 | 20.3276 | 20.2838 | 19.9236 | 19.5756 | 19.2562 | 18.1297 | 17.6593 | 15.8266 | 5.1164 | 4.7746 | 4.3878 | 19.3031 | 18.8725 | 18.4225 | 18.297 | 17.7246 | 17.1684 | 16.6582 | 15.0031 | 14.5287 | 14.4378
|  | ASHLUDIE | EE |  |  |  |  | 3.7787 | 3.3929 | 2.9756 | 18.6215 | 18.1878 | 17.7419 | 17.5021 | 16.9001 | 16.3144 | 15.7542 | 13.7858 | 13.5929 | 13.5552 | 7.0338 | 6.8205 | 6.5725 | 20.898 | 20.6215 | 20.3276 | 20.2838 | 19.9236 | 19.5756 | 19.2562 | 18.1297 | 17.6593 | 16.9082 | 5.1164 | 4.7746 | 4.3878 | 19.3031 | 18.8725 | 18.4225 | 18.297 | 17.7246 | 17.1684 | 16.6582 | 15.0031 | 14.8358 | 14.7807
|  | ASHLUDIE | HT |  |  |  |  | 3.8644 | 3.5052 | 3.1205 | 18.8062 | 18.4684 | 18.0797 | 17.5521 | 16.9736 | 16.7419 | 16.1746 | 14.0011 | 13.2287 | 13.1205 | 7.1246 | 6.948 | 6.7552 | 21.1378 | 20.9623 | 20.744 | 20.4562 | 20.1327 | 20.1133 | 19.8164 | 18.6205 | 18.2031 | 18.1358 | 5.2368 | 4.9256 | 4.5909 | 19.5684 | 19.2572 | 18.8868 | 18.397 | 17.8511 | 17.7348 | 17.2327 | 15.2164 | 14.5287 | 14.4378
|  | ASHLUDIE | HE |  |  |  |  | 3.894 | 3.6409 | 3.3766 | 19.1909 | 18.9715 | 18.7082 | 18.3103 | 17.848 | 17.7378 | 17.3154 | 15.2378 | 14.1531 | 13.944 | 7.1368 | 6.9766 | 6.8154 | 21.2327 | 21.0858 | 20.9001 | 20.6521 | 20.3511 | 20.3623 | 20.0991 | 18.7317 | 17.8756 | 17.0889 | 5.2654 | 5.0256 | 4.7868 | 19.8603 | 19.647 | 19.3756 | 18.9909 | 18.5327 | 18.5225 | 18.1256 | 16.1991 | 15.294 | 15.1276
|  | ASHLUDIE | CF |  |  |  |  | 3.9511 | 3.7868 | 3.5991 | 19.497 | 19.3276 | 19.1919 | 19.0082 | 18.7929 | 18.5746 | 18.6674 | 17.3582 | 15.7195 | 14.2991 | 7.1531 | 7.0399 | 6.9174 | 21.3736 | 21.2368 | 21.1205 | 20.9572 | 20.7593 | 20.5674 | 20.6419 | 19.5093 | 17.8654 | 15.8266 | 5.3103 | 5.1552 | 4.9817 | 20.1348 | 19.9521 | 19.8113 | 19.6133 | 19.3725 | 19.1378 | 19.2899 | 17.997 | 16.4868 | 15.3603
| GRUDIE BRIDGE | AULTBEA | MINIMUM HEADROOM | NG 87458 88885 | YES | NO | 0.235 | -0.64196 | -0.69094 | -0.75217 | -0.8287 | -0.88074 | -0.96135 | -1.0511 | -1.1634 | -1.2297 | -1.3195 | -1.5246 | -1.6011 | -1.6226 | -0.11135 | -0.14094 | -0.1787 | -0.2287 | -0.26645 | -0.31951 | -0.37972 | -0.45523 | -0.49707 | -0.55319 | -0.71237 | -0.78584 | -1.0144 | -0.50217 | -0.54707 | -0.60625 | -0.67768 | -0.72768 | -0.80523 | -0.88992 | -1.0001 | -1.0624 | -1.145 | -1.3399 | -1.4093 | -1.4287
|  | AULTBEA | EE |  |  |  |  | -0.64196 | -0.69094 | -0.75217 | -0.8287 | -0.88074 | -0.96135 | -1.0511 | -1.1634 | -1.2297 | -1.3195 | -1.5246 | -1.5634 | -1.5889 | -0.11135 | -0.14094 | -0.1787 | -0.2287 | -0.26645 | -0.31951 | -0.37972 | -0.45523 | -0.49707 | -0.55319 | -0.71237 | -0.78584 | -0.89911 | -0.50217 | -0.54707 | -0.60625 | -0.67768 | -0.72768 | -0.80523 | -0.88992 | -1.0001 | -1.0624 | -1.145 | -1.3399 | -1.3736 | -1.3991
|  | AULTBEA | HT |  |  |  |  | -0.60931 | -0.65421 | -0.69604 | -0.75217 | -0.80217 | -0.86849 | -0.944 | -1.0001 | -1.0705 | -1.1511 | -1.4552 | -1.6011 | -1.6226 | -0.086861 | -0.11135 | -0.13686 | -0.17053 | -0.20625 | -0.24502 | -0.29298 | -0.32972 | -0.3736 | -0.42564 | -0.62462 | -0.71441 | -0.72768 | -0.47053 | -0.51135 | -0.55115 | -0.60421 | -0.65115 | -0.71543 | -0.78686 | -0.83788 | -0.90523 | -0.9838 | -1.2746 | -1.4093 | -1.4287
|  | AULTBEA | HE |  |  |  |  | -0.60829 | -0.64298 | -0.68992 | -0.72258 | -0.76237 | -0.81339 | -0.88074 | -0.92564 | -0.98686 | -1.0573 | -1.3889 | -1.4777 | -1.4899 | -0.086861 | -0.10829 | -0.1389 | -0.16237 | -0.1889 | -0.22258 | -0.26849 | -0.30115 | -0.344 | -0.394 | -0.61951 | -0.72564 | -0.82564 | -0.46951 | -0.50115 | -0.54809 | -0.57768 | -0.61441 | -0.66645 | -0.72972 | -0.77053 | -0.82768 | -0.89604 | -1.2093 | -1.2889 | -1.3011
|  | AULTBEA | CF |  |  |  |  | -0.60115 | -0.63686 | -0.67053 | -0.69707 | -0.7389 | -0.77156 | -0.81747 | -0.87156 | -0.894 | -0.94298 | -1.2022 | -1.3797 | -1.4879 | -0.081759 | -0.10319 | -0.12666 | -0.14196 | -0.16951 | -0.19298 | -0.22564 | -0.26747 | -0.28482 | -0.32053 | -0.53482 | -0.75115 | -1.0144 | -0.46033 | -0.49707 | -0.5287 | -0.55217 | -0.594 | -0.62258 | -0.66747 | -0.71951 | -0.73992 | -0.78686 | -1.0358 | -1.2052 | -1.3032
| BOAT OF GARTEN | AVIEMORE | MINIMUM HEADROOM | NH 89856 11394 | NO | YES | 5.007 | 2.6009 | 2.2519 | 1.8591 | 1.4591 | 0.97133 | 0.44684 | -0.040914 | -0.66642 | -1.246 | -1.6797 | -3.7766 | -4.8491 | -4.9083 | 6.3397 | 6.1193 | 5.8377 | 5.5377 | 5.1968 | 4.8336 | 4.455 | 3.9907 | 3.5795 | 3.2468 | 1.4785 | 0.67745 | 0.62031 | 4.2703 | 3.9326 | 3.5366 | 3.1254 | 2.6581 | 2.157 | 1.6489 | 1.0264 | 0.47133 | 0.022351 | -2.2379 | -3.2674 | -3.3225
|  | AVIEMORE | EE |  |  |  |  | 2.6009 | 2.2519 | 1.8591 | 1.4591 | 0.97133 | 0.44684 | -0.040914 | -0.66642 | -1.246 | -1.6797 | -2.7817 | -3.0083 | -3.1317 | 6.3397 | 6.1193 | 5.8377 | 5.5377 | 5.1968 | 4.8336 | 4.455 | 3.9907 | 3.5795 | 3.2468 | 2.3121 | 2.1734 | 1.8683 | 4.2703 | 3.9326 | 3.5366 | 3.1254 | 2.6581 | 2.157 | 1.6489 | 1.0264 | 0.47133 | 0.022351 | -1.2195 | -1.4032 | -1.4746
|  | AVIEMORE | HT |  |  |  |  | 2.754 | 2.4591 | 2.156 | 1.8193 | 1.4285 | 0.98766 | 0.53766 | 0.052963 | -0.37357 | -0.68479 | -2.2491 | -2.9807 | -3.0399 | 6.453 | 6.2775 | 6.103 | 5.907 | 5.6764 | 5.4254 | 5.153 | 4.8295 | 4.5285 | 4.2479 | 2.9917 | 2.4356 | 2.403 | 4.4224 | 4.1693 | 3.903 | 3.605 | 3.2519 | 2.8621 | 2.456 | 2.0152 | 1.6244 | 1.2856 | -0.36744 | -1.0991 | -1.147
|  | AVIEMORE | HE |  |  |  |  | 2.7295 | 2.4356 | 2.1387 | 1.7958 | 1.3928 | 0.97847 | 0.54582 | 0.032555 | -0.5052 | -1.0899 | -3.7766 | -4.8491 | -4.9083 | 6.4326 | 6.2458 | 6.0346 | 5.7703 | 5.4632 | 5.1275 | 4.755 | 4.2968 | 3.8632 | 3.4377 | 1.4785 | 0.67745 | 0.62031 | 4.4009 | 4.1193 | 3.803 | 3.4499 | 3.0356 | 2.5764 | 2.0805 | 1.4724 | 0.89684 | 0.33562 | -2.2379 | -3.2674 | -3.3225
|  | AVIEMORE | CF |  |  |  |  | 2.8346 | 2.6458 | 2.3958 | 2.1479 | 1.8519 | 1.5213 | 1.2172 | 0.90296 | 0.55602 | 0.28868 | -1.1644 | -2.9205 | -4.0174 | 6.4968 | 6.3764 | 6.2203 | 6.0672 | 5.8836 | 5.6744 | 5.4652 | 5.2468 | 5.006 | 4.7591 | 3.304 | 2.0224 | 1.0642 | 4.4815 | 4.3213 | 4.103 | 3.8907 | 3.6285 | 3.3356 | 3.0662 | 2.7856 | 2.4621 | 2.1448 | 0.24582 | -1.4297 | -2.4695
| ALNESS | BALALDIE | MINIMUM HEADROOM | NH 87017 79720 | YES | NO | 0.177 | -1.7808 | -1.9216 | -2.0747 | -2.244 | -2.4216 | -2.5828 | -2.8053 | -3.1318 | -3.4073 | -3.6992 | -4.4665 | -4.9338 | -4.9706 | -0.61344 | -0.70323 | -0.80017 | -0.91446 | -1.044 | -1.1471 | -1.3032 | -1.5226 | -1.6869 | -1.8665 | -2.3655 | -2.7053 | -3.2696 | -1.1543 | -1.29 | -1.4338 | -1.5961 | -1.7736 | -1.9236 | -2.141 | -2.4502 | -2.6992 | -2.9655 | -3.6308 | -4.0369 | -4.0706
|  | BALALDIE | EE |  |  |  |  | -1.7808 | -1.9216 | -2.0747 | -2.244 | -2.4216 | -2.5828 | -2.8053 | -3.1318 | -3.4073 | -3.6992 | -4.4247 | -4.5338 | -4.5869 | -0.61344 | -0.70323 | -0.80017 | -0.91446 | -1.044 | -1.1471 | -1.3032 | -1.5226 | -1.6869 | -1.8665 | -2.3655 | -2.542 | -2.7859 | -1.1543 | -1.29 | -1.4338 | -1.5961 | -1.7736 | -1.9236 | -2.141 | -2.4502 | -2.6992 | -2.9655 | -3.6308 | -3.7287 | -3.7808
|  | BALALDIE | HT |  |  |  |  | -1.7257 | -1.844 | -1.9685 | -2.1083 | -2.2328 | -2.4471 | -2.6859 | -2.9287 | -3.1634 | -3.4063 | -4.193 | -4.5971 | -4.6471 | -0.55731 | -0.62466 | -0.69813 | -0.78487 | -0.8614 | -0.98384 | -1.1247 | -1.2604 | -1.4063 | -1.5614 | -2.1134 | -2.3675 | -2.393 | -1.0971 | -1.2053 | -1.3206 | -1.4522 | -1.5706 | -1.7645 | -1.9798 | -2.192 | -2.4083 | -2.6379 | -3.4094 | -3.7849 | -3.8287
|  | BALALDIE | HE |  |  |  |  | -1.7318 | -1.8318 | -1.942 | -2.0675 | -2.1736 | -2.3094 | -2.4736 | -2.7083 | -2.9573 | -3.2175 | -4.4665 | -4.9338 | -4.9706 | -0.56446 | -0.62976 | -0.70221 | -0.78895 | -0.86242 | -0.95833 | -1.0777 | -1.2216 | -1.3828 | -1.5532 | -2.3583 | -2.7053 | -2.8777 | -1.1043 | -1.1961 | -1.2981 | -1.4206 | -1.5236 | -1.6553 | -1.8165 | -2.0257 | -2.2573 | -2.4961 | -3.5889 | -4.0369 | -4.0706
|  | BALALDIE | CF |  |  |  |  | -1.7083 | -1.7838 | -1.8838 | -1.9726 | -2.0685 | -2.1502 | -2.2492 | -2.3736 | -2.5481 | -2.7053 | -3.592 | -4.2665 | -4.9114 | -0.54711 | -0.59303 | -0.65833 | -0.7165 | -0.78895 | -0.84507 | -0.91956 | -1.0216 | -1.1369 | -1.2349 | -1.9114 | -2.5563 | -3.2696 | -1.0808 | -1.1502 | -1.24 | -1.3236 | -1.4134 | -1.493 | -1.5889 | -1.7124 | -1.8706 | -2.0012 | -2.8389 | -3.442 | -4.0145
| ABERNETHY | BALBEGGIE | MINIMUM HEADROOM | NO 17499 29606 | YES | YES | 0.846 | 1.8548 | 1.7212 | 1.5385 | 1.2406 | 1.0548 | 0.58035 | 0.34055 | 0.077286 | -0.23394 | -0.58598 | -2.5686 | -4.1452 | -5.4462 | 2.9559 | 2.8803 | 2.7365 | 2.4752 | 2.3691 | 1.8906 | 1.7069 | 1.4691 | 1.2242 | 0.84667 | -1.0125 | -2.7401 | -4.4176 | 2.5079 | 2.3916 | 2.1763 | 1.8742 | 1.7232 | 1.1824 | 0.97116 | 0.73851 | 0.49667 | 0.042592 | -2.0911 | -3.9513 | -5.5564
|  | BALBEGGIE | EE |  |  |  |  | 1.8548 | 1.7212 | 1.5569 | 1.4048 | 1.1181 | 0.7232 | 0.4232 | 0.14463 | -0.23394 | -0.58598 | -1.9401 | -3.3605 | -3.8819 | 2.9559 | 2.8803 | 2.7793 | 2.6916 | 2.465 | 2.113 | 1.9089 | 1.7303 | 1.4314 | 1.1671 | 0.1181 | -1.4472 | -2.236 | 2.5079 | 2.3916 | 2.261 | 2.1252 | 1.862 | 1.4742 | 1.1752 | 0.9181 | 0.53443 | 0.18647 | -1.1482 | -2.788 | -3.4146
|  | BALBEGGIE | HT |  |  |  |  | 1.9161 | 1.7824 | 1.5385 | 1.2406 | 1.0548 | 0.58035 | 0.34055 | 0.077286 | -0.17782 | -0.537 | -2.1023 | -3.8074 | -4.9972 | 3.0038 | 2.9344 | 2.7365 | 2.4752 | 2.3691 | 1.8906 | 1.7385 | 1.564 | 1.413 | 1.1752 | -0.074755 | -1.8646 | -3.2778 | 2.5406 | 2.4252 | 2.1763 | 1.8742 | 1.7232 | 1.1824 | 0.97116 | 0.73851 | 0.52933 | 0.18749 | -1.3727 | -3.339 | -4.786
|  | BALBEGGIE | HE |  |  |  |  | 1.9201 | 1.8273 | 1.6436 | 1.3997 | 1.2018 | 0.7528 | 0.47218 | 0.18239 | -0.11863 | -0.537 | -2.5686 | -4.1452 | -5.4462 | 3.0028 | 2.9477 | 2.7824 | 2.5528 | 2.3987 | 1.9242 | 1.7069 | 1.4691 | 1.2242 | 0.84667 | -1.0125 | -2.7401 | -4.4176 | 2.5416 | 2.463 | 2.2763 | 2.0232 | 1.8457 | 1.3273 | 1.061 | 0.78545 | 0.49667 | 0.042592 | -2.0911 | -3.9513 | -5.5564
|  | BALBEGGIE | CF |  |  |  |  | 1.9416 | 1.8824 | 1.7936 | 1.7303 | 1.5844 | 1.3732 | 1.2283 | 1.0467 | 0.87729 | 0.64871 | -0.34618 | -1.286 | -1.8676 | 3.0171 | 2.9783 | 2.9191 | 2.8773 | 2.7518 | 2.5508 | 2.4283 | 2.2854 | 2.1467 | 1.9599 | 1.1201 | 0.22218 | -0.54108 | 2.564 | 2.515 | 2.4538 | 2.4018 | 2.2661 | 2.0599 | 1.914 | 1.7599 | 1.612 | 1.3854 | 0.39769 | -0.54516 | -1.1248
| MILTON OF CRAIGIE | BALDOVIE | MINIMUM HEADROOM | NO 45279 32147 | NO | NO | 0.708 | 12.6438 | 12.0755 | 11.3806 | 10.6163 | 9.6102 | 8.5081 | 7.3275 | 5.9887 | 4.7561 | 3.7244 | 0.36118 | -0.61433 | -0.77862 | 14.3851 | 13.934 | 13.3565 | 12.7116 | 11.8106 | 10.8004 | 9.8667 | 8.7963 | 7.8167 | 6.9891 | 4.3616 | 3.6238 | 1.8942 | 14.1391 | 13.634 | 13.0106 | 12.3146 | 11.3789 | 10.332 | 9.2973 | 8.0912 | 6.9371 | 5.933 | 2.8106 | 1.9861 | 1.8432
|  | BALDOVIE | EE |  |  |  |  | 12.6979 | 12.1326 | 11.4979 | 10.8 | 9.9122 | 8.9112 | 7.8387 | 6.6051 | 5.453 | 4.2897 | 0.36118 | -0.30005 | -0.42352 | 14.4412 | 13.981 | 13.4606 | 12.8687 | 12.0769 | 11.1708 | 10.284 | 9.2963 | 8.3738 | 7.43 | 4.3616 | 3.6238 | 2.7004 | 14.2014 | 13.7014 | 13.1177 | 12.4555 | 11.6095 | 10.6636 | 9.7687 | 8.6432 | 7.5759 | 6.5044 | 2.8106 | 2.2361 | 2.1279
|  | BALDOVIE | HT |  |  |  |  | 12.6438 | 12.0755 | 11.3806 | 10.6163 | 9.6102 | 8.5081 | 7.3275 | 5.9887 | 4.7561 | 3.7244 | 0.41526 | -0.61433 | -0.77862 | 14.3851 | 13.934 | 13.3565 | 12.7116 | 11.8106 | 10.8004 | 9.8667 | 8.7963 | 7.8167 | 6.9891 | 4.8953 | 4.3953 | 4.3034 | 14.1391 | 13.634 | 13.0106 | 12.3146 | 11.3789 | 10.332 | 9.2973 | 8.0912 | 6.9371 | 5.933 | 2.9034 | 1.9861 | 1.8432
|  | BALDOVIE | HE |  |  |  |  | 12.7632 | 12.3306 | 11.8489 | 11.2928 | 10.5581 | 9.7448 | 8.6438 | 7.5765 | 6.5795 | 5.7806 | 2.1173 | 0.84281 | 0.53771 | 14.4953 | 14.0963 | 13.6504 | 13.1269 | 12.4136 | 11.6116 | 10.6422 | 9.7289 | 8.8748 | 8.1238 | 5.1371 | 4.1667 | 3.1942 | 14.2555 | 13.832 | 13.3646 | 12.8197 | 12.0983 | 11.282 | 10.2555 | 9.2595 | 8.3351 | 7.5167 | 4.2789 | 3.2748 | 2.9861
|  | BALDOVIE | CF |  |  |  |  | 13.1255 | 12.8795 | 12.5877 | 12.3122 | 11.9234 | 11.4551 | 10.9693 | 10.3683 | 9.8295 | 9.2357 | 6.0642 | 2.9214 | 1.4397 | 14.8289 | 14.5779 | 14.2851 | 14.0034 | 13.6044 | 13.1146 | 12.6116 | 12.0044 | 11.4555 | 10.8473 | 7.6177 | 4.2953 | 1.8942 | 14.6095 | 14.3667 | 14.081 | 13.8065 | 13.4248 | 12.9616 | 12.4708 | 11.8789 | 11.3463 | 10.7606 | 7.5881 | 4.8024 | 3.7708
| TARLAND | BALLATER | MINIMUM HEADROOM | NO 37542 97131 | NO | NO | 0.818 | 4.9349 | 4.788 | 4.6268 | 4.4461 | 4.2747 | 4.0686 | 3.8115 | 3.5982 | 3.3655 | 3.1257 | 2.3115 | 2.1574 | 2.1247 | 8.3808 | 8.3166 | 8.2451 | 8.1492 | 8.0278 | 7.8696 | 7.6788 | 7.5135 | 7.3268 | 7.1492 | 6.5982 | 6.437 | 5.8951 | 7.0023 | 6.8482 | 6.6706 | 6.4615 | 6.2778 | 6.0421 | 5.7492 | 5.5002 | 5.2196 | 4.9502 | 4.1339 | 3.9676 | 3.9125
|  | BALLATER | EE |  |  |  |  | 4.9349 | 4.788 | 4.6268 | 4.4461 | 4.2747 | 4.0686 | 3.8115 | 3.5982 | 3.3655 | 3.1257 | 2.3115 | 2.2359 | 2.2145 | 8.3808 | 8.3166 | 8.2451 | 8.1492 | 8.0278 | 7.8696 | 7.6788 | 7.5135 | 7.3268 | 7.1492 | 6.5982 | 6.437 | 6.1829 | 7.0023 | 6.8482 | 6.6706 | 6.4615 | 6.2778 | 6.0421 | 5.7492 | 5.5002 | 5.2196 | 4.9502 | 4.1339 | 4.0472 | 3.9931
|  | BALLATER | HT |  |  |  |  | 4.9747 | 4.8247 | 4.6574 | 4.488 | 4.2941 | 4.1043 | 3.9329 | 3.7278 | 3.5002 | 3.2645 | 2.5094 | 2.1921 | 2.1257 | 8.4247 | 8.3696 | 8.3043 | 8.2421 | 8.1451 | 8.0186 | 7.9166 | 7.7594 | 7.6012 | 7.4574 | 6.8257 | 6.5972 | 6.5686 | 7.0676 | 6.9155 | 6.741 | 6.5727 | 6.3727 | 6.1706 | 5.9931 | 5.7615 | 5.5135 | 5.2696 | 4.3319 | 3.9676 | 3.9125
|  | BALLATER | HE |  |  |  |  | 4.9655 | 4.8584 | 4.7329 | 4.6023 | 4.4492 | 4.2778 | 4.0859 | 3.8819 | 3.6666 | 3.4227 | 2.3992 | 2.1574 | 2.1247 | 8.4023 | 8.34 | 8.2747 | 8.2002 | 8.1186 | 8.0247 | 7.9247 | 7.8012 | 7.6625 | 7.489 | 6.7829 | 6.5227 | 6.291 | 7.0635 | 6.9502 | 6.8135 | 6.6829 | 6.5257 | 6.3441 | 6.1615 | 5.941 | 5.7166 | 5.4635 | 4.4196 | 4.1737 | 4.14
|  | BALLATER | CF |  |  |  |  | 4.9727 | 4.9012 | 4.8145 | 4.7278 | 4.6237 | 4.5227 | 4.4033 | 4.2849 | 4.1615 | 4.0135 | 3.0849 | 2.6002 | 2.2257 | 8.4247 | 8.3931 | 8.3502 | 8.3064 | 8.2543 | 8.2002 | 8.1359 | 8.0604 | 7.9615 | 7.8472 | 7.1339 | 6.5115 | 5.8951 | 7.0727 | 6.9992 | 6.9104 | 6.8237 | 6.7155 | 6.6084 | 6.4798 | 6.3625 | 6.2257 | 6.0696 | 5.1074 | 4.5166 | 4.1849
| CARRADALE 1 | BALLIEKINE | MINIMUM HEADROOM | NR 87179 38819 | YES | YES | 0.012 | 0.48673 | 0.46837 | 0.45306 | 0.42551 | 0.40918 | 0.38571 | 0.34796 | 0.32551 | 0.29184 | 0.26122 | 0.20102 | 0.18265 | 0.17653 | 0.65918 | 0.64796 | 0.63776 | 0.61939 | 0.6102 | 0.59388 | 0.56837 | 0.55102 | 0.52755 | 0.50918 | 0.46735 | 0.45816 | 0.44898 | 0.56429 | 0.54796 | 0.53571 | 0.51122 | 0.49796 | 0.47449 | 0.44286 | 0.42143 | 0.3898 | 0.36429 | 0.30612 | 0.28673 | 0.28163
|  | BALLIEKINE | EE |  |  |  |  | 0.48673 | 0.46837 | 0.45306 | 0.42551 | 0.40918 | 0.38571 | 0.34796 | 0.32551 | 0.29184 | 0.26122 | 0.20102 | 0.19082 | 0.18367 | 0.65918 | 0.64796 | 0.63776 | 0.61939 | 0.6102 | 0.59388 | 0.56837 | 0.55102 | 0.52755 | 0.50918 | 0.46735 | 0.45918 | 0.44898 | 0.56429 | 0.54796 | 0.53571 | 0.51122 | 0.49796 | 0.47449 | 0.44286 | 0.42143 | 0.3898 | 0.36429 | 0.30612 | 0.29796 | 0.29082
|  | BALLIEKINE | HT |  |  |  |  | 0.49592 | 0.47857 | 0.46837 | 0.45 | 0.43469 | 0.41327 | 0.38673 | 0.37245 | 0.34388 | 0.31837 | 0.22041 | 0.18265 | 0.17653 | 0.66735 | 0.65612 | 0.65 | 0.63878 | 0.62959 | 0.61531 | 0.59898 | 0.59082 | 0.57245 | 0.55306 | 0.48265 | 0.45816 | 0.45408 | 0.57449 | 0.55918 | 0.55102 | 0.53469 | 0.52143 | 0.50102 | 0.47857 | 0.46735 | 0.44184 | 0.41735 | 0.32653 | 0.28673 | 0.28163
|  | BALLIEKINE | HE |  |  |  |  | 0.49694 | 0.48163 | 0.47449 | 0.46224 | 0.44898 | 0.42755 | 0.40612 | 0.39592 | 0.37245 | 0.34694 | 0.24184 | 0.21633 | 0.21224 | 0.66735 | 0.65612 | 0.65408 | 0.6449 | 0.63776 | 0.62143 | 0.60612 | 0.60204 | 0.58571 | 0.56837 | 0.49898 | 0.47959 | 0.47347 | 0.57551 | 0.56122 | 0.55612 | 0.54286 | 0.53265 | 0.51429 | 0.49286 | 0.48571 | 0.46327 | 0.44184 | 0.34796 | 0.32347 | 0.31837
|  | BALLIEKINE | CF |  |  |  |  | 0.49082 | 0.48776 | 0.47857 | 0.46837 | 0.45714 | 0.44898 | 0.43265 | 0.41327 | 0.4102 | 0.39286 | 0.32041 | 0.24184 | 0.21122 | 0.66224 | 0.66224 | 0.65306 | 0.64694 | 0.6398 | 0.63367 | 0.62143 | 0.60918 | 0.60816 | 0.5949 | 0.53878 | 0.48367 | 0.45816 | 0.56939 | 0.56633 | 0.55714 | 0.54796 | 0.53776 | 0.52857 | 0.51531 | 0.49898 | 0.49592 | 0.48061 | 0.41224 | 0.34082 | 0.31633
| BOAT OF GARTEN | BALLINDALLOCH | MINIMUM HEADROOM | NJ 19279 34652 |  | YES | 0.729 | 7.5692 | 7.4958 | 7.4029 | 7.3274 | 7.2325 | 7.1356 | 7.006 | 6.8958 | 6.7631 | 6.6427 | 6.3213 | 6.2223 | 6.1682 | 7.8514 | 7.8065 | 7.7503 | 7.7075 | 7.6493 | 7.5769 | 7.4983 | 7.434 | 7.3483 | 7.2718 | 7.0616 | 6.9708 | 6.6912 | 7.5057 | 7.4384 | 7.3465 | 7.2771 | 7.1873 | 7.0873 | 6.9618 | 6.8639 | 6.7353 | 6.619 | 6.3424 | 6.2251 | 6.1567
|  | BALLINDALLOCH | EE |  |  |  |  | 7.5692 | 7.4958 | 7.4029 | 7.3274 | 7.2325 | 7.1356 | 7.006 | 6.8958 | 6.7631 | 6.6427 | 6.3213 | 6.2631 | 6.2458 | 7.8514 | 7.8065 | 7.7503 | 7.7075 | 7.6493 | 7.5769 | 7.4983 | 7.434 | 7.3483 | 7.2718 | 7.0616 | 6.9708 | 6.8503 | 7.5057 | 7.4384 | 7.3465 | 7.2771 | 7.1873 | 7.0873 | 6.9618 | 6.8639 | 6.7353 | 6.619 | 6.3424 | 6.2945 | 6.2761
|  | BALLINDALLOCH | HT |  |  |  |  | 7.5896 | 7.5213 | 7.4549 | 7.3815 | 7.2998 | 7.2294 | 7.1376 | 7.0315 | 6.9253 | 6.8458 | 6.4202 | 6.2223 | 6.1876 | 7.8697 | 7.834 | 7.7973 | 7.7585 | 7.7106 | 7.6728 | 7.6157 | 7.5544 | 7.4871 | 7.4463 | 7.1667 | 7.0595 | 7.0197 | 7.5333 | 7.4731 | 7.4098 | 7.3445 | 7.271 | 7.2067 | 7.121 | 7.0251 | 6.9231 | 6.8577 | 6.4302 | 6.2598 | 6.2108
|  | BALLINDALLOCH | HE |  |  |  |  | 7.5886 | 7.5407 | 7.4896 | 7.4366 | 7.3733 | 7.3223 | 7.2356 | 7.1335 | 7.0345 | 6.9468 | 6.3886 | 6.2304 | 6.1682 | 7.8708 | 7.8361 | 7.8075 | 7.7748 | 7.733 | 7.6952 | 7.6422 | 7.5861 | 7.5208 | 7.4748 | 7.1187 | 7.0126 | 6.8912 | 7.5333 | 7.4863 | 7.4414 | 7.3894 | 7.3261 | 7.2741 | 7.1853 | 7.0843 | 6.9863 | 6.8986 | 6.3792 | 6.2251 | 6.1567
|  | BALLINDALLOCH | CF |  |  |  |  | 7.5978 | 7.557 | 7.5151 | 7.4651 | 7.4233 | 7.3672 | 7.3264 | 7.2641 | 7.2049 | 7.1447 | 6.8213 | 6.4866 | 6.2468 | 7.8759 | 7.8514 | 7.8248 | 7.7922 | 7.7616 | 7.7259 | 7.7003 | 7.6514 | 7.6116 | 7.5636 | 7.3228 | 7.0106 | 6.6912 | 7.5414 | 7.5047 | 7.4649 | 7.4159 | 7.3741 | 7.3179 | 7.2833 | 7.2179 | 7.1628 | 7.1006 | 6.7822 | 6.4526 | 6.2292
| CARRADALE 1 | BALLURE | MINIMUM HEADROOM | NR 71425 49944 | YES | YES | 0.115 | 1.8545 | 1.8249 | 1.7974 | 1.7586 | 1.7259 | 1.681 | 1.6443 | 1.5821 | 1.531 | 1.481 | 1.3566 | 1.3117 | 1.2994 | 1.9581 | 1.9377 | 1.9203 | 1.8938 | 1.8724 | 1.8438 | 1.8254 | 1.7816 | 1.7489 | 1.7183 | 1.6326 | 1.602 | 1.5448 | 1.7359 | 1.7145 | 1.692 | 1.6553 | 1.6267 | 1.5808 | 1.5502 | 1.489 | 1.441 | 1.393 | 1.2798 | 1.241 | 1.2308
|  | BALLURE | EE |  |  |  |  | 1.8545 | 1.8249 | 1.7974 | 1.7586 | 1.7259 | 1.681 | 1.6443 | 1.5821 | 1.531 | 1.481 | 1.3566 | 1.331 | 1.3178 | 1.9581 | 1.9377 | 1.9203 | 1.8938 | 1.8724 | 1.8438 | 1.8254 | 1.7816 | 1.7489 | 1.7183 | 1.6326 | 1.602 | 1.5632 | 1.7359 | 1.7145 | 1.692 | 1.6553 | 1.6267 | 1.5808 | 1.5502 | 1.489 | 1.441 | 1.393 | 1.2798 | 1.2573 | 1.2451
|  | BALLURE | HT |  |  |  |  | 1.8698 | 1.8433 | 1.8178 | 1.7882 | 1.7627 | 1.727 | 1.6953 | 1.6535 | 1.6055 | 1.58 | 1.3923 | 1.3117 | 1.2994 | 1.9734 | 1.9571 | 1.9438 | 1.9224 | 1.9112 | 1.8877 | 1.8693 | 1.8407 | 1.8112 | 1.7938 | 1.6693 | 1.6203 | 1.6112 | 1.7573 | 1.74 | 1.7226 | 1.6971 | 1.6777 | 1.64 | 1.6083 | 1.5634 | 1.5165 | 1.4981 | 1.3155 | 1.241 | 1.2308
|  | BALLURE | HE |  |  |  |  | 1.8698 | 1.8474 | 1.83 | 1.8055 | 1.7862 | 1.7617 | 1.7362 | 1.6953 | 1.6555 | 1.6331 | 1.427 | 1.3719 | 1.3647 | 1.9734 | 1.9581 | 1.9479 | 1.9265 | 1.9193 | 1.8989 | 1.8846 | 1.854 | 1.8285 | 1.8173 | 1.6795 | 1.6336 | 1.5999 | 1.7583 | 1.741 | 1.7247 | 1.7002 | 1.69 | 1.6655 | 1.643 | 1.5981 | 1.5573 | 1.5441 | 1.3471 | 1.2971 | 1.291
|  | BALLURE | CF |  |  |  |  | 1.8688 | 1.8566 | 1.8382 | 1.8208 | 1.7974 | 1.7841 | 1.7606 | 1.7351 | 1.7208 | 1.6964 | 1.5668 | 1.4402 | 1.3719 | 1.9744 | 1.9663 | 1.952 | 1.9428 | 1.9265 | 1.9193 | 1.905 | 1.8836 | 1.8734 | 1.8509 | 1.754 | 1.6387 | 1.5448 | 1.7604 | 1.7492 | 1.7339 | 1.7216 | 1.6981 | 1.6941 | 1.6685 | 1.64 | 1.6247 | 1.5961 | 1.4706 | 1.3522 | 1.2971
| DYCE | BALMEDIE | MINIMUM HEADROOM | NJ 95546 18627 | NO | YES | 0.056 | 0.91287 | 0.55981 | -0.091212 | -1.0198 | -2.1412 | -3.4371 | -4.3463 | -5.3392 | -6.2402 | -7.1841 | -8.7596 | -9.0973 | -9.2208 | 1.7945 | 1.5374 | 1.1965 | 0.68736 | 0.022053 | -0.79529 | -1.4218 | -2.1341 | -2.8249 | -3.6086 | -4.6637 | -4.833 | -5.0984 | 1.5221 | 1.1394 | 0.56797 | -0.21162 | -1.1565 | -2.2575 | -3.0504 | -3.9249 | -4.7392 | -5.6106 | -7.0586 | -7.3402 | -7.4422
|  | BALMEDIE | EE |  |  |  |  | 0.91287 | 0.66491 | 0.20164 | -0.55346 | -1.5473 | -2.8228 | -4.1963 | -5.0535 | -5.8433 | -6.6351 | -8.7014 | -9.033 | -9.1647 | 1.7965 | 1.6067 | 1.32 | 0.94144 | 0.35267 | -0.41774 | -1.2749 | -1.8861 | -2.4882 | -3.131 | -4.6637 | -4.833 | -5.0984 | 1.5221 | 1.269 | 0.78736 | 0.15369 | -0.68815 | -1.7749 | -2.9382 | -3.7065 | -4.4239 | -5.1412 | -7.0157 | -7.283 | -7.3922
|  | BALMEDIE | HT |  |  |  |  | 0.92205 | 0.55981 | -0.091212 | -1.0198 | -2.1412 | -3.4371 | -4.3463 | -5.3392 | -6.2402 | -7.1841 | -8.7596 | -9.0973 | -9.2208 | 1.7945 | 1.5374 | 1.1965 | 0.68736 | 0.022053 | -0.79529 | -1.4218 | -2.1341 | -2.8249 | -3.6086 | -4.5586 | -4.6524 | -4.7137 | 1.5363 | 1.1394 | 0.56797 | -0.21162 | -1.1565 | -2.2575 | -3.0504 | -3.9249 | -4.7392 | -5.6106 | -7.0586 | -7.3402 | -7.4422
|  | BALMEDIE | HE |  |  |  |  | 0.94756 | 0.73634 | 0.45164 | -0.0075388 | -0.74223 | -1.6555 | -2.6953 | -3.5024 | -4.1892 | -4.9157 | -7.2269 | -7.8535 | -8.3637 | 1.818 | 1.6374 | 1.4118 | 1.1037 | 0.72205 | 0.12716 | -0.58203 | -1.1749 | -1.7228 | -2.3412 | -4.0422 | -4.3504 | -4.7749 | 1.5618 | 1.3547 | 1.0731 | 0.61185 | -0.015702 | -0.79836 | -1.6963 | -2.4157 | -3.0228 | -3.6841 | -5.7922 | -6.3208 | -6.7463
|  | BALMEDIE | CF |  |  |  |  | 1.021 | 0.90062 | 0.75675 | 0.54654 | 0.21083 | -0.28509 | -0.94019 | -1.6657 | -2.1657 | -2.6545 | -5.0616 | -6.7494 | -7.7341 | 1.8751 | 1.7721 | 1.6465 | 1.4863 | 1.27 | 1.0016 | 0.60471 | 0.11899 | -0.25652 | -0.6555 | -2.6228 | -4.0779 | -4.9341 | 1.6302 | 1.5118 | 1.3731 | 1.1435 | 0.80062 | 0.38022 | -0.16774 | -0.78611 | -1.2249 | -1.6565 | -3.8392 | -5.3453 | -6.1902
| CLAYHILLS | BALNAGASK | MINIMUM HEADROOM | NJ 96055 05234 | YES | NO | 0 | 10.1027 | 9.9894 | 9.8506 | 9.7159 | 9.5618 | 9.3863 | 9.122 | 8.8343 | 8.5414 | 8.2751 | 7.019 | 6.0578 | 5.9129 | 8.8932 | 8.8187 | 8.7228 | 8.6309 | 8.5228 | 8.3952 | 8.2319 | 8.0554 | 7.8738 | 7.7146 | 6.9717 | 6.4432 | 5.9574 | 9.6443 | 9.5433 | 9.4168 | 9.2943 | 9.1474 | 8.976 | 8.7158 | 8.4423 | 8.1709 | 7.9229 | 6.7821 | 5.9219 | 5.7923
|  | BALNAGASK | EE |  |  |  |  | 10.1027 | 9.9894 | 9.8506 | 9.7159 | 9.5618 | 9.3863 | 9.122 | 8.8343 | 8.5414 | 8.2751 | 7.019 | 6.1669 | 5.9353 | 8.8932 | 8.8187 | 8.7228 | 8.6309 | 8.5228 | 8.3952 | 8.2319 | 8.0554 | 7.8738 | 7.7146 | 6.9717 | 6.4432 | 5.9574 | 9.6443 | 9.5433 | 9.4168 | 9.2943 | 9.1474 | 8.976 | 8.7158 | 8.4423 | 8.1709 | 7.9229 | 6.7821 | 6.0249 | 5.8168
|  | BALNAGASK | HT |  |  |  |  | 10.1445 | 10.0506 | 9.9445 | 9.8333 | 9.7027 | 9.571 | 9.32 | 9.0476 | 8.77 | 8.4884 | 7.0282 | 6.0578 | 5.9129 | 8.9156 | 8.8687 | 8.8085 | 8.7381 | 8.6534 | 8.5707 | 8.4309 | 8.2819 | 8.133 | 7.9768 | 7.2054 | 6.733 | 6.6697 | 9.6678 | 9.5984 | 9.4964 | 9.3892 | 9.2668 | 9.1443 | 8.9076 | 8.6576 | 8.4025 | 8.1433 | 6.8025 | 5.9219 | 5.7923
|  | BALNAGASK | HE |  |  |  |  | 10.1414 | 10.0782 | 10.0037 | 9.9282 | 9.8363 | 9.7486 | 9.5802 | 9.4006 | 9.2067 | 9.0078 | 7.9445 | 7.2271 | 7.0251 | 8.9105 | 8.8738 | 8.8279 | 8.7697 | 8.7003 | 8.6319 | 8.5248 | 8.4054 | 8.2819 | 8.1564 | 7.4799 | 6.9819 | 6.5493 | 9.6678 | 9.6239 | 9.5586 | 9.4882 | 9.4045 | 9.327 | 9.1576 | 8.976 | 8.7984 | 8.6127 | 7.6382 | 6.9913 | 6.8137
|  | BALNAGASK | CF |  |  |  |  | 10.17 | 10.1333 | 10.0904 | 10.0424 | 9.9904 | 9.9271 | 9.8761 | 9.7945 | 9.719 | 9.6496 | 9.1404 | 8.5384 | 7.8873 | 8.9258 | 8.8993 | 8.8738 | 8.8309 | 8.787 | 8.7309 | 8.6768 | 8.6013 | 8.5279 | 8.4585 | 7.9554 | 7.1972 | 6.1248 | 9.679 | 9.6637 | 9.6382 | 9.5964 | 9.5535 | 9.4994 | 9.4545 | 9.379 | 9.3086 | 9.2403 | 8.7403 | 8.1545 | 7.5637
| KINTORE | BANCHORY | MINIMUM HEADROOM | NO 69262 96297 | NO | YES | 2.251 | 2.3069 | 1.6079 | 0.75278 | 24.3095 | 23.5952 | 22.4391 | 21.5371 | 20.6044 | 20.0187 | 19.0799 | 15.7014 | 12.8014 | 11.3024 | 5.3058 | 4.8793 | 4.3599 | 27.7085 | 27.3738 | 26.5126 | 26.0269 | 25.4707 | 25.0718 | 24.4544 | 21.5738 | 19.3024 | 16.8452 | 3.5467 | 2.9589 | 2.2048 | 25.884 | 25.2585 | 24.1054 | 23.2881 | 22.4258 | 21.9391 | 21.0799 | 17.8636 | 14.8126 | 13.0718
|  | BANCHORY | EE |  |  |  |  | 2.3069 | 1.6365 | 0.91809 | 24.636 | 23.7503 | 22.7309 | 22.0177 | 21.1534 | 20.1932 | 19.2871 | 16.036 | 13.4218 | 12.6085 | 5.3344 | 4.9089 | 4.5099 | 28.0197 | 27.5126 | 26.8432 | 26.3677 | 25.8605 | 25.233 | 24.6605 | 22.5789 | 20.1789 | 18.7503 | 3.5467 | 2.9589 | 2.3344 | 26.1962 | 25.3738 | 24.3932 | 23.7932 | 22.9952 | 22.0779 | 21.236 | 18.2269 | 15.535 | 14.6442
|  | BANCHORY | HT |  |  |  |  | 2.3252 | 1.6079 | 0.75278 | 24.3095 | 23.5952 | 22.4391 | 21.5371 | 20.6044 | 20.0187 | 19.0799 | 15.7014 | 12.8014 | 11.3024 | 5.3058 | 4.8793 | 4.3599 | 27.7085 | 27.3738 | 26.5126 | 26.0269 | 25.4707 | 25.0718 | 24.4718 | 22.4411 | 20.1065 | 18.4167 | 3.5885 | 2.9742 | 2.2048 | 25.884 | 25.2585 | 24.1054 | 23.2881 | 22.4258 | 21.9391 | 21.0799 | 17.8636 | 14.8126 | 13.0718
|  | BANCHORY | HE |  |  |  |  | 2.4191 | 1.8875 | 1.2558 | 25.0177 | 24.386 | 23.3483 | 22.5126 | 21.7391 | 21.333 | 20.4942 | 16.6493 | 13.8136 | 11.9238 | 5.4028 | 5.016 | 4.5803 | 27.984 | 27.5962 | 26.7707 | 26.2054 | 25.6289 | 25.185 | 24.4544 | 21.5738 | 19.3024 | 16.8452 | 3.6711 | 3.2038 | 2.6303 | 26.4901 | 25.9238 | 24.8871 | 24.1075 | 23.3595 | 22.9993 | 22.1575 | 18.3575 | 15.4054 | 13.3156
|  | BANCHORY | CF |  |  |  |  | 2.6324 | 2.2834 | 1.9028 | 25.9891 | 25.5044 | 24.9779 | 24.4779 | 23.9789 | 23.5503 | 23.3891 | 21.032 | 18.5646 | 16.684 | 5.6171 | 5.3803 | 5.1528 | 28.8381 | 28.534 | 28.1473 | 27.8044 | 27.4248 | 27.0758 | 26.8503 | 25.0095 | 22.732 | 20.3432 | 3.8579 | 3.5558 | 3.2314 | 27.4238 | 26.9738 | 26.4707 | 25.9993 | 25.5269 | 25.1044 | 24.9779 | 22.7279 | 20.4024 | 18.733
| TAYNUILT | BARCALDINE | MINIMUM HEADROOM | NM 96356 42181 | YES | YES | 1.921 | -4.1608 | -4.2373 | -4.3414 | -4.4567 | -4.6046 | -4.7659 | -4.9067 | -5.0873 | -5.2516 | -5.4016 | -5.7332 | -5.824 | -5.8516 | -3.924 | -3.9689 | -4.0322 | -4.0955 | -4.1802 | -4.271 | -4.3516 | -4.471 | -4.5832 | -4.6822 | -4.9189 | -5.0179 | -5.3628 | -3.8822 | -3.9577 | -4.0577 | -4.1608 | -4.2955 | -4.4434 | -4.5689 | -4.7393 | -4.8975 | -5.0383 | -5.3516 | -5.4363 | -5.4608
|  | BARCALDINE | EE |  |  |  |  | -4.1608 | -4.2373 | -4.3414 | -4.4567 | -4.6046 | -4.7659 | -4.9067 | -5.0873 | -5.2516 | -5.4016 | -5.7332 | -5.7853 | -5.8087 | -3.924 | -3.9689 | -4.0322 | -4.0955 | -4.1802 | -4.271 | -4.3516 | -4.471 | -4.5832 | -4.6822 | -4.9189 | -5.0179 | -5.1648 | -3.8822 | -3.9577 | -4.0577 | -4.1608 | -4.2955 | -4.4434 | -4.5689 | -4.7393 | -4.8975 | -5.0383 | -5.3516 | -5.3995 | -5.424
|  | BARCALDINE | HT |  |  |  |  | -4.1312 | -4.1975 | -4.2761 | -4.3873 | -4.525 | -4.6516 | -4.7924 | -4.9485 | -5.0893 | -5.1883 | -5.6363 | -5.824 | -5.8516 | -3.9067 | -3.9465 | -3.9873 | -4.0465 | -4.121 | -4.1853 | -4.271 | -4.3648 | -4.4475 | -4.5046 | -4.7985 | -4.9108 | -4.9302 | -3.8536 | -3.9199 | -3.9924 | -4.0924 | -4.2169 | -4.3261 | -4.4618 | -4.6077 | -4.7404 | -4.8302 | -5.2587 | -5.4363 | -5.4608
|  | BARCALDINE | HE |  |  |  |  | -4.1322 | -4.1842 | -4.2495 | -4.3353 | -4.4618 | -4.5781 | -4.7128 | -4.8495 | -4.9791 | -5.0597 | -5.5791 | -5.7016 | -5.7199 | -3.9067 | -3.9404 | -3.9802 | -4.0302 | -4.1006 | -4.1638 | -4.2404 | -4.3281 | -4.4087 | -4.4659 | -4.8169 | -4.9577 | -5.1016 | -3.8546 | -3.9067 | -3.9679 | -4.0465 | -4.1577 | -4.2597 | -4.3822 | -4.5108 | -4.6353 | -4.7108 | -5.2046 | -5.3169 | -5.3363
|  | BARCALDINE | CF |  |  |  |  | -4.1179 | -4.1659 | -4.2138 | -4.2853 | -4.3791 | -4.4648 | -4.5291 | -4.6353 | -4.7189 | -4.8169 | -5.2057 | -5.5373 | -5.7159 | -3.8985 | -3.9281 | -3.9567 | -4.0026 | -4.0567 | -4.1057 | -4.1465 | -4.2159 | -4.271 | -4.3332 | -4.6353 | -4.9893 | -5.3628 | -3.8404 | -3.8873 | -3.9322 | -3.9975 | -4.0822 | -4.1597 | -4.2159 | -4.3138 | -4.3914 | -4.4822 | -4.8526 | -5.173 | -5.3353
| STORNOWAY | BARVAS | MINIMUM HEADROOM | NB 35613 48891 | NO | YES | 0.078 | 0.7359 | 0.60937 | 5.3657 | 5.2473 | 5.1014 | 4.9504 | 4.7892 | 4.5739 | 4.3524 | 4.1575 | 3.7086 | 3.6075 | 3.5688 | 1.6298 | 1.5481 | 6.4137 | 6.3667 | 6.3045 | 6.2034 | 6.1055 | 5.9534 | 5.8096 | 5.6881 | 5.3708 | 5.2228 | 4.6667 | 1.2553 | 1.139 | 5.9045 | 5.7973 | 5.6626 | 5.5218 | 5.3749 | 5.1871 | 5.0055 | 4.8412 | 4.4361 | 4.332 | 4.2932
|  | BARVAS | EE |  |  |  |  | 0.7359 | 0.61855 | 5.3657 | 5.2473 | 5.1014 | 4.9504 | 4.7892 | 4.5739 | 4.3524 | 4.1575 | 3.7086 | 3.6453 | 3.6167 | 1.6298 | 1.5981 | 6.4137 | 6.3667 | 6.3045 | 6.2034 | 6.1055 | 5.9534 | 5.8096 | 5.6881 | 5.3708 | 5.2228 | 4.9871 | 1.2553 | 1.1543 | 5.9045 | 5.7973 | 5.6626 | 5.5218 | 5.3749 | 5.1871 | 5.0055 | 4.8412 | 4.4361 | 4.3749 | 4.3534
|  | BARVAS | HT |  |  |  |  | 0.77467 | 0.60937 | 5.4279 | 5.3218 | 5.2004 | 5.0718 | 4.9524 | 4.7973 | 4.6432 | 4.5177 | 3.8851 | 3.6075 | 3.5688 | 1.6532 | 1.5481 | 6.4524 | 6.4147 | 6.3647 | 6.3106 | 6.2637 | 6.1912 | 6.0881 | 6.0167 | 5.581 | 5.4239 | 5.4014 | 1.2859 | 1.139 | 5.9667 | 5.8708 | 5.7596 | 5.6392 | 5.5341 | 5.3902 | 5.2483 | 5.132 | 4.5841 | 4.332 | 4.2932
|  | BARVAS | HE |  |  |  |  | 0.77365 | 0.69814 | 5.4861 | 5.4116 | 5.3269 | 5.2249 | 5.1239 | 4.9881 | 4.8545 | 4.7473 | 3.9422 | 3.7524 | 3.7279 | 1.6502 | 1.6267 | 6.4606 | 6.43 | 6.3881 | 6.3381 | 6.2932 | 6.2239 | 6.1402 | 6.0718 | 5.5208 | 5.2994 | 5.0708 | 1.2828 | 1.2267 | 6.0188 | 5.9524 | 5.8718 | 5.779 | 5.6861 | 5.5606 | 5.4361 | 5.3412 | 4.6198 | 4.4483 | 4.4249
|  | BARVAS | CF |  |  |  |  | 0.77467 | 0.71141 | 5.58 | 5.4545 | 5.3749 | 5.2973 | 5.2096 | 5.1381 | 5.0473 | 4.9555 | 4.4953 | 4.0116 | 3.7606 | 1.6543 | 1.64 | 6.5596 | 6.4647 | 6.4341 | 6.4014 | 6.3616 | 6.3279 | 6.2596 | 6.181 | 5.7637 | 5.2249 | 4.6667 | 1.291 | 1.242 | 6.1157 | 5.9912 | 5.9167 | 5.8432 | 5.7637 | 5.6973 | 5.6147 | 5.5279 | 5.1096 | 4.7147 | 4.4688
| STORNOWAY | BATTERY POINT | MINIMUM HEADROOM | NB 43147 32182 | NO | YES | 1.008 | 1.1478 | 14.3544 | 13.6319 | 12.7135 | 11.9033 | 10.7819 | 9.8421 | 8.5095 | 7.0962 | 5.0921 | -2.8701 | -6.9334 | -9.5303 | 4.1478 | 16.6942 | 15.9931 | 15.2166 | 14.635 | 13.286 | 12.4758 | 11.4717 | 10.2248 | 8.3676 | 1.3615 | -2.8242 | -5.9609 | 3.6927 | 16.4901 | 15.6931 | 14.7646 | 13.9574 | 12.6044 | 11.537 | 10.2095 | 8.8105 | 6.7799 | -1.2895 | -5.8579 | -9.0211
|  | BATTERY POINT | EE |  |  |  |  | 1.1478 | 14.3615 | 13.684 | 12.8635 | 11.9033 | 10.9299 | 9.8554 | 8.6748 | 7.1523 | 5.5911 | 0.52987 | -2.113 | -3.1069 | 4.1478 | 16.7278 | 16.0829 | 15.4748 | 14.686 | 13.7758 | 12.9982 | 12.134 | 10.8023 | 9.435 | 5.084 | 2.035 | 0.81049 | 3.6927 | 16.4901 | 15.7697 | 14.985 | 13.9574 | 12.834 | 11.7656 | 10.6329 | 9.1095 | 7.5697 | 2.4809 | -0.74972 | -1.962
|  | BATTERY POINT | HT |  |  |  |  | 1.3213 | 14.3544 | 13.6319 | 12.7135 | 12.1023 | 10.7819 | 9.8462 | 8.7686 | 7.6482 | 5.9156 | 1.2033 | -2.713 | -5.1528 | 4.3315 | 16.6942 | 15.9931 | 15.2166 | 14.8013 | 13.5278 | 12.8758 | 12.0829 | 11.0564 | 9.5666 | 5.3513 | 1.2268 | -1.6926 | 3.8907 | 16.5186 | 15.6931 | 14.7646 | 14.2482 | 12.8197 | 11.9033 | 10.8125 | 9.5809 | 7.8768 | 2.8431 | -1.6967 | -4.7262
|  | BATTERY POINT | HE |  |  |  |  | 1.2948 | 14.5676 | 13.8207 | 13.0044 | 12.334 | 10.9074 | 9.8421 | 8.5095 | 7.0962 | 5.0921 | -2.8701 | -6.9334 | -9.5303 | 4.2917 | 16.9095 | 16.1278 | 15.2707 | 14.635 | 13.286 | 12.4758 | 11.4717 | 10.2248 | 8.3676 | 1.3615 | -2.8242 | -5.9609 | 3.857 | 16.7574 | 15.9625 | 14.9982 | 14.1717 | 12.6044 | 11.537 | 10.2095 | 8.8105 | 6.7799 | -1.2895 | -5.8579 | -9.0211
|  | BATTERY POINT | CF |  |  |  |  | 1.4019 | 14.8105 | 14.6044 | 14.1248 | 13.5013 | 12.8289 | 12.2289 | 11.6003 | 10.8962 | 9.9717 | 5.0197 | 0.67885 | -1.4416 | 4.3835 | 17.1186 | 16.9442 | 16.4513 | 15.8758 | 15.2197 | 14.684 | 14.1105 | 13.4707 | 12.6533 | 8.6595 | 5.0319 | 3.3278 | 3.9713 | 16.9799 | 16.7003 | 16.2084 | 15.5829 | 14.9238 | 14.2891 | 13.5595 | 12.7748 | 11.8186 | 7.0207 | 2.7707 | 0.66763
| DOUNREAY | BETTYHILL | MINIMUM HEADROOM | NC 70763 61645 | YES | NO | 0.11 | 0.18362 | 0.14587 | 0.11322 | 0.065257 | 0.024441 | -0.022498 | -0.085763 | -0.1327 | -0.19495 | -0.24291 | -0.37454 | -0.41433 | -0.42658 | 0.45403 | 0.43158 | 0.41118 | 0.37954 | 0.35607 | 0.32036 | 0.27954 | 0.25301 | 0.2122 | 0.1826 | 0.094849 | 0.060155 | -0.063314 | 0.28567 | 0.25199 | 0.22036 | 0.17444 | 0.13669 | 0.089747 | 0.027502 | -0.013314 | -0.071478 | -0.11842 | -0.23882 | -0.27148 | -0.28372
|  | BETTYHILL | EE |  |  |  |  | 0.18362 | 0.14587 | 0.11322 | 0.065257 | 0.024441 | -0.022498 | -0.085763 | -0.1327 | -0.19495 | -0.24291 | -0.37454 | -0.39393 | -0.40617 | 0.45403 | 0.43158 | 0.41118 | 0.37954 | 0.35607 | 0.32036 | 0.27954 | 0.25301 | 0.2122 | 0.1826 | 0.094849 | 0.060155 | 0.0060735 | 0.28567 | 0.25199 | 0.22036 | 0.17444 | 0.13669 | 0.089747 | 0.027502 | -0.013314 | -0.071478 | -0.11842 | -0.23882 | -0.25719 | -0.26638
|  | BETTYHILL | HT |  |  |  |  | 0.19689 | 0.16832 | 0.13771 | 0.099951 | 0.07138 | 0.031584 | -0.0071918 | -0.058212 | -0.10719 | -0.15821 | -0.32964 | -0.41433 | -0.42658 | 0.46628 | 0.45199 | 0.43362 | 0.41118 | 0.39689 | 0.37342 | 0.35097 | 0.31832 | 0.28464 | 0.25097 | 0.14587 | 0.093829 | 0.087706 | 0.30097 | 0.27546 | 0.24791 | 0.21118 | 0.18669 | 0.14791 | 0.11424 | 0.065257 | 0.017298 | -0.034743 | -0.19393 | -0.27148 | -0.28372
|  | BETTYHILL | HE |  |  |  |  | 0.19893 | 0.17648 | 0.15199 | 0.12138 | 0.10301 | 0.070359 | 0.035665 | -0.0071918 | -0.05209 | -0.096988 | -0.30617 | -0.36331 | -0.37148 | 0.46934 | 0.45505 | 0.43771 | 0.4173 | 0.40709 | 0.38056 | 0.36526 | 0.33056 | 0.30301 | 0.27036 | 0.14179 | 0.083624 | 0.031584 | 0.30301 | 0.28158 | 0.25913 | 0.2275 | 0.2122 | 0.17852 | 0.14995 | 0.10607 | 0.064237 | 0.020359 | -0.17046 | -0.22352 | -0.23168
|  | BETTYHILL | CF |  |  |  |  | 0.20097 | 0.1826 | 0.15913 | 0.13975 | 0.1122 | 0.09791 | 0.068318 | 0.036686 | 0.015257 | -0.012294 | -0.15515 | -0.28576 | -0.36331 | 0.47036 | 0.45913 | 0.44179 | 0.42954 | 0.41016 | 0.40199 | 0.37954 | 0.35607 | 0.34179 | 0.31628 | 0.20709 | 0.07138 | -0.063314 | 0.30505 | 0.28873 | 0.26424 | 0.24689 | 0.21832 | 0.20607 | 0.17648 | 0.14383 | 0.12444 | 0.094849 | -0.038824 | -0.16638 | -0.22862
| GRUDIE BRIDGE | BIDEN CLAN RAONAILD | MINIMUM HEADROOM | NH 06927 58342 | YES | NO | 0 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201
|  | BIDEN CLAN RAONAILD | EE |  |  |  |  | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201
|  | BIDEN CLAN RAONAILD | HT |  |  |  |  | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201
|  | BIDEN CLAN RAONAILD | HE |  |  |  |  | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201
|  | BIDEN CLAN RAONAILD | CF |  |  |  |  | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.11651 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.10751 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201 | 0.11201
| ELGIN | BILBOHALL | MINIMUM HEADROOM | NJ 20782 61556 | YES | YES | 5.156 | 7.2936 | 7.1038 | 16.1054 | 15.9636 | 15.8421 | 15.6901 | 15.4911 | 15.287 | 15.0483 | 14.7666 | 13.8523 | 13.4564 | 13.3829 | 7.6003 | 7.5258 | 16.4656 | 16.3891 | 16.3268 | 16.2411 | 16.135 | 16.0238 | 15.8942 | 15.7636 | 15.2615 | 15.0187 | 14.7166 | 7.3015 | 7.1444 | 16.0952 | 15.9666 | 15.8595 | 15.7238 | 15.5462 | 15.3595 | 15.1523 | 14.9207 | 14.1044 | 13.7421 | 13.6748
|  | BILBOHALL | EE |  |  |  |  | 7.2936 | 7.1038 | 16.1054 | 15.9636 | 15.8421 | 15.6901 | 15.4911 | 15.287 | 15.0483 | 14.7962 | 13.8523 | 13.5023 | 13.4268 | 7.6003 | 7.5258 | 16.4656 | 16.3891 | 16.3268 | 16.2411 | 16.135 | 16.0238 | 15.8942 | 15.7636 | 15.2615 | 15.0187 | 14.7972 | 7.3015 | 7.1444 | 16.0952 | 15.9666 | 15.8595 | 15.7238 | 15.5462 | 15.3595 | 15.1523 | 14.9289 | 14.1044 | 13.786 | 13.7176
|  | BILBOHALL | HT |  |  |  |  | 7.3201 | 7.1476 | 16.1534 | 16.037 | 15.9115 | 15.7727 | 15.5493 | 15.337 | 15.0554 | 14.7666 | 13.8727 | 13.4564 | 13.3829 | 7.6156 | 7.5666 | 16.5054 | 16.4513 | 16.3901 | 16.3176 | 16.2095 | 16.1115 | 15.9707 | 15.8268 | 15.3778 | 15.184 | 15.1493 | 7.325 | 7.1832 | 16.137 | 16.0319 | 15.9187 | 15.7932 | 15.5952 | 15.4115 | 15.1707 | 14.9207 | 14.1217 | 13.7421 | 13.6748
|  | BILBOHALL | HE |  |  |  |  | 7.3221 | 7.1874 | 16.2258 | 16.1503 | 16.0554 | 15.9605 | 15.8329 | 15.6758 | 15.4819 | 15.2574 | 14.3085 | 13.8942 | 13.7401 | 7.6136 | 7.5727 | 16.5309 | 16.4901 | 16.436 | 16.3799 | 16.3054 | 16.2227 | 16.1166 | 15.9952 | 15.4574 | 15.1748 | 14.9207 | 7.326 | 7.2178 | 16.2034 | 16.136 | 16.0503 | 15.9646 | 15.8483 | 15.7156 | 15.5462 | 15.3544 | 14.5156 | 14.138 | 13.9942
|  | BILBOHALL | CF |  |  |  |  | 7.3456 | 7.2374 | 16.3003 | 16.2299 | 16.1819 | 16.1125 | 16.0523 | 15.9799 | 15.9207 | 15.8258 | 15.0523 | 14.5197 | 14.1125 | 7.6207 | 7.587 | 16.5656 | 16.5238 | 16.4942 | 16.4503 | 16.4064 | 16.3523 | 16.3156 | 16.2483 | 15.7605 | 15.284 | 14.7166 | 7.3495 | 7.2638 | 16.2707 | 16.2085 | 16.1656 | 16.1013 | 16.0483 | 15.985 | 15.936 | 15.8513 | 15.1972 | 14.7156 | 14.3401
| RANNOCH | BLACKMOUNT | MINIMUM HEADROOM | NN 30077 41404 | YES | YES | 0 | 0.015122 | 0.0079796 | 0.0079796 | 0.0079796 | 0.00083673 | -0.00018367 | -0.0073265 | -0.0073265 | -0.0083469 | -0.011408 | -0.0093673 | -0.0093673 | -0.012429 | 0.015724 | 0.0075612 | 0.0075612 | 0.0075612 | 0.00041837 | -0.00060204 | -0.0077449 | -0.0077449 | -0.0046837 | -0.0087653 | -0.0087653 | -0.0046837 | -0.0087653 | 0.014913 | 0.0077704 | 0.0077704 | 0.0077704 | 0.00062755 | -0.00039286 | -0.0075357 | -0.0075357 | -0.010597 | -0.012638 | -0.011617 | -0.011617 | -0.013658
|  | BLACKMOUNT | EE |  |  |  |  | 0.015122 | 0.0079796 | 0.0079796 | 0.0079796 | 0.00083673 | -0.00018367 | -0.0073265 | -0.0073265 | -0.0083469 | -0.011408 | -0.0063061 | -0.0063061 | -0.0063061 | 0.015724 | 0.0075612 | 0.0075612 | 0.0075612 | 0.00041837 | -0.00060204 | -0.0077449 | -0.0077449 | -0.0046837 | -0.0057041 | -0.0016224 | -0.0016224 | -0.0016224 | 0.014913 | 0.0077704 | 0.0077704 | 0.0077704 | 0.00062755 | -0.00039286 | -0.0075357 | -0.0075357 | -0.010597 | -0.012638 | -0.0085561 | -0.0085561 | -0.0085561
|  | BLACKMOUNT | HT |  |  |  |  | 0.015122 | 0.015122 | 0.015122 | 0.0079796 | 0.0079796 | 0.0079796 | 0.0069592 | -0.00018367 | -0.00018367 | -0.0073265 | -0.0042653 | -0.0052857 | -0.0052857 | 0.015724 | 0.015724 | 0.015724 | 0.0075612 | 0.0075612 | 0.0075612 | 0.0075612 | -0.00060204 | -0.00060204 | -0.0077449 | -0.00060204 | -0.0016224 | -0.0016224 | 0.014913 | 0.014913 | 0.014913 | 0.0077704 | 0.0077704 | 0.0077704 | 0.00675 | -0.00039286 | -0.00039286 | -0.0075357 | -0.0065153 | -0.0075357 | -0.0075357
|  | BLACKMOUNT | HE |  |  |  |  | 0.015122 | 0.015122 | 0.015122 | 0.0079796 | 0.0079796 | 0.0079796 | 0.0069592 | -0.00018367 | -0.00018367 | -0.0083469 | -0.0093673 | -0.0063061 | -0.0063061 | 0.015724 | 0.015724 | 0.014704 | 0.0075612 | 0.0075612 | 0.0075612 | 0.0075612 | 0.00041837 | -0.00060204 | -0.0087653 | -0.0046837 | -0.0016224 | -0.0016224 | 0.014913 | 0.014913 | 0.014913 | 0.0077704 | 0.0077704 | 0.0077704 | 0.0077704 | 0.00062755 | -0.00039286 | -0.0075357 | -0.011617 | -0.0075357 | -0.0075357
|  | BLACKMOUNT | CF |  |  |  |  | 0.015122 | 0.015122 | 0.015122 | 0.015122 | 0.0079796 | 0.0079796 | 0.0079796 | 0.0079796 | 0.0079796 | -0.00018367 | -0.0083469 | -0.0093673 | -0.012429 | 0.015724 | 0.015724 | 0.015724 | 0.015724 | 0.0075612 | 0.0075612 | 0.0075612 | 0.0075612 | 0.0075612 | -0.00060204 | -0.0087653 | -0.0046837 | -0.0087653 | 0.014913 | 0.014913 | 0.014913 | 0.014913 | 0.0077704 | 0.0077704 | 0.0077704 | 0.0077704 | 0.0077704 | -0.00039286 | -0.0075357 | -0.011617 | -0.013658
| BEAULY | BLACKSTAND | MINIMUM HEADROOM | NH 71036 59151 | YES | NO | 0.423 | 3.9998 | 3.8652 | 3.7376 | 3.5805 | 3.4386 | 3.2672 | 3.0672 | 2.8845 | 2.6947 | 2.5223 | 2.11 | 1.9743 | 1.9294 | 4.6731 | 4.5874 | 4.517 | 4.416 | 4.3343 | 4.2241 | 4.0976 | 3.9843 | 3.8629 | 3.7527 | 3.469 | 3.3333 | 2.8425 | 4.5217 | 4.3962 | 4.2798 | 4.1278 | 4.0003 | 3.8339 | 3.6349 | 3.4645 | 3.2788 | 3.1145 | 2.74 | 2.6145 | 2.5747
|  | BLACKSTAND | EE |  |  |  |  | 3.9998 | 3.8652 | 3.7376 | 3.5805 | 3.4386 | 3.2672 | 3.0672 | 2.8845 | 2.6947 | 2.5223 | 2.11 | 2.0458 | 2.0152 | 4.6731 | 4.5874 | 4.517 | 4.416 | 4.3343 | 4.2241 | 4.0976 | 3.9843 | 3.8629 | 3.7527 | 3.469 | 3.3333 | 3.1252 | 4.5217 | 4.3962 | 4.2798 | 4.1278 | 4.0003 | 3.8339 | 3.6349 | 3.4645 | 3.2788 | 3.1145 | 2.74 | 2.6788 | 2.6482
|  | BLACKSTAND | HT |  |  |  |  | 4.0233 | 3.9121 | 3.7876 | 3.6662 | 3.5284 | 3.3723 | 3.2386 | 3.0692 | 2.9284 | 2.7835 | 2.2366 | 1.9743 | 1.9294 | 4.6986 | 4.6405 | 4.5782 | 4.516 | 4.4405 | 4.3507 | 4.2803 | 4.1752 | 4.0833 | 3.9905 | 3.6313 | 3.4854 | 3.4588 | 4.5482 | 4.4492 | 4.338 | 4.2309 | 4.1054 | 3.9656 | 3.8452 | 3.686 | 3.5462 | 3.3982 | 2.8564 | 2.6145 | 2.5747
|  | BLACKSTAND | HE |  |  |  |  | 4.0223 | 3.9376 | 3.8396 | 3.7478 | 3.6335 | 3.508 | 3.3896 | 3.2356 | 3.1131 | 2.9866 | 2.3039 | 2.1345 | 2.1141 | 4.6976 | 4.6476 | 4.5894 | 4.5364 | 4.4639 | 4.3823 | 4.317 | 4.216 | 4.1303 | 4.0354 | 3.5864 | 3.3905 | 3.1925 | 4.5482 | 4.4717 | 4.3829 | 4.2992 | 4.1982 | 4.0768 | 3.9707 | 3.8237 | 3.6972 | 3.5645 | 2.9186 | 2.7605 | 2.739
|  | BLACKSTAND | CF |  |  |  |  | 4.0407 | 3.9723 | 3.8835 | 3.7845 | 3.6978 | 3.5917 | 3.4856 | 3.3754 | 3.3152 | 3.2274 | 2.806 | 2.3743 | 2.1488 | 4.7068 | 4.666 | 4.617 | 4.5568 | 4.5058 | 4.4394 | 4.3639 | 4.2782 | 4.2425 | 4.1711 | 3.8047 | 3.3364 | 2.8425 | 4.5635 | 4.5013 | 4.4247 | 4.3349 | 4.2594 | 4.1645 | 4.0645 | 3.9482 | 3.8952 | 3.8023 | 3.3645 | 2.9421 | 2.7554
| COUPAR ANGUS | BLAIRGOWRIE | MINIMUM HEADROOM | NO 18741 44551 | NO | NO | 2.181 | 12.8843 | 12.521 | 12.0884 | 11.6608 | 11.1476 | 10.5374 | 9.8016 | 8.7312 | 7.5833 | 6.8404 | 3.7925 | 2.0925 | 1.7955 | 15.2384 | 15.0323 | 14.7639 | 14.5088 | 14.1863 | 13.8078 | 13.5118 | 12.9047 | 12.2782 | 11.7149 | 10.0067 | 9.0537 | 8.2374 | 14.4103 | 14.0807 | 13.6828 | 13.2899 | 12.8195 | 12.2573 | 11.692 | 10.7236 | 9.6889 | 9.0613 | 6.3256 | 4.8266 | 4.5613
|  | BLAIRGOWRIE | EE |  |  |  |  | 12.8843 | 12.521 | 12.0884 | 11.6608 | 11.1476 | 10.5374 | 9.867 | 8.8904 | 7.8833 | 6.9414 | 3.8751 | 2.1986 | 1.8272 | 15.2384 | 15.0323 | 14.7639 | 14.5088 | 14.1863 | 13.8078 | 13.5118 | 12.9047 | 12.2782 | 11.7149 | 10.0067 | 9.0537 | 8.2374 | 14.4103 | 14.0807 | 13.6828 | 13.2899 | 12.8195 | 12.2573 | 11.7083 | 10.8205 | 9.9073 | 9.0613 | 6.3562 | 4.9246 | 4.592
|  | BLAIRGOWRIE | HT |  |  |  |  | 12.9598 | 12.5976 | 12.1863 | 11.7833 | 11.2823 | 10.7394 | 9.8016 | 8.7312 | 7.5833 | 6.8404 | 3.7925 | 2.0925 | 1.7955 | 15.3312 | 15.1465 | 14.9272 | 14.7261 | 14.4567 | 14.1782 | 13.6486 | 13.0016 | 12.3037 | 11.9914 | 10.3986 | 9.6333 | 9.5057 | 14.4971 | 14.1797 | 13.8124 | 13.4511 | 13.0042 | 12.5277 | 11.692 | 10.7236 | 9.6889 | 9.0889 | 6.3256 | 4.8266 | 4.5613
|  | BLAIRGOWRIE | HE |  |  |  |  | 12.968 | 12.7496 | 12.4792 | 12.2272 | 11.8812 | 11.4812 | 10.7884 | 10.0139 | 9.1904 | 8.7067 | 5.9261 | 4.1945 | 3.4863 | 15.3261 | 15.1874 | 15.0098 | 14.8527 | 14.6312 | 14.3945 | 13.968 | 13.4527 | 12.9047 | 12.6792 | 10.9078 | 9.8823 | 8.9965 | 14.5022 | 14.3062 | 14.0603 | 13.8277 | 13.5134 | 13.1624 | 12.542 | 11.8338 | 11.0828 | 10.7073 | 8.1715 | 6.6797 | 6.0807
|  | BLAIRGOWRIE | CF |  |  |  |  | 13.0414 | 12.8945 | 12.7129 | 12.5445 | 12.3261 | 12.0414 | 11.7578 | 11.3721 | 10.9772 | 10.5343 | 8.8945 | 6.8006 | 5.1425 | 15.3639 | 15.2588 | 15.1261 | 15.0118 | 14.8506 | 14.6537 | 14.4455 | 14.1414 | 13.8282 | 13.4894 | 12.1639 | 10.2721 | 8.2567 | 14.5664 | 14.442 | 14.2746 | 14.1185 | 13.9164 | 13.6593 | 13.4113 | 13.0522 | 12.6879 | 12.2858 | 10.7909 | 8.8756 | 7.446
| STRATHLEVEN | BLAIRLINNANS | MINIMUM HEADROOM | NS 40709 85121 | YES | YES | 0.012 | 0.48571 | 0.46429 | 0.44286 | 0.41939 | 0.39592 | 0.37041 | 0.33878 | 0.30204 | 0.27551 | 0.25 | 0.17653 | 0.13163 | 0.11327 | 0.58776 | 0.57653 | 0.56224 | 0.54796 | 0.53061 | 0.51122 | 0.49184 | 0.46327 | 0.44286 | 0.42653 | 0.36939 | 0.33673 | 0.32143 | 0.54592 | 0.52653 | 0.5051 | 0.48469 | 0.46122 | 0.43673 | 0.40816 | 0.37347 | 0.34694 | 0.32245 | 0.25204 | 0.20816 | 0.1898
|  | BLAIRLINNANS | EE |  |  |  |  | 0.48571 | 0.46429 | 0.44286 | 0.41939 | 0.39592 | 0.37041 | 0.33878 | 0.30204 | 0.27551 | 0.25 | 0.19184 | 0.18469 | 0.18367 | 0.58776 | 0.57653 | 0.56224 | 0.54796 | 0.53061 | 0.51122 | 0.49184 | 0.46327 | 0.44286 | 0.42653 | 0.38367 | 0.38061 | 0.38061 | 0.54592 | 0.52653 | 0.5051 | 0.48469 | 0.46122 | 0.43673 | 0.40816 | 0.37347 | 0.34694 | 0.32245 | 0.26531 | 0.25918 | 0.25816
|  | BLAIRLINNANS | HT |  |  |  |  | 0.4898 | 0.48265 | 0.46939 | 0.45408 | 0.43673 | 0.41837 | 0.39694 | 0.36735 | 0.34592 | 0.32143 | 0.22041 | 0.18469 | 0.17143 | 0.58878 | 0.58265 | 0.58061 | 0.57551 | 0.56122 | 0.55 | 0.53367 | 0.51531 | 0.49694 | 0.47959 | 0.40408 | 0.37959 | 0.37143 | 0.54898 | 0.54592 | 0.53265 | 0.51735 | 0.50102 | 0.48367 | 0.46327 | 0.43571 | 0.41224 | 0.39082 | 0.29388 | 0.2602 | 0.24796
|  | BLAIRLINNANS | HE |  |  |  |  | 0.48878 | 0.48061 | 0.46837 | 0.45102 | 0.43367 | 0.41429 | 0.39082 | 0.35918 | 0.33469 | 0.30408 | 0.17653 | 0.13163 | 0.11327 | 0.58878 | 0.58367 | 0.58163 | 0.57143 | 0.5602 | 0.5449 | 0.52551 | 0.50306 | 0.48571 | 0.46429 | 0.36939 | 0.33673 | 0.32143 | 0.54898 | 0.54286 | 0.53265 | 0.51429 | 0.49796 | 0.48061 | 0.45612 | 0.42653 | 0.40306 | 0.37347 | 0.25204 | 0.20816 | 0.1898
|  | BLAIRLINNANS | CF |  |  |  |  | 0.49388 | 0.4898 | 0.48061 | 0.46939 | 0.45816 | 0.44388 | 0.43163 | 0.41122 | 0.39286 | 0.37857 | 0.27449 | 0.18571 | 0.13776 | 0.59184 | 0.58367 | 0.58367 | 0.58061 | 0.57551 | 0.56633 | 0.55714 | 0.54286 | 0.52857 | 0.51735 | 0.4398 | 0.37551 | 0.34082 | 0.55306 | 0.55 | 0.54388 | 0.53367 | 0.52143 | 0.50714 | 0.4949 | 0.47551 | 0.45714 | 0.44388 | 0.3449 | 0.26122 | 0.21429
| BOAT OF GARTEN | BOAT OF GARTEN | MINIMUM HEADROOM | NH 95609 19427 | NO | YES | 0.501 | 7.5036 | 7.4271 | 7.3516 | 7.2485 | 7.1495 | 7.0332 | 6.9362 | 6.7454 | 6.5618 | 6.3995 | 6.1556 | 6.0414 | 6.0128 | 8.7893 | 8.7434 | 8.6934 | 8.624 | 8.5536 | 8.474 | 8.4107 | 8.2873 | 8.1658 | 8.0618 | 7.875 | 7.7638 | 7.3414 | 8.1944 | 8.1199 | 8.0485 | 7.9516 | 7.8536 | 7.7424 | 7.6505 | 7.4709 | 7.2985 | 7.1444 | 6.9189 | 6.8128 | 6.7883
|  | BOAT OF GARTEN | EE |  |  |  |  | 7.5036 | 7.4271 | 7.3516 | 7.2485 | 7.1495 | 7.0332 | 6.9362 | 6.7454 | 6.5618 | 6.3995 | 6.1556 | 6.1036 | 6.0669 | 8.7893 | 8.7434 | 8.6934 | 8.624 | 8.5536 | 8.474 | 8.4107 | 8.2873 | 8.1658 | 8.0618 | 7.875 | 7.7638 | 7.5771 | 8.1944 | 8.1199 | 8.0485 | 7.9516 | 7.8536 | 7.7424 | 7.6505 | 7.4709 | 7.2985 | 7.1444 | 6.9189 | 6.872 | 6.8373
|  | BOAT OF GARTEN | HT |  |  |  |  | 7.5485 | 7.4883 | 7.422 | 7.3424 | 7.2832 | 7.1587 | 7.0322 | 6.875 | 6.8005 | 6.6873 | 6.2414 | 6.0414 | 6.0128 | 8.8209 | 8.7862 | 8.7465 | 8.6975 | 8.6618 | 8.5852 | 8.5107 | 8.4138 | 8.3709 | 8.2954 | 8.0016 | 7.8791 | 7.8638 | 8.2199 | 8.172 | 8.1199 | 8.0434 | 7.9862 | 7.8709 | 7.7556 | 7.6067 | 7.5393 | 7.4301 | 7.0016 | 6.8128 | 6.7883
|  | BOAT OF GARTEN | HE |  |  |  |  | 7.5475 | 7.4965 | 7.4454 | 7.3791 | 7.3322 | 7.2587 | 7.176 | 7.0373 | 6.9485 | 6.8087 | 6.3342 | 6.2118 | 6.1914 | 8.8169 | 8.7873 | 8.7516 | 8.7087 | 8.674 | 8.624 | 8.5669 | 8.476 | 8.4209 | 8.3291 | 7.9954 | 7.8383 | 7.6638 | 8.2189 | 8.1781 | 8.1393 | 8.075 | 8.0311 | 7.9587 | 7.8832 | 7.7516 | 7.6689 | 7.5393 | 7.0903 | 6.973 | 6.9536
|  | BOAT OF GARTEN | CF |  |  |  |  | 7.5475 | 7.5016 | 7.4597 | 7.4138 | 7.3526 | 7.3148 | 7.2526 | 7.1842 | 7.0842 | 6.9832 | 6.6077 | 6.3352 | 6.2005 | 8.8199 | 8.7893 | 8.7648 | 8.7332 | 8.6934 | 8.6648 | 8.6169 | 8.5628 | 8.4954 | 8.425 | 8.1128 | 7.7699 | 7.3414 | 8.2281 | 8.1924 | 8.1546 | 8.1107 | 8.0516 | 8.0179 | 7.9546 | 7.8914 | 7.7985 | 7.7016 | 7.3444 | 7.0832 | 6.9607
| PETERHEAD SHELL | BODDAM | MINIMUM HEADROOM | NK 12219 42512 | YES | NO | 2.106 | -1.6338 | -1.7266 | -1.8419 | -1.9674 | -2.1032 | -2.5572 | -3.1154 | -3.8256 | -4.6164 | -5.5603 | -6.6644 | -6.8797 | -6.995 | -0.57764 | -0.65519 | -0.74805 | -0.85519 | -0.96744 | -1.4236 | -1.9664 | -2.6634 | -3.4409 | -4.3807 | -5.344 | -5.495 | -5.5807 | -0.49805 | -0.57764 | -0.67152 | -0.78274 | -0.89805 | -1.345 | -1.8817 | -2.5644 | -3.3276 | -4.2429 | -5.3083 | -5.5613 | -5.6593
|  | BODDAM | EE |  |  |  |  | -1.6338 | -1.7266 | -1.8419 | -1.9674 | -2.1032 | -2.4736 | -3.0195 | -3.6113 | -4.2327 | -4.9695 | -6.6644 | -6.8338 | -6.8603 | -0.57764 | -0.65519 | -0.74805 | -0.85519 | -0.96744 | -1.3215 | -1.847 | -2.4154 | -3.0185 | -3.7429 | -5.344 | -5.4583 | -5.4746 | -0.49805 | -0.57764 | -0.67152 | -0.78274 | -0.89805 | -1.247 | -1.7654 | -2.3246 | -2.9185 | -3.6358 | -5.3083 | -5.5062 | -5.5389
|  | BODDAM | HT |  |  |  |  | -1.6103 | -1.697 | -1.798 | -1.9164 | -2.0409 | -2.5572 | -3.1154 | -3.8256 | -4.6164 | -5.5603 | -6.6083 | -6.8797 | -6.9715 | -0.55723 | -0.63172 | -0.71131 | -0.81131 | -0.9205 | -1.4236 | -1.9664 | -2.6634 | -3.4409 | -4.3807 | -5.2848 | -5.4817 | -5.5532 | -0.47968 | -0.55315 | -0.63887 | -0.74091 | -0.85315 | -1.345 | -1.8817 | -2.5644 | -3.3276 | -4.2429 | -5.2623 | -5.5613 | -5.6593
|  | BODDAM | HE |  |  |  |  | -1.6062 | -1.6868 | -1.7736 | -1.8756 | -1.994 | -2.347 | -2.8634 | -3.4327 | -4.0511 | -4.794 | -6.6297 | -6.8736 | -6.995 | -0.55213 | -0.62356 | -0.69397 | -0.78478 | -0.8858 | -1.2246 | -1.7287 | -2.2797 | -2.8827 | -3.6174 | -5.3246 | -5.495 | -5.5807 | -0.47458 | -0.54703 | -0.61948 | -0.70927 | -0.81131 | -1.147 | -1.6409 | -2.1827 | -2.7776 | -3.4929 | -5.2287 | -5.5001 | -5.6256
|  | BODDAM | CF |  |  |  |  | -1.5756 | -1.6215 | -1.6725 | -1.7287 | -1.798 | -1.9511 | -2.1685 | -2.4634 | -2.7695 | -3.1532 | -5.0419 | -6.4736 | -6.8083 | -0.52764 | -0.56642 | -0.61336 | -0.66131 | -0.7205 | -0.86744 | -1.0776 | -1.3623 | -1.6623 | -2.0409 | -3.8715 | -5.2266 | -5.4705 | -0.44907 | -0.48784 | -0.53274 | -0.58172 | -0.64193 | -0.78376 | -0.99091 | -1.2715 | -1.5644 | -1.9348 | -3.7389 | -5.0827 | -5.4368
| TUMMEL BRIDGE | BONSKEID | MINIMUM HEADROOM | NN 90919 60658 | YES | YES | 0.468 | -3.0716 | -3.1288 | -3.2216 | -3.339 | -3.4553 | -3.6175 | -3.8063 | -3.9675 | -4.0961 | -4.2553 | -4.9512 | -5.2869 | -5.4002 | -1.9237 | -1.9604 | -2.0053 | -2.0594 | -2.1145 | -2.1839 | -2.289 | -2.3981 | -2.4798 | -2.6073 | -3.2022 | -3.4502 | -3.542 | -2.4339 | -2.5043 | -2.5869 | -2.6879 | -2.7961 | -2.9257 | -3.0696 | -3.2196 | -3.343 | -3.491 | -4.2553 | -4.5788 | -4.6635
|  | BONSKEID | EE |  |  |  |  | -3.0716 | -3.1288 | -3.2216 | -3.339 | -3.4553 | -3.6175 | -3.8063 | -3.9675 | -4.0961 | -4.2553 | -4.7941 | -4.9839 | -5.0288 | -1.9237 | -1.9604 | -2.0053 | -2.0594 | -2.1145 | -2.1839 | -2.289 | -2.3981 | -2.4798 | -2.5737 | -2.8726 | -2.9971 | -3.1165 | -2.4339 | -2.5043 | -2.5869 | -2.6879 | -2.7961 | -2.9257 | -3.0696 | -3.2196 | -3.343 | -3.4696 | -3.9237 | -4.0798 | -4.1237
|  | BONSKEID | HT |  |  |  |  | -3.0379 | -3.1032 | -3.2032 | -3.3267 | -3.4522 | -3.5788 | -3.693 | -3.8298 | -3.9777 | -4.1522 | -4.6992 | -4.9869 | -5.0349 | -1.8971 | -1.9298 | -1.9655 | -2.0073 | -2.0502 | -2.1063 | -2.1635 | -2.2471 | -2.3288 | -2.4277 | -2.7532 | -2.9063 | -2.9277 | -2.3951 | -2.4441 | -2.5094 | -2.5859 | -2.6869 | -2.8002 | -2.9022 | -3.0308 | -3.1624 | -3.3196 | -3.8308 | -4.09 | -4.1277
|  | BONSKEID | HE |  |  |  |  | -3.0522 | -3.1063 | -3.1594 | -3.2461 | -3.3532 | -3.489 | -3.6339 | -3.8002 | -3.9665 | -4.1471 | -4.9512 | -5.2869 | -5.3104 | -1.9104 | -1.9471 | -1.9849 | -2.0308 | -2.0839 | -2.1492 | -2.2369 | -2.3594 | -2.4777 | -2.6073 | -3.2022 | -3.4502 | -3.4675 | -2.4114 | -2.4808 | -2.5522 | -2.643 | -2.7441 | -2.8696 | -3.0053 | -3.1655 | -3.3196 | -3.491 | -4.2553 | -4.5788 | -4.6032
|  | BONSKEID | CF |  |  |  |  | -3.0328 | -3.0584 | -3.092 | -3.1288 | -3.1798 | -3.2461 | -3.3379 | -3.44 | -3.54 | -3.6675 | -4.3196 | -4.9206 | -5.4002 | -1.8961 | -1.9124 | -1.941 | -1.9655 | -1.9941 | -2.0308 | -2.0777 | -2.1298 | -2.1849 | -2.2747 | -2.7532 | -3.1941 | -3.542 | -2.392 | -2.4186 | -2.4655 | -2.5155 | -2.5737 | -2.6451 | -2.7277 | -2.8298 | -2.9237 | -3.042 | -3.6563 | -4.2206 | -4.6635
| PORT ANN | BOWMORE | MINIMUM HEADROOM | NR 32021 60211 | NO | YES | 0.821 | 4.5418 | 4.4448 | 4.2234 | 3.8897 | 3.7479 | 3.1122 | 2.6509 | 2.2356 | 1.9754 | 1.5458 | -0.53477 | -2.5327 | -4.3786 | 5.2101 | 5.1509 | 4.9367 | 4.6009 | 4.5091 | 3.8152 | 3.4091 | 3.0326 | 2.7203 | 2.1724 | -0.038849 | -2.5286 | -4.9817 | 4.9591 | 4.8724 | 4.6244 | 4.2438 | 4.1112 | 3.3571 | 2.8438 | 2.4152 | 2.1428 | 1.5612 | -0.82558 | -3.2766 | -5.5776
|  | BOWMORE | EE |  |  |  |  | 4.5418 | 4.4448 | 4.3142 | 4.1928 | 3.8979 | 3.4581 | 3.1846 | 2.8101 | 2.3418 | 1.9948 | 0.88768 | -0.86946 | -1.6174 | 5.2101 | 5.1509 | 5.0683 | 4.9958 | 4.7316 | 4.2948 | 4.0663 | 3.753 | 3.2887 | 2.9724 | 1.8652 | -0.38069 | -1.4593 | 4.9591 | 4.8724 | 4.7499 | 4.6397 | 4.3224 | 3.8285 | 3.5387 | 3.1377 | 2.6112 | 2.2336 | 1.0152 | -1.1644 | -2.0899
|  | BOWMORE | HT |  |  |  |  | 4.5652 | 4.4816 | 4.2234 | 3.8897 | 3.7479 | 3.1122 | 2.6509 | 2.2356 | 1.9754 | 1.7612 | 0.60605 | -1.5899 | -3.3552 | 5.2346 | 5.1887 | 4.9367 | 4.6009 | 4.5193 | 3.8152 | 3.4091 | 3.0326 | 2.8254 | 2.6356 | 1.5101 | -1.0909 | -3.2725 | 4.9836 | 4.9132 | 4.6244 | 4.2438 | 4.1112 | 3.3571 | 2.8438 | 2.4152 | 2.1591 | 1.9336 | 0.63054 | -2.045 | -4.2388
|  | BOWMORE | HE |  |  |  |  | 4.5795 | 4.5112 | 4.303 | 4.004 | 3.802 | 3.1897 | 2.904 | 2.453 | 2.054 | 1.5458 | -0.53477 | -2.5327 | -4.3786 | 5.2438 | 5.1979 | 4.9918 | 4.6836 | 4.5091 | 3.8224 | 3.5652 | 3.1265 | 2.7203 | 2.1724 | -0.038849 | -2.5286 | -4.9817 | 4.9969 | 4.9377 | 4.702 | 4.3632 | 4.1509 | 3.4214 | 3.1132 | 2.5999 | 2.1428 | 1.5612 | -0.82558 | -3.2766 | -5.5776
|  | BOWMORE | CF |  |  |  |  | 4.6009 | 4.554 | 4.5009 | 4.4265 | 4.253 | 3.9846 | 3.7989 | 3.6265 | 3.4407 | 3.205 | 2.2295 | 1.3591 | 0.89074 | 5.255 | 5.2234 | 5.1877 | 5.1397 | 4.9816 | 4.7112 | 4.5479 | 4.3989 | 4.2112 | 3.9683 | 3.0112 | 2.0438 | 1.2703 | 5.0152 | 4.9693 | 4.9193 | 4.8479 | 4.6581 | 4.3571 | 4.1612 | 3.9775 | 3.7734 | 3.5101 | 2.452 | 1.5101 | 1.002
| SHETLAND | BRAE | MINIMUM HEADROOM | HU3604068816 | YES | YES | 0.792 | -1.7854 | -1.8293 | -1.8752 | -1.9201 | -2.0925 | -2.3925 | -2.6681 | -2.9956 | -3.3568 | -3.6028 | -4.0721 | -4.1456 | -4.1579 | -0.68438 | -0.72418 | -0.75989 | -0.79561 | -0.94051 | -1.2528 | -1.5385 | -1.8793 | -2.2558 | -2.4946 | -2.764 | -2.814 | -3.015 | -1.2262 | -1.2732 | -1.316 | -1.3568 | -1.5283 | -1.8303 | -2.1099 | -2.4436 | -2.8099 | -3.0497 | -3.3803 | -3.4466 | -3.4721
|  | BRAE | EE |  |  |  |  | -1.7854 | -1.8293 | -1.8752 | -1.9201 | -2.0874 | -2.3313 | -2.6405 | -2.9262 | -3.2528 | -3.5181 | -4.0721 | -4.0997 | -4.1272 | -0.68438 | -0.72418 | -0.75989 | -0.79561 | -0.93438 | -1.1436 | -1.4354 | -1.714 | -2.0191 | -2.2619 | -2.764 | -2.7742 | -2.8803 | -1.2262 | -1.2732 | -1.316 | -1.3568 | -1.513 | -1.7425 | -2.0354 | -2.313 | -2.617 | -2.867 | -3.3803 | -3.4048 | -3.4283
|  | BRAE | HT |  |  |  |  | -1.7721 | -1.8079 | -1.8466 | -1.8874 | -2.0925 | -2.3925 | -2.6681 | -2.9956 | -3.3568 | -3.6028 | -4.0028 | -4.1456 | -4.1579 | -0.66806 | -0.69255 | -0.71602 | -0.74255 | -0.94051 | -1.2528 | -1.5385 | -1.8793 | -2.2558 | -2.4946 | -2.7395 | -2.7925 | -2.8089 | -1.214 | -1.2507 | -1.2885 | -1.3262 | -1.5283 | -1.8303 | -2.1099 | -2.4436 | -2.8099 | -3.0497 | -3.3456 | -3.4466 | -3.4579
|  | BRAE | HE |  |  |  |  | -1.7742 | -1.8028 | -1.8323 | -1.865 | -2.0028 | -2.2201 | -2.4844 | -2.7548 | -3.0395 | -3.2925 | -3.9374 | -4.016 | -4.0425 | -0.66908 | -0.69255 | -0.71296 | -0.73744 | -0.86806 | -1.0936 | -1.3681 | -1.6456 | -1.9456 | -2.1905 | -2.763 | -2.814 | -2.8374 | -1.217 | -1.2476 | -1.2752 | -1.3058 | -1.4446 | -1.663 | -1.9303 | -2.2089 | -2.5028 | -2.7507 | -3.3721 | -3.4456 | -3.4721
|  | BRAE | CF |  |  |  |  | -1.766 | -1.7874 | -1.8089 | -1.8334 | -1.8895 | -1.9895 | -2.1089 | -2.2497 | -2.4068 | -2.5589 | -3.317 | -3.8966 | -3.9936 | -0.65989 | -0.68132 | -0.69969 | -0.72316 | -0.77928 | -0.87112 | -0.99051 | -1.1272 | -1.2864 | -1.4415 | -2.1885 | -2.763 | -3.015 | -1.2048 | -1.2252 | -1.2436 | -1.2711 | -1.3313 | -1.4354 | -1.5568 | -1.6946 | -1.8517 | -1.9976 | -2.7385 | -3.3058 | -3.4181
| BRIDGE OF DUN | BRECHIN | MINIMUM HEADROOM | NO 60998 59682 | NO | NO | 1.621 | 4.0245 | 3.647 | 3.1266 | 2.3827 | 2.0347 | 0.64186 | -0.14488 | -0.99896 | -1.8102 | -2.7867 | -6.8928 | -11.3388 | -14.8143 | 5.9577 | 5.7485 | 5.3005 | 4.6475 | 4.4689 | 3.0699 | 2.5669 | 2.0128 | 1.4801 | 0.44441 | -3.9811 | -8.6331 | -13.1158 | 5.1457 | 4.813 | 4.2028 | 3.3947 | 3.0579 | 1.4916 | 0.75793 | -0.040031 | -0.77881 | -1.6839 | -6.4574 | -11.4819 | -15.638
|  | BRECHIN | EE |  |  |  |  | 4.0245 | 3.647 | 3.2612 | 2.8378 | 2.2449 | 1.2745 | 0.43063 | -0.33263 | -0.89182 | -1.7877 | -5.8898 | -10.1255 | -11.5959 | 5.9577 | 5.7485 | 5.5383 | 5.3118 | 4.8322 | 3.9587 | 3.3546 | 2.8771 | 2.3373 | 1.7097 | -1.3668 | -5.7331 | -7.8995 | 5.1457 | 4.813 | 4.4692 | 4.0712 | 3.4345 | 2.3732 | 1.5141 | 0.77119 | 0.16507 | -0.67574 | -4.6084 | -9.3717 | -11.0941
|  | BRECHIN | HT |  |  |  |  | 4.1143 | 3.7735 | 3.1266 | 2.3827 | 2.0347 | 0.64186 | -0.14488 | -0.99896 | -1.8102 | -2.7867 | -6.6326 | -11.3388 | -14.3877 | 6.0097 | 5.8281 | 5.3005 | 4.6475 | 4.4689 | 3.0699 | 2.5669 | 2.0128 | 1.522 | 0.88727 | -1.8627 | -6.5454 | -10.1556 | 5.2028 | 4.8845 | 4.2028 | 3.3947 | 3.0579 | 1.4916 | 0.75793 | -0.040031 | -0.77881 | -1.6839 | -5.4859 | -10.839 | -14.5553
|  | BRECHIN | HE |  |  |  |  | 4.1378 | 3.897 | 3.4041 | 2.797 | 2.4225 | 1.2123 | 0.5888 | -0.16324 | -0.93671 | -2.0551 | -6.8928 | -11.3306 | -14.8143 | 6.0179 | 5.8822 | 5.4556 | 4.8954 | 4.5944 | 3.3097 | 2.776 | 2.1424 | 1.4801 | 0.44441 | -3.9811 | -8.6331 | -13.1158 | 5.2202 | 5.012 | 4.5018 | 3.8518 | 3.4671 | 2.0834 | 1.413 | 0.63038 | -0.18697 | -1.3921 | -6.4574 | -11.4819 | -15.638
|  | BRECHIN | CF |  |  |  |  | 4.201 | 4.0408 | 3.8572 | 3.6898 | 3.4174 | 2.947 | 2.6051 | 2.2582 | 1.9643 | 1.5337 | -0.55406 | -3.0224 | -4.7449 | 6.0505 | 5.9556 | 5.8485 | 5.7444 | 5.4893 | 5.0148 | 4.6975 | 4.4016 | 4.1128 | 3.7148 | 1.724 | -0.76069 | -3.0454 | 5.2824 | 5.1518 | 4.9977 | 4.8559 | 4.5681 | 4.0579 | 3.7069 | 3.3487 | 3.0345 | 2.5814 | 0.42834 | -1.9696 | -3.6472
| PERSLEY | BRIDGE OF DON | MINIMUM HEADROOM | NJ 94130 10184 | NO | NO | 5.338 | -3.114 | -3.8925 | -5.9232 | -8.3946 | -9.6405 | -13.664 | -15.0578 | -16.5436 | -17.5548 | -19.413 | -30.3772 | -40.6038 | -50.8048 | 0.4146 | -0.20173 | -2.0466 | -4.4027 | -5.1527 | -9.3415 | -10.2681 | -11.7915 | -13.2017 | -15.8232 | -26.914 | -36.7456 | -46.2303 | -1.3492 | -2.089 | -4.2859 | -6.9757 | -8.0828 | -12.6737 | -13.9522 | -15.3084 | -16.4441 | -19.2604 | -31.5614 | -42.441 | -54.5655
|  | BRIDGE OF DON | EE |  |  |  |  | -3.114 | -3.8925 | -4.8364 | -6.0313 | -8.0262 | -10.6936 | -12.2272 | -13.3936 | -15.4395 | -17.013 | -24.5599 | -36.7109 | -41.2089 | 0.4146 | -0.20173 | -0.86499 | -1.5568 | -3.2415 | -5.7476 | -6.9456 | -7.5323 | -9.2701 | -10.4364 | -16.3456 | -29.9823 | -36.0691 | -1.3492 | -2.089 | -3.0196 | -4.0971 | -6.1277 | -9.0104 | -10.5635 | -11.5818 | -13.7114 | -15.2706 | -22.8553 | -37.1757 | -42.6114
|  | BRIDGE OF DON | HT |  |  |  |  | -3.0283 | -3.867 | -5.9232 | -8.3946 | -9.6405 | -13.664 | -15.0578 | -16.5436 | -17.5548 | -19.1874 | -27.0874 | -40.6038 | -50.8048 | 0.46256 | -0.19764 | -2.0466 | -4.4027 | -5.1527 | -9.3415 | -10.1385 | -10.9885 | -11.4405 | -12.3721 | -18.717 | -33.7915 | -46.2303 | -1.2675 | -2.0584 | -4.2859 | -6.9757 | -8.0828 | -12.6737 | -13.9522 | -15.3084 | -16.189 | -17.6757 | -25.8798 | -41.9645 | -54.5655
|  | BRIDGE OF DON | HE |  |  |  |  | -3.0119 | -3.7272 | -5.1303 | -7.114 | -8.4732 | -12.2293 | -13.8874 | -15.5609 | -16.9201 | -19.413 | -30.3772 | -39.8936 | -41.266 | 0.48399 | -0.092543 | -1.5864 | -3.5946 | -4.7507 | -8.8252 | -10.2681 | -11.7915 | -13.2017 | -15.8232 | -26.914 | -36.7456 | -38.3068 | -1.2492 | -1.9328 | -3.492 | -5.7237 | -7.1216 | -11.4747 | -13.1971 | -14.9441 | -16.4441 | -19.2604 | -31.5614 | -42.441 | -43.692
|  | BRIDGE OF DON | CF |  |  |  |  | -2.9048 | -3.3578 | -3.765 | -4.1823 | -5.1976 | -6.6762 | -7.6354 | -8.5201 | -9.3589 | -10.0823 | -14.2038 | -18.8395 | -23.0385 | 0.55746 | 0.21256 | -0.11907 | -0.45071 | -1.4038 | -2.8987 | -3.8272 | -4.6007 | -5.3946 | -6.2221 | -9.965 | -14.4895 | -19.314 | -1.1482 | -1.5716 | -1.9624 | -2.3573 | -3.4757 | -5.1288 | -6.141 | -7.0267 | -7.8839 | -8.7063 | -12.8798 | -17.5686 | -21.7839
| BRIDGE OF DUN | BRIDGE OF DUN | MINIMUM HEADROOM | NO 66018 58883 | YES | NO | 0.074 | 0.11687 | 0.081155 | 0.050543 | 0.015849 | -0.025988 | -0.071906 | -0.11272 | -0.17599 | -0.23313 | -0.28721 | -0.44844 | -0.52905 | -0.54946 | 0.36687 | 0.34544 | 0.32809 | 0.30258 | 0.27095 | 0.23932 | 0.21585 | 0.17299 | 0.13728 | 0.099522 | 0.0097265 | -0.03109 | -0.11987 | 0.22401 | 0.19034 | 0.16075 | 0.12809 | 0.084216 | 0.036257 | 0.00054286 | -0.062722 | -0.1168 | -0.16884 | -0.30966 | -0.37497 | -0.40252
|  | BRIDGE OF DUN | EE |  |  |  |  | 0.11687 | 0.081155 | 0.050543 | 0.015849 | -0.025988 | -0.071906 | -0.11272 | -0.17599 | -0.23313 | -0.28721 | -0.44844 | -0.51476 | -0.52905 | 0.36687 | 0.34544 | 0.32809 | 0.30258 | 0.27095 | 0.23932 | 0.21585 | 0.17299 | 0.13728 | 0.099522 | 0.0097265 | -0.03109 | -0.08109 | 0.22401 | 0.19034 | 0.16075 | 0.12809 | 0.084216 | 0.036257 | 0.00054286 | -0.062722 | -0.1168 | -0.16884 | -0.30966 | -0.35966 | -0.37191
|  | BRIDGE OF DUN | HT |  |  |  |  | 0.13218 | 0.10054 | 0.070951 | 0.033196 | 0.0046245 | -0.03109 | -0.074967 | -0.12701 | -0.16272 | -0.21272 | -0.42497 | -0.52905 | -0.54946 | 0.3832 | 0.36789 | 0.35156 | 0.32401 | 0.31279 | 0.28626 | 0.26483 | 0.23013 | 0.21585 | 0.18422 | 0.048502 | 0.0025837 | -0.017824 | 0.24238 | 0.21483 | 0.18626 | 0.15054 | 0.12707 | 0.089318 | 0.052584 | 0.0015633 | -0.03109 | -0.079049 | -0.28313 | -0.37497 | -0.40252
|  | BRIDGE OF DUN | HE |  |  |  |  | 0.13218 | 0.11279 | 0.09238 | 0.062788 | 0.047482 | 0.01891 | -0.012722 | -0.0566 | -0.099457 | -0.12497 | -0.36578 | -0.46272 | -0.51374 | 0.3832 | 0.37095 | 0.35769 | 0.33116 | 0.32299 | 0.2985 | 0.27809 | 0.2485 | 0.21789 | 0.19238 | 0.036257 | -0.019865 | -0.064763 | 0.24238 | 0.22299 | 0.20258 | 0.17401 | 0.15462 | 0.12503 | 0.087278 | 0.040339 | -0.0045592 | -0.041294 | -0.26782 | -0.35456 | -0.40252
|  | BRIDGE OF DUN | CF |  |  |  |  | 0.13932 | 0.12299 | 0.10667 | 0.086257 | 0.075033 | 0.052584 | 0.026053 | 0.0066653 | -0.018845 | -0.046396 | -0.17089 | -0.33313 | -0.44129 | 0.3883 | 0.37605 | 0.36585 | 0.34646 | 0.34034 | 0.32197 | 0.30054 | 0.28524 | 0.26381 | 0.23932 | 0.14034 | -0.0025184 | -0.11987 | 0.2485 | 0.23116 | 0.21585 | 0.1934 | 0.18626 | 0.16177 | 0.13626 | 0.11789 | 0.090339 | 0.061767 | -0.08109 | -0.23721 | -0.33619
| ABERNETHY | BRIDGE OF EARN | MINIMUM HEADROOM | NO 13343 17764 | NO | YES | 0.418 | 10.0661 | 9.6141 | 9.0814 | 8.4416 | 7.76 | 7.0274 | 6.4406 | 5.7794 | 5.0988 | 4.3763 | 2.1171 | 1.562 | 1.4794 | 11.3488 | 11.0488 | 10.6967 | 10.2722 | 9.809 | 9.3151 | 8.9325 | 8.4886 | 8.0141 | 7.4845 | 5.9182 | 5.5835 | 5.1171 | 11.1585 | 10.7615 | 10.2952 | 9.733 | 9.1268 | 8.4748 | 7.9544 | 7.3636 | 6.7534 | 6.1156 | 4.0748 | 3.6034 | 3.533
|  | BRIDGE OF EARN | EE |  |  |  |  | 10.0876 | 9.6457 | 9.1396 | 8.5671 | 7.9345 | 7.2508 | 6.5896 | 5.9345 | 5.2774 | 4.5916 | 2.1171 | 1.608 | 1.5161 | 11.3651 | 11.0712 | 10.7365 | 10.3539 | 9.9233 | 9.458 | 9.012 | 8.5641 | 8.1202 | 7.6457 | 5.9182 | 5.5835 | 5.2876 | 11.1636 | 10.7891 | 10.3421 | 9.835 | 9.2646 | 8.6472 | 8.0646 | 7.4697 | 6.8799 | 6.2636 | 4.0748 | 3.6503 | 3.5656
|  | BRIDGE OF EARN | HT |  |  |  |  | 10.0661 | 9.6141 | 9.0814 | 8.4416 | 7.76 | 7.0274 | 6.4406 | 5.7794 | 5.0988 | 4.3763 | 2.1437 | 1.562 | 1.4794 | 11.3488 | 11.0488 | 10.6967 | 10.2722 | 9.809 | 9.3151 | 8.9325 | 8.4886 | 8.0141 | 7.4845 | 6.0569 | 5.8182 | 5.7774 | 11.1585 | 10.7615 | 10.2952 | 9.733 | 9.1268 | 8.4748 | 7.9544 | 7.3636 | 6.7534 | 6.1156 | 4.1136 | 3.6034 | 3.533
|  | BRIDGE OF EARN | HE |  |  |  |  | 10.1314 | 9.7396 | 9.3049 | 8.7692 | 8.2029 | 7.5774 | 7.0059 | 6.4396 | 5.8682 | 5.2763 | 2.6804 | 2.0835 | 1.8896 | 11.4018 | 11.1274 | 10.8355 | 10.4671 | 10.0794 | 9.6488 | 9.2427 | 8.8365 | 8.4192 | 7.9661 | 6.0876 | 5.7733 | 5.4457 | 11.2177 | 10.8768 | 10.4972 | 10.0228 | 9.5228 | 8.9636 | 8.4554 | 7.9462 | 7.435 | 6.9126 | 4.5748 | 4.0605 | 3.8972
|  | BRIDGE OF EARN | CF |  |  |  |  | 10.3151 | 10.0304 | 9.6886 | 9.3365 | 8.9518 | 8.5182 | 8.1304 | 7.7406 | 7.3457 | 6.91 | 4.6029 | 2.8896 | 2.3406 | 11.5539 | 11.3661 | 11.1355 | 10.909 | 10.6508 | 10.3539 | 10.0702 | 9.7855 | 9.4967 | 9.1743 | 7.3722 | 5.8661 | 5.1171 | 11.3728 | 11.1401 | 10.8503 | 10.5534 | 10.2166 | 9.8289 | 9.484 | 9.1381 | 8.7891 | 8.4003 | 6.3146 | 4.7401 | 4.2697
| RANNOCH | BRIDGE OF GAUR | MINIMUM HEADROOM | NN 50676 57767 | YES | YES | 0.023 | 0.60355 | 0.60253 | 0.59947 | 0.59334 | 0.58314 | 0.57191 | 0.56375 | 0.54538 | 0.52804 | 0.51477 | 0.49742 | 0.49334 | 0.49028 | 0.64844 | 0.6413 | 0.64538 | 0.63824 | 0.62906 | 0.62191 | 0.61579 | 0.60253 | 0.5913 | 0.58212 | 0.57191 | 0.56579 | 0.54742 | 0.61681 | 0.61375 | 0.60865 | 0.59844 | 0.58416 | 0.57293 | 0.56579 | 0.54742 | 0.53212 | 0.51783 | 0.50253 | 0.49844 | 0.49538
|  | BRIDGE OF GAUR | EE |  |  |  |  | 0.60355 | 0.60559 | 0.59947 | 0.59334 | 0.58314 | 0.57191 | 0.56375 | 0.54538 | 0.52804 | 0.51477 | 0.49742 | 0.49334 | 0.49028 | 0.64844 | 0.65049 | 0.64538 | 0.63824 | 0.62906 | 0.62191 | 0.61579 | 0.60253 | 0.5913 | 0.58212 | 0.57191 | 0.56579 | 0.55661 | 0.61681 | 0.61375 | 0.60865 | 0.59844 | 0.58416 | 0.57293 | 0.56579 | 0.54742 | 0.53212 | 0.51783 | 0.50253 | 0.49947 | 0.49538
|  | BRIDGE OF GAUR | HT |  |  |  |  | 0.61171 | 0.60253 | 0.60559 | 0.59844 | 0.59742 | 0.58824 | 0.58314 | 0.57089 | 0.56069 | 0.55151 | 0.49844 | 0.49334 | 0.49028 | 0.65049 | 0.6413 | 0.65049 | 0.64436 | 0.6413 | 0.63212 | 0.6311 | 0.62293 | 0.61375 | 0.60865 | 0.57191 | 0.57293 | 0.57191 | 0.62702 | 0.61579 | 0.61477 | 0.60559 | 0.60151 | 0.5913 | 0.58416 | 0.57396 | 0.56273 | 0.55457 | 0.50457 | 0.49844 | 0.4964
|  | BRIDGE OF GAUR | HE |  |  |  |  | 0.61171 | 0.60355 | 0.60763 | 0.60355 | 0.59947 | 0.59232 | 0.58722 | 0.58008 | 0.56987 | 0.56375 | 0.50457 | 0.50661 | 0.50355 | 0.65049 | 0.64232 | 0.65253 | 0.6464 | 0.64538 | 0.63824 | 0.63314 | 0.626 | 0.61885 | 0.61681 | 0.57293 | 0.57396 | 0.56477 | 0.62702 | 0.61783 | 0.61681 | 0.60967 | 0.60661 | 0.59947 | 0.59232 | 0.58212 | 0.57089 | 0.56477 | 0.50865 | 0.51273 | 0.50763
|  | BRIDGE OF GAUR | CF |  |  |  |  | 0.61273 | 0.60355 | 0.60355 | 0.60457 | 0.60253 | 0.59947 | 0.59436 | 0.59028 | 0.58212 | 0.576 | 0.53824 | 0.51579 | 0.50049 | 0.65049 | 0.64232 | 0.64742 | 0.65049 | 0.6464 | 0.64232 | 0.63824 | 0.63212 | 0.626 | 0.62191 | 0.59334 | 0.57396 | 0.54742 | 0.62702 | 0.61681 | 0.61273 | 0.61273 | 0.60763 | 0.60457 | 0.5964 | 0.59334 | 0.58314 | 0.57702 | 0.54232 | 0.52089 | 0.50559
| BROADFORD | BROADFORD | MINIMUM HEADROOM | NG 62656 24360 | YES | YES | 2.15 | 2.8356 | 2.7876 | 2.7325 | 2.6611 | 2.6091 | 2.5315 | 2.4468 | 2.305 | 2.2081 | 2.0846 | 1.8836 | 1.8111 | 1.7887 | 2.7785 | 2.7489 | 2.7111 | 2.6672 | 2.6315 | 2.5764 | 2.5203 | 2.4285 | 2.3693 | 2.2968 | 2.1427 | 2.0672 | 1.8295 | 2.7351 | 2.6902 | 2.6371 | 2.5688 | 2.5177 | 2.4453 | 2.3616 | 2.231 | 2.1443 | 2.032 | 1.8453 | 1.7769 | 1.7586
|  | BROADFORD | EE |  |  |  |  | 2.8356 | 2.7876 | 2.7325 | 2.6611 | 2.6091 | 2.5315 | 2.4468 | 2.305 | 2.2081 | 2.0846 | 1.8836 | 1.8509 | 1.8295 | 2.7785 | 2.7489 | 2.7111 | 2.6672 | 2.6315 | 2.5764 | 2.5203 | 2.4285 | 2.3693 | 2.2968 | 2.1427 | 2.0672 | 1.9509 | 2.7351 | 2.6902 | 2.6371 | 2.5688 | 2.5177 | 2.4453 | 2.3616 | 2.231 | 2.1443 | 2.032 | 1.8453 | 1.8147 | 1.7922
|  | BROADFORD | HT |  |  |  |  | 2.8683 | 2.8264 | 2.7846 | 2.7295 | 2.6825 | 2.5805 | 2.4968 | 2.3836 | 2.3142 | 2.2356 | 1.9438 | 1.8111 | 1.7887 | 2.803 | 2.7754 | 2.7509 | 2.7183 | 2.6907 | 2.6366 | 2.5897 | 2.5234 | 2.4785 | 2.4274 | 2.2305 | 2.1448 | 2.1336 | 2.7667 | 2.7259 | 2.6861 | 2.6351 | 2.5892 | 2.5004 | 2.4249 | 2.3218 | 2.2545 | 2.182 | 1.9024 | 1.7769 | 1.7586
|  | BROADFORD | HE |  |  |  |  | 2.8683 | 2.8366 | 2.803 | 2.7601 | 2.7234 | 2.6713 | 2.6285 | 2.5325 | 2.4438 | 2.3499 | 2.0172 | 1.9336 | 1.9234 | 2.7989 | 2.7785 | 2.757 | 2.7295 | 2.705 | 2.6683 | 2.6427 | 2.5836 | 2.5244 | 2.4652 | 2.2346 | 2.1264 | 2.0203 | 2.7677 | 2.7351 | 2.7024 | 2.6616 | 2.6259 | 2.578 | 2.5392 | 2.4484 | 2.3698 | 2.282 | 1.9728 | 1.8963 | 1.8851
|  | BROADFORD | CF |  |  |  |  | 2.8764 | 2.8489 | 2.8111 | 2.7856 | 2.7458 | 2.7172 | 2.6754 | 2.6234 | 2.5764 | 2.507 | 2.2121 | 2.0397 | 1.9407 | 2.804 | 2.7876 | 2.7642 | 2.7448 | 2.7193 | 2.7009 | 2.6693 | 2.6325 | 2.6009 | 2.554 | 2.3172 | 2.0968 | 1.8295 | 2.7739 | 2.7484 | 2.7137 | 2.6912 | 2.6514 | 2.6239 | 2.582 | 2.532 | 2.4933 | 2.43 | 2.1535 | 1.9933 | 1.8994
| CARRADALE 1 | BRODICK | MINIMUM HEADROOM | NS 01976 35459 | NO | YES | 0.34 | 2.7305 | 2.6091 | 2.4529 | 2.2795 | 2.1274 | 1.9325 | 1.7009 | 1.4784 | 1.2346 | 1.0142 | 0.43661 | 0.23865 | 0.2009 | 3.9927 | 3.9131 | 3.8162 | 3.705 | 3.6091 | 3.4754 | 3.3244 | 3.1744 | 3.0131 | 2.8662 | 2.4182 | 2.2213 | 1.654 | 3.3805 | 3.2652 | 3.1254 | 2.9611 | 2.8182 | 2.6305 | 2.407 | 2.1968 | 1.9621 | 1.7529 | 1.205 | 1.0152 | 0.98049
|  | BRODICK | EE |  |  |  |  | 2.7305 | 2.6091 | 2.4529 | 2.2795 | 2.1274 | 1.9325 | 1.7009 | 1.4784 | 1.2346 | 1.0142 | 0.43661 | 0.33457 | 0.27029 | 3.9927 | 3.9131 | 3.8162 | 3.705 | 3.6091 | 3.4754 | 3.3244 | 3.1744 | 3.0131 | 2.8662 | 2.4182 | 2.2213 | 1.9274 | 3.3805 | 3.2652 | 3.1254 | 2.9611 | 2.8182 | 2.6305 | 2.407 | 2.1968 | 1.9621 | 1.7529 | 1.205 | 1.1091 | 1.0458
|  | BRODICK | HT |  |  |  |  | 2.7795 | 2.6805 | 2.5591 | 2.4448 | 2.305 | 2.1448 | 2.0019 | 1.804 | 1.6111 | 1.407 | 0.59886 | 0.23865 | 0.2009 | 4.0284 | 3.9703 | 3.8999 | 3.8315 | 3.7509 | 3.6499 | 3.5652 | 3.4356 | 3.3101 | 3.1815 | 2.6407 | 2.407 | 2.3815 | 3.4244 | 3.3295 | 3.2213 | 3.1162 | 2.9907 | 2.8407 | 2.708 | 2.5172 | 2.3315 | 2.1376 | 1.3591 | 1.0152 | 0.98049
|  | BRODICK | HE |  |  |  |  | 2.7784 | 2.7009 | 2.604 | 2.5131 | 2.4009 | 2.2662 | 2.1458 | 1.9733 | 1.8009 | 1.6264 | 0.79784 | 0.59069 | 0.57029 | 4.0295 | 3.9754 | 3.9142 | 3.854 | 3.7815 | 3.6876 | 3.6111 | 3.4917 | 3.3744 | 3.256 | 2.6652 | 2.408 | 2.1529 | 3.4162 | 3.3478 | 3.2631 | 3.1774 | 3.0784 | 2.9519 | 2.8397 | 2.6733 | 2.5101 | 2.3407 | 1.555 | 1.358 | 1.3417
|  | BRODICK | CF |  |  |  |  | 2.7856 | 2.7305 | 2.6672 | 2.5795 | 2.5101 | 2.4162 | 2.3162 | 2.1907 | 2.1193 | 2.0029 | 1.405 | 0.85498 | 0.55294 | 4.0438 | 3.9978 | 3.954 | 3.8948 | 3.8468 | 3.7784 | 3.704 | 3.6121 | 3.5529 | 3.4672 | 2.9631 | 2.3417 | 1.654 | 3.4448 | 3.3856 | 3.3193 | 3.2376 | 3.1733 | 3.0856 | 2.9968 | 2.8815 | 2.8142 | 2.7029 | 2.1295 | 1.5999 | 1.3213
| BRORA | BRORA | MINIMUM HEADROOM | NC 90482 04236 | NO | NO | 0.917 | 3.7545 | 3.6739 | 3.5953 | 3.4912 | 3.3881 | 3.2728 | 3.1718 | 2.9994 | 2.829 | 2.6779 | 2.4402 | 2.3412 | 2.3126 | 4.6228 | 4.583 | 4.5381 | 4.483 | 4.4269 | 4.3616 | 4.3106 | 4.2136 | 4.1096 | 4.0208 | 3.8534 | 3.7708 | 3.53 | 4.2963 | 4.2279 | 4.1555 | 4.0555 | 3.9575 | 3.8483 | 3.7555 | 3.5902 | 3.431 | 3.2912 | 3.0718 | 2.982 | 2.9565
|  | BRORA | EE |  |  |  |  | 3.7545 | 3.6739 | 3.5953 | 3.4912 | 3.3881 | 3.2728 | 3.1718 | 2.9994 | 2.829 | 2.6779 | 2.4402 | 2.3922 | 2.3636 | 4.6228 | 4.583 | 4.5381 | 4.483 | 4.4269 | 4.3616 | 4.3106 | 4.2136 | 4.1096 | 4.0208 | 3.8534 | 3.7708 | 3.6453 | 4.2963 | 4.2279 | 4.1555 | 4.0555 | 3.9575 | 3.8483 | 3.7555 | 3.5902 | 3.431 | 3.2912 | 3.0718 | 3.0279 | 3.0024
|  | BRORA | HT |  |  |  |  | 3.7932 | 3.731 | 3.6473 | 3.5749 | 3.5096 | 3.4024 | 3.2881 | 3.1483 | 3.0739 | 2.9616 | 2.5341 | 2.3412 | 2.3126 | 4.6483 | 4.6157 | 4.5739 | 4.5351 | 4.5014 | 4.4422 | 4.382 | 4.3085 | 4.2698 | 4.2106 | 3.9616 | 3.8494 | 3.8351 | 4.3188 | 4.2647 | 4.2045 | 4.1381 | 4.079 | 3.9779 | 3.8739 | 3.7422 | 3.6728 | 3.5677 | 3.1616 | 2.982 | 2.9565
|  | BRORA | HE |  |  |  |  | 3.7932 | 3.7473 | 3.679 | 3.6239 | 3.5534 | 3.5055 | 3.4228 | 3.3034 | 3.1851 | 3.1014 | 2.5555 | 2.4932 | 2.479 | 4.6453 | 4.6198 | 4.581 | 4.5524 | 4.5136 | 4.4851 | 4.4412 | 4.3759 | 4.3065 | 4.2606 | 3.931 | 3.8422 | 3.7279 | 4.3177 | 4.281 | 4.2351 | 4.183 | 4.1157 | 4.0708 | 3.9932 | 3.881 | 3.7698 | 3.6943 | 3.181 | 3.1269 | 3.1126
|  | BRORA | CF |  |  |  |  | 3.7983 | 3.7504 | 3.7065 | 3.6606 | 3.6014 | 3.5371 | 3.4994 | 3.4361 | 3.3534 | 3.2677 | 2.9167 | 2.6585 | 2.5096 | 4.6463 | 4.6249 | 4.5983 | 4.5728 | 4.5432 | 4.5034 | 4.481 | 4.4422 | 4.3932 | 4.3412 | 4.1045 | 3.8351 | 3.53 | 4.3228 | 4.2881 | 4.2534 | 4.2208 | 4.1626 | 4.1014 | 4.0688 | 4.0085 | 3.929 | 3.8494 | 3.5167 | 3.2728 | 3.1402
| MILTON OF CRAIGIE | BROUGHTY FERRY | MINIMUM HEADROOM | NO 46658 30758 | NO | NO | 1.734 | 4.681 | 4.3973 | 4.1167 | 3.7738 | 3.4636 | 3.085 | 2.5228 | 2.2871 | 1.7493 | 1.2646 | -0.62007 | -1.519 | -1.6517 | 7.1095 | 7.0371 | 6.931 | 6.6942 | 6.4769 | 6.2014 | 5.8401 | 5.7391 | 5.3963 | 5.085 | 3.7473 | 2.7442 | -0.6966 | 5.9952 | 5.7534 | 5.5167 | 5.2167 | 4.9269 | 4.581 | 4.0626 | 3.8208 | 3.3228 | 2.8728 | 1.1136 | 0.28402 | 0.16259
|  | BROUGHTY FERRY | EE |  |  |  |  | 4.681 | 4.3973 | 4.1167 | 3.7738 | 3.4636 | 3.085 | 2.5228 | 2.2871 | 1.7493 | 1.2646 | -0.62007 | -1.2354 | -1.4129 | 7.1095 | 7.0371 | 6.931 | 6.6942 | 6.4769 | 6.2014 | 5.8401 | 5.7391 | 5.3963 | 5.085 | 3.7473 | 2.7442 | 1.2687 | 5.9952 | 5.7534 | 5.5167 | 5.2167 | 4.9269 | 4.581 | 4.0626 | 3.8208 | 3.3228 | 2.8728 | 1.1136 | 0.54116 | 0.37483
|  | BROUGHTY FERRY | HT |  |  |  |  | 4.7942 | 4.5697 | 4.3146 | 4.0799 | 3.7963 | 3.4861 | 3.0616 | 2.5493 | 2.0514 | 1.532 | -0.44149 | -1.519 | -1.6517 | 7.1636 | 7.1146 | 7.0585 | 7.0146 | 6.8412 | 6.6514 | 6.4238 | 6.134 | 5.8452 | 5.5493 | 4.5534 | 3.9881 | 3.9126 | 6.0759 | 5.8728 | 5.6524 | 5.4452 | 5.2065 | 4.9463 | 4.5503 | 4.082 | 3.6187 | 3.1401 | 1.2901 | 0.28402 | 0.16259
|  | BROUGHTY FERRY | HE |  |  |  |  | 4.7932 | 4.6565 | 4.4871 | 4.3391 | 4.1401 | 3.9269 | 3.6116 | 3.2054 | 2.8116 | 2.4014 | 0.8881 | -0.24558 | -0.52721 | 7.1432 | 7.0881 | 7.0279 | 6.9667 | 6.8789 | 6.7014 | 6.4963 | 6.2095 | 5.934 | 5.6422 | 4.4463 | 3.1861 | 1.7065 | 6.0718 | 5.9575 | 5.8218 | 5.6993 | 5.5432 | 5.3544 | 5.0595 | 4.685 | 4.3218 | 3.9442 | 2.5197 | 1.4626 | 1.2003
|  | BROUGHTY FERRY | CF |  |  |  |  | 4.8595 | 4.784 | 4.6799 | 4.5636 | 4.4738 | 4.3463 | 4.183 | 4.035 | 3.8575 | 3.6738 | 2.8677 | 1.4238 | 0.20034 | 7.1687 | 7.133 | 7.0881 | 7.0391 | 6.9942 | 6.885 | 6.7044 | 6.5299 | 6.332 | 6.1248 | 5.0452 | 2.7799 | -0.6966 | 6.131 | 6.0759 | 5.9963 | 5.9105 | 5.8422 | 5.7401 | 5.5963 | 5.4544 | 5.2932 | 5.1259 | 4.3585 | 3.0146 | 1.8605
| DUNOON | BRUCHAG | MINIMUM HEADROOM | NS 11372 57191 | NO | YES | 0.294 | 26.2446 | 26.167 | 26.066 | 25.9701 | 25.8395 | 25.7068 | 25.5456 | 25.3936 | 25.2232 | 25.0772 | 24.6752 | 24.4977 | 24.4783 | 26.0558 | 26.013 | 25.963 | 25.913 | 25.8272 | 25.7354 | 25.6303 | 25.5221 | 25.4007 | 25.2977 | 24.9946 | 24.8915 | 24.7221 | 26.1548 | 26.0752 | 25.9793 | 25.8854 | 25.7599 | 25.6323 | 25.4762 | 25.3313 | 25.165 | 25.0252 | 24.6385 | 24.4711 | 24.4528
|  | BRUCHAG | EE |  |  |  |  | 26.2446 | 26.167 | 26.066 | 25.9701 | 25.8395 | 25.7068 | 25.5456 | 25.3936 | 25.2232 | 25.0772 | 24.6752 | 24.5977 | 24.5283 | 26.0558 | 26.013 | 25.963 | 25.913 | 25.8272 | 25.7354 | 25.6303 | 25.5221 | 25.4007 | 25.2977 | 24.9946 | 24.8915 | 24.7221 | 26.1548 | 26.0752 | 25.9793 | 25.8854 | 25.7599 | 25.6323 | 25.4762 | 25.3313 | 25.165 | 25.0252 | 24.6385 | 24.5691 | 24.4977
|  | BRUCHAG | HT |  |  |  |  | 26.3017 | 26.2293 | 26.1589 | 26.0783 | 25.9803 | 25.8721 | 25.7752 | 25.6405 | 25.5089 | 25.367 | 24.7915 | 24.4977 | 24.4783 | 26.0844 | 26.0517 | 26.017 | 25.9783 | 25.9334 | 25.8711 | 25.8089 | 25.7232 | 25.6334 | 25.5415 | 25.1334 | 24.9303 | 24.9201 | 26.2089 | 26.1395 | 26.0711 | 25.9936 | 25.9017 | 25.7956 | 25.7058 | 25.5762 | 25.4477 | 25.3099 | 24.7528 | 24.4711 | 24.4528
|  | BRUCHAG | HE |  |  |  |  | 26.3028 | 26.2456 | 26.1895 | 26.1293 | 26.0538 | 25.967 | 25.8864 | 25.7813 | 25.6742 | 25.5609 | 25.0466 | 24.8905 | 24.8691 | 26.0854 | 26.0538 | 26.0272 | 25.9926 | 25.9517 | 25.9068 | 25.8589 | 25.7844 | 25.7119 | 25.6354 | 25.2752 | 25.113 | 24.9834 | 26.2109 | 26.1558 | 26.1017 | 26.0426 | 25.9681 | 25.8834 | 25.8089 | 25.7068 | 25.6028 | 25.4915 | 25.0017 | 24.8548 | 24.8344
|  | BRUCHAG | CF |  |  |  |  | 26.3089 | 26.267 | 26.2272 | 26.1721 | 26.1181 | 26.0568 | 25.9895 | 25.9344 | 25.864 | 25.7997 | 25.4252 | 25.064 | 24.8701 | 26.0905 | 26.065 | 26.0446 | 26.015 | 25.9803 | 25.9466 | 25.9058 | 25.8701 | 25.8262 | 25.7742 | 25.4609 | 25.0915 | 24.7293 | 26.2191 | 26.1803 | 26.1415 | 26.0915 | 26.0385 | 25.9813 | 25.916 | 25.863 | 25.7946 | 25.7293 | 25.3589 | 25.0119 | 24.8293
| KEITH 1 | BUCKIE | MINIMUM HEADROOM | NJ 43291 64802 | NO | YES | 3.461 | 10.8899 | 10.2358 | 9.3705 | 8.2307 | 7.4144 | 5.6715 | 4.3399 | 3.245 | 1.9603 | 0.64395 | -4.6622 | -10.004 | -13.2356 | 12.3933 | 11.9831 | 11.3423 | 10.4413 | 9.9821 | 8.4393 | 7.5995 | 6.9148 | 6.2005 | 5.1066 | 0.12191 | -4.8771 | -9.6005 | 12.0658 | 11.4811 | 10.6607 | 9.5209 | 8.8107 | 6.9678 | 5.7617 | 4.8219 | 3.6984 | 2.5168 | -3.0424 | -8.6046 | -12.9852
|  | BUCKIE | EE |  |  |  |  | 10.8899 | 10.2358 | 9.5113 | 8.7001 | 7.6174 | 6.5297 | 5.2062 | 4.0684 | 2.6776 | 1.4052 | -3.8805 | -8.8091 | -10.3632 | 12.3933 | 11.9831 | 11.5444 | 11.0546 | 10.2648 | 9.3668 | 8.525 | 7.8525 | 6.8831 | 6.0637 | 2.6056 | -2.1271 | -4.472 | 12.0658 | 11.4811 | 10.8352 | 10.1015 | 9.0464 | 7.9811 | 6.7566 | 5.728 | 4.3933 | 3.2209 | -1.6301 | -6.9271 | -8.7138
|  | BUCKIE | HT |  |  |  |  | 10.9837 | 10.3307 | 9.3705 | 8.2307 | 7.4144 | 5.6715 | 4.3399 | 3.245 | 1.9603 | 0.64395 | -4.6622 | -10.004 | -13.1816 | 12.4637 | 12.0719 | 11.3423 | 10.4413 | 9.9821 | 8.4393 | 7.5995 | 6.9148 | 6.2005 | 5.4209 | 2.1454 | -2.7965 | -6.4771 | 12.1821 | 11.6025 | 10.6607 | 9.5209 | 8.8107 | 6.9678 | 5.7617 | 4.8219 | 3.6984 | 2.5168 | -2.5128 | -8.3801 | -12.2036
|  | BUCKIE | HE |  |  |  |  | 10.995 | 10.498 | 9.748 | 8.8052 | 8.0348 | 6.4419 | 5.2899 | 4.1184 | 3.2123 | 1.8154 | -4.3367 | -9.4612 | -13.2356 | 12.4699 | 12.127 | 11.5056 | 10.7035 | 10.1382 | 8.6454 | 7.826 | 6.9525 | 6.2801 | 5.1066 | 0.12191 | -4.8771 | -9.6005 | 12.1903 | 11.7413 | 10.9974 | 10.0423 | 9.3148 | 7.6086 | 6.5158 | 5.3821 | 4.5668 | 3.1515 | -3.0424 | -8.6046 | -12.9852
|  | BUCKIE | CF |  |  |  |  | 11.097 | 10.7103 | 10.2582 | 9.8011 | 9.1572 | 8.3735 | 7.7062 | 7.0888 | 6.5358 | 6.1358 | 2.7644 | -0.3683 | -2.7703 | 12.5301 | 12.2433 | 11.9168 | 11.5944 | 11.0688 | 10.3862 | 9.8331 | 9.3617 | 8.9393 | 8.5852 | 6.0178 | 3.1964 | 0.2668 | 12.279 | 11.9331 | 11.528 | 11.1229 | 10.4954 | 9.7097 | 9.0658 | 8.476 | 7.9454 | 7.5995 | 4.4597 | 1.4893 | -0.73626
| FORT AUGUSTUS | BUNOICH | MINIMUM HEADROOM | NH 37662 09672 | YES | YES | 0 | 2.1457 | 2.1304 | 2.112 | 2.0865 | 2.0722 | 2.0447 | 2.0141 | 1.9886 | 1.9559 | 1.9284 | 1.8855 | 1.8682 | 1.8631 | 2.0208 | 2.0106 | 1.9963 | 1.98 | 1.9688 | 1.9504 | 1.9269 | 1.9127 | 1.8871 | 1.8667 | 1.8249 | 1.7484 | 1.581 | 2.0863 | 2.072 | 2.0537 | 2.0282 | 2.0159 | 1.9873 | 1.9557 | 1.9322 | 1.8996 | 1.87 | 1.8322 | 1.82 | 1.8139
|  | BUNOICH | EE |  |  |  |  | 2.1457 | 2.1304 | 2.112 | 2.0865 | 2.0722 | 2.0447 | 2.0141 | 1.9886 | 1.9559 | 1.9284 | 1.8855 | 1.8773 | 1.8733 | 2.0208 | 2.0106 | 1.9963 | 1.98 | 1.9688 | 1.9504 | 1.9269 | 1.9127 | 1.8871 | 1.8667 | 1.8249 | 1.778 | 1.7045 | 2.0863 | 2.072 | 2.0537 | 2.0282 | 2.0159 | 1.9873 | 1.9557 | 1.9322 | 1.8996 | 1.87 | 1.8353 | 1.8271 | 1.8231
|  | BUNOICH | HT |  |  |  |  | 2.1569 | 2.1406 | 2.1243 | 2.1069 | 2.0927 | 2.0702 | 2.0447 | 2.0314 | 2.008 | 1.9896 | 1.8855 | 1.8682 | 1.8631 | 2.0269 | 2.0188 | 2.0096 | 1.9984 | 1.9902 | 1.9769 | 1.9606 | 1.9545 | 1.9382 | 1.928 | 1.8484 | 1.8453 | 1.8433 | 2.0986 | 2.0822 | 2.07 | 2.0506 | 2.0363 | 2.0149 | 1.9894 | 1.9792 | 1.9547 | 1.9394 | 1.8322 | 1.82 | 1.8139
|  | BUNOICH | HE |  |  |  |  | 2.1569 | 2.1437 | 2.1335 | 2.1192 | 2.108 | 2.0906 | 2.0671 | 2.0549 | 2.0345 | 2.01 | 1.9008 | 1.8947 | 1.8916 | 2.0269 | 2.0188 | 2.0116 | 2.0004 | 1.9922 | 1.981 | 1.9627 | 1.9555 | 1.9371 | 1.9198 | 1.8331 | 1.7933 | 1.7198 | 2.0986 | 2.0853 | 2.0761 | 2.0598 | 2.0506 | 2.0322 | 2.0078 | 1.9996 | 1.9761 | 1.9537 | 1.8455 | 1.8455 | 1.8435
|  | BUNOICH | CF |  |  |  |  | 2.1518 | 2.1478 | 2.1376 | 2.1263 | 2.1141 | 2.1059 | 2.0906 | 2.0733 | 2.0682 | 2.0518 | 1.9794 | 1.9284 | 1.8978 | 2.0229 | 2.0188 | 2.0127 | 2.0035 | 1.9943 | 1.9892 | 1.9759 | 1.9576 | 1.9535 | 1.9412 | 1.8586 | 1.7484 | 1.581 | 2.0924 | 2.0884 | 2.0802 | 2.068 | 2.0547 | 2.0476 | 2.0322 | 2.0139 | 2.0098 | 1.9945 | 1.919 | 1.871 | 1.8455
| THURSO | BURGARHILL | MINIMUM HEADROOM | HY 34441 26078 | YES | NO | 0.059 | -0.73331 | -0.76902 | -0.81698 | -0.85576 | -0.91086 | -0.96494 | -1.0354 | -1.0956 | -1.1649 | -1.2313 | -1.3996 | -1.4547 | -1.4802 | 0.44016 | 0.40955 | 0.37179 | 0.34118 | 0.28914 | 0.23914 | 0.17485 | 0.13302 | 0.06669 | 0.0075061 | -0.12107 | -0.16698 | -0.28535 | -0.32209 | -0.3629 | -0.41188 | -0.45678 | -0.52107 | -0.58025 | -0.6629 | -0.72107 | -0.8027 | -0.87617 | -1.0456 | -1.1027 | -1.1241
|  | BURGARHILL | EE |  |  |  |  | -0.73331 | -0.76902 | -0.81698 | -0.85576 | -0.91086 | -0.96494 | -1.0354 | -1.0956 | -1.1649 | -1.2313 | -1.3996 | -1.4313 | -1.4435 | 0.44016 | 0.40955 | 0.37179 | 0.34118 | 0.28914 | 0.23914 | 0.17485 | 0.13302 | 0.06669 | 0.0075061 | -0.12107 | -0.16698 | -0.22821 | -0.32209 | -0.3629 | -0.41188 | -0.45678 | -0.52107 | -0.58025 | -0.6629 | -0.72107 | -0.8027 | -0.87617 | -1.0456 | -1.0762 | -1.0915
|  | BURGARHILL | HT |  |  |  |  | -0.71392 | -0.74862 | -0.78331 | -0.82311 | -0.87004 | -0.90576 | -0.95882 | -1.0139 | -1.0731 | -1.1292 | -1.3466 | -1.4547 | -1.4802 | 0.46873 | 0.43914 | 0.41771 | 0.39016 | 0.35036 | 0.32791 | 0.28302 | 0.23812 | 0.18506 | 0.13098 | -0.059841 | -0.13331 | -0.14964 | -0.30576 | -0.33841 | -0.368 | -0.40882 | -0.46086 | -0.4976 | -0.5578 | -0.62004 | -0.68433 | -0.75372 | -0.99249 | -1.1027 | -1.1241
|  | BURGARHILL | HE |  |  |  |  | -0.71494 | -0.74045 | -0.76698 | -0.79453 | -0.83025 | -0.86086 | -0.9078 | -0.95474 | -1.0078 | -1.0619 | -1.3292 | -1.4047 | -1.4251 | 0.46771 | 0.44322 | 0.42179 | 0.3973 | 0.36159 | 0.34118 | 0.29832 | 0.2524 | 0.20444 | 0.15138 | -0.060861 | -0.13841 | -0.1976 | -0.30678 | -0.33331 | -0.36086 | -0.38841 | -0.42719 | -0.45882 | -0.51086 | -0.56596 | -0.62617 | -0.68841 | -0.96392 | -1.0394 | -1.0568
|  | BURGARHILL | CF |  |  |  |  | -0.7078 | -0.73127 | -0.75474 | -0.78331 | -0.8078 | -0.83943 | -0.86188 | -0.90066 | -0.93025 | -0.96698 | -1.1364 | -1.2986 | -1.3956 | 0.47383 | 0.45342 | 0.43506 | 0.40853 | 0.38608 | 0.35649 | 0.3422 | 0.30138 | 0.27383 | 0.2371 | 0.061588 | -0.14147 | -0.28535 | -0.29964 | -0.31596 | -0.33637 | -0.368 | -0.39351 | -0.43127 | -0.45066 | -0.49658 | -0.52923 | -0.57209 | -0.76188 | -0.94862 | -1.0374
| ELGIN | BURGHEAD | MINIMUM HEADROOM | NJ 12666 68781 | NO | YES | 2.222 | 6.0137 | 5.831 | 5.5912 | 5.3749 | 5.1014 | 4.8575 | 4.5188 | 4.1545 | 3.8137 | 3.5126 | 2.8279 | 2.58 | 2.4535 | 6.7943 | 6.6953 | 6.5443 | 6.4177 | 6.2422 | 6.1014 | 5.8871 | 5.6453 | 5.4188 | 5.2208 | 4.7545 | 4.4524 | 3.8749 | 6.354 | 6.1907 | 5.9713 | 5.7774 | 5.5295 | 5.305 | 4.9958 | 4.6631 | 4.3529 | 4.0754 | 3.4478 | 3.2478 | 3.106
|  | BURGHEAD | EE |  |  |  |  | 6.0137 | 5.831 | 5.5912 | 5.3749 | 5.1014 | 4.8575 | 4.5188 | 4.1545 | 3.8137 | 3.5126 | 3.0157 | 2.8616 | 2.8157 | 6.7943 | 6.6953 | 6.5443 | 6.4177 | 6.2422 | 6.1014 | 5.8871 | 5.6453 | 5.4188 | 5.2208 | 4.8841 | 4.7841 | 4.4698 | 6.354 | 6.1907 | 5.9713 | 5.7774 | 5.5295 | 5.305 | 4.9958 | 4.6631 | 4.3529 | 4.0754 | 3.5948 | 3.458 | 3.4111
|  | BURGHEAD | HT |  |  |  |  | 6.0953 | 5.9198 | 5.733 | 5.5167 | 5.279 | 5.0698 | 4.8106 | 4.5177 | 4.2881 | 4.0014 | 2.8279 | 2.7514 | 2.6228 | 6.8667 | 6.7759 | 6.6779 | 6.5606 | 6.4259 | 6.3126 | 6.1616 | 5.98 | 5.8259 | 5.6473 | 4.8779 | 4.6932 | 4.5973 | 6.4274 | 6.2713 | 6.0999 | 5.908 | 5.6907 | 5.5009 | 5.2652 | 4.9968 | 4.7846 | 4.5223 | 3.4478 | 3.3591 | 3.2876
|  | BURGHEAD | HE |  |  |  |  | 6.0912 | 5.9504 | 5.8024 | 5.63 | 5.4279 | 5.2555 | 5.0065 | 4.729 | 4.5208 | 4.2626 | 2.9963 | 2.58 | 2.4535 | 6.8626 | 6.7769 | 6.6851 | 6.5759 | 6.4504 | 6.3208 | 6.1565 | 5.9586 | 5.7871 | 5.5973 | 4.7545 | 4.4524 | 4.3392 | 6.4234 | 6.2968 | 6.1611 | 6.0091 | 5.8264 | 5.6693 | 5.4438 | 5.1917 | 4.9989 | 4.7601 | 3.6662 | 3.2478 | 3.106
|  | BURGHEAD | CF |  |  |  |  | 6.1147 | 6.0004 | 5.8861 | 5.7473 | 5.6004 | 5.4341 | 5.3065 | 5.1147 | 4.9463 | 4.8147 | 3.7708 | 3.2167 | 2.5759 | 6.879 | 6.8065 | 6.7381 | 6.6535 | 6.5545 | 6.4432 | 6.3637 | 6.2269 | 6.1014 | 6.0116 | 5.23 | 4.781 | 3.8749 | 6.4468 | 6.3427 | 6.2397 | 6.1152 | 5.9795 | 5.8295 | 5.7162 | 5.5468 | 5.3887 | 5.2652 | 4.3182 | 3.8285 | 3.1989
| BURGHMUIR | BURGHMUIR | MINIMUM HEADROOM | NO 08256 23702 | NO | YES | 12.989 | -8.1137 | -9.0555 | -10.7463 | -13.0433 | -15.5882 | -18.4361 | -21.7708 | -25.73 | -29.2535 | -32.8933 | -47.3606 | -54.6433 | -56.729 | -5.6264 | -6.706 | -8.0621 | -9.6642 | -11.5877 | -13.7274 | -16.2366 | -19.255 | -21.9264 | -24.6938 | -35.5611 | -41.0417 | -42.5499 | -6.5752 | -7.917 | -9.8058 | -12.018 | -14.468 | -17.2037 | -20.4078 | -24.2201 | -27.6139 | -31.1007 | -44.9609 | -51.9323 | -53.8823
|  | BURGHMUIR | EE |  |  |  |  | -8.1137 | -9.0555 | -10.7463 | -13.0433 | -15.5882 | -18.4361 | -21.7708 | -25.73 | -29.2535 | -32.8933 | -47.3606 | -54.6433 | -56.729 | -5.6264 | -6.706 | -8.0621 | -9.6642 | -11.5877 | -13.7274 | -16.2366 | -19.255 | -21.9264 | -24.6938 | -35.5611 | -41.0417 | -42.5499 | -6.5752 | -7.917 | -9.8058 | -12.018 | -14.468 | -17.2037 | -20.4078 | -24.2201 | -27.6139 | -31.1007 | -44.9609 | -51.9323 | -53.8823
|  | BURGHMUIR | HT |  |  |  |  | -7.7198 | -8.4984 | -9.3759 | -10.4055 | -12.1484 | -14.2014 | -16.8055 | -19.8096 | -22.7984 | -26.1198 | -39.2616 | -46.6004 | -49.231 | -5.1479 | -5.8632 | -6.7713 | -7.7836 | -8.9683 | -10.4448 | -12.4203 | -14.7132 | -16.9642 | -19.4887 | -29.2764 | -34.7448 | -36.6468 | -6.1752 | -6.919 | -8.0435 | -9.4598 | -11.1303 | -13.1037 | -15.6037 | -18.4915 | -21.3609 | -24.5231 | -37.1078 | -44.1313 | -46.6139
|  | BURGHMUIR | HE |  |  |  |  | -7.7657 | -8.5229 | -9.4769 | -11.2259 | -13.278 | -15.8076 | -18.9494 | -22.6688 | -26.3729 | -29.9698 | -46.4463 | -51.7218 | -52.2841 | -5.1928 | -6.1795 | -7.2019 | -8.4274 | -9.8836 | -11.7938 | -14.1723 | -17.0152 | -19.8326 | -22.5774 | -35.0417 | -38.8795 | -39.2244 | -6.2211 | -7.1843 | -8.5854 | -10.269 | -12.2476 | -14.6772 | -17.6986 | -21.2782 | -24.8415 | -28.2884 | -44.0986 | -49.1088 | -49.5915
|  | BURGHMUIR | CF |  |  |  |  | -7.3922 | -7.7606 | -8.1882 | -8.6892 | -9.4576 | -10.6922 | -12.1371 | -14.0382 | -15.8504 | -17.6565 | -29.0504 | -39.4218 | -45.2259 | -4.9264 | -5.2244 | -5.7805 | -6.4448 | -7.207 | -8.0774 | -9.1081 | -10.5203 | -11.9172 | -13.3081 | -22.003 | -29.7499 | -33.9081 | -5.8701 | -6.2252 | -6.6384 | -7.5374 | -8.5711 | -9.7639 | -11.1568 | -12.9925 | -14.7394 | -16.4711 | -27.3966 | -37.2976 | -42.7782
| CLACHAN | BUTTERBRIDGE | MINIMUM HEADROOM | NN 19306 09936 | YES | YES | 0 | 0.11086 | 0.10984 | 0.10984 | 0.10882 | 0.10678 | 0.10678 | 0.10576 | 0.097592 | 0.096571 | 0.096571 | 0.090449 | 0.089429 | 0.089429 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.10288 | 0.10288 | 0.10186 | 0.093694 | 0.092673 | 0.092673 | 0.088592 | 0.087571 | 0.086551 | 0.1084 | 0.10738 | 0.10738 | 0.10636 | 0.10534 | 0.10534 | 0.10432 | 0.095133 | 0.095133 | 0.094112 | 0.08901 | 0.08799 | 0.08799
|  | BUTTERBRIDGE | EE |  |  |  |  | 0.11086 | 0.10984 | 0.10984 | 0.10882 | 0.10678 | 0.10678 | 0.10576 | 0.097592 | 0.096571 | 0.096571 | 0.090449 | 0.089429 | 0.089429 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.10288 | 0.10288 | 0.10186 | 0.093694 | 0.092673 | 0.092673 | 0.088592 | 0.087571 | 0.087571 | 0.1084 | 0.10738 | 0.10738 | 0.10636 | 0.10534 | 0.10534 | 0.10432 | 0.095133 | 0.095133 | 0.094112 | 0.08901 | 0.08799 | 0.08799
|  | BUTTERBRIDGE | HT |  |  |  |  | 0.11086 | 0.11086 | 0.10984 | 0.10984 | 0.10882 | 0.10882 | 0.10576 | 0.10576 | 0.10473 | 0.096571 | 0.09249 | 0.089429 | 0.089429 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.1039 | 0.10186 | 0.10186 | 0.10084 | 0.092673 | 0.089612 | 0.087571 | 0.087571 | 0.1084 | 0.1084 | 0.10738 | 0.10738 | 0.10636 | 0.10636 | 0.10432 | 0.10432 | 0.1033 | 0.094112 | 0.090031 | 0.08799 | 0.08799
|  | BUTTERBRIDGE | HE |  |  |  |  | 0.11086 | 0.11086 | 0.10984 | 0.10984 | 0.10882 | 0.10678 | 0.10678 | 0.10576 | 0.10473 | 0.096571 | 0.091469 | 0.089429 | 0.089429 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.10288 | 0.10288 | 0.10186 | 0.10084 | 0.092673 | 0.088592 | 0.087571 | 0.087571 | 0.1084 | 0.1084 | 0.10738 | 0.10738 | 0.10636 | 0.10534 | 0.10534 | 0.10432 | 0.10228 | 0.095133 | 0.090031 | 0.08799 | 0.08799
|  | BUTTERBRIDGE | CF |  |  |  |  | 0.11086 | 0.11086 | 0.11086 | 0.10984 | 0.10984 | 0.10984 | 0.10882 | 0.10882 | 0.10678 | 0.10678 | 0.095551 | 0.091469 | 0.089429 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10492 | 0.1039 | 0.1039 | 0.10288 | 0.10288 | 0.091653 | 0.089612 | 0.086551 | 0.1084 | 0.1084 | 0.1084 | 0.10738 | 0.10738 | 0.10738 | 0.10636 | 0.10636 | 0.10534 | 0.10534 | 0.093092 | 0.090031 | 0.08799
| BRACO | CALLANDER | MINIMUM HEADROOM | NN 62995 07081 | NO | YES | 0.435 | 2.0373 | 1.9016 | 1.7455 | 1.5628 | 1.3618 | 1.1445 | 0.83835 | 0.45978 | 0.079167 | -0.27287 | -1.6525 | -2.6106 | -2.9392 | 3.1853 | 3.122 | 3.0475 | 2.9384 | 2.7965 | 2.6363 | 2.4384 | 2.1884 | 1.9455 | 1.7271 | 0.88427 | 0.35366 | -0.094302 | 2.7067 | 2.5863 | 2.4414 | 2.2618 | 2.0659 | 1.8618 | 1.572 | 1.2149 | 0.87713 | 0.55468 | -0.75655 | -1.5953 | -1.8392
|  | CALLANDER | EE |  |  |  |  | 2.0373 | 1.9016 | 1.7455 | 1.5628 | 1.3618 | 1.1445 | 0.83835 | 0.45978 | 0.079167 | -0.27287 | -1.5974 | -2.4361 | -2.7514 | 3.1853 | 3.122 | 3.0475 | 2.9384 | 2.7965 | 2.6363 | 2.4384 | 2.1884 | 1.9455 | 1.7271 | 0.88427 | 0.35366 | -0.094302 | 2.7067 | 2.5863 | 2.4414 | 2.2618 | 2.0659 | 1.8618 | 1.572 | 1.2149 | 0.87713 | 0.55468 | -0.73002 | -1.4688 | -1.7035
|  | CALLANDER | HT |  |  |  |  | 2.0567 | 1.921 | 1.7832 | 1.5863 | 1.3822 | 1.1649 | 0.88019 | 0.54958 | 0.221 | -0.085118 | -1.6525 | -2.6106 | -2.9392 | 3.1965 | 3.1445 | 3.0843 | 2.9771 | 2.8577 | 2.7281 | 2.5741 | 2.3751 | 2.1832 | 1.9986 | 1.0404 | 0.53631 | 0.3557 | 2.7281 | 2.6251 | 2.5006 | 2.3006 | 2.1108 | 1.9139 | 1.6608 | 1.3496 | 1.0332 | 0.74141 | -0.75655 | -1.5953 | -1.8392
|  | CALLANDER | HE |  |  |  |  | 2.0669 | 1.9771 | 1.8894 | 1.7547 | 1.6169 | 1.4802 | 1.2904 | 1.0547 | 0.81284 | 0.59243 | -0.82798 | -1.7004 | -2.1198 | 3.2067 | 3.1547 | 3.1037 | 3.0149 | 2.9261 | 2.8179 | 2.672 | 2.4853 | 2.3026 | 2.1312 | 1.2292 | 0.71488 | 0.24549 | 2.7363 | 2.6496 | 2.5516 | 2.4088 | 2.2537 | 2.0873 | 1.8955 | 1.6547 | 1.4169 | 1.1812 | 0.0046776 | -0.74634 | -1.0882
|  | CALLANDER | CF |  |  |  |  | 2.1098 | 2.0516 | 1.9873 | 1.9108 | 1.823 | 1.7302 | 1.6312 | 1.5281 | 1.4169 | 1.3006 | 0.39549 | -0.66573 | -1.4443 | 3.2445 | 3.2118 | 3.173 | 3.123 | 3.0669 | 3.0026 | 2.9373 | 2.8598 | 2.7639 | 2.6404 | 1.9128 | 0.95468 | -0.070833 | 2.7771 | 2.7332 | 2.6771 | 2.5986 | 2.5057 | 2.4088 | 2.3006 | 2.1751 | 2.0496 | 1.9067 | 1.0486 | 0.1608 | -0.53002
| STORNOWAY | CALLANISH | MINIMUM HEADROOM | NB 22040 33554 | YES | YES | 0.25 | -0.48002 | -0.59839 | -0.71165 | -0.78002 | -0.86471 | -0.95451 | -1.0423 | -1.1637 | -1.279 | -1.3841 | -1.6014 | -1.6637 | -1.6872 | 0.44753 | 0.36488 | 0.28529 | 0.24141 | 0.1812 | 0.11794 | 0.066918 | -0.021857 | -0.10655 | -0.17492 | -0.31982 | -0.42492 | -0.73104 | -0.24839 | -0.35859 | -0.46471 | -0.52798 | -0.60757 | -0.69431 | -0.77186 | -0.88614 | -0.99533 | -1.0923 | -1.2902 | -1.3433 | -1.3657
|  | CALLANISH | EE |  |  |  |  | -0.48002 | -0.55043 | -0.71165 | -0.78002 | -0.86471 | -0.95451 | -1.0423 | -1.1637 | -1.279 | -1.3841 | -1.6014 | -1.6402 | -1.6514 | 0.44753 | 0.40467 | 0.28529 | 0.24141 | 0.1812 | 0.11794 | 0.066918 | -0.021857 | -0.10655 | -0.17492 | -0.31982 | -0.40043 | -0.53104 | -0.24839 | -0.31369 | -0.46471 | -0.52798 | -0.60757 | -0.69431 | -0.77186 | -0.88614 | -0.99533 | -1.0923 | -1.2902 | -1.3219 | -1.3351
|  | CALLANISH | HT |  |  |  |  | -0.45757 | -0.59839 | -0.65757 | -0.72084 | -0.79431 | -0.85145 | -0.93308 | -1.027 | -1.1178 | -1.1841 | -1.5423 | -1.6637 | -1.6872 | 0.4659 | 0.36488 | 0.33324 | 0.30263 | 0.25978 | 0.2261 | 0.17814 | 0.11386 | 0.053653 | 0.021 | -0.23716 | -0.29022 | -0.30349 | -0.22696 | -0.35859 | -0.41267 | -0.47084 | -0.53614 | -0.59227 | -0.66676 | -0.75451 | -0.83818 | -0.89839 | -1.2341 | -1.3433 | -1.3657
|  | CALLANISH | HE |  |  |  |  | -0.45757 | -0.50655 | -0.62594 | -0.67288 | -0.729 | -0.77186 | -0.84124 | -0.92288 | -1.0045 | -1.0576 | -1.5127 | -1.6208 | -1.6382 | 0.4659 | 0.43529 | 0.34447 | 0.31488 | 0.27712 | 0.25059 | 0.20365 | 0.14243 | 0.083245 | 0.053653 | -0.26471 | -0.3892 | -0.51676 | -0.22696 | -0.27186 | -0.38308 | -0.42798 | -0.48002 | -0.5188 | -0.58512 | -0.66267 | -0.73512 | -0.78716 | -1.2076 | -1.3066 | -1.3208
|  | CALLANISH | CF |  |  |  |  | -0.45145 | -0.49227 | -0.53002 | -0.64329 | -0.69124 | -0.74329 | -0.77696 | -0.83512 | -0.88308 | -0.94022 | -1.2025 | -1.4566 | -1.6066 | 0.47202 | 0.44855 | 0.42304 | 0.33324 | 0.30263 | 0.26692 | 0.24447 | 0.19651 | 0.15773 | 0.11284 | -0.11676 | -0.42492 | -0.73104 | -0.22084 | -0.25757 | -0.29329 | -0.39941 | -0.44329 | -0.49124 | -0.52288 | -0.57798 | -0.62288 | -0.67696 | -0.92288 | -1.1627 | -1.2953
| TUMMEL BRIDGE | CALVINE | MINIMUM HEADROOM | NN 80186 65270 | YES | YES | 0.592 | -0.5441 | -0.56349 | -0.58492 | -0.60941 | -0.6339 | -0.65839 | -0.69104 | -0.72369 | -0.75737 | -0.78798 | -0.87369 | -0.90022 | -0.92267 | -0.50941 | -0.51553 | -0.52573 | -0.5339 | -0.54614 | -0.55329 | -0.56757 | -0.57982 | -0.5941 | -0.60635 | -0.6492 | -0.67369 | -0.69206 | -0.50227 | -0.51859 | -0.54002 | -0.56043 | -0.5839 | -0.60533 | -0.6339 | -0.66655 | -0.70431 | -0.73594 | -0.82982 | -0.85839 | -0.88288
|  | CALVINE | EE |  |  |  |  | -0.5441 | -0.56349 | -0.58492 | -0.60941 | -0.6339 | -0.65839 | -0.69104 | -0.72369 | -0.75737 | -0.78798 | -0.87369 | -0.8839 | -0.88594 | -0.50941 | -0.51553 | -0.52573 | -0.5339 | -0.54614 | -0.55329 | -0.56757 | -0.57982 | -0.5941 | -0.60635 | -0.6492 | -0.65839 | -0.66961 | -0.50227 | -0.51859 | -0.54002 | -0.56043 | -0.5839 | -0.60533 | -0.6339 | -0.66655 | -0.70431 | -0.73594 | -0.82982 | -0.84308 | -0.84512
|  | CALVINE | HT |  |  |  |  | -0.53696 | -0.55124 | -0.56655 | -0.58492 | -0.60431 | -0.62267 | -0.64716 | -0.67063 | -0.69614 | -0.72369 | -0.8339 | -0.87676 | -0.89716 | -0.50431 | -0.51043 | -0.51553 | -0.52165 | -0.52778 | -0.53594 | -0.54614 | -0.55431 | -0.56655 | -0.57471 | -0.62369 | -0.65227 | -0.66757 | -0.4941 | -0.50941 | -0.52471 | -0.54104 | -0.55839 | -0.57369 | -0.59716 | -0.61757 | -0.64002 | -0.66655 | -0.78696 | -0.83798 | -0.85839
|  | CALVINE | HE |  |  |  |  | -0.53696 | -0.55227 | -0.56553 | -0.58084 | -0.5992 | -0.61859 | -0.6441 | -0.66859 | -0.69512 | -0.72676 | -0.86043 | -0.90022 | -0.92267 | -0.50431 | -0.51043 | -0.51655 | -0.52063 | -0.52982 | -0.53696 | -0.54512 | -0.55737 | -0.56655 | -0.5788 | -0.64206 | -0.67369 | -0.69206 | -0.4941 | -0.50941 | -0.51961 | -0.53492 | -0.55227 | -0.56961 | -0.59206 | -0.61553 | -0.63798 | -0.66757 | -0.81451 | -0.85839 | -0.88288
|  | CALVINE | CF |  |  |  |  | -0.53492 | -0.54104 | -0.5492 | -0.56145 | -0.57165 | -0.58594 | -0.59716 | -0.61553 | -0.63084 | -0.64614 | -0.74614 | -0.83492 | -0.89104 | -0.50533 | -0.50737 | -0.51145 | -0.51553 | -0.52063 | -0.52573 | -0.53288 | -0.539 | -0.54818 | -0.55329 | -0.59716 | -0.64614 | -0.68798 | -0.49614 | -0.50022 | -0.51247 | -0.52267 | -0.53288 | -0.54614 | -0.55431 | -0.56961 | -0.58492 | -0.59308 | -0.69308 | -0.79104 | -0.85329
| CARRADALE 1 | CAMPBELTOWN | MINIMUM HEADROOM | NR 71509 20746 | NO | YES | 1.025 | 8.2144 | 8.0246 | 7.0174 | 5.4909 | 5.2195 | 1.948 | 1.0307 | -0.11217 | -1.3122 | -3.4071 | -12.0816 | -19.8958 | -21.8805 | 9.0562 | 8.9052 | 7.7633 | 6.0154 | 5.7501 | 1.9521 | 0.80109 | -0.39789 | -1.6805 | -4.0897 | -13.9826 | -23.2826 | -24.3244 | 9.0843 | 8.8567 | 7.6353 | 5.8057 | 5.5587 | 1.5843 | 0.44548 | -0.8637 | -2.2494 | -4.7596 | -15.1525 | -24.6208 | -26.6402
|  | CAMPBELTOWN | EE |  |  |  |  | 8.2144 | 8.0246 | 7.7807 | 7.4868 | 6.3786 | 4.5358 | 3.4307 | 2.8613 | 1.3837 | 0.84803 | -3.4867 | -14.3479 | -18.6479 | 9.0562 | 8.9052 | 8.7562 | 8.5613 | 7.3807 | 5.3001 | 4.2654 | 3.898 | 2.3827 | 1.9103 | -2.4428 | -15.5275 | -21.1397 | 9.0843 | 8.8567 | 8.6271 | 8.3516 | 7.0751 | 4.8853 | 3.6812 | 3.1485 | 1.4751 | 0.84854 | -4.0555 | -17.3239 | -22.631
|  | CAMPBELTOWN | HT |  |  |  |  | 8.3031 | 8.1378 | 7.0174 | 5.4909 | 5.2195 | 1.948 | 1.2827 | 0.59293 | 0.068441 | -0.68156 | -5.7081 | -11.6805 | -21.8805 | 9.1317 | 9.0205 | 7.7633 | 6.0154 | 5.8705 | 2.0082 | 1.4888 | 0.94293 | 0.61436 | -0.018294 | -5.0601 | -11.7112 | -24.3244 | 9.1567 | 8.9751 | 7.6353 | 5.8057 | 5.5587 | 1.5843 | 0.9016 | 0.18936 | -0.30452 | -1.0964 | -6.8504 | -13.9596 | -26.6402
|  | CAMPBELTOWN | HE |  |  |  |  | 8.3031 | 8.2001 | 7.3011 | 5.9746 | 5.3286 | 2.1542 | 1.0307 | -0.11217 | -1.3122 | -3.4071 | -12.0816 | -19.8958 | -20.3326 | 9.1317 | 9.0368 | 7.998 | 6.4368 | 5.7501 | 1.9521 | 0.80109 | -0.39789 | -1.6805 | -4.0897 | -13.9826 | -23.2826 | -23.9856 | 9.1587 | 9.0322 | 7.9465 | 6.3414 | 5.5965 | 1.721 | 0.44548 | -0.8637 | -2.2494 | -4.7596 | -15.1525 | -24.6208 | -25.0474
|  | CAMPBELTOWN | CF |  |  |  |  | 8.3399 | 8.2725 | 8.2021 | 8.095 | 7.4664 | 6.4021 | 5.7419 | 5.1756 | 4.6103 | 3.9317 | 1.3021 | -0.9938 | -3.2887 | 9.1572 | 9.0888 | 9.0164 | 8.9358 | 8.2246 | 6.9674 | 6.2358 | 5.6552 | 5.0552 | 4.296 | 1.5307 | -1.0795 | -4.155 | 9.1975 | 9.1159 | 9.0292 | 8.9251 | 8.1832 | 6.8965 | 6.1322 | 5.5026 | 4.8659 | 4.072 | 1.1373 | -1.4902 | -4.0739
| COUPAR ANGUS | CAPUTH | MINIMUM HEADROOM | NO 09277 40265 | NO | NO | 0.621 | 6.25 | 6.1021 | 5.9184 | 5.7439 | 5.4827 | 5.2347 | 4.8766 | 4.4592 | 4.0153 | 3.6174 | 2.8919 | 2.4929 | 2.401 | 8.6429 | 8.5694 | 8.4704 | 8.3755 | 8.2459 | 8.098 | 7.8735 | 7.598 | 7.3051 | 7.049 | 6.7021 | 6.5388 | 5.9847 | 7.547 | 7.3898 | 7.1857 | 7.0082 | 6.7725 | 6.5449 | 6.2164 | 5.8378 | 5.4296 | 5.0653 | 4.398 | 4.0398 | 3.9561
|  | CAPUTH | EE |  |  |  |  | 6.25 | 6.1021 | 5.9184 | 5.7439 | 5.4827 | 5.2347 | 4.8766 | 4.4592 | 4.0153 | 3.6174 | 2.8919 | 2.5653 | 2.4776 | 8.6429 | 8.5694 | 8.4704 | 8.3755 | 8.2459 | 8.098 | 7.8735 | 7.598 | 7.3051 | 7.049 | 6.7021 | 6.5388 | 6.2143 | 7.547 | 7.3898 | 7.1857 | 7.0082 | 6.7725 | 6.5449 | 6.2164 | 5.8378 | 5.4296 | 5.0653 | 4.398 | 4.1072 | 4.0255
|  | CAPUTH | HT |  |  |  |  | 6.3061 | 6.1664 | 6.0286 | 5.8755 | 5.6949 | 5.4888 | 5.1786 | 4.8898 | 4.4878 | 4.1123 | 3.0806 | 2.4929 | 2.401 | 8.6806 | 8.6164 | 8.549 | 8.4735 | 8.3806 | 8.2725 | 8.1153 | 7.9561 | 7.6806 | 7.4551 | 6.8715 | 6.6082 | 6.5255 | 7.6225 | 7.4715 | 7.3225 | 7.1541 | 6.9612 | 6.7766 | 6.4939 | 6.2255 | 5.8531 | 5.5112 | 4.5755 | 4.0398 | 3.9561
|  | CAPUTH | HE |  |  |  |  | 6.3021 | 6.1888 | 6.0827 | 5.9602 | 5.8164 | 5.6643 | 5.448 | 5.1827 | 4.9041 | 4.5919 | 3.4306 | 3.0153 | 2.8419 | 8.6786 | 8.6184 | 8.5572 | 8.4878 | 8.4041 | 8.3123 | 8.1806 | 8.0123 | 7.798 | 7.5827 | 6.8398 | 6.6082 | 6.4347 | 7.6215 | 7.5102 | 7.4061 | 7.2817 | 7.1296 | 6.9908 | 6.7664 | 6.5041 | 6.247 | 5.9582 | 4.9245 | 4.5204 | 4.4
|  | CAPUTH | CF |  |  |  |  | 6.3347 | 6.2664 | 6.1939 | 6.1112 | 6.0153 | 5.9133 | 5.7602 | 5.5786 | 5.3878 | 5.2337 | 4.2082 | 3.6919 | 3.1174 | 8.699 | 8.6643 | 8.6215 | 8.5786 | 8.5245 | 8.4684 | 8.398 | 8.2653 | 8.1255 | 8.0184 | 7.2194 | 6.7908 | 5.9847 | 7.647 | 7.5643 | 7.4827 | 7.3857 | 7.2704 | 7.1674 | 7.0296 | 6.8674 | 6.6949 | 6.5521 | 5.6123 | 5.1357 | 4.6408
| ARBROATH | CARNOUSTIE | MINIMUM HEADROOM | NO 55631 35403 | NO | YES | 1.169 | 5.6326 | 5.0071 | 4.3489 | 3.6898 | 2.9755 | 2.4071 | 1.6918 | 0.9714 | 0.45711 | -0.19901 | -3.1511 | -4.9398 | -5.2419 | 7.5112 | 7.1306 | 6.7296 | 6.2745 | 5.7704 | 5.5602 | 5.2061 | 4.8173 | 4.4092 | 4.0449 | 2.701 | 1.6306 | 0.73874 | 6.5515 | 5.9903 | 5.3852 | 4.7801 | 4.1433 | 3.6137 | 2.9699 | 2.3127 | 1.8566 | 1.2586 | -1.3526 | -2.9414 | -3.2036
|  | CARNOUSTIE | EE |  |  |  |  | 5.6326 | 5.0112 | 4.3571 | 3.6898 | 2.9755 | 2.6489 | 1.9081 | 1.1632 | 0.45711 | -0.19901 | -2.9368 | -4.8123 | -5.2051 | 7.5112 | 7.1306 | 6.7296 | 6.2745 | 5.7704 | 5.6653 | 5.2438 | 4.8173 | 4.4092 | 4.0449 | 2.701 | 1.6306 | 0.73874 | 6.5515 | 5.9923 | 5.4137 | 4.8005 | 4.1433 | 3.8474 | 3.1678 | 2.4954 | 1.8566 | 1.2586 | -1.1761 | -2.823 | -3.1679
|  | CARNOUSTIE | HT |  |  |  |  | 5.6428 | 5.0071 | 4.3489 | 3.6928 | 3.0061 | 2.4071 | 1.6918 | 0.9714 | 0.57446 | -0.077584 | -3.1511 | -4.9398 | -5.2419 | 7.5571 | 7.1836 | 6.7806 | 6.3571 | 5.9214 | 5.5602 | 5.2061 | 4.8336 | 4.7673 | 4.4592 | 3.0438 | 2.2979 | 2.1745 | 6.5566 | 5.9903 | 5.3852 | 4.7801 | 4.1617 | 3.6137 | 2.9699 | 2.3127 | 1.9903 | 1.4005 | -1.3526 | -2.9414 | -3.2036
|  | CARNOUSTIE | HE |  |  |  |  | 5.7581 | 5.2714 | 4.7857 | 4.3132 | 3.8408 | 3.3979 | 2.8775 | 2.3592 | 2.2387 | 1.8081 | -0.68575 | -2.5786 | -3.397 | 7.6347 | 7.3143 | 6.9857 | 6.6428 | 6.301 | 5.9847 | 5.6459 | 5.2867 | 5.3204 | 5.0704 | 3.6336 | 2.4969 | 1.4806 | 6.6576 | 6.2311 | 5.7974 | 5.3576 | 4.9219 | 4.5127 | 4.0372 | 3.5668 | 3.4617 | 3.0739 | 0.80762 | -0.85054 | -1.5699
|  | CARNOUSTIE | CF |  |  |  |  | 5.9765 | 5.7132 | 5.3836 | 5.1255 | 4.803 | 4.5224 | 4.2347 | 3.9245 | 3.6622 | 3.3887 | 2.1102 | 0.11323 | -1.4398 | 7.7836 | 7.5959 | 7.35 | 7.1571 | 6.8979 | 6.6867 | 6.4377 | 6.1612 | 5.9224 | 5.6683 | 4.7632 | 2.9449 | 0.77854 | 6.8597 | 6.6321 | 6.3403 | 6.1035 | 5.8107 | 5.5576 | 5.2984 | 5.0178 | 4.7729 | 4.5127 | 3.3535 | 1.5321 | 0.11987
| KILLIN | CASHLIE | MINIMUM HEADROOM | NN 50711 42144 | YES | YES | 0 | 0.62449 | 0.62347 | 0.62245 | 0.61735 | 0.61224 | 0.61122 | 0.60204 | 0.59592 | 0.58571 | 0.58469 | 0.54898 | 0.52755 | 0.52041 | 0.75 | 0.75306 | 0.74286 | 0.74796 | 0.7449 | 0.74184 | 0.73367 | 0.72653 | 0.71633 | 0.71122 | 0.67041 | 0.65714 | 0.65102 | 0.66429 | 0.66531 | 0.65816 | 0.65306 | 0.65 | 0.64592 | 0.63673 | 0.62755 | 0.61633 | 0.60918 | 0.5551 | 0.53673 | 0.53061
|  | CASHLIE | EE |  |  |  |  | 0.62449 | 0.62347 | 0.62347 | 0.61735 | 0.61224 | 0.61122 | 0.60204 | 0.59592 | 0.58571 | 0.58469 | 0.57041 | 0.56735 | 0.56633 | 0.75 | 0.75306 | 0.75306 | 0.74796 | 0.7449 | 0.74184 | 0.73367 | 0.72653 | 0.71633 | 0.71429 | 0.69388 | 0.6898 | 0.67959 | 0.66429 | 0.66531 | 0.65918 | 0.65306 | 0.65 | 0.64592 | 0.63673 | 0.62755 | 0.61633 | 0.60918 | 0.58265 | 0.57857 | 0.57755
|  | CASHLIE | HT |  |  |  |  | 0.6398 | 0.63061 | 0.62245 | 0.62653 | 0.62245 | 0.61735 | 0.61735 | 0.60918 | 0.6051 | 0.59898 | 0.57959 | 0.57143 | 0.56837 | 0.76531 | 0.75714 | 0.74796 | 0.75714 | 0.75102 | 0.74796 | 0.74694 | 0.73673 | 0.73469 | 0.72857 | 0.70612 | 0.69796 | 0.69592 | 0.68061 | 0.66837 | 0.6602 | 0.66429 | 0.65816 | 0.6551 | 0.65306 | 0.64388 | 0.63878 | 0.63265 | 0.60306 | 0.58571 | 0.58367
|  | CASHLIE | HE |  |  |  |  | 0.6398 | 0.63163 | 0.62347 | 0.62653 | 0.62245 | 0.61939 | 0.61735 | 0.60918 | 0.60816 | 0.60102 | 0.54898 | 0.52755 | 0.52449 | 0.76429 | 0.75306 | 0.74286 | 0.75612 | 0.75 | 0.74388 | 0.73776 | 0.72755 | 0.71939 | 0.71122 | 0.67041 | 0.65714 | 0.65612 | 0.67959 | 0.66837 | 0.65816 | 0.66633 | 0.65918 | 0.65306 | 0.6449 | 0.63163 | 0.62041 | 0.6102 | 0.5551 | 0.53673 | 0.53367
|  | CASHLIE | CF |  |  |  |  | 0.6398 | 0.63163 | 0.62347 | 0.62347 | 0.62857 | 0.62347 | 0.62143 | 0.62041 | 0.61633 | 0.61122 | 0.5898 | 0.54796 | 0.52041 | 0.76531 | 0.75714 | 0.74592 | 0.75306 | 0.75714 | 0.75306 | 0.75 | 0.7449 | 0.73878 | 0.73265 | 0.7 | 0.67143 | 0.65102 | 0.67959 | 0.67041 | 0.6602 | 0.66531 | 0.66633 | 0.66122 | 0.65714 | 0.65306 | 0.64592 | 0.63878 | 0.59694 | 0.55612 | 0.53061
| KILLIN | CHAORACH | MINIMUM HEADROOM | NN 45400 27553 | YES | YES | 0 | 0.5602 | 0.55918 | 0.55102 | 0.54388 | 0.54082 | 0.5398 | 0.53776 | 0.53265 | 0.53265 | 0.52755 | 0.52041 | 0.5102 | 0.5051 | 0.76735 | 0.76633 | 0.75918 | 0.75102 | 0.75 | 0.75612 | 0.74796 | 0.75 | 0.75 | 0.75 | 0.74592 | 0.73878 | 0.73061 | 0.65816 | 0.65612 | 0.64796 | 0.6398 | 0.63878 | 0.63776 | 0.63571 | 0.63163 | 0.63163 | 0.62653 | 0.62041 | 0.6102 | 0.60612
|  | CHAORACH | EE |  |  |  |  | 0.5602 | 0.55918 | 0.55102 | 0.54388 | 0.54082 | 0.5398 | 0.54286 | 0.53878 | 0.53265 | 0.52755 | 0.52041 | 0.51429 | 0.50714 | 0.76735 | 0.76633 | 0.75918 | 0.75102 | 0.75 | 0.75714 | 0.75918 | 0.7551 | 0.75204 | 0.75 | 0.74694 | 0.73878 | 0.73061 | 0.65816 | 0.65612 | 0.64796 | 0.6398 | 0.63878 | 0.63776 | 0.6398 | 0.63776 | 0.63163 | 0.62653 | 0.62041 | 0.61429 | 0.60918
|  | CHAORACH | HT |  |  |  |  | 0.56735 | 0.55918 | 0.55918 | 0.55816 | 0.54898 | 0.54796 | 0.53776 | 0.53265 | 0.53776 | 0.53061 | 0.52041 | 0.5102 | 0.5051 | 0.77449 | 0.76735 | 0.76633 | 0.76633 | 0.75714 | 0.75612 | 0.74796 | 0.7551 | 0.75714 | 0.75306 | 0.74592 | 0.73878 | 0.73571 | 0.66531 | 0.65714 | 0.65612 | 0.6551 | 0.64592 | 0.6449 | 0.63571 | 0.63163 | 0.63571 | 0.63061 | 0.62143 | 0.6102 | 0.60612
|  | CHAORACH | HE |  |  |  |  | 0.56735 | 0.55918 | 0.55918 | 0.55918 | 0.55 | 0.54796 | 0.53776 | 0.53571 | 0.54082 | 0.53878 | 0.52041 | 0.51633 | 0.51122 | 0.77449 | 0.76735 | 0.76633 | 0.76633 | 0.75816 | 0.75714 | 0.74898 | 0.7551 | 0.75816 | 0.75714 | 0.74592 | 0.7398 | 0.73367 | 0.66531 | 0.65714 | 0.65612 | 0.65612 | 0.64694 | 0.64592 | 0.63673 | 0.63571 | 0.63878 | 0.63673 | 0.62041 | 0.61531 | 0.61122
|  | CHAORACH | CF |  |  |  |  | 0.56735 | 0.56735 | 0.5602 | 0.55918 | 0.55918 | 0.55204 | 0.55102 | 0.54286 | 0.54082 | 0.53776 | 0.53265 | 0.51837 | 0.51531 | 0.77449 | 0.77449 | 0.76735 | 0.76633 | 0.76633 | 0.75918 | 0.75816 | 0.75 | 0.75 | 0.75612 | 0.75204 | 0.74184 | 0.73163 | 0.66531 | 0.66531 | 0.65816 | 0.65612 | 0.65612 | 0.64898 | 0.64796 | 0.64082 | 0.63776 | 0.63673 | 0.63265 | 0.61939 | 0.61429
| ARBROATH | CHARLES AVENUE | MINIMUM HEADROOM | NO 62954 41097 | NO | YES | 0.046 | 4.4041 | 4.0806 | 3.7 | 3.3367 | 2.9204 | 2.4735 | 1.8133 | 0.83776 | -0.0071429 | -0.62551 | -3.7929 | -5.7102 | -6.0184 | 6.5898 | 6.4765 | 6.3316 | 6.1194 | 5.8673 | 5.5969 | 5.2796 | 4.6541 | 4.1469 | 3.6561 | 1.8296 | 0.65204 | -0.88163 | 5.4092 | 5.1214 | 4.7806 | 4.4531 | 4.0786 | 3.6816 | 3.0255 | 2.1143 | 1.3327 | 0.79694 | -2.1184 | -3.8388 | -4.1102
|  | CHARLES AVENUE | EE |  |  |  |  | 4.4041 | 4.0806 | 3.7 | 3.3367 | 2.9204 | 2.4735 | 1.9949 | 1.0255 | 0.1602 | -0.62551 | -3.6939 | -5.5092 | -5.9286 | 6.5898 | 6.4765 | 6.3316 | 6.1194 | 5.8673 | 5.5969 | 5.3388 | 4.6959 | 4.1469 | 3.6561 | 1.8296 | 0.65204 | -0.40306 | 5.4092 | 5.1214 | 4.7806 | 4.4531 | 4.0786 | 3.6816 | 3.2194 | 2.3204 | 1.5214 | 0.79694 | -2.0306 | -3.651 | -4.0224
|  | CHARLES AVENUE | HT |  |  |  |  | 4.5071 | 4.199 | 3.8602 | 3.5378 | 3.1673 | 2.8122 | 1.8133 | 0.83776 | -0.0071429 | -0.47959 | -3.7929 | -5.7102 | -6.0184 | 6.651 | 6.5592 | 6.4582 | 6.3245 | 6.1306 | 5.9459 | 5.2796 | 4.6541 | 4.1531 | 3.9418 | 2.2898 | 1.4031 | 1.2643 | 5.5 | 5.2214 | 4.9184 | 4.6286 | 4.2969 | 3.9745 | 3.0255 | 2.1143 | 1.3327 | 0.8898 | -2.1184 | -3.8388 | -4.1102
|  | CHARLES AVENUE | HE |  |  |  |  | 4.5051 | 4.3245 | 4.1194 | 3.9224 | 3.6857 | 3.4643 | 2.9449 | 2.1908 | 1.5296 | 1.2071 | -1.8 | -3.752 | -4.4653 | 6.6429 | 6.5643 | 6.4796 | 6.3918 | 6.2745 | 6.1224 | 5.7755 | 5.2245 | 4.7582 | 4.5408 | 2.5969 | 1.2571 | 0.11735 | 5.499 | 5.3347 | 5.151 | 4.9786 | 4.7643 | 4.5622 | 4.0684 | 3.3622 | 2.7459 | 2.4337 | -0.33163 | -2.1163 | -2.7449
|  | CHARLES AVENUE | CF |  |  |  |  | 4.5939 | 4.5 | 4.3816 | 4.2765 | 4.1357 | 3.9867 | 3.8296 | 3.5796 | 3.298 | 3.0082 | 1.35 | -0.8602 | -2.6418 | 6.6653 | 6.6194 | 6.5582 | 6.501 | 6.4245 | 6.3367 | 6.2092 | 5.9837 | 5.7265 | 5.4612 | 3.9939 | 1.7827 | -0.88163 | 5.5786 | 5.4918 | 5.3878 | 5.2969 | 5.1704 | 5.0388 | 4.8847 | 4.6541 | 4.3908 | 4.1194 | 2.5745 | 0.53061 | -1.1122
| CHARLESTON | CHARLESTON | MINIMUM HEADROOM | NO 35734 31818 | NO | YES | 3.353 | 6.6791 | 6.528 | 6.3546 | 6.1566 | 5.9393 | 5.6903 | 5.378 | 5.0556 | 4.7229 | 4.3995 | 2.8382 | 2.0995 | 1.9893 | 2.2454 | 2.1638 | 2.0689 | 1.9648 | 1.8168 | 1.6505 | 1.4372 | 1.2413 | 0.99844 | 0.75763 | -0.45768 | -1.0138 | -1.4567 | 1.9561 | 1.8806 | 1.7847 | 1.6949 | 1.5775 | 1.4469 | 1.2826 | 1.1581 | 1.0102 | 0.86936 | 0.54896 | 0.48977 | 0.47549
|  | CHARLESTON | EE |  |  |  |  | 6.6791 | 6.528 | 6.3546 | 6.1566 | 5.9393 | 5.6903 | 5.378 | 5.0556 | 4.7229 | 4.3995 | 3.3464 | 3.2474 | 3.2005 | 2.2454 | 2.1638 | 2.0689 | 1.9648 | 1.8168 | 1.6505 | 1.4372 | 1.2413 | 0.99844 | 0.75763 | -0.030127 | -0.13829 | -0.4138 | 1.9561 | 1.8806 | 1.7847 | 1.6949 | 1.5775 | 1.4469 | 1.2826 | 1.1581 | 1.0102 | 0.86936 | 0.54896 | 0.54283 | 0.51834
|  | CHARLESTON | HT |  |  |  |  | 6.7525 | 6.6321 | 6.5035 | 6.3454 | 6.1321 | 5.926 | 5.7076 | 5.4638 | 5.2413 | 4.975 | 3.7066 | 3.1566 | 3.0903 | 2.2872 | 2.2229 | 2.1576 | 2.0627 | 1.9342 | 1.8199 | 1.6882 | 1.5342 | 1.3964 | 1.225 | 0.29232 | -0.13625 | -0.19033 | 1.9939 | 1.9275 | 1.8592 | 1.7775 | 1.6755 | 1.5949 | 1.4898 | 1.3694 | 1.253 | 1.1418 | 0.63161 | 0.48977 | 0.47549
|  | CHARLESTON | HE |  |  |  |  | 6.7393 | 6.6097 | 6.475 | 6.3066 | 6.1015 | 5.874 | 5.578 | 5.2515 | 4.9413 | 4.5617 | 2.8382 | 2.0995 | 2.0525 | 2.2791 | 2.2107 | 2.1413 | 2.0515 | 1.9403 | 1.8138 | 1.627 | 1.3954 | 1.1423 | 0.84947 | -0.45768 | -1.0138 | -1.075 | 1.9949 | 1.9418 | 1.8857 | 1.8153 | 1.7285 | 1.649 | 1.5285 | 1.4132 | 1.3092 | 1.1847 | 0.72651 | 0.58467 | 0.58263
|  | CHARLESTON | CF |  |  |  |  | 6.7903 | 6.7301 | 6.6535 | 6.5627 | 6.4617 | 6.3423 | 6.1923 | 5.9699 | 5.7872 | 5.578 | 4.3617 | 3.0566 | 1.9893 | 2.3025 | 2.2689 | 2.227 | 2.176 | 2.1178 | 2.0484 | 1.9617 | 1.8189 | 1.6995 | 1.5678 | 0.6413 | -0.34441 | -1.4567 | 2.0163 | 1.9877 | 1.9581 | 1.9122 | 1.8714 | 1.8173 | 1.751 | 1.6724 | 1.6 | 1.5224 | 1.1408 | 0.76732 | 0.58875
| ARDMORE | CLACHAN | MINIMUM HEADROOM | NF 81863 64360 | YES | YES | 1.09 | -0.14192 | -0.23478 | -0.36335 | -0.4858 | -0.5909 | -0.74192 | -0.82662 | -0.96437 | -1.0929 | -1.2062 | -1.4582 | -1.4766 | -1.496 | 0.92032 | 0.84889 | 0.76624 | 0.67134 | 0.59481 | 0.47542 | 0.42747 | 0.33359 | 0.24991 | 0.17747 | 0.012159 | 0.0080776 | -0.19294 | 0.42032 | 0.3591 | 0.23461 | 0.13359 | 0.042771 | -0.094984 | -0.16641 | -0.29498 | -0.41845 | -0.52458 | -0.75519 | -0.77356 | -0.79192
|  | CLACHAN | EE |  |  |  |  | -0.14192 | -0.21029 | -0.36335 | -0.4858 | -0.5909 | -0.74192 | -0.82662 | -0.96437 | -1.0929 | -1.2062 | -1.4582 | -1.4378 | -1.4593 | 0.92032 | 0.88767 | 0.76624 | 0.67134 | 0.59481 | 0.47542 | 0.42747 | 0.33359 | 0.24991 | 0.17747 | 0.012159 | 0.011139 | -0.074576 | 0.42032 | 0.36318 | 0.23461 | 0.13359 | 0.042771 | -0.094984 | -0.16641 | -0.29498 | -0.41845 | -0.52458 | -0.75519 | -0.73784 | -0.75825
|  | CLACHAN | HT |  |  |  |  | -0.11029 | -0.23478 | -0.346 | -0.42458 | -0.55009 | -0.60519 | -0.68682 | -0.78886 | -0.88988 | -0.95009 | -1.3746 | -1.4766 | -1.496 | 0.93359 | 0.84889 | 0.77134 | 0.7193 | 0.61624 | 0.58563 | 0.53665 | 0.46828 | 0.40298 | 0.37338 | 0.086649 | 0.03971 | 0.028486 | 0.45706 | 0.3591 | 0.27236 | 0.2142 | 0.087669 | 0.03971 | -0.037841 | -0.12968 | -0.22049 | -0.27458 | -0.67764 | -0.77356 | -0.79192
|  | CLACHAN | HE |  |  |  |  | -0.11131 | -0.16335 | -0.26845 | -0.37356 | -0.45519 | -0.54498 | -0.61743 | -0.70825 | -0.79907 | -0.85009 | -1.3246 | -1.4378 | -1.4511 | 0.93053 | 0.9091 | 0.82849 | 0.72849 | 0.6744 | 0.57849 | 0.53257 | 0.48053 | 0.42644 | 0.38461 | 0.099914 | 0.0080776 | -0.068453 | 0.45604 | 0.4142 | 0.32849 | 0.24073 | 0.17032 | 0.090731 | 0.022363 | -0.06029 | -0.14498 | -0.1909 | -0.6307 | -0.73274 | -0.74396
|  | CLACHAN | CF |  |  |  |  | -0.10111 | -0.14192 | -0.17866 | -0.28274 | -0.38988 | -0.46233 | -0.54294 | -0.61029 | -0.66131 | -0.7256 | -1.0185 | -1.3062 | -1.4297 | 0.93563 | 0.92032 | 0.90196 | 0.82236 | 0.73767 | 0.68257 | 0.60502 | 0.5642 | 0.52951 | 0.48257 | 0.27134 | 0.012159 | -0.19294 | 0.46828 | 0.43461 | 0.4091 | 0.32849 | 0.23971 | 0.18053 | 0.096853 | 0.036649 | -0.012331 | -0.071514 | -0.34907 | -0.61947 | -0.72356
| CARRADALE 1 | CLAONAIG | MINIMUM HEADROOM | NR 86915 56467 | YES | YES | 0 | 0.25435 | 0.25231 | 0.24823 | 0.24211 | 0.24109 | 0.23497 | 0.22578 | 0.21762 | 0.20639 | 0.20435 | 0.18394 | 0.17986 | 0.17986 | 0.25866 | 0.2607 | 0.25662 | 0.25355 | 0.25457 | 0.25151 | 0.24437 | 0.23825 | 0.23111 | 0.22906 | 0.2158 | 0.21376 | 0.21274 | 0.26161 | 0.25957 | 0.25855 | 0.25242 | 0.24936 | 0.24426 | 0.23508 | 0.22691 | 0.21467 | 0.21467 | 0.19324 | 0.19018 | 0.18916
|  | CLAONAIG | EE |  |  |  |  | 0.25435 | 0.25231 | 0.24925 | 0.24211 | 0.24109 | 0.23497 | 0.22578 | 0.21762 | 0.20639 | 0.20435 | 0.18394 | 0.18292 | 0.18088 | 0.25866 | 0.2607 | 0.26172 | 0.25355 | 0.25457 | 0.25151 | 0.24437 | 0.23825 | 0.23111 | 0.22906 | 0.2158 | 0.21478 | 0.21274 | 0.26161 | 0.25957 | 0.25855 | 0.25242 | 0.24936 | 0.24426 | 0.23508 | 0.22691 | 0.21467 | 0.21467 | 0.19324 | 0.19222 | 0.18916
|  | CLAONAIG | HT |  |  |  |  | 0.26864 | 0.25843 | 0.24823 | 0.25129 | 0.24721 | 0.24211 | 0.23905 | 0.22782 | 0.22578 | 0.21762 | 0.19109 | 0.17986 | 0.17986 | 0.27294 | 0.2658 | 0.25662 | 0.26376 | 0.25968 | 0.25559 | 0.25457 | 0.24539 | 0.24641 | 0.24029 | 0.22192 | 0.21376 | 0.21376 | 0.27793 | 0.26773 | 0.25855 | 0.25957 | 0.2565 | 0.2514 | 0.24732 | 0.23712 | 0.23508 | 0.22691 | 0.2014 | 0.19018 | 0.19018
|  | CLAONAIG | HE |  |  |  |  | 0.26864 | 0.25843 | 0.24925 | 0.25537 | 0.24925 | 0.24619 | 0.24415 | 0.23599 | 0.23088 | 0.22476 | 0.19721 | 0.19007 | 0.18905 | 0.27294 | 0.2658 | 0.25662 | 0.26478 | 0.2607 | 0.25764 | 0.25662 | 0.25049 | 0.24947 | 0.24437 | 0.22498 | 0.2209 | 0.21988 | 0.27793 | 0.26671 | 0.25855 | 0.26365 | 0.25855 | 0.25548 | 0.25344 | 0.24528 | 0.2412 | 0.23406 | 0.2065 | 0.20038 | 0.19936
|  | CLAONAIG | CF |  |  |  |  | 0.26966 | 0.26048 | 0.25231 | 0.25129 | 0.25537 | 0.24823 | 0.24517 | 0.24007 | 0.24007 | 0.23394 | 0.21252 | 0.19619 | 0.19007 | 0.27294 | 0.2658 | 0.25866 | 0.26172 | 0.26478 | 0.26172 | 0.25764 | 0.25355 | 0.25355 | 0.24845 | 0.23519 | 0.22396 | 0.21784 | 0.27793 | 0.26977 | 0.26059 | 0.26059 | 0.26365 | 0.25752 | 0.25344 | 0.25038 | 0.24936 | 0.24324 | 0.22181 | 0.2065 | 0.20038
| CLAYHILLS | CLAYHILLS | MINIMUM HEADROOM | NJ 94047 05518 | NO | NO | 6.003 | 5.3424 | 4.8924 | 4.3873 | 3.8679 | 3.273 | 2.6005 | 1.523 | 0.26889 | -0.94029 | -2.0729 | -7.1505 | -10.7393 | -11.0934 | 8.3975 | 8.1822 | 7.9301 | 7.6658 | 7.2638 | 6.7852 | 6.1485 | 5.3842 | 4.6556 | 3.975 | 0.76889 | -1.7536 | -6.0178 | 7.5087 | 7.0679 | 6.5668 | 6.0505 | 5.4617 | 4.826 | 3.8342 | 2.6383 | 1.4883 | 0.42705 | -4.1046 | -7.2607 | -7.5117
|  | CLAYHILLS | EE |  |  |  |  | 5.3424 | 4.8924 | 4.3873 | 3.8679 | 3.273 | 2.6005 | 1.523 | 0.26889 | -0.94029 | -2.0729 | -7.1505 | -10.4301 | -11.0097 | 8.3975 | 8.1822 | 7.9301 | 7.6658 | 7.2638 | 6.7852 | 6.1485 | 5.3842 | 4.6556 | 3.975 | 0.76889 | -1.7536 | -4.2025 | 7.5087 | 7.0679 | 6.5668 | 6.0505 | 5.4617 | 4.826 | 3.8342 | 2.6383 | 1.4883 | 0.42705 | -4.1046 | -6.9505 | -7.4485
|  | CLAYHILLS | HT |  |  |  |  | 5.5128 | 5.1424 | 4.7556 | 4.3373 | 3.8832 | 3.4046 | 2.4158 | 1.3291 | 0.28318 | -0.84438 | -6.6985 | -10.7393 | -11.0934 | 8.5393 | 8.3873 | 8.2209 | 8.0332 | 7.8189 | 7.5771 | 7.0883 | 6.5015 | 5.9515 | 5.3444 | 2.3117 | 0.36787 | 0.29542 | 7.6934 | 7.3342 | 6.9617 | 6.5485 | 6.0944 | 5.6209 | 4.7148 | 3.725 | 2.775 | 1.7526 | -3.626 | -7.2607 | -7.5117
|  | CLAYHILLS | HE |  |  |  |  | 5.4771 | 5.2158 | 4.9454 | 4.6413 | 4.3015 | 3.9403 | 3.2342 | 2.4046 | 1.6158 | 0.76277 | -3.9678 | -6.9617 | -8.024 | 8.5087 | 8.3332 | 8.1536 | 7.9393 | 7.6934 | 7.4138 | 7.0515 | 6.5689 | 6.0556 | 5.4791 | 2.173 | -0.31376 | -2.9668 | 7.6638 | 7.4005 | 7.1322 | 6.823 | 6.476 | 6.1128 | 5.4362 | 4.6546 | 3.9311 | 3.1424 | -1.1995 | -3.8413 | -4.7719
|  | CLAYHILLS | CF |  |  |  |  | 5.5913 | 5.4526 | 5.2995 | 5.1189 | 4.924 | 4.7077 | 4.475 | 4.1617 | 3.8638 | 3.5413 | 1.0975 | -1.5097 | -4.4607 | 8.572 | 8.4771 | 8.3638 | 8.2311 | 8.0832 | 7.9128 | 7.7097 | 7.3546 | 7.0138 | 6.6424 | 4.0689 | 0.18216 | -6.0178 | 7.775 | 7.6322 | 7.4771 | 7.2903 | 7.0893 | 6.8607 | 6.6322 | 6.3087 | 6.0056 | 5.6791 | 3.2985 | 0.86379 | -1.7525
| DOUNREAY | COLDBACKIE | MINIMUM HEADROOM | NC 62182 59590 | YES | NO | 1.378 | -0.34925 | -0.38496 | -0.41762 | -0.44721 | -0.48904 | -0.52272 | -0.57374 | -0.63496 | -0.66353 | -0.71047 | -0.85639 | -0.93394 | -0.94517 | -0.11558 | -0.13904 | -0.15639 | -0.17476 | -0.20231 | -0.22272 | -0.25537 | -0.29823 | -0.31149 | -0.34313 | -0.45945 | -0.51251 | -0.56353 | -0.29007 | -0.32374 | -0.35639 | -0.3819 | -0.42068 | -0.45231 | -0.49925 | -0.55843 | -0.58496 | -0.62782 | -0.76966 | -0.84211 | -0.85333
|  | COLDBACKIE | EE |  |  |  |  | -0.34925 | -0.38496 | -0.41762 | -0.44721 | -0.48904 | -0.52272 | -0.57374 | -0.63496 | -0.66353 | -0.71047 | -0.82272 | -0.84211 | -0.84823 | -0.11558 | -0.13904 | -0.15639 | -0.17476 | -0.20231 | -0.22272 | -0.25537 | -0.29823 | -0.31149 | -0.34313 | -0.41558 | -0.44517 | -0.49007 | -0.29007 | -0.32374 | -0.35639 | -0.3819 | -0.42068 | -0.45231 | -0.49925 | -0.55843 | -0.58496 | -0.62782 | -0.7319 | -0.74925 | -0.75741
|  | COLDBACKIE | HT |  |  |  |  | -0.33598 | -0.36353 | -0.39109 | -0.41558 | -0.45027 | -0.47374 | -0.51353 | -0.55639 | -0.587 | -0.63292 | -0.78088 | -0.85231 | -0.86353 | -0.10537 | -0.12068 | -0.13394 | -0.14823 | -0.1717 | -0.1819 | -0.20639 | -0.23394 | -0.25027 | -0.27884 | -0.37374 | -0.41251 | -0.41558 | -0.27782 | -0.30333 | -0.32782 | -0.35027 | -0.38394 | -0.40333 | -0.44211 | -0.48496 | -0.51251 | -0.55333 | -0.69517 | -0.76251 | -0.7717
|  | COLDBACKIE | HE |  |  |  |  | -0.337 | -0.35945 | -0.38088 | -0.40027 | -0.43088 | -0.44619 | -0.48904 | -0.537 | -0.5768 | -0.62782 | -0.85639 | -0.93394 | -0.94007 | -0.10537 | -0.11966 | -0.13394 | -0.15027 | -0.1717 | -0.19211 | -0.21966 | -0.25231 | -0.27986 | -0.31251 | -0.45945 | -0.51251 | -0.51456 | -0.27782 | -0.30027 | -0.32068 | -0.337 | -0.36558 | -0.38496 | -0.42374 | -0.46966 | -0.50639 | -0.55231 | -0.76966 | -0.84211 | -0.84721
|  | COLDBACKIE | CF |  |  |  |  | -0.33496 | -0.35231 | -0.36966 | -0.39211 | -0.40741 | -0.43496 | -0.46047 | -0.47374 | -0.50027 | -0.51864 | -0.69313 | -0.84007 | -0.94517 | -0.10537 | -0.11353 | -0.12476 | -0.13802 | -0.15027 | -0.1666 | -0.18802 | -0.19721 | -0.21762 | -0.23496 | -0.35945 | -0.45741 | -0.56353 | -0.2768 | -0.29109 | -0.30945 | -0.32986 | -0.34415 | -0.36864 | -0.39415 | -0.40843 | -0.43292 | -0.45027 | -0.6166 | -0.75435 | -0.85333
| DUNOON | COLINTRAIVE | MINIMUM HEADROOM | NS 03209 74814 | YES | YES | 0 | 0.47163 | 0.46143 | 0.45429 | 0.44408 | 0.4349 | 0.4298 | 0.41041 | 0.39408 | 0.39204 | 0.37878 | 0.35429 | 0.34612 | 0.34408 | 0.46847 | 0.46643 | 0.46031 | 0.4552 | 0.44704 | 0.44602 | 0.43276 | 0.42051 | 0.41847 | 0.41133 | 0.39704 | 0.39194 | 0.38786 | 0.47056 | 0.46138 | 0.45423 | 0.44505 | 0.43689 | 0.42974 | 0.41342 | 0.39709 | 0.39505 | 0.38281 | 0.35934 | 0.35219 | 0.35117
|  | COLINTRAIVE | EE |  |  |  |  | 0.47163 | 0.46143 | 0.45429 | 0.44408 | 0.4349 | 0.4298 | 0.41041 | 0.39408 | 0.39204 | 0.37878 | 0.35429 | 0.35122 | 0.34714 | 0.47255 | 0.46745 | 0.46031 | 0.4552 | 0.44704 | 0.44602 | 0.43276 | 0.42051 | 0.41847 | 0.41133 | 0.39704 | 0.39296 | 0.3899 | 0.47056 | 0.4624 | 0.45423 | 0.44505 | 0.43689 | 0.42974 | 0.41342 | 0.39709 | 0.39505 | 0.38281 | 0.35934 | 0.35628 | 0.35321
|  | COLINTRAIVE | HT |  |  |  |  | 0.47265 | 0.46143 | 0.46245 | 0.45327 | 0.44816 | 0.44204 | 0.43184 | 0.41653 | 0.41041 | 0.39714 | 0.36245 | 0.34612 | 0.34408 | 0.46847 | 0.46643 | 0.46745 | 0.46133 | 0.45929 | 0.45622 | 0.44806 | 0.43888 | 0.4348 | 0.42663 | 0.40214 | 0.39194 | 0.39092 | 0.47056 | 0.46138 | 0.4624 | 0.45423 | 0.44913 | 0.44301 | 0.43383 | 0.41954 | 0.41342 | 0.40219 | 0.36852 | 0.35219 | 0.35117
|  | COLINTRAIVE | HE |  |  |  |  | 0.47265 | 0.46245 | 0.46551 | 0.45735 | 0.45224 | 0.44612 | 0.43796 | 0.42571 | 0.41959 | 0.40939 | 0.36551 | 0.35429 | 0.35224 | 0.46847 | 0.46643 | 0.46949 | 0.46235 | 0.46031 | 0.45827 | 0.45112 | 0.44194 | 0.43786 | 0.43071 | 0.40418 | 0.39602 | 0.395 | 0.47056 | 0.4624 | 0.46444 | 0.4573 | 0.45219 | 0.44709 | 0.43995 | 0.42668 | 0.4226 | 0.41138 | 0.3726 | 0.36036 | 0.35832
|  | COLINTRAIVE | CF |  |  |  |  | 0.47367 | 0.46245 | 0.46347 | 0.46041 | 0.45939 | 0.44816 | 0.4451 | 0.43694 | 0.42776 | 0.42776 | 0.38388 | 0.36347 | 0.35122 | 0.46847 | 0.46745 | 0.46847 | 0.46745 | 0.46643 | 0.45724 | 0.45724 | 0.45112 | 0.445 | 0.44398 | 0.41235 | 0.39908 | 0.38786 | 0.4726 | 0.4624 | 0.46444 | 0.46138 | 0.46036 | 0.44913 | 0.44607 | 0.43893 | 0.42872 | 0.42872 | 0.38689 | 0.36852 | 0.3573
| STORNOWAY | COLL | MINIMUM HEADROOM | NB 47510 40182 | YES | YES | 0.094 | 0.44592 | 0.34388 | 5.4931 | 5.3849 | 5.291 | 5.1727 | 5.0186 | 4.8512 | 4.7308 | 4.591 | 4.2451 | 4.142 | 4.1104 | 1.4485 | 1.3872 | 6.7941 | 6.7155 | 6.6553 | 6.5655 | 6.4533 | 6.3176 | 6.241 | 6.138 | 5.891 | 5.7788 | 5.3727 | 1.1079 | 0.99974 | 6.2594 | 6.1461 | 6.0573 | 5.9288 | 5.7676 | 5.5849 | 5.4706 | 5.3257 | 5.0084 | 4.9165 | 4.889
|  | COLL | EE |  |  |  |  | 0.44592 | 0.34388 | 5.4931 | 5.3849 | 5.291 | 5.1727 | 5.0186 | 4.8512 | 4.7308 | 4.591 | 4.2451 | 4.1951 | 4.1778 | 1.4485 | 1.3872 | 6.7941 | 6.7155 | 6.6553 | 6.5655 | 6.4533 | 6.3176 | 6.241 | 6.138 | 5.891 | 5.7818 | 5.6094 | 1.1079 | 0.99974 | 6.2594 | 6.1461 | 6.0573 | 5.9288 | 5.7676 | 5.5849 | 5.4706 | 5.3257 | 5.0084 | 4.9584 | 4.938
|  | COLL | HT |  |  |  |  | 0.47449 | 0.39082 | 5.5492 | 5.4686 | 5.3706 | 5.2757 | 5.1594 | 5.0594 | 4.938 | 4.8135 | 4.3563 | 4.142 | 4.1104 | 1.4719 | 1.4301 | 6.8533 | 6.8135 | 6.7594 | 6.6982 | 6.6186 | 6.5604 | 6.4747 | 6.3808 | 6.038 | 5.9124 | 5.8951 | 1.1446 | 1.0691 | 6.338 | 6.2624 | 6.1614 | 6.0655 | 5.9461 | 5.8522 | 5.7278 | 5.5941 | 5.1124 | 4.9165 | 4.889
|  | COLL | HE |  |  |  |  | 0.47347 | 0.41327 | 5.5931 | 5.5339 | 5.4604 | 5.3869 | 5.2869 | 5.2002 | 5.0941 | 4.9839 | 4.392 | 4.2451 | 4.2257 | 1.4719 | 1.4362 | 6.8635 | 6.8288 | 6.7788 | 6.7227 | 6.6482 | 6.592 | 6.5084 | 6.4196 | 5.9992 | 5.8298 | 5.6635 | 1.1446 | 1.0855 | 6.3716 | 6.3155 | 6.2339 | 6.1573 | 6.0492 | 5.9686 | 5.8563 | 5.7369 | 5.1614 | 5.0247 | 5.0063
|  | COLL | CF |  |  |  |  | 0.48469 | 0.43265 | 5.6186 | 5.5573 | 5.5094 | 5.4461 | 5.3818 | 5.3033 | 5.2533 | 5.1808 | 4.8216 | 4.4747 | 4.2624 | 1.477 | 1.4495 | 6.8829 | 6.842 | 6.8124 | 6.7665 | 6.7165 | 6.6461 | 6.6124 | 6.5461 | 6.2084 | 5.7788 | 5.3727 | 1.1589 | 1.112 | 6.4114 | 6.3451 | 6.3002 | 6.2318 | 6.1676 | 6.0818 | 6.039 | 5.9614 | 5.5767 | 5.2012 | 5.0308
| CLAYHILLS | COMMERCE STREET | MINIMUM HEADROOM | NJ 94816 06282 | NO | NO | 5.999 | 4.884 | 4.7564 | 4.5962 | 4.4442 | 4.2646 | 4.0605 | 3.8248 | 3.535 | 3.1217 | 2.6942 | 0.99418 | 0.38398 | 0.10234 | 6.8013 | 6.7003 | 6.5779 | 6.4697 | 6.3319 | 6.1748 | 5.9952 | 5.7738 | 5.5717 | 5.3819 | 4.3411 | 3.8932 | 3.2309 | 6.3794 | 6.2478 | 6.0641 | 5.8763 | 5.6529 | 5.3988 | 5.0988 | 4.6835 | 4.2733 | 3.8651 | 2.2386 | 1.6518 | 1.3814
|  | COMMERCE STREET | EE |  |  |  |  | 4.884 | 4.7564 | 4.5962 | 4.4442 | 4.2646 | 4.0605 | 3.8248 | 3.535 | 3.1217 | 2.6942 | 0.99418 | 0.49316 | 0.42479 | 6.8013 | 6.7003 | 6.5779 | 6.4697 | 6.3319 | 6.1748 | 5.9952 | 5.7738 | 5.5717 | 5.3819 | 4.3421 | 3.9881 | 3.9115 | 6.3794 | 6.2478 | 6.0641 | 5.8763 | 5.6529 | 5.3988 | 5.0988 | 4.6835 | 4.2733 | 3.8651 | 2.2386 | 1.7631 | 1.6978
|  | COMMERCE STREET | HT |  |  |  |  | 4.9156 | 4.8125 | 4.687 | 4.5564 | 4.3942 | 4.234 | 4.0319 | 3.784 | 3.5381 | 3.1779 | 1.2197 | 0.38398 | 0.10234 | 6.8289 | 6.7513 | 6.6625 | 6.5697 | 6.4513 | 6.335 | 6.1881 | 6.0044 | 5.8248 | 5.6391 | 4.5717 | 3.9687 | 3.7564 | 6.409 | 6.3049 | 6.1814 | 6.0202 | 5.8263 | 5.6222 | 5.3733 | 5.062 | 4.7141 | 4.3284 | 2.4518 | 1.6518 | 1.3814
|  | COMMERCE STREET | HE |  |  |  |  | 4.9166 | 4.8176 | 4.7044 | 4.5819 | 4.4299 | 4.2728 | 4.0728 | 3.8156 | 3.5646 | 3.1095 | 1.0279 | 0.40744 | 0.13908 | 6.8279 | 6.7483 | 6.6605 | 6.5656 | 6.4483 | 6.3309 | 6.1768 | 5.9779 | 5.786 | 5.584 | 4.3411 | 3.8932 | 3.6615 | 6.411 | 6.3069 | 6.1957 | 6.0396 | 5.8498 | 5.6508 | 5.3957 | 5.0488 | 4.6804 | 4.258 | 2.259 | 1.6671 | 1.412
|  | COMMERCE STREET | CF |  |  |  |  | 4.9564 | 4.9023 | 4.8493 | 4.7819 | 4.7064 | 4.6176 | 4.5381 | 4.4074 | 4.284 | 4.1391 | 2.9881 | 1.4676 | 0.32683 | 6.8656 | 6.8176 | 6.7717 | 6.7115 | 6.6462 | 6.5646 | 6.5013 | 6.3932 | 6.2881 | 6.1687 | 5.4534 | 4.5707 | 3.2309 | 6.462 | 6.4069 | 6.3529 | 6.2804 | 6.1947 | 6.0763 | 5.9661 | 5.7967 | 5.6355 | 5.4478 | 4.1253 | 2.6671 | 1.5784
| ST FILLANS | COMRIE | MINIMUM HEADROOM | NN 76887 22417 | YES | YES | 0 | 0.042673 | 0.032469 | 0.032469 | 0.025327 | 0.022265 | 0.015122 | 0.014102 | 0.012061 | 0.012061 | 0.012061 | 0.011041 | 0.01002 | 0.009 | 0.044296 | 0.036133 | 0.035112 | 0.027969 | 0.025929 | 0.018786 | 0.017765 | 0.020827 | 0.017765 | 0.017765 | 0.020827 | 0.021847 | 0.018786 | 0.043485 | 0.035321 | 0.034301 | 0.027158 | 0.024097 | 0.016954 | 0.015934 | 0.013893 | 0.014913 | 0.014913 | 0.013893 | 0.012872 | 0.011852
|  | COMRIE | EE |  |  |  |  | 0.042673 | 0.032469 | 0.032469 | 0.025327 | 0.022265 | 0.015122 | 0.014102 | 0.012061 | 0.018184 | 0.017163 | 0.011041 | 0.01002 | 0.01002 | 0.044296 | 0.036133 | 0.035112 | 0.027969 | 0.025929 | 0.018786 | 0.017765 | 0.020827 | 0.025929 | 0.024908 | 0.022867 | 0.021847 | 0.021847 | 0.043485 | 0.035321 | 0.034301 | 0.027158 | 0.024097 | 0.016954 | 0.015934 | 0.013893 | 0.020015 | 0.018995 | 0.013893 | 0.012872 | 0.012872
|  | COMRIE | HT |  |  |  |  | 0.042673 | 0.040633 | 0.03349 | 0.032469 | 0.031449 | 0.030429 | 0.022265 | 0.020224 | 0.012061 | 0.012061 | 0.011041 | 0.01002 | 0.009 | 0.044296 | 0.043276 | 0.036133 | 0.035112 | 0.034092 | 0.034092 | 0.026949 | 0.025929 | 0.017765 | 0.017765 | 0.022867 | 0.021847 | 0.021847 | 0.044505 | 0.043485 | 0.036342 | 0.034301 | 0.033281 | 0.03226 | 0.024097 | 0.023077 | 0.014913 | 0.014913 | 0.013893 | 0.012872 | 0.012872
|  | COMRIE | HE |  |  |  |  | 0.042673 | 0.040633 | 0.03349 | 0.032469 | 0.032469 | 0.032469 | 0.024306 | 0.021245 | 0.014102 | 0.014102 | 0.011041 | 0.011041 | 0.01002 | 0.044296 | 0.043276 | 0.036133 | 0.035112 | 0.035112 | 0.035112 | 0.026949 | 0.024908 | 0.017765 | 0.017765 | 0.022867 | 0.021847 | 0.021847 | 0.044505 | 0.043485 | 0.036342 | 0.034301 | 0.034301 | 0.034301 | 0.026138 | 0.023077 | 0.015934 | 0.015934 | 0.013893 | 0.012872 | 0.011852
|  | COMRIE | CF |  |  |  |  | 0.042673 | 0.040633 | 0.03349 | 0.03349 | 0.032469 | 0.032469 | 0.032469 | 0.024306 | 0.024306 | 0.023286 | 0.013082 | 0.013082 | 0.011041 | 0.044296 | 0.043276 | 0.036133 | 0.036133 | 0.035112 | 0.035112 | 0.035112 | 0.026949 | 0.026949 | 0.025929 | 0.020827 | 0.022867 | 0.018786 | 0.044505 | 0.043485 | 0.036342 | 0.036342 | 0.034301 | 0.034301 | 0.034301 | 0.026138 | 0.026138 | 0.025117 | 0.014913 | 0.014913 | 0.013893
| TAYNUILT | CONNEL | MINIMUM HEADROOM | NM 91213 33970 | YES | YES | 0.147 | -0.51329 | -0.55819 | -0.60819 | -0.67452 | -0.71942 | -0.7837 | -0.87044 | -1.0184 | -1.1041 | -1.2082 | -1.4439 | -1.5102 | -1.5337 | 0.061196 | 0.032624 | -0.0030898 | -0.050029 | -0.080641 | -0.12554 | -0.18472 | -0.30513 | -0.36942 | -0.45003 | -0.63676 | -0.70105 | -0.9735 | -0.20717 | -0.25105 | -0.30105 | -0.36533 | -0.41125 | -0.47146 | -0.55411 | -0.69697 | -0.77452 | -0.87248 | -1.0878 | -1.149 | -1.1715
|  | CONNEL | EE |  |  |  |  | -0.51329 | -0.55819 | -0.60819 | -0.67452 | -0.71942 | -0.7837 | -0.87044 | -1.0184 | -1.1041 | -1.2082 | -1.4439 | -1.4796 | -1.5021 | 0.061196 | 0.032624 | -0.0030898 | -0.050029 | -0.080641 | -0.12554 | -0.18472 | -0.30513 | -0.36942 | -0.45003 | -0.63676 | -0.69391 | -0.80513 | -0.20717 | -0.25105 | -0.30105 | -0.36533 | -0.41125 | -0.47146 | -0.55411 | -0.69697 | -0.77452 | -0.87248 | -1.0878 | -1.1204 | -1.1429
|  | CONNEL | HT |  |  |  |  | -0.48472 | -0.52758 | -0.56636 | -0.61636 | -0.65819 | -0.71942 | -0.8388 | -0.95309 | -1.0398 | -1.1255 | -1.3898 | -1.5102 | -1.5337 | 0.086706 | 0.061196 | 0.036706 | 0.0040531 | -0.022478 | -0.062273 | -0.15717 | -0.24901 | -0.30717 | -0.37248 | -0.56227 | -0.6388 | -0.65105 | -0.17656 | -0.2184 | -0.25717 | -0.30513 | -0.34595 | -0.40615 | -0.51329 | -0.6235 | -0.70411 | -0.78676 | -1.0388 | -1.149 | -1.1715
|  | CONNEL | HE |  |  |  |  | -0.48574 | -0.51738 | -0.54799 | -0.59289 | -0.62656 | -0.67554 | -0.71227 | -0.8286 | -0.91942 | -1.0113 | -1.3623 | -1.4378 | -1.448 | 0.085686 | 0.065278 | 0.042829 | 0.012216 | -0.013294 | -0.052069 | -0.072478 | -0.16738 | -0.23982 | -0.31431 | -0.5786 | -0.66636 | -0.76431 | -0.17758 | -0.21023 | -0.24084 | -0.28676 | -0.31738 | -0.36738 | -0.40003 | -0.51227 | -0.59289 | -0.67962 | -1.0092 | -1.0786 | -1.0878
|  | CONNEL | CF |  |  |  |  | -0.47962 | -0.50513 | -0.54187 | -0.56636 | -0.59084 | -0.6286 | -0.67044 | -0.69799 | -0.75717 | -0.81125 | -1.0908 | -1.3531 | -1.4633 | 0.088747 | 0.073441 | 0.044869 | 0.026502 | 0.0071143 | -0.020437 | -0.055131 | -0.075539 | -0.12452 | -0.17044 | -0.41636 | -0.70105 | -0.9735 | -0.17146 | -0.19697 | -0.23268 | -0.25615 | -0.28064 | -0.31738 | -0.35717 | -0.38166 | -0.43982 | -0.4888 | -0.75615 | -1.0092 | -1.1062
| BEAULY | CONON BRIDGE | MINIMUM HEADROOM | NH 54996 55499 | NO | NO | 1.281 | 1.4795 | 1.2693 | 1.0631 | 0.82845 | 9.0986 | 8.8415 | 8.3996 | 7.9639 | 7.4629 | 7.1823 | 6.0853 | 5.4527 | 5.3292 | 2.6864 | 2.567 | 2.4547 | 2.3108 | 10.2323 | 10.0731 | 9.8619 | 9.568 | 9.2833 | 9.3231 | 8.6741 | 8.2996 | 7.6731 | 2.2518 | 2.0518 | 1.863 | 1.6334 | 9.694 | 9.443 | 9.0971 | 8.6195 | 8.1563 | 8.0807 | 7.1165 | 6.5654 | 6.4593
|  | CONON BRIDGE | EE |  |  |  |  | 1.4795 | 1.2693 | 1.0631 | 0.82845 | 9.0986 | 8.8445 | 8.4843 | 7.9639 | 7.4629 | 7.3231 | 6.0853 | 5.5568 | 5.4323 | 2.6864 | 2.567 | 2.4547 | 2.3108 | 10.2323 | 10.0731 | 9.8619 | 9.568 | 9.2833 | 9.3231 | 8.6741 | 8.2996 | 7.9088 | 2.2518 | 2.0518 | 1.863 | 1.6334 | 9.694 | 9.443 | 9.0971 | 8.6195 | 8.1563 | 8.1573 | 7.1165 | 6.6552 | 6.5481
|  | CONON BRIDGE | HT |  |  |  |  | 1.5223 | 1.3264 | 1.1356 | 0.91722 | 9.2057 | 8.8415 | 8.3996 | 7.9721 | 7.5833 | 7.1823 | 6.1119 | 5.4527 | 5.3292 | 2.7292 | 2.6333 | 2.5455 | 2.4262 | 10.3802 | 10.1955 | 9.9751 | 9.77 | 9.5649 | 9.3557 | 8.8782 | 8.5782 | 8.5231 | 2.31 | 2.1344 | 1.9671 | 1.762 | 9.8583 | 9.542 | 9.1573 | 8.793 | 8.443 | 8.0807 | 7.1593 | 6.5654 | 6.4593
|  | CONON BRIDGE | HE |  |  |  |  | 1.5346 | 1.4019 | 1.2846 | 1.1397 | 9.4976 | 9.3394 | 9.1057 | 8.8037 | 8.47 | 8.1333 | 6.8251 | 6.1833 | 5.9374 | 2.7313 | 2.6537 | 2.5853 | 2.4894 | 10.4649 | 10.3578 | 10.217 | 10.0496 | 9.8608 | 9.6598 | 8.9935 | 8.5517 | 8.1313 | 2.3232 | 2.1926 | 2.0804 | 1.9355 | 10.0889 | 9.9256 | 9.7012 | 9.4338 | 9.1307 | 8.8195 | 7.7542 | 7.2083 | 6.9848
|  | CONON BRIDGE | CF |  |  |  |  | 1.5601 | 1.4682 | 1.3784 | 1.2733 | 9.6455 | 9.5527 | 9.4251 | 9.2792 | 9.1017 | 8.8833 | 7.6874 | 7.1568 | 6.471 | 2.7425 | 2.6874 | 2.6302 | 2.5568 | 10.5251 | 10.4629 | 10.3659 | 10.2527 | 10.1394 | 9.9935 | 9.1568 | 8.6262 | 7.6731 | 2.3446 | 2.2548 | 2.1661 | 2.063 | 10.2124 | 10.1287 | 9.9991 | 9.845 | 9.6899 | 9.4889 | 8.3634 | 7.9736 | 7.4277
| BEAULY | CONON FALLS | MINIMUM HEADROOM | NH 38745 57593 | YES | NO | 0.246 | 0.27199 | 0.25975 | 0.25158 | 0.24138 | 0.23118 | 0.21893 | 0.20362 | 0.1822 | 0.18016 | 0.16485 | 0.13526 | 0.12505 | 0.11995 | 0.33005 | 0.32291 | 0.31679 | 0.31169 | 0.30454 | 0.29842 | 0.2872 | 0.27189 | 0.27291 | 0.25964 | 0.24128 | 0.23516 | 0.21475 | 0.33112 | 0.32602 | 0.31888 | 0.3097 | 0.29949 | 0.29031 | 0.27602 | 0.25766 | 0.25357 | 0.23929 | 0.21174 | 0.20255 | 0.19847
|  | CONON FALLS | EE |  |  |  |  | 0.27199 | 0.25975 | 0.25158 | 0.24138 | 0.23118 | 0.21893 | 0.20362 | 0.1822 | 0.18016 | 0.16485 | 0.13526 | 0.12913 | 0.12607 | 0.33005 | 0.32393 | 0.31679 | 0.31169 | 0.30454 | 0.29842 | 0.2872 | 0.27189 | 0.27291 | 0.25964 | 0.24128 | 0.23516 | 0.22291 | 0.33521 | 0.32602 | 0.31888 | 0.3097 | 0.29949 | 0.29031 | 0.27602 | 0.25766 | 0.25357 | 0.23929 | 0.21174 | 0.20663 | 0.20255
|  | CONON FALLS | HT |  |  |  |  | 0.27301 | 0.26077 | 0.26077 | 0.25158 | 0.24138 | 0.23424 | 0.22199 | 0.21383 | 0.2026 | 0.18526 | 0.14444 | 0.12505 | 0.11995 | 0.33107 | 0.32291 | 0.32495 | 0.31985 | 0.31271 | 0.30964 | 0.3025 | 0.29638 | 0.28924 | 0.27597 | 0.25046 | 0.23822 | 0.23618 | 0.33112 | 0.32704 | 0.32704 | 0.3199 | 0.31174 | 0.30459 | 0.29541 | 0.28623 | 0.27398 | 0.26072 | 0.21888 | 0.20255 | 0.19847
|  | CONON FALLS | HE |  |  |  |  | 0.27301 | 0.26281 | 0.26383 | 0.25771 | 0.24852 | 0.2424 | 0.23322 | 0.22403 | 0.20873 | 0.19852 | 0.14546 | 0.13322 | 0.12913 | 0.33107 | 0.32393 | 0.32495 | 0.32189 | 0.31475 | 0.31169 | 0.30658 | 0.30148 | 0.2923 | 0.28107 | 0.24842 | 0.23618 | 0.22699 | 0.33112 | 0.32908 | 0.32806 | 0.32398 | 0.31684 | 0.31072 | 0.30255 | 0.29337 | 0.28317 | 0.2699 | 0.22092 | 0.2097 | 0.20766
|  | CONON FALLS | CF |  |  |  |  | 0.27301 | 0.26281 | 0.26281 | 0.25873 | 0.25464 | 0.24546 | 0.2424 | 0.23424 | 0.22403 | 0.22097 | 0.18628 | 0.14954 | 0.13118 | 0.33107 | 0.32495 | 0.32699 | 0.32393 | 0.32087 | 0.31475 | 0.31271 | 0.30556 | 0.29842 | 0.29638 | 0.27087 | 0.24026 | 0.21475 | 0.33112 | 0.32908 | 0.3301 | 0.32806 | 0.32296 | 0.31582 | 0.31276 | 0.30459 | 0.29541 | 0.29235 | 0.2597 | 0.225 | 0.21072
| DUDHOPE | CONSTABLE STREET | MINIMUM HEADROOM | NO 40903 30821 | NO | NO | 3.252 | 13.8564 | 13.5247 | 13.1094 | 12.6288 | 12.1635 | 11.6839 | 10.9982 | 10.0931 | 9.2513 | 8.5319 | 6.289 | 5.6982 | 5.7135 | 15.9411 | 15.6798 | 15.3615 | 14.989 | 14.5962 | 14.187 | 13.7104 | 13.1053 | 12.5319 | 12.0166 | 9.9717 | 8.8033 | 3.8186 | 14.7594 | 14.4023 | 13.9798 | 13.4747 | 12.9482 | 12.4176 | 11.7727 | 10.9217 | 10.1339 | 9.4686 | 7.3849 | 6.8574 | 6.8717
|  | CONSTABLE STREET | EE |  |  |  |  | 13.8564 | 13.5247 | 13.1094 | 12.6288 | 12.1635 | 11.6839 | 10.9982 | 10.0931 | 9.2513 | 8.5319 | 6.289 | 6.6237 | 6.4656 | 15.9411 | 15.6798 | 15.3615 | 14.989 | 14.5962 | 14.187 | 13.7104 | 13.1053 | 12.5319 | 12.0166 | 9.9717 | 8.9768 | 6.8931 | 14.7594 | 14.4023 | 13.9798 | 13.4747 | 12.9482 | 12.4176 | 11.7727 | 10.9217 | 10.1339 | 9.4686 | 7.3849 | 7.6666 | 7.5013
|  | CONSTABLE STREET | HT |  |  |  |  | 13.9482 | 13.7196 | 13.3992 | 13.0166 | 12.6717 | 12.2156 | 11.636 | 11.0156 | 10.3104 | 9.5594 | 6.6319 | 5.6982 | 5.7135 | 16.0829 | 15.9033 | 15.69 | 15.4319 | 15.1849 | 14.8635 | 14.487 | 14.0686 | 13.6431 | 13.2053 | 11.2911 | 10.4717 | 10.4339 | 14.9278 | 14.6696 | 14.3553 | 13.9727 | 13.6176 | 13.1482 | 12.5635 | 11.8972 | 11.2268 | 10.536 | 7.7819 | 6.8574 | 6.8717
|  | CONSTABLE STREET | HE |  |  |  |  | 13.939 | 13.8043 | 13.5747 | 13.286 | 13.0411 | 12.7574 | 12.3523 | 11.8319 | 11.3533 | 10.7676 | 8.4319 | 7.6115 | 7.7666 | 16.0604 | 15.8951 | 15.6962 | 15.4513 | 15.2207 | 14.9421 | 14.6115 | 14.188 | 13.8013 | 13.3656 | 11.2645 | 9.7104 | 7.8125 | 14.9166 | 14.7349 | 14.4911 | 14.187 | 13.9186 | 13.5972 | 13.187 | 12.6584 | 12.1584 | 11.589 | 9.4145 | 8.6635 | 8.8053
|  | CONSTABLE STREET | CF |  |  |  |  | 13.9666 | 13.8921 | 13.7819 | 13.5972 | 13.437 | 13.2676 | 13.1125 | 12.9125 | 12.687 | 12.4451 | 10.789 | 8.9023 | 7.2727 | 16.1104 | 15.9931 | 15.8309 | 15.6482 | 15.4615 | 15.2513 | 15.0156 | 14.7298 | 14.436 | 14.1207 | 12.0615 | 8.8033 | 3.8186 | 14.9798 | 14.8809 | 14.6962 | 14.487 | 14.2911 | 14.0941 | 13.8951 | 13.637 | 13.3686 | 13.0839 | 11.4788 | 9.8156 | 8.3258
| ALNESS | CONTULLICH | MINIMUM HEADROOM | NN 59226 32752 | YES | NO | 0 | 0.090449 | 0.089429 | 0.080245 | 0.079224 | 0.071061 | 0.071061 | 0.06902 | 0.070041 | 0.06902 | 0.068 | 0.063918 | 0.061878 | 0.061878 | 0.088592 | 0.088592 | 0.080429 | 0.079408 | 0.071245 | 0.074306 | 0.071245 | 0.072265 | 0.071245 | 0.073286 | 0.070224 | 0.068184 | 0.064102 | 0.091051 | 0.091051 | 0.081867 | 0.080847 | 0.072684 | 0.071663 | 0.070643 | 0.070643 | 0.069622 | 0.068602 | 0.0635 | 0.06248 | 0.06248
|  | CONTULLICH | EE |  |  |  |  | 0.090449 | 0.089429 | 0.080245 | 0.079224 | 0.071061 | 0.071061 | 0.075143 | 0.073102 | 0.072082 | 0.068 | 0.063918 | 0.061878 | 0.061878 | 0.088592 | 0.088592 | 0.080429 | 0.079408 | 0.071245 | 0.074306 | 0.079408 | 0.077367 | 0.075327 | 0.073286 | 0.070224 | 0.068184 | 0.067163 | 0.091051 | 0.091051 | 0.081867 | 0.080847 | 0.072684 | 0.071663 | 0.075745 | 0.072684 | 0.071663 | 0.068602 | 0.0635 | 0.06248 | 0.06248
|  | CONTULLICH | HT |  |  |  |  | 0.098612 | 0.090449 | 0.089429 | 0.087388 | 0.079224 | 0.078204 | 0.06902 | 0.070041 | 0.070041 | 0.075143 | 0.063918 | 0.061878 | 0.061878 | 0.096755 | 0.088592 | 0.088592 | 0.087571 | 0.079408 | 0.078388 | 0.071245 | 0.074306 | 0.074306 | 0.078388 | 0.070224 | 0.070224 | 0.070224 | 0.099214 | 0.091051 | 0.091051 | 0.08901 | 0.080847 | 0.079827 | 0.070643 | 0.070643 | 0.069622 | 0.075745 | 0.0635 | 0.06248 | 0.06248
|  | CONTULLICH | HE |  |  |  |  | 0.097592 | 0.090449 | 0.089429 | 0.087388 | 0.079224 | 0.079224 | 0.070041 | 0.071061 | 0.06902 | 0.075143 | 0.064939 | 0.063918 | 0.061878 | 0.095735 | 0.088592 | 0.088592 | 0.087571 | 0.079408 | 0.079408 | 0.071245 | 0.074306 | 0.073286 | 0.078388 | 0.070224 | 0.068184 | 0.067163 | 0.098194 | 0.091051 | 0.091051 | 0.08901 | 0.080847 | 0.080847 | 0.071663 | 0.070643 | 0.069622 | 0.075745 | 0.06452 | 0.06452 | 0.06248
|  | CONTULLICH | CF |  |  |  |  | 0.098612 | 0.097592 | 0.090449 | 0.089429 | 0.087388 | 0.080245 | 0.080245 | 0.072082 | 0.070041 | 0.072082 | 0.073102 | 0.064939 | 0.063918 | 0.096755 | 0.095735 | 0.088592 | 0.087571 | 0.087571 | 0.080429 | 0.080429 | 0.072265 | 0.071245 | 0.074306 | 0.076347 | 0.068184 | 0.064102 | 0.099214 | 0.098194 | 0.091051 | 0.090031 | 0.08799 | 0.080847 | 0.080847 | 0.072684 | 0.070643 | 0.071663 | 0.073704 | 0.065541 | 0.06452
| FORT WILLIAM | CORRAN | MINIMUM HEADROOM | NN 02545 63126 | YES | NO | 0.436 | -0.44697 | -0.48472 | -0.52248 | -0.57554 | -0.61738 | -0.6786 | -0.72758 | -0.80615 | -0.87656 | -0.94391 | -1.1419 | -1.2204 | -1.2776 | -0.24391 | -0.2684 | -0.29391 | -0.32962 | -0.35615 | -0.40207 | -0.42758 | -0.4837 | -0.52656 | -0.57248 | -0.70309 | -0.76431 | -0.91329 | -0.36636 | -0.40411 | -0.43676 | -0.48676 | -0.5286 | -0.58676 | -0.63268 | -0.70819 | -0.77452 | -0.83982 | -1.0266 | -1.1153 | -1.1786
|  | CORRAN | EE |  |  |  |  | -0.44697 | -0.48472 | -0.52248 | -0.57554 | -0.61738 | -0.6786 | -0.72758 | -0.80615 | -0.87656 | -0.94391 | -1.1419 | -1.1959 | -1.2164 | -0.24391 | -0.2684 | -0.29391 | -0.32962 | -0.35615 | -0.40207 | -0.42758 | -0.4837 | -0.52656 | -0.57248 | -0.70309 | -0.76431 | -0.82554 | -0.36636 | -0.40411 | -0.43676 | -0.48676 | -0.5286 | -0.58676 | -0.63268 | -0.70819 | -0.77452 | -0.83982 | -1.0266 | -1.098 | -1.1174
|  | CORRAN | HT |  |  |  |  | -0.42656 | -0.45921 | -0.49595 | -0.53676 | -0.56942 | -0.62044 | -0.66329 | -0.72962 | -0.79289 | -0.83574 | -1.1 | -1.2204 | -1.2674 | -0.2286 | -0.24595 | -0.26738 | -0.29799 | -0.31329 | -0.34799 | -0.37146 | -0.41533 | -0.45717 | -0.4786 | -0.65615 | -0.72656 | -0.76636 | -0.34493 | -0.37656 | -0.41023 | -0.45105 | -0.48166 | -0.53166 | -0.57248 | -0.6337 | -0.69493 | -0.73268 | -0.98778 | -1.1153 | -1.1674
|  | CORRAN | HE |  |  |  |  | -0.42656 | -0.45309 | -0.4786 | -0.51738 | -0.53982 | -0.58472 | -0.62044 | -0.67962 | -0.73778 | -0.78064 | -1.1021 | -1.197 | -1.2235 | -0.2286 | -0.24493 | -0.26533 | -0.28982 | -0.30513 | -0.3388 | -0.36125 | -0.40309 | -0.44391 | -0.46227 | -0.66023 | -0.73064 | -0.78472 | -0.34493 | -0.37044 | -0.39697 | -0.43268 | -0.45309 | -0.49595 | -0.53268 | -0.58982 | -0.65105 | -0.70411 | -1.0153 | -1.1031 | -1.1286
|  | CORRAN | CF |  |  |  |  | -0.42248 | -0.44595 | -0.46227 | -0.49289 | -0.51023 | -0.54084 | -0.57452 | -0.60003 | -0.6388 | -0.67758 | -0.86125 | -1.0735 | -1.2776 | -0.22452 | -0.23982 | -0.25309 | -0.27452 | -0.28676 | -0.30513 | -0.3337 | -0.35411 | -0.38268 | -0.41227 | -0.55411 | -0.73676 | -0.91329 | -0.34187 | -0.36431 | -0.38166 | -0.40921 | -0.42656 | -0.45717 | -0.48778 | -0.51738 | -0.55105 | -0.5888 | -0.76942 | -0.98982 | -1.1786
| KILLIN | COSHIEVILLE | MINIMUM HEADROOM | NN 77193 48683 | YES | YES | 1.738 | -0.28002 | -0.28002 | -0.34532 | -0.41063 | -0.49532 | -0.55655 | -0.65451 | -0.75349 | -0.85451 | -0.94736 | -1.1504 | -1.2147 | -1.2321 | 0.46437 | 0.7108 | 0.66488 | 0.62815 | 0.57611 | 0.53835 | 0.47815 | 0.41386 | 0.35264 | 0.29243 | 0.16182 | 0.1006 | -0.10042 | 0.2932 | 0.4108 | 0.34651 | 0.28631 | 0.20876 | 0.15264 | 0.0608 | -0.032057 | -0.12696 | -0.21471 | -0.38614 | -0.44634 | -0.46267
|  | COSHIEVILLE | EE |  |  |  |  | -0.28002 | -0.28002 | -0.34532 | -0.41063 | -0.49532 | -0.55655 | -0.65451 | -0.75349 | -0.85451 | -0.94736 | -1.1504 | -1.1851 | -1.2035 | 0.46437 | 0.7108 | 0.66488 | 0.62815 | 0.57611 | 0.53835 | 0.47815 | 0.41386 | 0.35264 | 0.29243 | 0.16182 | 0.1006 | 0.0026367 | 0.2932 | 0.4108 | 0.34651 | 0.28631 | 0.20876 | 0.15264 | 0.0608 | -0.032057 | -0.12696 | -0.21471 | -0.38614 | -0.41777 | -0.43716
|  | COSHIEVILLE | HT |  |  |  |  | -0.25144 | -0.2494 | -0.30144 | -0.35655 | -0.42593 | -0.48614 | -0.55961 | -0.62696 | -0.71267 | -0.80144 | -1.081 | -1.2147 | -1.2321 | 0.48478 | 0.73427 | 0.70468 | 0.67815 | 0.63529 | 0.60366 | 0.55774 | 0.52202 | 0.471 | 0.421 | 0.24141 | 0.16284 | 0.15366 | 0.32177 | 0.44141 | 0.39243 | 0.34549 | 0.28019 | 0.22611 | 0.15672 | 0.098555 | 0.021004 | -0.060629 | -0.32287 | -0.44634 | -0.46267
|  | COSHIEVILLE | HE |  |  |  |  | -0.25144 | -0.2392 | -0.28104 | -0.32185 | -0.37798 | -0.42696 | -0.4994 | -0.55655 | -0.629 | -0.70144 | -1.03 | -1.1157 | -1.1259 | 0.48478 | 0.73835 | 0.7108 | 0.68631 | 0.65264 | 0.621 | 0.57611 | 0.54141 | 0.49753 | 0.45162 | 0.24039 | 0.1506 | 0.05978 | 0.32177 | 0.44958 | 0.40978 | 0.37304 | 0.31998 | 0.27509 | 0.20876 | 0.15672 | 0.090392 | 0.024065 | -0.27593 | -0.35451 | -0.36471
|  | COSHIEVILLE | CF |  |  |  |  | -0.24736 | -0.229 | -0.26165 | -0.29022 | -0.329 | -0.35961 | -0.40451 | -0.46165 | -0.49226 | -0.55553 | -0.82083 | -0.9994 | -1.1198 | 0.48682 | 0.74549 | 0.72304 | 0.7057 | 0.68019 | 0.65876 | 0.62815 | 0.58631 | 0.56794 | 0.52713 | 0.321 | 0.12815 | -0.10042 | 0.32687 | 0.45876 | 0.42815 | 0.4006 | 0.36386 | 0.33325 | 0.28937 | 0.23427 | 0.20774 | 0.14958 | -0.099404 | -0.26675 | -0.36573
| COUPAR ANGUS | COUPAR ANGUS | MINIMUM HEADROOM | NO 21784 39212 | NO | NO | 1.49 | 6.8874 | 6.6568 | 6.4119 | 6.1659 | 5.8221 | 5.4241 | 4.9364 | 4.4812 | 3.867 | 2.9241 | 0.72309 | -0.43814 | -1.0136 | 8.067 | 7.9221 | 7.7598 | 7.5915 | 7.3649 | 7.1037 | 6.8149 | 6.5272 | 6.1272 | 5.4935 | 4.0843 | 3.471 | 2.8272 | 6.8807 | 6.6726 | 6.4491 | 6.2226 | 5.9175 | 5.5685 | 5.1318 | 4.7236 | 4.1603 | 3.2991 | 1.3491 | 0.34707 | -0.12436
|  | COUPAR ANGUS | EE |  |  |  |  | 6.8874 | 6.6568 | 6.4119 | 6.1659 | 5.8221 | 5.4241 | 4.9364 | 4.4812 | 3.9027 | 3.1772 | 0.83227 | -0.23304 | -0.83814 | 8.067 | 7.9221 | 7.7598 | 7.5915 | 7.3649 | 7.1037 | 6.8149 | 6.5272 | 6.1272 | 5.6108 | 4.0843 | 3.471 | 2.8904 | 6.8807 | 6.6726 | 6.4491 | 6.2226 | 5.9195 | 5.5685 | 5.1318 | 4.7236 | 4.195 | 3.5318 | 1.4246 | 0.51033 | 0.020535
|  | COUPAR ANGUS | HT |  |  |  |  | 6.9108 | 6.6853 | 6.4557 | 6.1986 | 5.8292 | 5.4608 | 5.0425 | 4.5823 | 3.867 | 2.9241 | 0.72309 | -0.43814 | -1.0136 | 8.0864 | 7.9486 | 7.8027 | 7.6312 | 7.3986 | 7.168 | 6.92 | 6.6486 | 6.1598 | 5.4935 | 4.217 | 3.6721 | 3.3976 | 6.8991 | 6.692 | 6.4838 | 6.245 | 5.9175 | 5.5899 | 5.2165 | 4.8073 | 4.1603 | 3.2991 | 1.3491 | 0.34707 | -0.12436
|  | COUPAR ANGUS | HE |  |  |  |  | 6.9445 | 6.7751 | 6.6108 | 6.419 | 6.1404 | 5.8282 | 5.3986 | 5.0159 | 4.4802 | 3.819 | 1.4017 | 0.34043 | -0.29732 | 8.1068 | 7.9915 | 7.8751 | 7.7343 | 7.5425 | 7.3374 | 7.0721 | 6.8241 | 6.4547 | 5.9782 | 4.3476 | 3.72 | 3.1466 | 6.9256 | 6.7746 | 6.6246 | 6.4491 | 6.2011 | 5.9297 | 5.5532 | 5.2154 | 4.7348 | 4.1358 | 1.9644 | 1.045 | 0.51441
|  | COUPAR ANGUS | CF |  |  |  |  | 7.0323 | 6.9445 | 6.8241 | 6.7139 | 6.567 | 6.3864 | 6.1843 | 5.9812 | 5.7374 | 5.4057 | 3.4415 | 1.5751 | 0.37104 | 8.1741 | 8.1108 | 8.019 | 7.9384 | 7.8292 | 7.6955 | 7.5466 | 7.3945 | 7.2047 | 6.9486 | 5.468 | 3.9864 | 2.8272 | 7.0062 | 6.9246 | 6.8195 | 6.7195 | 6.5869 | 6.4277 | 6.2522 | 6.0726 | 5.8552 | 5.5562 | 3.8083 | 2.1562 | 1.1144
| CRAIGIEBUCKLER | CRAIGIEBUCKLER | MINIMUM HEADROOM | NJ 90775 04519 | NO | NO | 10.089 | 9.6702 | 9.358 | 9.0111 | 8.7182 | 8.3886 | 8.0447 | 7.5294 | 7.0774 | 6.5447 | 6.2896 | 4.1529 | 2.9274 | 2.7213 | 10.6962 | 10.5196 | 10.2911 | 10.1156 | 9.8819 | 9.636 | 9.3125 | 9.3788 | 9.0829 | 8.8574 | 7.9931 | 7.4166 | 7.0247 | 9.4707 | 9.2033 | 8.8737 | 8.6105 | 8.2798 | 7.9349 | 7.4554 | 7.2115 | 6.7298 | 6.5237 | 4.6105 | 3.5186 | 3.338
|  | CRAIGIEBUCKLER | EE |  |  |  |  | 9.6702 | 9.358 | 9.0111 | 8.7182 | 8.3886 | 8.0447 | 7.5294 | 7.2886 | 6.7998 | 6.3294 | 4.3621 | 3.0356 | 2.7549 | 10.6962 | 10.5196 | 10.2911 | 10.1156 | 9.8819 | 9.636 | 9.3125 | 9.3829 | 9.1054 | 8.8574 | 7.9931 | 7.4166 | 7.0247 | 9.4707 | 9.2033 | 8.8737 | 8.6105 | 8.2798 | 7.9349 | 7.4554 | 7.387 | 6.9451 | 6.5237 | 4.7798 | 3.6156 | 3.3676
|  | CRAIGIEBUCKLER | HT |  |  |  |  | 9.7162 | 9.3876 | 9.0407 | 8.7498 | 8.4254 | 8.1172 | 7.6131 | 7.0774 | 6.5447 | 6.2896 | 4.1529 | 2.9274 | 2.7213 | 10.7798 | 10.6166 | 10.4339 | 10.2849 | 10.0962 | 9.9431 | 9.6768 | 9.3788 | 9.0829 | 9.1788 | 8.136 | 7.638 | 7.5543 | 9.5584 | 9.287 | 8.9798 | 8.7186 | 8.4247 | 8.1472 | 7.6951 | 7.2115 | 6.7298 | 6.5288 | 4.6105 | 3.5186 | 3.338
|  | CRAIGIEBUCKLER | HE |  |  |  |  | 9.7305 | 9.5427 | 9.3315 | 9.1764 | 8.9907 | 8.8223 | 8.5162 | 8.1723 | 7.8345 | 7.7835 | 5.9927 | 4.5284 | 3.8784 | 10.7747 | 10.6564 | 10.4992 | 10.3921 | 10.239 | 10.1237 | 9.9156 | 9.6686 | 9.4278 | 9.588 | 8.5523 | 7.8554 | 7.3707 | 9.5625 | 9.3951 | 9.1829 | 9.0329 | 8.8309 | 8.6656 | 8.3707 | 8.0258 | 7.6911 | 7.7819 | 6.2135 | 4.9196 | 4.3502
|  | CRAIGIEBUCKLER | CF |  |  |  |  | 9.7886 | 9.6631 | 9.5243 | 9.4325 | 9.3151 | 9.1917 | 9.109 | 8.9713 | 8.7947 | 8.609 | 7.8437 | 6.4305 | 5.159 | 10.7982 | 10.6982 | 10.5788 | 10.4972 | 10.3768 | 10.2472 | 10.1645 | 10.0033 | 9.8472 | 9.686 | 9.2288 | 8.2002 | 7.1339 | 9.6115 | 9.4839 | 9.3298 | 9.2298 | 9.087 | 8.9319 | 8.836 | 8.6502 | 8.4737 | 8.29 | 7.6472 | 6.4176 | 5.4513
| REDMOSS | CRAIGINCHES | MINIMUM HEADROOM | NJ 94694 04089 | NO | NO | 3.209 | 9.2868 | 9.0521 | 8.7837 | 8.495 | 8.1215 | 7.6939 | 7.0776 | 6.349 | 5.696 | 5.0766 | 2.6276 | 1.247 | 0.70211 | 11.696 | 11.497 | 11.2674 | 11.0215 | 10.7419 | 10.4521 | 10.0817 | 9.6297 | 9.2246 | 8.8501 | 7.2633 | 6.4572 | 6.146 | 10.245 | 10.0909 | 9.9154 | 9.7276 | 9.4562 | 9.0715 | 8.5654 | 7.9531 | 7.349 | 6.7715 | 4.5001 | 3.1756 | 2.6613
|  | CRAIGINCHES | EE |  |  |  |  | 9.2868 | 9.0521 | 8.7837 | 8.495 | 8.1215 | 7.6939 | 7.0776 | 6.349 | 5.696 | 5.0766 | 2.6276 | 1.5266 | 1.3113 | 11.696 | 11.497 | 11.2674 | 11.0215 | 10.7419 | 10.4521 | 10.0817 | 9.6297 | 9.2246 | 8.8501 | 7.496 | 7.1031 | 6.9868 | 10.245 | 10.0909 | 9.9154 | 9.7276 | 9.4562 | 9.0715 | 8.5654 | 7.9531 | 7.349 | 6.7715 | 4.5001 | 3.5144 | 3.3184
|  | CRAIGINCHES | HT |  |  |  |  | 9.3552 | 9.2082 | 9.0092 | 8.7888 | 8.5429 | 8.1786 | 7.6195 | 6.9858 | 6.3654 | 5.7388 | 2.7725 | 1.247 | 0.83272 | 11.7909 | 11.6429 | 11.4776 | 11.295 | 11.0899 | 10.849 | 10.546 | 10.1786 | 9.8225 | 9.4582 | 7.7644 | 6.9797 | 6.748 | 10.3103 | 10.1909 | 10.0623 | 9.9123 | 9.7552 | 9.5439 | 9.1062 | 8.5817 | 8.0021 | 7.4164 | 4.645 | 3.2439 | 2.8552
|  | CRAIGINCHES | HE |  |  |  |  | 9.347 | 9.1878 | 8.997 | 8.7746 | 8.5246 | 8.196 | 7.7388 | 7.1286 | 6.5256 | 5.895 | 2.7878 | 1.2562 | 0.70211 | 11.7776 | 11.6144 | 11.448 | 11.2541 | 11.0307 | 10.7766 | 10.4511 | 10.048 | 9.6541 | 9.2348 | 7.2633 | 6.4572 | 6.146 | 10.3021 | 10.1848 | 10.0623 | 9.9235 | 9.7674 | 9.5256 | 9.0858 | 8.5531 | 8.0297 | 7.4797 | 4.5919 | 3.1756 | 2.6613
|  | CRAIGINCHES | CF |  |  |  |  | 9.398 | 9.3307 | 9.2307 | 9.1021 | 8.9521 | 8.7909 | 8.599 | 8.3419 | 8.0623 | 7.7511 | 5.7531 | 3.6848 | 1.9439 | 11.8368 | 11.7501 | 11.646 | 11.5307 | 11.398 | 11.2501 | 11.0817 | 10.8511 | 10.6388 | 10.4001 | 8.9225 | 7.5041 | 6.3786 | 10.347 | 10.2858 | 10.2103 | 10.1297 | 10.0337 | 9.9337 | 9.8154 | 9.6572 | 9.3878 | 9.0878 | 7.1939 | 5.3797 | 3.7674
| CRAIGIEBUCKLER | CRAIGTON | MINIMUM HEADROOM | NJ 89195 03438 | NO | NO | 0.619 | 4.5321 | 2.1576 | 1.0842 | -0.52807 | -1.9954 | -3.426 | -4.2883 | -5.1536 | -5.9128 | -6.6362 | -8.1924 | -8.8719 | -9.0383 | 6.2883 | 4.5403 | 3.4903 | 2.3066 | 1.3913 | 0.66377 | 0.16785 | -0.31684 | -0.77092 | -1.1913 | -2.0036 | -2.3066 | -2.473 | 2.0291 | -0.13725 | -1.1546 | -2.5383 | -3.8495 | -5.0801 | -5.7964 | -6.4699 | -7.1168 | -7.7138 | -8.7975 | -9.3883 | -9.5403
|  | CRAIGTON | EE |  |  |  |  | 4.6168 | 2.2474 | 1.2515 | -0.30562 | -1.7413 | -3.2128 | -4.2168 | -5.1536 | -5.6709 | -6.4026 | -8.127 | -8.7699 | -8.9811 | 6.4199 | 4.6872 | 3.773 | 2.6903 | 1.7842 | 0.97602 | 0.30969 | -0.26786 | -0.625 | -1.0801 | -2.0036 | -2.3066 | -2.473 | 2.1342 | -0.026024 | -0.93419 | -2.1995 | -3.4852 | -4.7893 | -5.6628 | -6.4515 | -6.9036 | -7.5128 | -8.7342 | -9.3036 | -9.4883
|  | CRAIGTON | HT |  |  |  |  | 4.5321 | 2.1576 | 1.0842 | -0.52807 | -1.9954 | -3.426 | -4.2883 | -5.1179 | -5.9128 | -6.6362 | -8.1924 | -8.8719 | -9.0383 | 6.2883 | 4.5403 | 3.4903 | 2.3066 | 1.3913 | 0.66377 | 0.16785 | -0.31684 | -0.77092 | -1.1913 | -1.9536 | -2.277 | -2.3546 | 2.0291 | -0.13725 | -1.1546 | -2.5383 | -3.8495 | -5.0801 | -5.7964 | -6.4699 | -7.1168 | -7.7138 | -8.7975 | -9.3883 | -9.5403
|  | CRAIGTON | HE |  |  |  |  | 4.6648 | 2.3321 | 1.426 | 0.099486 | -1.2485 | -2.6117 | -3.4138 | -4.1617 | -4.8444 | -5.4862 | -6.977 | -7.7801 | -8.2536 | 6.4515 | 4.7474 | 3.8566 | 2.8168 | 1.9281 | 1.1546 | 0.59847 | 0.11683 | -0.31582 | -0.73419 | -1.7281 | -2.0903 | -2.2566 | 2.1689 | 0.045404 | -0.83827 | -1.8832 | -3.0975 | -4.2924 | -4.9872 | -5.6056 | -6.1628 | -6.6811 | -7.7107 | -8.4301 | -8.8832
|  | CRAIGTON | CF |  |  |  |  | 5.0505 | 2.9097 | 2.1903 | 1.2617 | 0.20765 | -0.93623 | -1.6934 | -2.4026 | -3.0872 | -3.7709 | -6.1934 | -7.0975 | -7.4689 | 6.9148 | 5.4199 | 4.7281 | 4.0168 | 3.3383 | 2.6525 | 2.1046 | 1.5832 | 1.1056 | 0.62704 | -0.92602 | -1.7597 | -2.1107 | 2.5628 | 0.625 | -0.076024 | -0.79541 | -1.5475 | -2.5597 | -3.2158 | -3.8291 | -4.4128 | -4.9893 | -6.9413 | -7.7862 | -8.1219
| BRACO | CRIEFF | MINIMUM HEADROOM | NN 85626 22119 | NO | YES | 2.124 | 5.3691 | 13.6767 | 13.194 | 12.7022 | 12.1604 | 11.5787 | 10.8879 | 10.5216 | 9.8777 | 9.2777 | 7.043 | 5.742 | 5.4991 | 7.81 | 15.8451 | 15.5604 | 15.2747 | 14.9502 | 14.5951 | 14.1889 | 14.0206 | 13.644 | 13.293 | 11.9247 | 11.0889 | 10.2145 | 7.1748 | 15.3032 | 14.8716 | 14.4369 | 13.9481 | 13.4277 | 12.8053 | 12.4859 | 11.9094 | 11.3685 | 9.3369 | 8.1328 | 7.9032
|  | CRIEFF | EE |  |  |  |  | 5.3691 | 13.6767 | 13.194 | 12.7022 | 12.1604 | 11.5787 | 10.8879 | 10.5216 | 9.8777 | 9.2777 | 7.043 | 5.8696 | 5.5614 | 7.81 | 15.8451 | 15.5604 | 15.2747 | 14.9502 | 14.5951 | 14.1889 | 14.0206 | 13.644 | 13.293 | 11.9247 | 11.0889 | 10.3236 | 7.1748 | 15.3032 | 14.8716 | 14.4369 | 13.9481 | 13.4277 | 12.8053 | 12.4859 | 11.9094 | 11.3685 | 9.3369 | 8.241 | 7.9604
|  | CRIEFF | HT |  |  |  |  | 5.46 | 13.7828 | 13.343 | 12.8961 | 12.4022 | 11.9104 | 11.3216 | 10.6849 | 10.0604 | 9.4124 | 7.1502 | 5.742 | 5.4991 | 7.8804 | 15.9328 | 15.691 | 15.441 | 15.1645 | 14.891 | 14.5696 | 14.2114 | 13.8583 | 13.4879 | 12.3379 | 11.6481 | 11.5196 | 7.2513 | 15.3991 | 15.0002 | 14.5951 | 14.1502 | 13.7094 | 13.1757 | 12.6022 | 12.0389 | 11.4512 | 9.4287 | 8.1328 | 7.9032
|  | CRIEFF | HE |  |  |  |  | 5.4763 | 13.9022 | 13.5757 | 13.2389 | 12.8594 | 12.4512 | 12.04 | 11.5542 | 11.0828 | 10.6012 | 8.6491 | 7.3889 | 6.9022 | 7.8845 | 15.9798 | 15.7767 | 15.5696 | 15.3328 | 15.0736 | 14.8226 | 14.5155 | 14.2165 | 13.9053 | 12.691 | 11.7879 | 10.9685 | 7.2697 | 15.5094 | 15.2185 | 14.9165 | 14.5767 | 14.2094 | 13.843 | 13.4104 | 12.9889 | 12.5583 | 10.8124 | 9.643 | 9.1818
|  | CRIEFF | CF |  |  |  |  | 5.5804 | 14.0889 | 13.8491 | 13.5818 | 13.3481 | 13.0594 | 12.8073 | 12.5604 | 12.2961 | 12.0206 | 10.6991 | 9.1542 | 8.0104 | 7.9528 | 16.094 | 15.9389 | 15.7696 | 15.6134 | 15.4196 | 15.2318 | 15.0461 | 14.841 | 14.6267 | 13.5736 | 12.0359 | 10.2145 | 7.3635 | 15.6777 | 15.4716 | 15.2369 | 15.0287 | 14.7696 | 14.5481 | 14.3359 | 14.1022 | 13.8583 | 12.7042 | 11.3022 | 10.2379
| PORT ANN | CRINAN | MINIMUM HEADROOM | NR 79620 92347 | YES | YES | 0.023 | 0.19742 | 0.16987 | 0.13212 | 0.10865 | 0.080078 | 0.040282 | -0.0056367 | -0.054616 | -0.11074 | -0.1587 | -0.26278 | -0.28829 | -0.29747 | 0.17293 | 0.15763 | 0.1362 | 0.12396 | 0.10661 | 0.080078 | 0.046404 | 0.019873 | -0.024004 | -0.057678 | -0.10564 | -0.11278 | -0.14237 | 0.11579 | 0.094363 | 0.064771 | 0.047424 | 0.024976 | -0.0076776 | -0.046453 | -0.081147 | -0.12911 | -0.16584 | -0.23115 | -0.23829 | -0.24339
|  | CRINAN | EE |  |  |  |  | 0.19742 | 0.16987 | 0.13212 | 0.10865 | 0.080078 | 0.040282 | -0.0056367 | -0.054616 | -0.11074 | -0.1587 | -0.26278 | -0.27809 | -0.28625 | 0.17293 | 0.15763 | 0.1362 | 0.12396 | 0.10661 | 0.080078 | 0.046404 | 0.019873 | -0.024004 | -0.057678 | -0.10564 | -0.11278 | -0.1189 | 0.11579 | 0.094363 | 0.064771 | 0.047424 | 0.024976 | -0.0076776 | -0.046453 | -0.081147 | -0.12911 | -0.16584 | -0.23115 | -0.23829 | -0.24237
|  | CRINAN | HT |  |  |  |  | 0.20865 | 0.19028 | 0.16375 | 0.13926 | 0.10763 | 0.090282 | 0.034159 | -0.0076776 | -0.054616 | -0.098494 | -0.22911 | -0.28829 | -0.29747 | 0.18212 | 0.17293 | 0.15967 | 0.14844 | 0.12906 | 0.12191 | 0.08518 | 0.059669 | 0.029057 | -0.0025755 | -0.084208 | -0.10666 | -0.11176 | 0.12702 | 0.11579 | 0.095384 | 0.078037 | 0.054567 | 0.042322 | -0.0025755 | -0.035229 | -0.068902 | -0.10462 | -0.20666 | -0.23727 | -0.24339
|  | CRINAN | HE |  |  |  |  | 0.20865 | 0.19436 | 0.17191 | 0.15355 | 0.12804 | 0.11273 | 0.081098 | 0.041302 | -0.0015551 | -0.043392 | -0.20666 | -0.24645 | -0.2536 | 0.18212 | 0.176 | 0.16069 | 0.15049 | 0.13416 | 0.12804 | 0.10865 | 0.082118 | 0.048445 | 0.015792 | -0.083188 | -0.10564 | -0.10972 | 0.12702 | 0.11783 | 0.098445 | 0.083139 | 0.063751 | 0.054567 | 0.027016 | -0.0076776 | -0.041351 | -0.078086 | -0.19849 | -0.22502 | -0.22911
|  | CRINAN | CF |  |  |  |  | 0.21273 | 0.20049 | 0.18314 | 0.16987 | 0.1464 | 0.1362 | 0.11579 | 0.090282 | 0.072935 | 0.042322 | -0.086249 | -0.20258 | -0.25156 | 0.18416 | 0.1811 | 0.16987 | 0.16273 | 0.14742 | 0.14538 | 0.1311 | 0.11273 | 0.10151 | 0.081098 | -0.01482 | -0.098494 | -0.14237 | 0.1311 | 0.12293 | 0.11069 | 0.10049 | 0.083139 | 0.075996 | 0.059669 | 0.039261 | 0.022935 | 0.0015061 | -0.10666 | -0.20564 | -0.22707
| PORT ANN | CROMALT | MINIMUM HEADROOM | NN 08395 07755 | YES | YES | 0 | 2.1755 | 2.1571 | 2.1327 | 2.1031 | 2.1276 | 2.0959 | 2.0612 | 2 | 1.9429 | 1.8888 | 1.6541 | 1.5857 | 1.5592 | 2.2189 | 2.2077 | 2.1934 | 2.1719 | 2.4347 | 2.4061 | 2.3878 | 2.3418 | 2.3 | 2.2653 | 2.0929 | 2.0439 | 2.0184 | 2.2089 | 2.1916 | 2.1722 | 2.1416 | 2.2867 | 2.2551 | 2.2265 | 2.1694 | 2.1143 | 2.0633 | 1.8398 | 1.7745 | 1.748
|  | CROMALT | EE |  |  |  |  | 2.1755 | 2.1571 | 2.1327 | 2.1031 | 2.1276 | 2.0959 | 2.0612 | 2 | 1.9469 | 1.9031 | 1.7837 | 1.7551 | 1.752 | 2.2189 | 2.2077 | 2.1934 | 2.1719 | 2.4347 | 2.4061 | 2.3878 | 2.3418 | 2.3 | 2.2653 | 2.1898 | 2.1541 | 2.1122 | 2.2089 | 2.1916 | 2.1722 | 2.1416 | 2.2867 | 2.2551 | 2.2265 | 2.1694 | 2.1194 | 2.0745 | 1.9653 | 1.9378 | 1.9337
|  | CROMALT | HT |  |  |  |  | 2.1898 | 2.1735 | 2.1551 | 2.1347 | 2.1643 | 2.1388 | 2.0908 | 2.0398 | 2.001 | 1.9653 | 1.8316 | 1.7755 | 1.7571 | 2.2291 | 2.2189 | 2.2087 | 2.1934 | 2.4561 | 2.4388 | 2.402 | 2.3684 | 2.3347 | 2.3163 | 2.2276 | 2.1908 | 2.1827 | 2.2222 | 2.2089 | 2.1916 | 2.1722 | 2.3153 | 2.2898 | 2.25 | 2.2041 | 2.1643 | 2.1378 | 2.0092 | 1.9582 | 1.9408
|  | CROMALT | HE |  |  |  |  | 2.1827 | 2.1602 | 2.1378 | 2.1143 | 2.1378 | 2.102 | 2.0684 | 2.002 | 1.9429 | 1.8888 | 1.6541 | 1.5857 | 1.5837 | 2.2291 | 2.2179 | 2.2087 | 2.1954 | 2.4602 | 2.4388 | 2.4133 | 2.3571 | 2.3082 | 2.2694 | 2.0929 | 2.0439 | 2.0439 | 2.2212 | 2.2089 | 2.1895 | 2.1651 | 2.302 | 2.2704 | 2.2367 | 2.1714 | 2.1143 | 2.0633 | 1.8398 | 1.7745 | 1.7724
|  | CROMALT | CF |  |  |  |  | 2.1908 | 2.1776 | 2.1663 | 2.149 | 2.1786 | 2.1602 | 2.1378 | 2.1082 | 2.0796 | 2.0429 | 1.8418 | 1.6724 | 1.5592 | 2.2311 | 2.223 | 2.2168 | 2.2087 | 2.4694 | 2.4622 | 2.4459 | 2.4286 | 2.4153 | 2.3867 | 2.2296 | 2.1 | 2.0184 | 2.2242 | 2.212 | 2.2059 | 2.1916 | 2.3357 | 2.3255 | 2.3041 | 2.2735 | 2.248 | 2.2133 | 2.0194 | 1.8551 | 1.748
| ALNESS | CROSSHILLS | MINIMUM HEADROOM | NH 65470 70156 | NO | NO | 3.937 | 4.7166 | 4.3676 | 4.0186 | 3.6727 | 3.3166 | 2.6533 | 1.9584 | 1.2227 | 0.54513 | -0.084461 | -1.7579 | -2.7763 | -2.9671 | 5.5502 | 5.2574 | 5.0308 | 4.7972 | 4.5564 | 4.3084 | 4.0227 | 3.6972 | 3.4196 | 3.139 | 2.1951 | 1.5727 | 0.96146 | 5.4977 | 5.1334 | 4.8416 | 4.5028 | 4.1528 | 3.6171 | 3.013 | 2.3599 | 1.7569 | 1.1875 | -0.29211 | -1.2095 | -1.3748
|  | CROSSHILLS | EE |  |  |  |  | 4.7166 | 4.3676 | 4.0635 | 3.7064 | 3.3359 | 2.94 | 2.4655 | 1.6757 | 1.1666 | 0.45942 | -1.6396 | -2.6487 | -2.8722 | 5.5615 | 5.2737 | 5.0421 | 4.7972 | 4.5564 | 4.3176 | 4.0686 | 3.6972 | 3.488 | 3.187 | 2.1951 | 1.5727 | 1.0247 | 5.4977 | 5.1334 | 4.8487 | 4.5028 | 4.1528 | 3.7691 | 3.3099 | 2.5865 | 2.2334 | 1.613 | -0.20946 | -1.0931 | -1.2921
|  | CROSSHILLS | HT |  |  |  |  | 4.7268 | 4.3706 | 4.0186 | 3.6727 | 3.3166 | 2.6533 | 1.9584 | 1.2227 | 0.54513 | -0.084461 | -1.7579 | -2.7763 | -2.9671 | 5.5502 | 5.2574 | 5.0308 | 4.8084 | 4.6094 | 4.3084 | 4.0227 | 3.7053 | 3.4196 | 3.139 | 2.3676 | 1.937 | 1.8441 | 5.5099 | 5.1405 | 4.8416 | 4.513 | 4.1946 | 3.6171 | 3.013 | 2.3599 | 1.7569 | 1.1875 | -0.29211 | -1.2095 | -1.3748
|  | CROSSHILLS | HE |  |  |  |  | 4.7727 | 4.4655 | 4.24 | 4.0339 | 3.8196 | 3.538 | 3.2574 | 2.7564 | 2.2645 | 1.7727 | -0.25385 | -1.5406 | -1.9875 | 5.5962 | 5.338 | 5.1431 | 4.9645 | 4.7686 | 4.5676 | 4.3819 | 4.1074 | 3.8451 | 3.5778 | 2.5737 | 2.038 | 1.4308 | 5.5538 | 5.2385 | 5.0028 | 4.7803 | 4.562 | 4.3069 | 4.0385 | 3.6365 | 3.2007 | 2.7538 | 1.0324 | -0.084971 | -0.46967
|  | CROSSHILLS | CF |  |  |  |  | 4.9288 | 4.7574 | 4.6094 | 4.4768 | 4.3247 | 4.1594 | 4.0135 | 3.8431 | 3.5543 | 3.2247 | 1.641 | 0.14819 | -0.91099 | 5.737 | 5.5859 | 5.4635 | 5.3625 | 5.237 | 5.1013 | 4.9757 | 4.8247 | 4.6451 | 4.4502 | 3.4941 | 2.3186 | 0.96146 | 5.7181 | 5.5405 | 5.3865 | 5.2497 | 5.0956 | 4.9222 | 4.7824 | 4.614 | 4.3732 | 4.0742 | 2.7069 | 1.3569 | 0.44258
| KEITH 1 | CULLEN | MINIMUM HEADROOM | NJ 51590 65032 | YES | YES | 0.188 | 6.0289 | 5.8912 | 5.7177 | 5.5167 | 5.3371 | 5.133 | 4.8381 | 4.5636 | 4.282 | 4.0187 | 3.031 | 2.4249 | 2.3177 | 6.2448 | 6.1652 | 6.0672 | 5.9417 | 5.8427 | 5.7111 | 5.5437 | 5.3805 | 5.2029 | 5.0468 | 4.509 | 4.1754 | 3.8305 | 6.2088 | 6.0802 | 5.9261 | 5.7302 | 5.57 | 5.367 | 5.0894 | 4.8384 | 4.567 | 4.318 | 3.4782 | 2.9649 | 2.8721
|  | CULLEN | EE |  |  |  |  | 6.0289 | 5.8912 | 5.7259 | 5.5167 | 5.3371 | 5.133 | 4.8381 | 4.5636 | 4.282 | 4.0187 | 3.031 | 2.4769 | 2.3596 | 6.2448 | 6.1652 | 6.0672 | 5.9417 | 5.8427 | 5.7111 | 5.5437 | 5.3805 | 5.2029 | 5.0468 | 4.509 | 4.1754 | 3.8764 | 6.2088 | 6.0802 | 5.9261 | 5.7302 | 5.57 | 5.367 | 5.0894 | 4.8384 | 4.567 | 4.318 | 3.4782 | 3.0159 | 2.9119
|  | CULLEN | HT |  |  |  |  | 6.0402 | 5.9034 | 5.7177 | 5.5371 | 5.3524 | 5.1687 | 4.9147 | 4.6494 | 4.3983 | 4.1463 | 3.0463 | 2.4249 | 2.3177 | 6.2713 | 6.206 | 6.105 | 6.0162 | 5.9203 | 5.8182 | 5.6886 | 5.5397 | 5.3988 | 5.258 | 4.6703 | 4.3886 | 4.3437 | 6.2292 | 6.1078 | 5.9476 | 5.7894 | 5.6241 | 5.4557 | 5.2261 | 4.9833 | 4.7516 | 4.519 | 3.5149 | 2.9649 | 2.8721
|  | CULLEN | HE |  |  |  |  | 6.0616 | 5.98 | 5.8636 | 5.7218 | 5.5881 | 5.4391 | 5.2718 | 5.0789 | 4.8973 | 4.7167 | 3.7442 | 3.1402 | 2.8912 | 6.2774 | 6.2305 | 6.1529 | 6.0754 | 5.9958 | 5.8999 | 5.8111 | 5.6795 | 5.557 | 5.4366 | 4.8264 | 4.4509 | 4.1203 | 6.2445 | 6.1721 | 6.0649 | 5.9414 | 5.819 | 5.6782 | 5.5333 | 5.3455 | 5.171 | 4.9884 | 4.0904 | 3.5955 | 3.3874
|  | CULLEN | CF |  |  |  |  | 6.0973 | 6.0524 | 5.9942 | 5.9289 | 5.8402 | 5.7596 | 5.6504 | 5.5432 | 5.4432 | 5.334 | 4.7473 | 4.0259 | 3.4483 | 6.2988 | 6.2672 | 6.2244 | 6.1805 | 6.1141 | 6.0539 | 5.9713 | 5.8999 | 5.8203 | 5.7284 | 5.2346 | 4.5652 | 3.8305 | 6.2772 | 6.2333 | 6.1782 | 6.118 | 6.0323 | 5.9537 | 5.8527 | 5.7547 | 5.6496 | 5.5394 | 4.9486 | 4.27 | 3.8261
| INVERNESS | CULLODEN | MINIMUM HEADROOM | NH 71240 45502 | NO | NO | 3.604 | 7.2509 | 6.4887 | 15.254 | 14.354 | 13.458 | 12.7713 | 11.807 | 10.9132 | 9.9295 | 9.2478 | 6.4203 | 4.7652 | 4.4632 | 10.7795 | 10.3774 | 18.0478 | 17.5785 | 17.0999 | 16.8856 | 16.3846 | 15.8295 | 15.2897 | 14.9019 | 13.4611 | 12.4427 | 11.0427 | 9.2417 | 8.5846 | 16.7162 | 15.9234 | 15.1193 | 14.6989 | 13.8642 | 12.958 | 12.0795 | 11.456 | 9.1621 | 7.7142 | 7.4662
|  | CULLODEN | EE |  |  |  |  | 7.2509 | 6.4887 | 15.254 | 14.354 | 13.458 | 12.8611 | 11.9121 | 10.9132 | 9.9295 | 9.2478 | 6.6162 | 5.004 | 4.6223 | 10.7795 | 10.3774 | 18.0478 | 17.5785 | 17.0999 | 16.8856 | 16.3846 | 15.8295 | 15.2897 | 14.9019 | 13.4611 | 12.4427 | 11.4438 | 9.2417 | 8.5846 | 16.7162 | 15.9234 | 15.1193 | 14.6989 | 13.8642 | 12.958 | 12.0795 | 11.456 | 9.2346 | 7.9346 | 7.5978
|  | CULLODEN | HT |  |  |  |  | 7.3427 | 6.5938 | 15.3713 | 14.4989 | 13.6917 | 12.7713 | 11.807 | 11.1244 | 10.1907 | 9.506 | 6.4203 | 4.7652 | 4.4632 | 10.8693 | 10.5029 | 18.2152 | 17.7938 | 17.4234 | 16.9764 | 16.5091 | 16.2703 | 15.8223 | 15.4907 | 13.8866 | 13.1172 | 12.9825 | 9.3672 | 8.7438 | 16.9203 | 16.1815 | 15.505 | 14.7121 | 13.8744 | 13.3999 | 12.5948 | 11.9723 | 9.1621 | 7.7142 | 7.4662
|  | CULLODEN | HE |  |  |  |  | 7.3591 | 6.7754 | 15.7285 | 15.0254 | 14.3907 | 13.657 | 12.9325 | 12.4999 | 11.8019 | 11.3601 | 8.7274 | 6.9387 | 6.1774 | 10.8652 | 10.5519 | 18.3142 | 17.9478 | 17.6264 | 17.2407 | 16.8448 | 16.6825 | 16.306 | 16.0274 | 14.3723 | 13.207 | 12.1121 | 9.3774 | 8.8836 | 17.1958 | 16.5938 | 16.0519 | 15.406 | 14.7601 | 14.4723 | 13.8591 | 13.4264 | 10.9907 | 9.5315 | 8.9509
|  | CULLODEN | CF |  |  |  |  | 7.5744 | 7.2029 | 16.256 | 15.6366 | 15.1417 | 14.5683 | 14.1029 | 13.5866 | 13.4029 | 13.1611 | 11.4693 | 9.3907 | 7.7203 | 10.9703 | 10.757 | 18.556 | 18.2203 | 17.955 | 17.6325 | 17.3366 | 17.0029 | 16.9325 | 16.7376 | 15.408 | 13.4519 | 11.0427 | 9.5519 | 9.2315 | 17.6356 | 17.1142 | 16.6948 | 16.1989 | 15.7795 | 15.2999 | 15.2366 | 14.9887 | 13.3866 | 11.4948 | 10.0856
| CRAIGIEBUCKLER | CULTER | MINIMUM HEADROOM | NJ 84009 00884 | NO | NO | 1.49 | 9.7337 | 9.3031 | 8.9021 | 8.4572 | 8.0144 | 7.5429 | 7.0654 | 6.5225 | 6.3715 | 5.8552 | 4.2011 | 3.0756 | 2.8766 | 12.0337 | 11.8001 | 11.5807 | 11.3368 | 11.1103 | 10.847 | 10.5817 | 10.2715 | 10.2562 | 10.0195 | 9.0582 | 8.3837 | 7.5735 | 10.7521 | 10.3827 | 10.0307 | 9.6297 | 9.2388 | 8.8072 | 8.3654 | 7.8613 | 7.7562 | 7.3031 | 5.8215 | 4.7878 | 4.6052
|  | CULTER | EE |  |  |  |  | 9.7337 | 9.3031 | 8.9021 | 8.4572 | 8.0144 | 7.5429 | 7.0654 | 6.5225 | 6.3837 | 5.949 | 4.246 | 3.2133 | 2.9501 | 12.0337 | 11.8001 | 11.5807 | 11.3368 | 11.1103 | 10.847 | 10.5817 | 10.2715 | 10.2562 | 10.0195 | 9.0582 | 8.3837 | 7.7878 | 10.7521 | 10.3827 | 10.0307 | 9.6297 | 9.2388 | 8.8072 | 8.3654 | 7.8613 | 7.7562 | 7.3572 | 5.847 | 4.9072 | 4.6695
|  | CULTER | HT |  |  |  |  | 9.8113 | 9.4123 | 9.0113 | 8.6276 | 8.1888 | 7.7531 | 7.3409 | 6.8572 | 6.3715 | 5.8552 | 4.2011 | 3.0756 | 2.8766 | 12.0939 | 11.898 | 11.698 | 11.5123 | 11.2919 | 11.0715 | 10.8705 | 10.6184 | 10.3684 | 10.097 | 9.3225 | 8.7848 | 8.6919 | 10.8317 | 10.4939 | 10.1419 | 9.8092 | 9.4195 | 9.0276 | 8.6572 | 8.2133 | 7.7705 | 7.3031 | 5.8215 | 4.7878 | 4.6052
|  | CULTER | HE |  |  |  |  | 9.8144 | 9.5164 | 9.2184 | 8.9256 | 8.5848 | 8.246 | 7.995 | 7.6511 | 7.3052 | 6.9419 | 5.4807 | 4.2858 | 3.8256 | 12.0899 | 11.9235 | 11.7541 | 11.5929 | 11.4062 | 11.2133 | 11.0695 | 10.8623 | 10.648 | 10.4246 | 9.5603 | 8.7613 | 8.1011 | 10.8327 | 10.5817 | 10.3235 | 10.0674 | 9.7654 | 9.4603 | 9.2266 | 8.9072 | 8.5848 | 8.2511 | 6.9439 | 5.8735 | 5.4684
|  | CULTER | CF |  |  |  |  | 9.8756 | 9.6409 | 9.4215 | 9.1705 | 8.9511 | 8.7052 | 8.5705 | 8.447 | 8.2868 | 8.1184 | 7.1817 | 5.9225 | 4.8348 | 12.1174 | 11.9837 | 11.8511 | 11.7011 | 11.5725 | 11.4225 | 11.3133 | 11.2133 | 11.0817 | 10.947 | 10.2439 | 9.0695 | 7.5735 | 10.8909 | 10.695 | 10.5072 | 10.2878 | 10.096 | 9.8756 | 9.746 | 9.6297 | 9.4746 | 9.3123 | 8.4766 | 7.3154 | 6.3399
| ELGIN | CUMMING STREET | MINIMUM HEADROOM | NJ 21542 63007 | NO | YES | 0.913 | 7.9355 | 7.7926 | 7.6365 | 7.41 | 6.963 | 6.76 | 6.2263 | 5.9171 | 5.911 | 5.6437 | 4.2222 | 2.9263 | 2.6886 | 11.1988 | 11.1253 | 11.0314 | 10.9049 | 10.462 | 10.3559 | 9.8977 | 9.6906 | 9.6232 | 9.4079 | 8.4416 | 7.6651 | 6.9794 | 8.9217 | 8.8105 | 8.6697 | 8.4819 | 7.9738 | 7.8125 | 7.2748 | 7.0503 | 6.935 | 6.5421 | 4.9431 | 3.7768 | 3.5891
|  | CUMMING STREET | EE |  |  |  |  | 7.9355 | 7.7926 | 7.6365 | 7.41 | 6.963 | 6.76 | 6.2263 | 5.9171 | 5.9396 | 5.7079 | 4.3059 | 3.0181 | 2.7457 | 11.1988 | 11.1253 | 11.0314 | 10.9049 | 10.462 | 10.3559 | 9.8977 | 9.6906 | 9.6232 | 9.4079 | 8.4416 | 7.6651 | 7.0212 | 8.9217 | 8.8105 | 8.6697 | 8.4819 | 7.9738 | 7.8125 | 7.2748 | 7.0503 | 6.935 | 6.5421 | 4.9431 | 3.9044 | 3.6431
|  | CUMMING STREET | HT |  |  |  |  | 7.9804 | 7.8559 | 7.6998 | 7.4834 | 7.063 | 6.8926 | 6.3906 | 6.1651 | 5.911 | 5.6437 | 4.2222 | 2.9263 | 2.6886 | 11.2375 | 11.1773 | 11.0947 | 10.9824 | 10.5641 | 10.4865 | 10.061 | 9.9324 | 9.7437 | 9.5477 | 8.7141 | 8.1202 | 8.0151 | 8.9646 | 8.8738 | 8.7401 | 8.5646 | 8.088 | 7.9666 | 7.4727 | 7.3074 | 7.0829 | 6.6523 | 4.9493 | 3.7768 | 3.5891
|  | CUMMING STREET | HE |  |  |  |  | 7.9875 | 7.9028 | 7.8028 | 7.6406 | 7.261 | 7.1365 | 6.7212 | 6.5804 | 6.41 | 6.2324 | 5.5161 | 4.2457 | 3.6743 | 11.2334 | 11.1794 | 11.1059 | 11.0028 | 10.5865 | 10.5079 | 10.0824 | 9.9845 | 9.8783 | 9.763 | 9.0202 | 8.1783 | 7.4539 | 8.9625 | 8.887 | 8.7809 | 8.6309 | 8.1615 | 8.0482 | 7.5697 | 7.4207 | 7.2636 | 7.0952 | 6.2187 | 5.1044 | 4.688
|  | CUMMING STREET | CF |  |  |  |  | 8.0069 | 7.9579 | 7.8947 | 7.7916 | 7.4406 | 7.3845 | 7.0528 | 6.961 | 6.9151 | 6.8345 | 6.2375 | 5.8202 | 5.0753 | 11.2508 | 11.2141 | 11.1661 | 11.0957 | 10.7039 | 10.659 | 10.2722 | 10.1977 | 10.1437 | 10.0753 | 9.5426 | 8.5681 | 6.9794 | 8.986 | 8.9421 | 8.8758 | 8.7789 | 8.3533 | 8.2942 | 7.8789 | 7.7829 | 7.7115 | 7.6217 | 7.0105 | 6.5105 | 5.7421
| ST FILLANS | DALCHONZIE | MINIMUM HEADROOM | NN 74079 21921 | YES | YES | 0.516 | 5.0275 | 4.9193 | 4.807 | 4.6724 | 4.5213 | 4.3917 | 4.204 | 4.0152 | 3.8356 | 3.7081 | 3.1244 | 2.7744 | 2.7132 | 5.2109 | 5.1497 | 5.0885 | 5.0068 | 4.9119 | 4.8426 | 4.7324 | 4.6109 | 4.4987 | 4.4385 | 4.1191 | 3.915 | 3.6956 | 5.1473 | 5.0483 | 4.9483 | 4.8217 | 4.6809 | 4.5666 | 4.3942 | 4.2095 | 4.0401 | 3.9279 | 3.4136 | 3.1115 | 3.0554
|  | DALCHONZIE | EE |  |  |  |  | 5.0275 | 4.9193 | 4.807 | 4.6724 | 4.5213 | 4.3917 | 4.204 | 4.0152 | 3.8356 | 3.7081 | 3.1244 | 2.7968 | 2.7224 | 5.2109 | 5.1497 | 5.0885 | 5.0068 | 4.9119 | 4.8426 | 4.7324 | 4.6109 | 4.4987 | 4.4385 | 4.1191 | 3.915 | 3.7293 | 5.1473 | 5.0483 | 4.9483 | 4.8217 | 4.6809 | 4.5666 | 4.3942 | 4.2095 | 4.0401 | 3.9279 | 3.4136 | 3.134 | 3.0666
|  | DALCHONZIE | HT |  |  |  |  | 5.0591 | 4.9499 | 4.8305 | 4.6907 | 4.5622 | 4.4468 | 4.2938 | 4.1295 | 4.0019 | 3.8407 | 3.1438 | 2.7744 | 2.7132 | 5.2456 | 5.1915 | 5.1303 | 5.0568 | 4.9956 | 4.9324 | 4.8487 | 4.7548 | 4.6966 | 4.6048 | 4.2252 | 4.0538 | 4.0242 | 5.1789 | 5.085 | 4.9789 | 4.8575 | 4.7462 | 4.6391 | 4.4993 | 4.3462 | 4.233 | 4.0819 | 3.4411 | 3.1115 | 3.0554
|  | DALCHONZIE | HE |  |  |  |  | 5.0622 | 4.9917 | 4.9111 | 4.8081 | 4.7162 | 4.6142 | 4.4968 | 4.3754 | 4.2948 | 4.1785 | 3.5622 | 3.206 | 3.0632 | 5.2436 | 5.2028 | 5.1528 | 5.0905 | 5.0405 | 4.9773 | 4.9048 | 4.8211 | 4.7773 | 4.6946 | 4.314 | 4.0844 | 3.8834 | 5.1809 | 5.1207 | 5.0483 | 4.9554 | 4.8748 | 4.7799 | 4.6687 | 4.5513 | 4.4779 | 4.3656 | 3.7952 | 3.486 | 3.3687
|  | DALCHONZIE | CF |  |  |  |  | 5.0795 | 5.0417 | 4.9856 | 4.9346 | 4.8662 | 4.8193 | 4.7489 | 4.6662 | 4.6009 | 4.5611 | 4.1407 | 3.707 | 3.3632 | 5.2517 | 5.2252 | 5.1844 | 5.1497 | 5.1028 | 5.0711 | 5.0211 | 4.9558 | 4.9007 | 4.8701 | 4.5262 | 4.1466 | 3.6956 | 5.1983 | 5.1636 | 5.1105 | 5.0636 | 4.9962 | 4.9575 | 4.8911 | 4.8115 | 4.7462 | 4.7115 | 4.2983 | 3.9024 | 3.6095
| NAIRN | DALCROSS | MINIMUM HEADROOM | NH 76333 51847 | NO | YES | 4.775 | 6.7228 | 6.4218 | 6.0637 | 5.6422 | 5.1392 | 4.5198 | 3.9983 | 3.4494 | 2.931 | 2.7392 | 2.2004 | 2.0514 | 2.0024 | 7.1024 | 6.9534 | 6.779 | 6.5779 | 6.3504 | 6.0953 | 5.8637 | 5.5749 | 5.3198 | 5.1881 | 4.829 | 4.7034 | 4.4637 | 7.0417 | 6.7999 | 6.508 | 6.1591 | 5.7489 | 5.2591 | 4.8397 | 4.3938 | 3.9703 | 3.7846 | 3.2825 | 3.1458 | 3.104
|  | DALCROSS | EE |  |  |  |  | 6.7228 | 6.4218 | 6.0637 | 5.6422 | 5.1392 | 4.5616 | 4.1075 | 3.532 | 2.9932 | 2.7637 | 2.2004 | 2.0881 | 2.0626 | 7.1024 | 6.9534 | 6.779 | 6.5779 | 6.3504 | 6.0953 | 5.8637 | 5.5749 | 5.3198 | 5.1881 | 4.829 | 4.7034 | 4.5912 | 7.0417 | 6.7999 | 6.508 | 6.1591 | 5.7489 | 5.2733 | 4.8999 | 4.4233 | 3.9876 | 3.7846 | 3.2825 | 3.1774 | 3.154
|  | DALCROSS | HT |  |  |  |  | 6.7463 | 6.4473 | 6.0994 | 5.6932 | 5.1953 | 4.5198 | 3.9983 | 3.4494 | 2.931 | 2.7392 | 2.2779 | 2.0514 | 2.0024 | 7.1259 | 6.9769 | 6.8157 | 6.631 | 6.4096 | 6.1116 | 5.8698 | 5.6004 | 5.3432 | 5.233 | 4.9228 | 4.781 | 4.7514 | 7.0662 | 6.8254 | 6.5448 | 6.2121 | 5.808 | 5.2591 | 4.8397 | 4.3938 | 3.9703 | 3.8019 | 3.357 | 3.1458 | 3.104
|  | DALCROSS | HE |  |  |  |  | 6.7473 | 6.4606 | 6.13 | 5.7463 | 5.2534 | 4.6973 | 4.2912 | 3.7963 | 3.2932 | 3.1239 | 2.3208 | 2.183 | 2.1555 | 7.1228 | 6.983 | 6.8249 | 6.6504 | 6.4279 | 6.181 | 5.9871 | 5.7432 | 5.4892 | 5.3851 | 4.9045 | 4.7708 | 4.6596 | 7.0672 | 6.8376 | 6.5723 | 6.2621 | 5.8621 | 5.405 | 5.0764 | 4.6733 | 4.2621 | 4.1101 | 3.3989 | 3.2733 | 3.2478
|  | DALCROSS | CF |  |  |  |  | 6.8412 | 6.6555 | 6.3657 | 6.0259 | 5.6116 | 5.1351 | 4.7524 | 4.3688 | 3.9137 | 3.7361 | 3.0453 | 2.5381 | 2.182 | 7.1718 | 7.081 | 6.9402 | 6.7739 | 6.5902 | 6.3718 | 6.1861 | 5.9973 | 5.7769 | 5.679 | 5.2514 | 4.8514 | 4.4637 | 7.1387 | 6.9907 | 6.7631 | 6.4917 | 6.1601 | 5.7764 | 5.4723 | 5.1662 | 4.8009 | 4.6499 | 4.0427 | 3.5764 | 3.2591
| TAYNUILT | DALMALLY | MINIMUM HEADROOM | NN 15538 26930 | YES | YES | 0.003 | 0.81963 | 0.81044 | 0.80228 | 0.79412 | 0.78289 | 0.77065 | 0.76249 | 0.74514 | 0.72677 | 0.72881 | 0.7033 | 0.6982 | 0.69412 | 0.87983 | 0.87167 | 0.87167 | 0.86861 | 0.86044 | 0.85228 | 0.84514 | 0.83187 | 0.82167 | 0.82269 | 0.8033 | 0.78698 | 0.74922 | 0.86044 | 0.85126 | 0.8431 | 0.83596 | 0.82677 | 0.81249 | 0.80534 | 0.78902 | 0.77371 | 0.77473 | 0.74922 | 0.74412 | 0.74106
|  | DALMALLY | EE |  |  |  |  | 0.81963 | 0.81044 | 0.80228 | 0.79412 | 0.78289 | 0.77065 | 0.76249 | 0.74514 | 0.72677 | 0.72881 | 0.7033 | 0.6982 | 0.69514 | 0.88187 | 0.87881 | 0.87167 | 0.86861 | 0.86044 | 0.85228 | 0.84514 | 0.83187 | 0.82167 | 0.82269 | 0.8033 | 0.79412 | 0.77473 | 0.86044 | 0.85228 | 0.8431 | 0.83596 | 0.82677 | 0.81249 | 0.80534 | 0.78902 | 0.77371 | 0.77473 | 0.74922 | 0.74616 | 0.7431
|  | DALMALLY | HT |  |  |  |  | 0.82167 | 0.81044 | 0.8084 | 0.80126 | 0.79412 | 0.79004 | 0.78187 | 0.76861 | 0.76249 | 0.7482 | 0.71249 | 0.6982 | 0.69412 | 0.87983 | 0.87779 | 0.87677 | 0.87269 | 0.86963 | 0.86657 | 0.86044 | 0.8533 | 0.85024 | 0.84004 | 0.81657 | 0.8084 | 0.80636 | 0.86249 | 0.85126 | 0.85126 | 0.8431 | 0.83698 | 0.83187 | 0.82473 | 0.81147 | 0.8084 | 0.79412 | 0.75942 | 0.74412 | 0.74106
|  | DALMALLY | HE |  |  |  |  | 0.82167 | 0.81249 | 0.81044 | 0.80432 | 0.80126 | 0.79616 | 0.78698 | 0.77575 | 0.77269 | 0.76044 | 0.71555 | 0.70534 | 0.70432 | 0.87983 | 0.87779 | 0.87881 | 0.87269 | 0.87167 | 0.87065 | 0.86147 | 0.8533 | 0.85126 | 0.84514 | 0.81249 | 0.79718 | 0.78085 | 0.86249 | 0.85228 | 0.8533 | 0.84514 | 0.84208 | 0.838 | 0.82983 | 0.81861 | 0.81453 | 0.8033 | 0.76351 | 0.75228 | 0.75126
|  | DALMALLY | CF |  |  |  |  | 0.82167 | 0.81044 | 0.81555 | 0.80942 | 0.80636 | 0.7982 | 0.79514 | 0.78698 | 0.77881 | 0.76861 | 0.73596 | 0.71351 | 0.70432 | 0.87983 | 0.87167 | 0.88085 | 0.87881 | 0.87677 | 0.86759 | 0.86555 | 0.86147 | 0.8533 | 0.84616 | 0.81453 | 0.78698 | 0.74922 | 0.86249 | 0.85228 | 0.85636 | 0.85228 | 0.84922 | 0.84004 | 0.83698 | 0.82881 | 0.82167 | 0.81249 | 0.77983 | 0.75942 | 0.75024
| TAYNUILT | DALMALLY SCHOOL | MINIMUM HEADROOM | NN 17249 27128 | YES | YES | 2.298 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014
|  | DALMALLY SCHOOL | EE |  |  |  |  | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.5789 | -1.5789 | -1.5789 | -1.5789 | -1.5789 | -1.5789 | -1.5789 | -1.5789 | -1.5789 | -1.5789 | -1.5789 | -1.5789 | -1.5789 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014 | -1.6014
|  | DALMALLY SCHOOL | HT |  |  |  |  | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006
|  | DALMALLY SCHOOL | HE |  |  |  |  | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006
|  | DALMALLY SCHOOL | CF |  |  |  |  | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.6572 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.5847 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006 | -1.6006
| INVERNESS | DALNEIGH | MINIMUM HEADROOM | NH 65564 44955 | YES | NO | 0.119 | 6.3488 | 5.9253 | 5.4988 | 5.012 | 4.4978 | 4.2212 | 3.4569 | 2.6304 | 1.8182 | 1.0294 | -2.2767 | -3.9124 | -4.1665 | 6.879 | 6.6973 | 6.478 | 6.229 | 5.9606 | 5.8371 | 5.4698 | 5.0586 | 4.5647 | 4.0912 | 2.2453 | 1.1545 | -1.0333 | 3.2639 | 2.8322 | 2.3914 | 1.8731 | 1.2914 | 1.122 | 0.36694 | -0.47694 | -1.2851 | -2.0269 | -4.7912 | -6.2739 | -6.482
|  | DALNEIGH | EE |  |  |  |  | 6.3488 | 5.9253 | 5.4988 | 5.012 | 4.4978 | 4.2212 | 3.4569 | 2.6304 | 1.8182 | 1.0294 | -2.1063 | -3.3859 | -3.6931 | 6.879 | 6.6973 | 6.478 | 6.229 | 5.9606 | 5.8371 | 5.4698 | 5.0586 | 4.5647 | 4.0912 | 2.2453 | 1.1545 | -0.12306 | 3.2639 | 2.8322 | 2.3914 | 1.8731 | 1.2914 | 1.122 | 0.36694 | -0.47694 | -1.2851 | -2.0269 | -4.7596 | -5.7994 | -6.0902
|  | DALNEIGH | HT |  |  |  |  | 6.4253 | 6.0059 | 5.608 | 5.1835 | 4.7498 | 4.2569 | 3.4824 | 2.8967 | 2.1273 | 1.3437 | -2.2767 | -3.9124 | -4.1665 | 6.9484 | 6.7841 | 6.6065 | 6.4014 | 6.2024 | 5.9667 | 5.6229 | 5.3912 | 5.0463 | 4.6933 | 2.8647 | 2.0004 | 1.8678 | 3.4037 | 2.9884 | 2.5935 | 2.1557 | 1.7363 | 1.2465 | 0.5098 | 0.028163 | -0.69531 | -1.4392 | -4.7912 | -6.2739 | -6.482
|  | DALNEIGH | HE |  |  |  |  | 6.4396 | 6.2008 | 5.9927 | 5.7529 | 5.5151 | 5.2212 | 4.7008 | 4.359 | 3.8416 | 3.31 | 0.45694 | -1.4645 | -2.0573 | 6.9453 | 6.8239 | 6.7198 | 6.5739 | 6.431 | 6.2576 | 5.9841 | 5.8229 | 5.5422 | 5.2576 | 3.4269 | 2.032 | 0.70041 | 3.4139 | 3.1578 | 2.9261 | 2.6537 | 2.3986 | 2.0639 | 1.5322 | 1.3037 | 0.78531 | 0.25163 | -2.5035 | -4.1137 | -4.5963
|  | DALNEIGH | CF |  |  |  |  | 6.5182 | 6.408 | 6.2947 | 6.1682 | 6.0263 | 5.8988 | 5.7233 | 5.5018 | 5.2947 | 5.3182 | 3.711 | 1.3365 | -0.75327 | 6.9831 | 6.9086 | 6.8331 | 6.7463 | 6.6504 | 6.5514 | 6.4137 | 6.2433 | 6.081 | 6.0565 | 4.6902 | 2.2218 | -1.0333 | 3.5129 | 3.3751 | 3.2302 | 3.07 | 2.8567 | 2.6812 | 2.4404 | 2.1302 | 1.8424 | 2.0435 | 0.31796 | -1.8443 | -3.6116
| COUPAR ANGUS | DALRULZION | MINIMUM HEADROOM | NO 13498 58153 | NO | NO | 0.126 | 1.0163 | 0.96635 | 0.90818 | 0.83369 | 0.78165 | 0.70512 | 0.61533 | 0.5092 | 0.40512 | 0.36227 | 0.15716 | 0.090837 | 0.067367 | 2.0714 | 2.0408 | 2.0021 | 1.9572 | 1.9194 | 1.8694 | 1.8133 | 1.7449 | 1.6745 | 1.648 | 1.5041 | 1.4368 | 1.2398 | 1.6398 | 1.5919 | 1.5357 | 1.4663 | 1.4163 | 1.3408 | 1.2572 | 1.1531 | 1.0541 | 1.0133 | 0.81839 | 0.75614 | 0.73471
|  | DALRULZION | EE |  |  |  |  | 1.0163 | 0.96635 | 0.90818 | 0.83369 | 0.78165 | 0.70512 | 0.61533 | 0.5092 | 0.40512 | 0.36227 | 0.15716 | 0.11533 | 0.096959 | 2.0714 | 2.0408 | 2.0021 | 1.9572 | 1.9194 | 1.8694 | 1.8133 | 1.7449 | 1.6745 | 1.648 | 1.5041 | 1.4368 | 1.3419 | 1.6398 | 1.5919 | 1.5357 | 1.4663 | 1.4163 | 1.3408 | 1.2572 | 1.1531 | 1.0541 | 1.0133 | 0.81839 | 0.77859 | 0.76227
|  | DALRULZION | HT |  |  |  |  | 1.0459 | 1 | 0.94288 | 0.90104 | 0.8541 | 0.79288 | 0.71839 | 0.66329 | 0.58778 | 0.51635 | 0.22553 | 0.090837 | 0.067367 | 2.0929 | 2.0663 | 2.0317 | 2.0072 | 1.9806 | 1.9419 | 1.897 | 1.8623 | 1.8143 | 1.7704 | 1.5878 | 1.5051 | 1.4919 | 1.6684 | 1.6266 | 1.5694 | 1.5317 | 1.4857 | 1.4255 | 1.3551 | 1.3031 | 1.2296 | 1.1633 | 0.88369 | 0.75614 | 0.73471
|  | DALRULZION | HE |  |  |  |  | 1.0459 | 1.0092 | 0.96533 | 0.93165 | 0.89492 | 0.84492 | 0.77859 | 0.72349 | 0.65716 | 0.59186 | 0.23573 | 0.12145 | 0.070429 | 2.0929 | 2.0714 | 2.0388 | 2.0184 | 1.9919 | 1.9592 | 1.9163 | 1.8878 | 1.8408 | 1.7959 | 1.5786 | 1.4817 | 1.3868 | 1.6674 | 1.6327 | 1.5908 | 1.5602 | 1.5255 | 1.4745 | 1.4123 | 1.3704 | 1.3061 | 1.248 | 0.93369 | 0.83369 | 0.78471
|  | DALRULZION | CF |  |  |  |  | 1.0541 | 1.0184 | 0.98676 | 0.96022 | 0.92043 | 0.89186 | 0.84696 | 0.79594 | 0.77349 | 0.72451 | 0.47859 | 0.299 | 0.1439 | 2.098 | 2.0786 | 2.0551 | 2.0398 | 2.0123 | 1.9939 | 1.9592 | 1.9225 | 1.9041 | 1.8694 | 1.6704 | 1.4725 | 1.2398 | 1.6766 | 1.6398 | 1.6112 | 1.5868 | 1.549 | 1.5204 | 1.4786 | 1.4276 | 1.4082 | 1.3612 | 1.1235 | 0.95002 | 0.85002
| BOAT OF GARTEN | DALWHINNIE | MINIMUM HEADROOM | NN 63711 84671 | YES | YES | 0.872 | -0.11322 | -0.1326 | -0.15199 | -0.1775 | -0.21118 | -0.22036 | -0.25607 | -0.28669 | -0.32036 | -0.35199 | -0.42546 | -0.44689 | -0.45811 | 0.082702 | 0.069437 | 0.058212 | 0.036784 | 0.016376 | 0.011273 | -0.013216 | -0.031584 | -0.056073 | -0.074441 | -0.12648 | -0.14485 | -0.19893 | -0.017298 | -0.036686 | -0.054033 | -0.076482 | -0.10709 | -0.11832 | -0.15403 | -0.17852 | -0.2122 | -0.24281 | -0.31118 | -0.32954 | -0.34077
|  | DALWHINNIE | EE |  |  |  |  | -0.11322 | -0.1326 | -0.15199 | -0.1775 | -0.21118 | -0.22036 | -0.25607 | -0.28669 | -0.32036 | -0.35199 | -0.42546 | -0.43771 | -0.44281 | 0.082702 | 0.069437 | 0.058212 | 0.036784 | 0.016376 | 0.011273 | -0.013216 | -0.031584 | -0.056073 | -0.074441 | -0.12648 | -0.14485 | -0.16832 | -0.017298 | -0.036686 | -0.054033 | -0.076482 | -0.10709 | -0.11832 | -0.15403 | -0.17852 | -0.2122 | -0.24281 | -0.31118 | -0.32138 | -0.32648
|  | DALWHINNIE | HT |  |  |  |  | -0.10199 | -0.11934 | -0.13056 | -0.15301 | -0.16934 | -0.19179 | -0.21832 | -0.2326 | -0.26322 | -0.29077 | -0.39893 | -0.44689 | -0.45505 | 0.089845 | 0.079641 | 0.073518 | 0.060253 | 0.051069 | 0.035763 | 0.019437 | 0.010253 | -0.0081143 | -0.026482 | -0.09689 | -0.12852 | -0.1326 | -0.0081143 | -0.02342 | -0.034645 | -0.054033 | -0.069339 | -0.091788 | -0.11628 | -0.12852 | -0.15709 | -0.1826 | -0.28567 | -0.32954 | -0.33669
|  | DALWHINNIE | HE |  |  |  |  | -0.10403 | -0.11628 | -0.12546 | -0.14179 | -0.15505 | -0.17342 | -0.19893 | -0.21526 | -0.23873 | -0.26628 | -0.39587 | -0.43669 | -0.45811 | 0.089845 | 0.080661 | 0.075559 | 0.061273 | 0.054131 | 0.039845 | 0.024539 | 0.016376 | 4.898e-05 | -0.020359 | -0.10199 | -0.13567 | -0.15913 | -0.0091347 | -0.02138 | -0.029543 | -0.044849 | -0.057094 | -0.07342 | -0.09689 | -0.11424 | -0.13669 | -0.16118 | -0.2826 | -0.3224 | -0.34077
|  | DALWHINNIE | CF |  |  |  |  | -0.10811 | -0.1122 | -0.1224 | -0.13464 | -0.14587 | -0.15607 | -0.1724 | -0.19281 | -0.19689 | -0.21628 | -0.29689 | -0.37954 | -0.43056 | 0.086784 | 0.083722 | 0.074539 | 0.068416 | 0.060253 | 0.054131 | 0.039845 | 0.0276 | 0.021478 | 0.0092327 | -0.056073 | -0.13567 | -0.19893 | -0.013216 | -0.017298 | -0.026482 | -0.036686 | -0.048931 | -0.058114 | -0.07138 | -0.089747 | -0.095869 | -0.11118 | -0.19281 | -0.26934 | -0.31526
| WILLOWDALE | DENBURN | MINIMUM HEADROOM | NJ 93484 06342 | NO | NO | 0.585 | 7.126 | 6.9627 | 6.7801 | 6.5862 | 6.3719 | 6.1331 | 5.7046 | 5.1382 | 4.5852 | 4.024 | 1.2025 | -0.92707 | -1.3138 | 9.1331 | 9.0168 | 8.8821 | 8.7403 | 8.5811 | 8.3995 | 8.1893 | 7.9321 | 7.7015 | 7.4862 | 5.7556 | 3.7219 | -1.7536 | 8.8969 | 8.7449 | 8.5734 | 8.3908 | 8.1898 | 7.9622 | 7.6836 | 7.2173 | 6.7 | 6.2234 | 3.6683 | 1.7898 | 1.4459
|  | DENBURN | EE |  |  |  |  | 7.126 | 6.9627 | 6.7801 | 6.5862 | 6.3719 | 6.1331 | 5.7046 | 5.1382 | 4.5852 | 4.024 | 1.2025 | -0.68829 | -1.1812 | 9.1331 | 9.0168 | 8.8821 | 8.7403 | 8.5811 | 8.3995 | 8.1893 | 7.9321 | 7.7015 | 7.4862 | 5.7556 | 3.7219 | 1.0301 | 8.8969 | 8.7449 | 8.5734 | 8.3908 | 8.1898 | 7.9622 | 7.6836 | 7.2173 | 6.7 | 6.2234 | 3.6683 | 2.0041 | 1.5581
|  | DENBURN | HT |  |  |  |  | 7.2015 | 7.0688 | 6.9291 | 6.7709 | 6.6015 | 6.4076 | 6.0474 | 5.5352 | 5.027 | 4.5209 | 1.3413 | -0.92707 | -1.3138 | 9.1995 | 9.1097 | 9.0188 | 8.9107 | 8.7933 | 8.6566 | 8.4913 | 8.2903 | 8.0984 | 7.9066 | 6.9719 | 6.0382 | 5.8454 | 8.9683 | 8.8469 | 8.7163 | 8.5704 | 8.4112 | 8.2275 | 7.9867 | 7.6561 | 7.1959 | 6.7387 | 3.8367 | 1.7898 | 1.4459
|  | DENBURN | HE |  |  |  |  | 7.1954 | 7.077 | 6.9546 | 6.8168 | 6.6648 | 6.4882 | 6.2546 | 5.9729 | 5.6403 | 5.2535 | 2.8495 | 1.4291 | 0.8464 | 9.1882 | 9.0974 | 9.0025 | 8.8964 | 8.775 | 8.6331 | 8.4627 | 8.2515 | 8.0484 | 7.8423 | 6.7984 | 4.8382 | 2.1964 | 8.9632 | 8.852 | 8.7367 | 8.6071 | 8.4643 | 8.2959 | 8.0765 | 7.8132 | 7.4204 | 6.9428 | 4.4867 | 3.1326 | 2.5143
|  | DENBURN | CF |  |  |  |  | 7.2423 | 7.1842 | 7.1117 | 7.0352 | 6.9484 | 6.8546 | 6.7484 | 6.6076 | 6.4801 | 6.3372 | 5.2576 | 3.6505 | 2.3791 | 9.2209 | 9.1668 | 9.1035 | 9.0352 | 8.9586 | 8.8678 | 8.7678 | 8.6382 | 8.5158 | 8.3811 | 7.5209 | 4.0597 | -1.7536 | 9.0071 | 8.953 | 8.8857 | 8.8143 | 8.7306 | 8.6408 | 8.5387 | 8.4081 | 8.2847 | 8.151 | 6.8877 | 5.3622 | 4.1061
| TAYNUILT | DERVAIG | MINIMUM HEADROOM | NM 42441 51227 | YES | YES | 1.533 | 0.7321 | 0.68924 | 0.62802 | 0.54537 | 0.47802 | 0.38006 | 0.28312 | 0.11271 | -0.034224 | -0.12606 | -0.41484 | -0.49443 | -0.51178 | 1.1211 | 1.0997 | 1.0772 | 1.0364 | 1.0068 | 0.96292 | 0.87924 | 0.80169 | 0.71904 | 0.6568 | 0.44965 | 0.38741 | 0.18741 | 0.75618 | 0.70924 | 0.64904 | 0.56741 | 0.50618 | 0.41027 | 0.31537 | 0.15414 | 0.012306 | -0.069327 | -0.33769 | -0.41729 | -0.42953
|  | DERVAIG | EE |  |  |  |  | 0.7321 | 0.68924 | 0.62802 | 0.54537 | 0.47802 | 0.38006 | 0.28312 | 0.11271 | -0.034224 | -0.12606 | -0.41484 | -0.44749 | -0.47606 | 1.1211 | 1.0997 | 1.0772 | 1.0364 | 1.0068 | 0.96292 | 0.91904 | 0.80986 | 0.71904 | 0.6568 | 0.44965 | 0.38741 | 0.28231 | 0.75618 | 0.70924 | 0.64904 | 0.56741 | 0.50618 | 0.41027 | 0.31537 | 0.15414 | 0.012306 | -0.069327 | -0.33769 | -0.37137 | -0.39994
|  | DERVAIG | HT |  |  |  |  | 0.75761 | 0.71782 | 0.6668 | 0.59843 | 0.53924 | 0.45659 | 0.29027 | 0.17394 | 0.062714 | -0.030143 | -0.34137 | -0.49443 | -0.51178 | 1.1354 | 1.118 | 1.0935 | 1.067 | 1.0425 | 1.0048 | 0.87924 | 0.80169 | 0.73639 | 0.68639 | 0.53639 | 0.43639 | 0.42924 | 0.78169 | 0.74598 | 0.68986 | 0.63067 | 0.57455 | 0.49598 | 0.34088 | 0.23578 | 0.12761 | 0.038837 | -0.27035 | -0.41729 | -0.42953
|  | DERVAIG | HE |  |  |  |  | 0.75761 | 0.72598 | 0.6872 | 0.6372 | 0.59231 | 0.51476 | 0.44027 | 0.32394 | 0.21373 | 0.11884 | -0.27198 | -0.36688 | -0.38116 | 1.1333 | 1.119 | 1.1007 | 1.0752 | 1.0527 | 1.019 | 0.98435 | 0.89557 | 0.82006 | 0.75884 | 0.52006 | 0.43231 | 0.34455 | 0.78169 | 0.75312 | 0.70924 | 0.66333 | 0.61945 | 0.547 | 0.47659 | 0.37251 | 0.26639 | 0.17455 | -0.1979 | -0.28565 | -0.2979
|  | DERVAIG | CF |  |  |  |  | 0.7668 | 0.73516 | 0.70557 | 0.67598 | 0.63822 | 0.60047 | 0.55761 | 0.49741 | 0.44129 | 0.36271 | 0.00046939 | -0.25361 | -0.38831 | 1.1364 | 1.1241 | 1.1068 | 1.0925 | 1.0701 | 1.0517 | 1.0272 | 0.99557 | 0.95476 | 0.90476 | 0.65578 | 0.41496 | 0.18741 | 0.79088 | 0.76537 | 0.73476 | 0.70516 | 0.66639 | 0.62863 | 0.58578 | 0.52863 | 0.47965 | 0.40822 | 0.057204 | -0.18769 | -0.31014
| BEAULY | DINGWALL | MINIMUM HEADROOM | NH 53956 59680 | NO | NO | 0 | 6 | 5.8112 | 5.5867 | 5.298 | 4.851 | 4.352 | 3.7367 | 3.3041 | 2.751 | 2.1663 | 0.17245 | -1.0449 | -1.3143 | 8.3765 | 8.2704 | 8.15 | 8.0276 | 7.8184 | 7.5408 | 7.2255 | 7.0571 | 6.7378 | 6.4378 | 5.3082 | 4.5694 | 3.602 | 6.9862 | 6.7219 | 6.426 | 6.1179 | 5.7342 | 5.2709 | 4.7046 | 4.4046 | 3.8383 | 3.3077 | 1.5179 | 0.46071 | 0.24133
|  | DINGWALL | EE |  |  |  |  | 6 | 5.8112 | 5.5867 | 5.298 | 4.851 | 4.352 | 3.7367 | 3.3806 | 2.7551 | 2.1663 | 0.17245 | -0.86735 | -1.1306 | 8.3765 | 8.2704 | 8.15 | 8.0276 | 7.8184 | 7.5408 | 7.2255 | 7.0571 | 6.7378 | 6.4378 | 5.3082 | 4.5694 | 3.8837 | 6.9862 | 6.7219 | 6.426 | 6.1179 | 5.7342 | 5.2709 | 4.7046 | 4.4046 | 3.8383 | 3.3077 | 1.5179 | 0.64847 | 0.39541
|  | DINGWALL | HT |  |  |  |  | 6.0735 | 5.9173 | 5.7255 | 5.4204 | 5.0051 | 4.4622 | 3.8918 | 3.3041 | 2.751 | 2.1857 | 0.20612 | -1.0449 | -1.3143 | 8.4214 | 8.3418 | 8.2398 | 8.1398 | 8 | 7.7204 | 7.449 | 7.1469 | 6.8633 | 6.5714 | 5.6214 | 5.0265 | 4.848 | 7.0597 | 6.8219 | 6.5505 | 6.276 | 5.927 | 5.4862 | 5.0056 | 4.4454 | 3.9158 | 3.3709 | 1.5801 | 0.46071 | 0.24133
|  | DINGWALL | HE |  |  |  |  | 6.0694 | 5.9327 | 5.7704 | 5.6041 | 5.3378 | 5.0347 | 4.7153 | 4.2929 | 3.8796 | 3.4296 | 1.3439 | 0.2051 | -0.27857 | 8.4173 | 8.349 | 8.2612 | 8.1745 | 8.048 | 7.902 | 7.7235 | 7.4745 | 7.2296 | 6.951 | 5.6888 | 5.0531 | 4.3092 | 7.0566 | 6.8832 | 6.6852 | 6.4801 | 6.1985 | 5.8781 | 5.5311 | 5.1117 | 4.7056 | 4.2893 | 2.3209 | 1.2964 | 0.85663
|  | DINGWALL | CF |  |  |  |  | 6.1224 | 6.048 | 5.9378 | 5.8204 | 5.6745 | 5.4418 | 5.2459 | 5.099 | 4.8776 | 4.649 | 3.4265 | 1.9653 | 0.62857 | 8.4378 | 8.3908 | 8.3184 | 8.2429 | 8.151 | 8.0378 | 7.9378 | 7.8439 | 7.6827 | 7.5133 | 6.6316 | 5.3255 | 3.602 | 7.1209 | 7.023 | 6.8934 | 6.7474 | 6.5719 | 6.3577 | 6.175 | 5.9954 | 5.7832 | 5.5587 | 4.2587 | 2.8689 | 1.6587
| CARRADALE 1 | DIPPEN | MINIMUM HEADROOM | NR 80026 37592 | YES | YES | 1.885 | -0.50151 | -0.52498 | -0.55865 | -0.58212 | -0.61886 | -0.65049 | -0.69947 | -0.75151 | -0.77906 | -0.81886 | -0.93212 | -0.96478 | -0.97396 | -0.29845 | -0.31171 | -0.3311 | -0.34641 | -0.36988 | -0.38824 | -0.4209 | -0.45559 | -0.46988 | -0.49641 | -0.5709 | -0.60865 | -0.74335 | -0.37804 | -0.39947 | -0.43212 | -0.45457 | -0.49029 | -0.51784 | -0.56376 | -0.61478 | -0.63824 | -0.67498 | -0.77906 | -0.80967 | -0.8158
|  | DIPPEN | EE |  |  |  |  | -0.50151 | -0.52498 | -0.55865 | -0.58212 | -0.61886 | -0.65049 | -0.69947 | -0.75151 | -0.77906 | -0.81886 | -0.93212 | -0.95151 | -0.95865 | -0.29845 | -0.31171 | -0.3311 | -0.34641 | -0.36988 | -0.38824 | -0.4209 | -0.45559 | -0.46988 | -0.49641 | -0.5709 | -0.60865 | -0.66682 | -0.37804 | -0.39947 | -0.43212 | -0.45457 | -0.49029 | -0.51784 | -0.56376 | -0.61478 | -0.63824 | -0.67498 | -0.77906 | -0.79641 | -0.80253
|  | DIPPEN | HT |  |  |  |  | -0.49029 | -0.50763 | -0.5362 | -0.56376 | -0.59539 | -0.61886 | -0.65253 | -0.68212 | -0.72294 | -0.76376 | -0.91273 | -0.96478 | -0.97396 | -0.29335 | -0.30355 | -0.31478 | -0.33008 | -0.34845 | -0.35865 | -0.37804 | -0.39437 | -0.41886 | -0.44539 | -0.54233 | -0.57192 | -0.576 | -0.36886 | -0.38416 | -0.40967 | -0.43416 | -0.46478 | -0.48518 | -0.51784 | -0.54539 | -0.5811 | -0.6209 | -0.75967 | -0.80967 | -0.8158
|  | DIPPEN | HE |  |  |  |  | -0.48927 | -0.50253 | -0.526 | -0.54743 | -0.57396 | -0.59131 | -0.62498 | -0.66171 | -0.68824 | -0.72498 | -0.89029 | -0.92702 | -0.93008 | -0.29335 | -0.29947 | -0.31273 | -0.326 | -0.34131 | -0.34947 | -0.37192 | -0.39233 | -0.41069 | -0.43212 | -0.53927 | -0.59029 | -0.64641 | -0.36784 | -0.37804 | -0.40151 | -0.41988 | -0.44539 | -0.46069 | -0.49233 | -0.52498 | -0.55151 | -0.58518 | -0.7362 | -0.77294 | -0.77498
|  | DIPPEN | CF |  |  |  |  | -0.48314 | -0.49845 | -0.51376 | -0.53008 | -0.54539 | -0.56478 | -0.576 | -0.60253 | -0.6209 | -0.63722 | -0.74845 | -0.86988 | -0.92294 | -0.29029 | -0.29743 | -0.30763 | -0.31682 | -0.32498 | -0.33824 | -0.34845 | -0.36478 | -0.37804 | -0.39029 | -0.47906 | -0.60661 | -0.74335 | -0.36273 | -0.37702 | -0.38927 | -0.40559 | -0.41886 | -0.43722 | -0.44743 | -0.47294 | -0.49131 | -0.50457 | -0.60763 | -0.7209 | -0.76886
| BRORA | DORNOCH | MINIMUM HEADROOM | NH 79721 89953 | YES | NO | 0.265 | 0.63102 | 0.5249 | 0.40245 | 0.26673 | 0.15143 | 0.002449 | -0.19143 | -0.4149 | -0.66694 | -0.85061 | -1.3078 | -1.4822 | -1.5333 | 1.8271 | 1.7639 | 1.6853 | 1.5955 | 1.5271 | 1.4312 | 1.3098 | 1.1802 | 1.0282 | 0.91286 | 0.60061 | 0.46388 | 0.056735 | 1.1357 | 1.0551 | 0.9551 | 0.82041 | 0.71224 | 0.56327 | 0.37653 | 0.17143 | -0.065306 | -0.23878 | -0.6602 | -0.81633 | -0.8602
|  | DORNOCH | EE |  |  |  |  | 0.63102 | 0.5249 | 0.40245 | 0.26673 | 0.15143 | 0.002449 | -0.19143 | -0.4149 | -0.66694 | -0.85061 | -1.3078 | -1.4027 | -1.4455 | 1.8271 | 1.7639 | 1.6853 | 1.5955 | 1.5271 | 1.4312 | 1.3098 | 1.1802 | 1.0282 | 0.91286 | 0.60061 | 0.46388 | 0.26082 | 1.1357 | 1.0551 | 0.9551 | 0.82041 | 0.71224 | 0.56327 | 0.37653 | 0.17143 | -0.065306 | -0.23878 | -0.6602 | -0.7449 | -0.78469
|  | DORNOCH | HT |  |  |  |  | 0.65143 | 0.57082 | 0.46673 | 0.37184 | 0.26061 | 0.090204 | -0.11184 | -0.24041 | -0.39041 | -0.54959 | -1.1822 | -1.4822 | -1.5333 | 1.8588 | 1.8088 | 1.7516 | 1.6996 | 1.6363 | 1.5384 | 1.4271 | 1.3557 | 1.2608 | 1.1629 | 0.76286 | 0.59245 | 0.5649 | 1.1582 | 1.0827 | 1.001 | 0.92551 | 0.83163 | 0.67653 | 0.49286 | 0.37551 | 0.22959 | 0.071429 | -0.54082 | -0.81633 | -0.8602
|  | DORNOCH | HE |  |  |  |  | 0.65041 | 0.59531 | 0.52286 | 0.45551 | 0.37388 | 0.28 | 0.16061 | 0.03102 | -0.11898 | -0.27816 | -1.0343 | -1.2373 | -1.2802 | 1.8567 | 1.8139 | 1.7659 | 1.7231 | 1.668 | 1.6037 | 1.522 | 1.4496 | 1.3527 | 1.2516 | 0.77306 | 0.56898 | 0.37102 | 1.1571 | 1.1051 | 1.049 | 0.9949 | 0.92959 | 0.83571 | 0.71735 | 0.60306 | 0.45714 | 0.3051 | -0.40102 | -0.58673 | -0.62449
|  | DORNOCH | CF |  |  |  |  | 0.65755 | 0.61571 | 0.55959 | 0.48816 | 0.43204 | 0.36061 | 0.28102 | 0.19122 | 0.10959 | 0.0085714 | -0.50367 | -0.96694 | -1.2057 | 1.869 | 1.8343 | 1.7945 | 1.7445 | 1.7098 | 1.6608 | 1.6006 | 1.5302 | 1.4822 | 1.4057 | 1.0139 | 0.54959 | 0.056735 | 1.1653 | 1.1214 | 1.0714 | 1.0184 | 0.97041 | 0.91531 | 0.84592 | 0.75408 | 0.68776 | 0.59082 | 0.09898 | -0.33571 | -0.56224
| CLACHAN | DOUGLAS PIER | MINIMUM HEADROOM | NS 19396 99616 | YES | YES | 0.25 | -0.0073469 | -0.0063265 | -0.019592 | -0.030816 | -0.052245 | -0.074694 | -0.11143 | -0.15837 | -0.18694 | -0.22367 | -0.31449 | -0.34816 | -0.35429 | 0.27429 | 0.28143 | 0.26612 | 0.25082 | 0.22735 | 0.21408 | 0.18857 | 0.15796 | 0.13857 | 0.11612 | 0.045714 | 0.014082 | -0.073673 | 0.2049 | 0.18653 | 0.16 | 0.13551 | 0.10388 | 0.08551 | 0.047755 | 0.004898 | -0.023673 | -0.057347 | -0.14306 | -0.17571 | -0.18082
|  | DOUGLAS PIER | EE |  |  |  |  | 0.00081633 | -0.0063265 | -0.019592 | -0.030816 | -0.052245 | -0.074694 | -0.11143 | -0.15837 | -0.18694 | -0.22367 | -0.31449 | -0.33082 | -0.34306 | 0.28755 | 0.28143 | 0.26612 | 0.25082 | 0.22735 | 0.21408 | 0.18857 | 0.15796 | 0.13857 | 0.11612 | 0.045714 | 0.014082 | -0.035918 | 0.2049 | 0.18653 | 0.16 | 0.13551 | 0.10388 | 0.08551 | 0.047755 | 0.004898 | -0.023673 | -0.057347 | -0.14306 | -0.16041 | -0.17061
|  | DOUGLAS PIER | HT |  |  |  |  | 0.004898 | -0.0012245 | -0.010408 | -0.018571 | -0.029796 | -0.04102 | -0.070612 | -0.10531 | -0.12367 | -0.15633 | -0.28592 | -0.34816 | -0.35429 | 0.28857 | 0.28653 | 0.27939 | 0.2702 | 0.2549 | 0.24265 | 0.22224 | 0.1998 | 0.18959 | 0.16714 | 0.082449 | 0.044694 | 0.041633 | 0.21 | 0.19878 | 0.17837 | 0.16 | 0.13653 | 0.11714 | 0.087551 | 0.051837 | 0.037551 | 0.0038776 | -0.11653 | -0.17571 | -0.18082
|  | DOUGLAS PIER | HE |  |  |  |  | 0.004898 | -0.00020408 | -0.0083673 | -0.01551 | -0.024694 | -0.031837 | -0.046122 | -0.071633 | -0.085918 | -0.11245 | -0.24714 | -0.28898 | -0.2951 | 0.28857 | 0.28653 | 0.28143 | 0.27429 | 0.26204 | 0.25082 | 0.23449 | 0.21306 | 0.20388 | 0.18551 | 0.090612 | 0.042653 | 0.00081633 | 0.21102 | 0.20286 | 0.18755 | 0.17327 | 0.1549 | 0.14163 | 0.1151 | 0.08551 | 0.073265 | 0.047755 | -0.081837 | -0.12163 | -0.12776
|  | DOUGLAS PIER | CF |  |  |  |  | -0.0073469 | 0.0038776 | -0.00020408 | -0.0053061 | -0.010408 | -0.017551 | -0.023673 | -0.032857 | -0.051224 | -0.071633 | -0.14918 | -0.23592 | -0.28592 | 0.27429 | 0.28959 | 0.28551 | 0.28245 | 0.27327 | 0.26204 | 0.25388 | 0.23551 | 0.22429 | 0.20796 | 0.13653 | 0.037551 | -0.073673 | 0.21306 | 0.20796 | 0.19673 | 0.18755 | 0.17224 | 0.15796 | 0.14571 | 0.12633 | 0.10898 | 0.087551 | 0.015102 | -0.071633 | -0.11959
| ARDMORE | DRIMORE | MINIMUM HEADROOM | NF 77377 40049 | YES | YES | 0.104 | 1.1448 | 1.1122 | 1.0775 | 1.0428 | 0.99382 | 0.94586 | 0.90811 | 0.84382 | 0.79076 | 0.7377 | 0.62239 | 0.5979 | 0.5877 | 1.7979 | 1.7775 | 1.7581 | 1.7326 | 1.701 | 1.6652 | 1.6448 | 1.601 | 1.5673 | 1.5326 | 1.4652 | 1.4561 | 1.4489 | 1.353 | 1.3336 | 1.3132 | 1.2928 | 1.2652 | 1.2387 | 1.2152 | 1.1785 | 1.151 | 1.1214 | 1.0316 | 1.0081 | 0.99076
|  | DRIMORE | EE |  |  |  |  | 1.1448 | 1.1122 | 1.0775 | 1.0428 | 0.99382 | 0.94586 | 0.90811 | 0.84382 | 0.79076 | 0.7377 | 0.62239 | 0.60504 | 0.59484 | 1.7979 | 1.7775 | 1.7581 | 1.7326 | 1.701 | 1.6652 | 1.6448 | 1.601 | 1.5673 | 1.5326 | 1.4652 | 1.4561 | 1.4489 | 1.353 | 1.3336 | 1.3132 | 1.2928 | 1.2652 | 1.2387 | 1.2152 | 1.1785 | 1.151 | 1.1214 | 1.0316 | 1.0152 | 1.0061
|  | DRIMORE | HT |  |  |  |  | 1.1652 | 1.1377 | 1.1081 | 1.0734 | 1.0459 | 1.0091 | 0.97545 | 0.92443 | 0.87851 | 0.85198 | 0.67341 | 0.5979 | 0.5877 | 1.8142 | 1.801 | 1.7826 | 1.7612 | 1.7469 | 1.7214 | 1.701 | 1.6673 | 1.6367 | 1.6275 | 1.4999 | 1.4561 | 1.4499 | 1.3642 | 1.3479 | 1.3306 | 1.3122 | 1.2959 | 1.2724 | 1.252 | 1.2234 | 1.1989 | 1.1775 | 1.0704 | 1.0112 | 1.003
|  | DRIMORE | HE |  |  |  |  | 1.1673 | 1.1448 | 1.1214 | 1.0938 | 1.0744 | 1.0448 | 1.0173 | 0.97545 | 0.93158 | 0.90913 | 0.69892 | 0.64586 | 0.64178 | 1.8163 | 1.804 | 1.7897 | 1.7714 | 1.7601 | 1.7387 | 1.7224 | 1.6908 | 1.6622 | 1.653 | 1.5214 | 1.4908 | 1.4867 | 1.3632 | 1.3499 | 1.3346 | 1.3173 | 1.304 | 1.2836 | 1.2652 | 1.2336 | 1.2061 | 1.1857 | 1.0499 | 1.0081 | 0.99076
|  | DRIMORE | CF |  |  |  |  | 1.1683 | 1.151 | 1.1316 | 1.1112 | 1.0836 | 1.0704 | 1.0428 | 1.0224 | 0.9928 | 0.96627 | 0.8326 | 0.71015 | 0.64586 | 1.8173 | 1.8071 | 1.7948 | 1.7816 | 1.7632 | 1.7571 | 1.7377 | 1.7255 | 1.705 | 1.6836 | 1.5959 | 1.5132 | 1.4846 | 1.3673 | 1.3561 | 1.3459 | 1.3367 | 1.3214 | 1.3112 | 1.2959 | 1.2806 | 1.2652 | 1.2479 | 1.154 | 1.0714 | 1.0081
| CEANNACROC | DRUMNADROCHIT | MINIMUM HEADROOM | NH 50306 29824 | YES | NO | 1.47 | 2.263 | 2.2109 | 2.1405 | 2.0752 | 2.0007 | 1.8824 | 1.7762 | 1.615 | 1.465 | 1.3303 | 1.0783 | 0.97216 | 0.94052 | 3.3711 | 3.3487 | 3.3068 | 3.2579 | 3.1875 | 3.1109 | 3.0466 | 2.9415 | 2.8436 | 2.7579 | 2.5824 | 2.4854 | 2.1803 | 3.0487 | 2.9711 | 2.8711 | 2.7946 | 2.6926 | 2.5773 | 2.4824 | 2.3293 | 2.1854 | 2.0589 | 1.8252 | 1.7273 | 1.6987
|  | DRUMNADROCHIT | EE |  |  |  |  | 2.263 | 2.2109 | 2.1405 | 2.0752 | 2.0007 | 1.8824 | 1.7762 | 1.615 | 1.465 | 1.3303 | 1.0783 | 1.0262 | 0.9946 | 3.3711 | 3.3487 | 3.3068 | 3.2579 | 3.1875 | 3.1109 | 3.0466 | 2.9415 | 2.8436 | 2.7579 | 2.5824 | 2.4854 | 2.3385 | 3.0487 | 2.9711 | 2.8711 | 2.7946 | 2.6926 | 2.5773 | 2.4824 | 2.3293 | 2.1854 | 2.0589 | 1.8252 | 1.7762 | 1.7466
|  | DRUMNADROCHIT | HT |  |  |  |  | 2.2824 | 2.2405 | 2.1854 | 2.1283 | 2.0691 | 2.0007 | 1.9222 | 1.8109 | 1.7324 | 1.6181 | 1.1171 | 0.97216 | 0.94052 | 3.3824 | 3.3671 | 3.3466 | 3.3252 | 3.2946 | 3.2375 | 3.1752 | 3.0987 | 3.0548 | 2.9824 | 2.6609 | 2.5813 | 2.563 | 3.0895 | 3.0293 | 2.9507 | 2.8813 | 2.8181 | 2.7303 | 2.6385 | 2.5201 | 2.4466 | 2.3395 | 1.8589 | 1.7273 | 1.6987
|  | DRUMNADROCHIT | HE |  |  |  |  | 2.2803 | 2.2436 | 2.2038 | 2.1579 | 2.1099 | 2.0538 | 1.9813 | 1.8977 | 1.815 | 1.7528 | 1.1977 | 1.1293 | 1.1068 | 3.3813 | 3.3671 | 3.3487 | 3.3303 | 3.3099 | 3.2589 | 3.2028 | 3.1313 | 3.063 | 3.0222 | 2.6568 | 2.5568 | 2.4232 | 3.0885 | 3.0415 | 2.9742 | 2.9191 | 2.8732 | 2.8017 | 2.7211 | 2.6171 | 2.5181 | 2.4609 | 1.9385 | 1.8742 | 1.8548
|  | DRUMNADROCHIT | CF |  |  |  |  | 2.2936 | 2.2671 | 2.2405 | 2.2099 | 2.1681 | 2.1354 | 2.0895 | 2.0334 | 1.964 | 1.8915 | 1.5456 | 1.2732 | 1.1181 | 3.3854 | 3.3752 | 3.364 | 3.3517 | 3.3232 | 3.3017 | 3.2558 | 3.2038 | 3.1517 | 3.0966 | 2.8201 | 2.5171 | 2.1803 | 3.0905 | 3.0436 | 3.0028 | 2.9589 | 2.8977 | 2.8609 | 2.7987 | 2.7324 | 2.663 | 2.5915 | 2.2609 | 2.0038 | 1.863
| GRUDIE BRIDGE | DRUMRUNIE | MINIMUM HEADROOM | NC 16664 05298 | YES | NO | 0 | 0.11967 | 0.11457 | 0.10743 | 0.10029 | 0.093143 | 0.079878 | 0.062531 | 0.053347 | 0.036 | 0.022735 | -0.01298 | -0.023184 | -0.025224 | 0.13637 | 0.13331 | 0.13331 | 0.12718 | 0.1231 | 0.11596 | 0.10473 | 0.099633 | 0.087388 | 0.079224 | 0.055755 | 0.052694 | 0.041469 | 0.12292 | 0.11782 | 0.11169 | 0.10047 | 0.094347 | 0.083122 | 0.067816 | 0.058633 | 0.042306 | 0.029041 | -0.0046327 | -0.013816 | -0.014837
|  | DRUMRUNIE | EE |  |  |  |  | 0.11967 | 0.11559 | 0.10743 | 0.10029 | 0.093143 | 0.079878 | 0.062531 | 0.053347 | 0.036 | 0.022735 | -0.01298 | -0.016041 | -0.020122 | 0.13637 | 0.13841 | 0.13331 | 0.12718 | 0.1231 | 0.11596 | 0.10473 | 0.099633 | 0.087388 | 0.079224 | 0.055755 | 0.052694 | 0.041469 | 0.12292 | 0.11782 | 0.11169 | 0.10047 | 0.094347 | 0.083122 | 0.067816 | 0.058633 | 0.042306 | 0.029041 | -0.0046327 | -0.0076939 | -0.010755
|  | DRUMRUNIE | HT |  |  |  |  | 0.12784 | 0.11457 | 0.11049 | 0.10845 | 0.10131 | 0.094163 | 0.08702 | 0.072735 | 0.06049 | 0.048245 | -0.00073469 | -0.023184 | -0.025224 | 0.14453 | 0.13331 | 0.13433 | 0.13535 | 0.13024 | 0.12616 | 0.12208 | 0.11392 | 0.10678 | 0.097592 | 0.064939 | 0.052694 | 0.050653 | 0.13108 | 0.11884 | 0.11271 | 0.10965 | 0.10353 | 0.097408 | 0.091286 | 0.077 | 0.065776 | 0.055571 | 0.0076122 | -0.013816 | -0.014837
|  | DRUMRUNIE | HE |  |  |  |  | 0.12784 | 0.11763 | 0.11355 | 0.11151 | 0.10539 | 0.10437 | 0.091102 | 0.08498 | 0.074776 | 0.06151 | 0.01049 | -0.0048163 | -0.008898 | 0.14453 | 0.13535 | 0.13535 | 0.13637 | 0.13229 | 0.13127 | 0.1231 | 0.11698 | 0.11392 | 0.10473 | 0.072082 | 0.059837 | 0.050653 | 0.13108 | 0.12088 | 0.11578 | 0.11373 | 0.10965 | 0.10659 | 0.092306 | 0.087204 | 0.081082 | 0.065776 | 0.018837 | 0.0035306 | 0.00046939
|  | DRUMRUNIE | CF |  |  |  |  | 0.13702 | 0.12478 | 0.11661 | 0.12069 | 0.11049 | 0.10641 | 0.10437 | 0.095184 | 0.092122 | 0.081918 | 0.050286 | 0.014571 | -0.0027755 | 0.15269 | 0.14351 | 0.13535 | 0.14147 | 0.13637 | 0.13331 | 0.13229 | 0.12514 | 0.12514 | 0.11596 | 0.09249 | 0.064939 | 0.044531 | 0.14027 | 0.12904 | 0.11986 | 0.1219 | 0.11271 | 0.11067 | 0.10761 | 0.098429 | 0.097408 | 0.087204 | 0.054551 | 0.020878 | 0.0055714
| STRATHLEVEN | DRYMEN | MINIMUM HEADROOM | NS 48494 88026 | YES | YES | 0.992 | -2.2442 | -2.3299 | -2.4401 | -2.534 | -2.6483 | -2.7738 | -2.9013 | -3.0819 | -3.2574 | -3.4085 | -3.8666 | -4.1881 | -4.3054 | -1.2534 | -1.3044 | -1.3728 | -1.4289 | -1.5023 | -1.5809 | -1.6534 | -1.7656 | -1.8707 | -1.9585 | -2.2248 | -2.4095 | -2.7034 | -1.7166 | -1.7972 | -1.9003 | -1.987 | -2.0932 | -2.2146 | -2.3279 | -2.4962 | -2.6615 | -2.8023 | -3.187 | -3.4442 | -3.535
|  | DRYMEN | EE |  |  |  |  | -2.2442 | -2.3299 | -2.4401 | -2.534 | -2.6483 | -2.7738 | -2.9013 | -3.0819 | -3.2574 | -3.4085 | -3.8666 | -4.1248 | -4.237 | -1.2534 | -1.3044 | -1.3728 | -1.4289 | -1.5023 | -1.5809 | -1.6534 | -1.7656 | -1.8707 | -1.9585 | -2.2248 | -2.4095 | -2.6034 | -1.7166 | -1.7972 | -1.9003 | -1.987 | -2.0932 | -2.2146 | -2.3279 | -2.4962 | -2.6615 | -2.8023 | -3.187 | -3.3962 | -3.483
|  | DRYMEN | HT |  |  |  |  | -2.2064 | -2.284 | -2.3707 | -2.4687 | -2.5554 | -2.6605 | -2.7972 | -2.9503 | -3.0687 | -3.2166 | -3.8462 | -4.1881 | -4.3054 | -1.2207 | -1.2605 | -1.3074 | -1.3605 | -1.4115 | -1.4748 | -1.5472 | -1.636 | -1.6972 | -1.7809 | -2.1319 | -2.3074 | -2.3687 | -1.6768 | -1.7462 | -1.8228 | -1.9136 | -1.9891 | -2.087 | -2.2074 | -2.3523 | -2.4534 | -2.5911 | -3.1564 | -3.4442 | -3.535
|  | DRYMEN | HE |  |  |  |  | -2.2074 | -2.2585 | -2.3176 | -2.3881 | -2.4493 | -2.5299 | -2.634 | -2.7574 | -2.8421 | -2.9625 | -3.5768 | -3.9136 | -4.0697 | -1.2238 | -1.2585 | -1.2942 | -1.3411 | -1.3799 | -1.4319 | -1.4972 | -1.5768 | -1.6268 | -1.7003 | -2.0921 | -2.3268 | -2.534 | -1.6779 | -1.7258 | -1.7799 | -1.8483 | -1.9034 | -1.9779 | -2.0758 | -2.1911 | -2.2666 | -2.3768 | -2.934 | -3.2156 | -3.3401
|  | DRYMEN | CF |  |  |  |  | -2.1952 | -2.2391 | -2.2819 | -2.3289 | -2.387 | -2.4319 | -2.4993 | -2.5646 | -2.6381 | -2.7166 | -3.1238 | -3.5299 | -3.8442 | -1.2176 | -1.2472 | -1.2779 | -1.3095 | -1.3483 | -1.383 | -1.4299 | -1.4819 | -1.535 | -1.5921 | -1.8983 | -2.2748 | -2.7034 | -1.6656 | -1.7105 | -1.7472 | -1.7911 | -1.8483 | -1.886 | -1.9493 | -2.0136 | -2.084 | -2.1544 | -2.5299 | -2.8983 | -3.1585
| DUNVEGAN | DRYNOCH | MINIMUM HEADROOM | NG 41080 31292 | YES | NO | 0.371 | 1.0972 | 1.035 | 0.96047 | 0.86965 | 0.8074 | 0.72067 | 0.60638 | 0.47169 | 0.39312 | 0.28496 | 0.012506 | -0.079331 | -0.11096 | 1.2946 | 1.2651 | 1.2202 | 1.16 | 1.1191 | 1.062 | 0.98649 | 0.89261 | 0.84465 | 0.77526 | 0.58342 | 0.50996 | 0.24057 | 1.201 | 1.1429 | 1.0735 | 0.98776 | 0.9296 | 0.84592 | 0.73674 | 0.60919 | 0.5347 | 0.4347 | 0.17654 | 0.08572 | 0.056129
|  | DRYNOCH | EE |  |  |  |  | 1.0972 | 1.035 | 0.96047 | 0.86965 | 0.8074 | 0.72067 | 0.60638 | 0.47169 | 0.39312 | 0.28496 | 0.012506 | -0.045657 | -0.070147 | 1.2946 | 1.2651 | 1.2202 | 1.16 | 1.1191 | 1.062 | 0.98649 | 0.89261 | 0.84465 | 0.77526 | 0.58342 | 0.50996 | 0.38444 | 1.201 | 1.1429 | 1.0735 | 0.98776 | 0.9296 | 0.84592 | 0.73674 | 0.60919 | 0.5347 | 0.4347 | 0.17654 | 0.12041 | 0.094904
|  | DRYNOCH | HT |  |  |  |  | 1.1329 | 1.0737 | 1.0186 | 0.94822 | 0.88802 | 0.80842 | 0.7421 | 0.64414 | 0.55842 | 0.45944 | 0.092098 | -0.079331 | -0.11096 | 1.3079 | 1.2814 | 1.2538 | 1.2222 | 1.1875 | 1.1344 | 1.0998 | 1.0344 | 0.97934 | 0.91404 | 0.67016 | 0.56812 | 0.54669 | 1.2265 | 1.1765 | 1.1255 | 1.0653 | 1.0102 | 0.93164 | 0.8745 | 0.7796 | 0.6949 | 0.60307 | 0.24899 | 0.08572 | 0.056129
|  | DRYNOCH | HE |  |  |  |  | 1.1319 | 1.085 | 1.0452 | 0.98802 | 0.93802 | 0.87271 | 0.81863 | 0.73087 | 0.65434 | 0.56761 | 0.15026 | 0.040057 | -0.0048408 | 1.3079 | 1.2814 | 1.2569 | 1.2263 | 1.1957 | 1.1559 | 1.114 | 1.0569 | 1.0028 | 0.94567 | 0.67628 | 0.57118 | 0.45996 | 1.2255 | 1.1847 | 1.1469 | 1.099 | 1.052 | 0.98776 | 0.93878 | 0.85307 | 0.77552 | 0.68776 | 0.27552 | 0.16021 | 0.11735
|  | DRYNOCH | CF |  |  |  |  | 1.139 | 1.1013 | 1.0543 | 1.0207 | 0.98087 | 0.92985 | 0.87373 | 0.83802 | 0.77781 | 0.72475 | 0.4472 | 0.16965 | 0.019649 | 1.3161 | 1.2998 | 1.2824 | 1.262 | 1.2344 | 1.1998 | 1.1579 | 1.1314 | 1.0885 | 1.0498 | 0.83036 | 0.55179 | 0.24057 | 1.2367 | 1.2071 | 1.1612 | 1.1306 | 1.0949 | 1.0469 | 0.99184 | 0.95919 | 0.90205 | 0.85205 | 0.58368 | 0.31735 | 0.13776
| KEITH 2 | DUFFTOWN | MINIMUM HEADROOM | NJ 32060 39722 | NO | YES | 0.326 | 2.0683 | 1.9469 | 1.8296 | 1.6765 | 9.5888 | 9.402 | 9.1357 | 8.8837 | 8.7051 | 8.4969 | 7.7837 | 7.3551 | 7.2592 | 3.1806 | 3.1255 | 3.0714 | 3.001 | 10.2357 | 10.1388 | 9.999 | 9.8643 | 9.7643 | 9.652 | 9.2388 | 8.9704 | 8.6928 | 2.4918 | 2.3959 | 2.2847 | 2.15 | 9.6974 | 9.527 | 9.2791 | 9.0342 | 8.876 | 8.678 | 8.0321 | 7.6495 | 7.5638
|  | DUFFTOWN | EE |  |  |  |  | 2.0683 | 1.9469 | 1.8296 | 1.6765 | 9.5888 | 9.402 | 9.1357 | 8.8837 | 8.7051 | 8.4969 | 7.7837 | 7.4 | 7.302 | 3.1806 | 3.1255 | 3.0714 | 3.001 | 10.2357 | 10.1388 | 9.999 | 9.8643 | 9.7643 | 9.652 | 9.2388 | 8.9704 | 8.7428 | 2.4918 | 2.3959 | 2.2847 | 2.15 | 9.6974 | 9.527 | 9.2791 | 9.0342 | 8.876 | 8.678 | 8.0321 | 7.6913 | 7.6025
|  | DUFFTOWN | HT |  |  |  |  | 2.1112 | 2.0245 | 1.8918 | 1.7602 | 9.6449 | 9.4857 | 9.2724 | 9.0939 | 8.8918 | 8.6877 | 7.8224 | 7.3551 | 7.2592 | 3.1959 | 3.1551 | 3.0949 | 3.0337 | 10.2602 | 10.1898 | 10.0847 | 10 | 9.899 | 9.7959 | 9.3581 | 9.1306 | 9.0786 | 2.5122 | 2.4347 | 2.3337 | 2.2102 | 9.7372 | 9.5923 | 9.4005 | 9.2393 | 9.0546 | 8.8689 | 8.0729 | 7.6495 | 7.5638
|  | DUFFTOWN | HE |  |  |  |  | 2.1102 | 2.0541 | 1.9612 | 1.8714 | 9.799 | 9.6694 | 9.4796 | 9.351 | 9.201 | 9.052 | 8.2755 | 7.8377 | 7.6837 | 3.1939 | 3.1663 | 3.1214 | 3.0734 | 10.3112 | 10.2449 | 10.152 | 10.0724 | 9.9888 | 9.9041 | 9.4581 | 9.1592 | 8.9081 | 2.5112 | 2.4602 | 2.3928 | 2.3153 | 9.8903 | 9.7709 | 9.6005 | 9.4791 | 9.3413 | 9.2025 | 8.476 | 8.0831 | 7.9454
|  | DUFFTOWN | CF |  |  |  |  | 2.1337 | 2.0918 | 2.0398 | 1.9714 | 9.9714 | 9.8949 | 9.8051 | 9.6643 | 9.602 | 9.499 | 8.9796 | 8.4204 | 8.0214 | 3.201 | 3.1857 | 3.1632 | 3.1316 | 10.402 | 10.3663 | 10.3204 | 10.2459 | 10.203 | 10.1398 | 9.7796 | 9.2867 | 8.6928 | 2.5326 | 2.5 | 2.4643 | 2.4204 | 10.0505 | 9.9821 | 9.9015 | 9.777 | 9.7199 | 9.627 | 9.1423 | 8.6107 | 8.2382
| BRACO | DUNBLANE | MINIMUM HEADROOM | NN 77907 01544 | NO | YES | 2.553 | 1.248 | 0.90816 | 0.49285 | 0.064282 | -0.42143 | -0.93062 | -1.398 | -2.1439 | -2.8796 | -3.4459 | -6.6061 | -8.6622 | -9.4255 | 3.8719 | 3.6821 | 3.4199 | 3.1597 | 2.8556 | 2.5332 | 2.3944 | 1.974 | 1.5709 | 1.1862 | -0.37194 | -1.5036 | -2.4781 | 2.513 | 2.2089 | 1.815 | 1.4324 | 0.98137 | 0.50484 | 0.22321 | -0.4421 | -1.0941 | -1.6554 | -4.2482 | -5.9401 | -6.5125
|  | DUNBLANE | EE |  |  |  |  | 1.248 | 0.90816 | 0.49285 | 0.064282 | -0.42143 | -0.93062 | -1.3163 | -2.051 | -2.7633 | -3.4459 | -6.3327 | -8.2765 | -9.0163 | 3.8719 | 3.6821 | 3.4199 | 3.1597 | 2.8556 | 2.5332 | 2.3944 | 1.974 | 1.5709 | 1.1862 | -0.37194 | -1.5036 | -2.476 | 2.513 | 2.2089 | 1.815 | 1.4324 | 0.98137 | 0.50484 | 0.24158 | -0.41761 | -1.0543 | -1.6554 | -4.0819 | -5.6339 | -6.2033
|  | DUNBLANE | HT |  |  |  |  | 1.3245 | 0.98163 | 0.61428 | 0.17755 | -0.27756 | -0.71021 | -1.398 | -2.1439 | -2.8796 | -3.2908 | -6.6061 | -8.6622 | -9.4255 | 3.9566 | 3.7862 | 3.5974 | 3.3556 | 3.0995 | 2.8556 | 2.5015 | 2.0974 | 1.7025 | 1.5913 | -0.13623 | -1.126 | -1.5362 | 2.6161 | 2.3253 | 2.0018 | 1.6171 | 1.2079 | 0.82525 | 0.22321 | -0.4421 | -1.0941 | -1.3635 | -4.2482 | -5.9401 | -6.5125
|  | DUNBLANE | HE |  |  |  |  | 1.3357 | 1.1347 | 0.91224 | 0.63367 | 0.32244 | 0.029588 | -0.45919 | -1.0092 | -1.2122 | -1.7163 | -4.5571 | -6.5725 | -7.6541 | 3.9536 | 3.824 | 3.676 | 3.4821 | 3.2699 | 3.0791 | 2.7872 | 2.4454 | 2.3811 | 2.073 | 0.36377 | -0.84643 | -1.9117 | 2.6242 | 2.4365 | 2.2334 | 1.9671 | 1.6753 | 1.414 | 0.97219 | 0.46607 | 0.36301 | -0.083933 | -2.5727 | -4.1982 | -5.0268
|  | DUNBLANE | CF |  |  |  |  | 1.4112 | 1.2786 | 1.1133 | 0.94183 | 0.72244 | 0.52959 | 0.28163 | -0.012249 | -0.29592 | -0.59286 | -2.0439 | -4.1725 | -6.0163 | 3.9913 | 3.8893 | 3.7576 | 3.6291 | 3.475 | 3.3321 | 3.1403 | 2.9148 | 2.6944 | 2.4668 | 1.3974 | -0.38827 | -2.4781 | 2.6906 | 2.561 | 2.3957 | 2.2436 | 2.0375 | 1.864 | 1.6334 | 1.3518 | 1.0865 | 0.80382 | -0.41352 | -2.2686 | -3.7727
| DUNOON | DUNOON | MINIMUM HEADROOM | NS 17135 77531 | NO | YES | 0.274 | 16.7061 | 16.4204 | 16.1285 | 15.7887 | 15.453 | 15.0581 | 14.4459 | 13.7653 | 13.0928 | 12.4632 | 9.9 | 8.0632 | 7.7306 | 18.6244 | 18.4897 | 18.3438 | 18.1775 | 18.0132 | 17.8173 | 17.5 | 17.0459 | 16.6734 | 16.3459 | 14.8102 | 13.7 | 12.5959 | 18.2622 | 17.9887 | 17.7142 | 17.3724 | 17.0469 | 16.651 | 16.0755 | 15.6071 | 14.9918 | 14.404 | 12.101 | 10.4989 | 10.201
|  | DUNOON | EE |  |  |  |  | 16.7061 | 16.4204 | 16.1285 | 15.7887 | 15.453 | 15.0581 | 14.4459 | 13.9224 | 13.202 | 12.5489 | 9.9112 | 8.2 | 7.802 | 18.6244 | 18.4897 | 18.3438 | 18.1775 | 18.0132 | 17.8173 | 17.5 | 17.1836 | 16.7418 | 16.353 | 14.8102 | 13.7 | 12.7132 | 18.2622 | 17.9887 | 17.7142 | 17.3724 | 17.0469 | 16.651 | 16.0755 | 15.6714 | 15.001 | 14.404 | 12.101 | 10.6295 | 10.2704
|  | DUNOON | HT |  |  |  |  | 16.7959 | 16.5561 | 16.2867 | 16.0214 | 15.704 | 15.3612 | 14.5938 | 13.7653 | 13.0928 | 12.4632 | 9.9 | 8.0632 | 7.7306 | 18.6806 | 18.5734 | 18.4551 | 18.3316 | 18.1877 | 18.0306 | 17.5479 | 17.0459 | 16.6734 | 16.3459 | 15.2091 | 14.4346 | 14.2755 | 18.3653 | 18.1459 | 17.9 | 17.6602 | 17.3663 | 17.0408 | 16.3612 | 15.6071 | 14.9918 | 14.4081 | 12.1326 | 10.4989 | 10.201
|  | DUNOON | HE |  |  |  |  | 16.7897 | 16.6377 | 16.4612 | 16.2673 | 16.0704 | 15.8275 | 15.4734 | 14.8918 | 14.3438 | 13.8255 | 11.7193 | 10.1632 | 9.5551 | 18.6704 | 18.5897 | 18.4989 | 18.3969 | 18.2846 | 18.151 | 17.9785 | 17.5948 | 17.2224 | 16.8826 | 15.5571 | 14.5234 | 13.4857 | 18.3612 | 18.2163 | 18.0489 | 17.853 | 17.6673 | 17.4244 | 17.1061 | 16.5673 | 16.0612 | 15.5734 | 13.7081 | 12.3795 | 11.8428
|  | DUNOON | CF |  |  |  |  | 16.8428 | 16.7469 | 16.6469 | 16.5244 | 16.403 | 16.2459 | 16.0826 | 15.8826 | 15.7234 | 15.4908 | 14.3244 | 12.6938 | 11.3459 | 18.6948 | 18.6377 | 18.5755 | 18.5051 | 18.4244 | 18.3204 | 18.2091 | 18.0734 | 17.9285 | 17.7316 | 16.65 | 14.8908 | 12.5959 | 18.4112 | 18.3153 | 18.2163 | 18.0938 | 17.9785 | 17.8163 | 17.65 | 17.4408 | 17.2795 | 17.0428 | 15.9642 | 14.4744 | 13.3183
| DUNVEGAN | DUNVEGAN | MINIMUM HEADROOM | NG 27646 47150 | YES | NO | 0.678 | 1.0409 | 0.95824 | 0.87763 | 0.79906 | 0.70008 | 0.60416 | 0.47355 | 0.3664 | 0.23069 | 0.11436 | -0.18156 | -0.29176 | -0.32441 | 1.5378 | 1.4878 | 1.4378 | 1.3929 | 1.3307 | 1.2684 | 1.1889 | 1.1225 | 1.0368 | 0.9664 | 0.74804 | 0.64498 | 0.30518 | 1.1735 | 1.095 | 1.0215 | 0.94804 | 0.85416 | 0.76028 | 0.63885 | 0.53783 | 0.40926 | 0.29906 | 0.022527 | -0.080535 | -0.10707
|  | DUNVEGAN | EE |  |  |  |  | 1.0409 | 0.95824 | 0.87763 | 0.79906 | 0.70008 | 0.60416 | 0.47355 | 0.3664 | 0.23069 | 0.11436 | -0.18156 | -0.23258 | -0.26727 | 1.5378 | 1.4878 | 1.4378 | 1.3929 | 1.3307 | 1.2684 | 1.1889 | 1.1225 | 1.0368 | 0.9664 | 0.74804 | 0.64498 | 0.48477 | 1.1735 | 1.095 | 1.0215 | 0.94804 | 0.85416 | 0.76028 | 0.63885 | 0.53783 | 0.40926 | 0.29906 | 0.022527 | -0.024412 | -0.056045
|  | DUNVEGAN | HT |  |  |  |  | 1.0664 | 0.99906 | 0.93681 | 0.87151 | 0.79293 | 0.72355 | 0.62661 | 0.52661 | 0.42049 | 0.31232 | -0.095841 | -0.29176 | -0.32441 | 1.5582 | 1.5225 | 1.4899 | 1.4511 | 1.4062 | 1.3684 | 1.3093 | 1.248 | 1.1848 | 1.1195 | 0.8664 | 0.746 | 0.72967 | 1.2021 | 1.1399 | 1.0848 | 1.0215 | 0.94396 | 0.88171 | 0.79191 | 0.69498 | 0.59498 | 0.49396 | 0.10416 | -0.080535 | -0.10707
|  | DUNVEGAN | HE |  |  |  |  | 1.0654 | 1.0144 | 0.96742 | 0.91947 | 0.85518 | 0.80518 | 0.72457 | 0.63477 | 0.54293 | 0.44906 | -0.0050245 | -0.12543 | -0.14278 | 1.5572 | 1.5256 | 1.495 | 1.4654 | 1.4235 | 1.3909 | 1.3409 | 1.2868 | 1.2235 | 1.1644 | 0.8613 | 0.7164 | 0.57253 | 1.2011 | 1.1552 | 1.1082 | 1.0603 | 1.0001 | 0.95416 | 0.87661 | 0.79293 | 0.70722 | 0.61538 | 0.19396 | 0.078649 | 0.062322
|  | DUNVEGAN | CF |  |  |  |  | 1.0735 | 1.0348 | 0.996 | 0.94498 | 0.90314 | 0.8511 | 0.81232 | 0.74906 | 0.696 | 0.63375 | 0.33171 | 0.034771 | -0.12747 | 1.5613 | 1.5389 | 1.5144 | 1.4807 | 1.4531 | 1.4144 | 1.3878 | 1.3429 | 1.3011 | 1.2562 | 1.0093 | 0.68171 | 0.30518 | 1.2113 | 1.1715 | 1.1368 | 1.0848 | 1.046 | 0.99191 | 0.96028 | 0.89702 | 0.84702 | 0.78477 | 0.5011 | 0.21844 | 0.074567
| DYCE | DYCE NORTH | MINIMUM HEADROOM | NJ 89092 12705 | NO | YES | 0.398 | 7.6199 | 6.8985 | 5.6128 | 4.0556 | 3.4066 | 0.5393 | -0.62091 | -2.0127 | -3.3383 | -5.375 | -14.0332 | -23.5178 | -32.2199 | 9.0458 | 8.4815 | 7.2162 | 5.6622 | 5.3305 | 2.1009 | 0.85399 | -0.4807 | -1.7889 | -3.9664 | -13.1011 | -24.0287 | -34.4256 | 8.1866 | 7.504 | 6.0826 | 4.3071 | 3.703 | 0.33562 | -0.97866 | -2.4725 | -3.9246 | -6.2511 | -16.1134 | -27.496 | -38.1144
|  | DYCE NORTH | EE |  |  |  |  | 7.7883 | 6.9556 | 6.2281 | 5.4709 | 4.0791 | 2.1556 | 0.86787 | -0.061722 | -1.526 | -2.4311 | -6.8229 | -15.0444 | -18.2076 | 9.3611 | 8.7244 | 8.2591 | 7.7152 | 6.3856 | 4.3999 | 3.255 | 2.5856 | 1.1632 | 0.34685 | -3.8032 | -13.4868 | -17.3378 | 8.3448 | 7.556 | 6.8683 | 6.1428 | 4.6591 | 2.5071 | 1.1673 | 0.28869 | -1.3113 | -2.2674 | -7.0409 | -17.0511 | -20.9583
|  | DYCE NORTH | HT |  |  |  |  | 7.6199 | 6.8985 | 5.6128 | 4.0556 | 3.4066 | 0.5393 | -0.32601 | -1.2638 | -1.9791 | -2.8995 | -8.3464 | -18.2627 | -26.276 | 9.0458 | 8.4815 | 7.2162 | 5.6622 | 5.3305 | 2.1264 | 1.455 | 0.71216 | 0.20093 | -0.55723 | -5.7246 | -17.2787 | -27.0062 | 8.1866 | 7.504 | 6.0826 | 4.3071 | 3.703 | 0.33562 | -0.5256 | -1.4583 | -2.144 | -3.0797 | -8.997 | -20.9623 | -30.8113
|  | DYCE NORTH | HE |  |  |  |  | 7.9362 | 7.176 | 6.0158 | 4.5281 | 3.5648 | 0.68216 | -0.62091 | -2.0127 | -3.3383 | -5.375 | -14.0332 | -23.5178 | -32.2199 | 9.4152 | 8.8111 | 7.6938 | 6.2224 | 5.3448 | 2.1009 | 0.85399 | -0.4807 | -1.7889 | -3.9664 | -13.1011 | -24.0287 | -34.4256 | 8.4897 | 7.7652 | 6.4958 | 4.8305 | 3.804 | 0.42338 | -0.97866 | -2.4725 | -3.9246 | -6.2511 | -16.1134 | -27.496 | -38.1144
|  | DYCE NORTH | CF |  |  |  |  | 8.9015 | 8.3975 | 7.9189 | 7.4505 | 6.5873 | 5.3842 | 4.5281 | 3.7097 | 2.9954 | 2.1322 | -1.925 | -5.5607 | -8.2495 | 10.4448 | 9.9887 | 9.6122 | 9.2826 | 8.4897 | 7.2989 | 6.4448 | 5.6683 | 4.9673 | 4.0917 | 0.38869 | -2.9123 | -5.3276 | 9.4326 | 8.9315 | 8.4785 | 8.0397 | 7.1152 | 5.7703 | 4.8601 | 4.005 | 3.2417 | 2.2968 | -1.9134 | -5.7236 | -8.5838
| THURSO | EDAY | MINIMUM HEADROOM | HY 56341 33422 | YES | NO | 0.579 | 0.42186 | 0.41369 | 0.40349 | 0.39635 | 0.38206 | 0.37594 | 0.35757 | 0.33716 | 0.3341 | 0.31982 | 0.28818 | 0.27492 | 0.26573 | 0.51369 | 0.50961 | 0.50349 | 0.49839 | 0.4892 | 0.4841 | 0.47288 | 0.45553 | 0.45247 | 0.44431 | 0.41778 | 0.40655 | 0.38002 | 0.47186 | 0.46063 | 0.45247 | 0.44431 | 0.43308 | 0.4239 | 0.40757 | 0.38716 | 0.38512 | 0.36982 | 0.3392 | 0.329 | 0.32696
|  | EDAY | EE |  |  |  |  | 0.4239 | 0.41369 | 0.40349 | 0.39635 | 0.38206 | 0.37594 | 0.35757 | 0.33716 | 0.3341 | 0.31982 | 0.28818 | 0.28104 | 0.279 | 0.51676 | 0.50961 | 0.50349 | 0.49839 | 0.4892 | 0.4841 | 0.47288 | 0.45553 | 0.45247 | 0.44431 | 0.41778 | 0.40655 | 0.39431 | 0.47186 | 0.46063 | 0.45247 | 0.44431 | 0.43308 | 0.4239 | 0.40757 | 0.38716 | 0.38512 | 0.36982 | 0.3392 | 0.33308 | 0.33002
|  | EDAY | HT |  |  |  |  | 0.42186 | 0.42288 | 0.41573 | 0.40859 | 0.40247 | 0.39227 | 0.379 | 0.37084 | 0.35757 | 0.34227 | 0.29839 | 0.27798 | 0.27186 | 0.51369 | 0.5188 | 0.51369 | 0.50757 | 0.50451 | 0.49737 | 0.48818 | 0.48206 | 0.47288 | 0.46267 | 0.43002 | 0.41676 | 0.41267 | 0.479 | 0.47084 | 0.46573 | 0.45859 | 0.45247 | 0.44124 | 0.43104 | 0.42186 | 0.40961 | 0.39431 | 0.34941 | 0.329 | 0.32696
|  | EDAY | HE |  |  |  |  | 0.42186 | 0.41778 | 0.41676 | 0.41267 | 0.40349 | 0.39635 | 0.38716 | 0.37798 | 0.36573 | 0.35145 | 0.29227 | 0.27492 | 0.26573 | 0.51471 | 0.51369 | 0.51471 | 0.51165 | 0.50247 | 0.49839 | 0.49329 | 0.48716 | 0.47492 | 0.46676 | 0.42696 | 0.41471 | 0.40349 | 0.479 | 0.46471 | 0.46573 | 0.46369 | 0.45145 | 0.44635 | 0.43716 | 0.43002 | 0.41676 | 0.40553 | 0.35655 | 0.34329 | 0.34022
|  | EDAY | CF |  |  |  |  | 0.42288 | 0.4188 | 0.41778 | 0.41369 | 0.40859 | 0.40553 | 0.39839 | 0.3892 | 0.379 | 0.37594 | 0.34124 | 0.29839 | 0.27186 | 0.51471 | 0.51471 | 0.51573 | 0.51267 | 0.50961 | 0.50655 | 0.49839 | 0.49329 | 0.48512 | 0.48308 | 0.45247 | 0.41267 | 0.38002 | 0.479 | 0.46778 | 0.46778 | 0.46267 | 0.45757 | 0.45451 | 0.44737 | 0.4392 | 0.429 | 0.42492 | 0.39124 | 0.35043 | 0.33818
| THURSO | EDAY TIDAL | MINIMUM HEADROOM | HY 54226 31320 | YES | NO | 0 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694
|  | EDAY TIDAL | EE |  |  |  |  | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694
|  | EDAY TIDAL | HT |  |  |  |  | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694
|  | EDAY TIDAL | HE |  |  |  |  | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694
|  | EDAY TIDAL | CF |  |  |  |  | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.83673 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.64082 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694 | 0.34694
| FIDDES | EDZELL | MINIMUM HEADROOM | NO 63500 70513 | YES | NO | 1.673 | 0.91906 | 0.80682 | 0.67927 | 0.52518 | 0.35069 | 0.056816 | -0.29012 | -0.73604 | -1.2758 | -1.9207 | -3.0085 | -3.3299 | -3.3942 | 1.7162 | 1.6438 | 1.5723 | 1.4866 | 1.3887 | 1.1631 | 0.87845 | 0.556 | 0.23355 | -0.13176 | -0.70522 | -0.91339 | -1.292 | 1.3319 | 1.2013 | 1.087 | 0.94518 | 0.78294 | 0.52682 | 0.19212 | -0.21298 | -0.67318 | -1.2262 | -2.165 | -2.4436 | -2.4967
|  | EDZELL | EE |  |  |  |  | 0.91906 | 0.80682 | 0.67927 | 0.52518 | 0.35069 | 0.056816 | -0.29012 | -0.71665 | -1.1544 | -1.6105 | -3.0085 | -3.2881 | -3.333 | 1.7162 | 1.6438 | 1.5723 | 1.4866 | 1.3887 | 1.1631 | 0.87845 | 0.556 | 0.23355 | -0.079714 | -0.70522 | -0.91339 | -1.1134 | 1.3319 | 1.2013 | 1.087 | 0.94518 | 0.78294 | 0.52682 | 0.19212 | -0.21298 | -0.61706 | -1.0181 | -2.165 | -2.4018 | -2.4436
|  | EDZELL | HT |  |  |  |  | 0.94763 | 0.82824 | 0.70784 | 0.57314 | 0.45784 | 0.14151 | -0.2891 | -0.73604 | -1.2758 | -1.9207 | -2.9401 | -3.3299 | -3.3942 | 1.7397 | 1.6774 | 1.6193 | 1.5417 | 1.4876 | 1.2438 | 0.93151 | 0.61416 | 0.2611 | -0.13176 | -0.57155 | -0.7542 | -0.78686 | 1.3778 | 1.2493 | 1.138 | 1.0105 | 0.90539 | 0.60437 | 0.20437 | -0.19665 | -0.67318 | -1.2262 | -2.1007 | -2.4436 | -2.4967
|  | EDZELL | HE |  |  |  |  | 0.94559 | 0.8711 | 0.78437 | 0.67927 | 0.57314 | 0.29049 | -0.011551 | -0.35747 | -0.73502 | -1.134 | -2.2605 | -2.8299 | -3.1626 | 1.7356 | 1.6866 | 1.6407 | 1.5754 | 1.5172 | 1.2662 | 0.98967 | 0.69784 | 0.38967 | 0.075388 | -0.43788 | -0.71339 | -1.0369 | 1.3748 | 1.285 | 1.1982 | 1.0911 | 1.0023 | 0.73906 | 0.44824 | 0.13294 | -0.22216 | -0.59563 | -1.5507 | -2.0252 | -2.2926
|  | EDZELL | CF |  |  |  |  | 0.9609 | 0.90273 | 0.84355 | 0.76396 | 0.68743 | 0.40171 | 0.15171 | -0.11155 | -0.38502 | -0.66359 | -1.5503 | -2.3003 | -2.935 | 1.7489 | 1.7091 | 1.6764 | 1.6223 | 1.5774 | 1.3478 | 1.0999 | 0.84784 | 0.58967 | 0.33661 | -0.10216 | -0.65216 | -1.292 | 1.3911 | 1.3156 | 1.2533 | 1.1697 | 1.1033 | 0.84416 | 0.60437 | 0.35029 | 0.080898 | -0.18135 | -0.92931 | -1.566 | -2.0967
| MILTON OF CRAIGIE | EDZELL STREET | MINIMUM HEADROOM | NO 47103 32070 | YES | NO | 0 | 9.1051 | 8.9837 | 8.8296 | 8.6939 | 8.5306 | 8.3429 | 8.099 | 7.7847 | 7.4837 | 7.2071 | 6.3806 | 6.3194 | 6.2796 | 9.0204 | 8.9306 | 8.7898 | 8.6816 | 8.5265 | 8.3602 | 8.1949 | 7.952 | 7.7204 | 7.5092 | 6.9908 | 5.2939 | 1.7102 | 9.0735 | 8.9561 | 8.7969 | 8.6643 | 8.4949 | 8.3163 | 8.0929 | 7.801 | 7.5245 | 7.2724 | 6.5286 | 6.5367 | 6.5031
|  | EDZELL STREET | EE |  |  |  |  | 9.1051 | 8.9837 | 8.8296 | 8.6939 | 8.5306 | 8.3429 | 8.099 | 7.7847 | 7.4837 | 7.2071 | 6.6204 | 6.501 | 6.4847 | 9.0204 | 8.9306 | 8.7898 | 8.6816 | 8.5265 | 8.3602 | 8.1949 | 7.952 | 7.7204 | 7.5092 | 6.9908 | 6.0888 | 4.4929 | 9.0735 | 8.9561 | 8.7969 | 8.6643 | 8.4949 | 8.3163 | 8.0929 | 7.801 | 7.5245 | 7.2724 | 6.7908 | 6.6878 | 6.6633
|  | EDZELL STREET | HT |  |  |  |  | 9.1398 | 9.0163 | 8.8898 | 8.7561 | 8.6082 | 8.4816 | 8.2439 | 7.9898 | 7.7735 | 7.5235 | 6.3806 | 6.3194 | 6.2796 | 9.0796 | 9.0153 | 8.9459 | 8.8592 | 8.7571 | 8.6837 | 8.5429 | 8.3816 | 8.2714 | 8.1153 | 7.3939 | 7.5714 | 7.5367 | 9.1286 | 9.0082 | 8.8908 | 8.7622 | 8.6173 | 8.4969 | 8.2786 | 8.0357 | 7.8378 | 7.601 | 6.5286 | 6.5367 | 6.5031
|  | EDZELL STREET | HE |  |  |  |  | 9.149 | 9.0878 | 9.0286 | 8.9531 | 8.8673 | 8.8071 | 8.6327 | 8.4306 | 8.2755 | 8.0796 | 7.0918 | 6.902 | 6.7898 | 9.0714 | 9.0092 | 8.9398 | 8.8531 | 8.75 | 8.6724 | 8.5255 | 8.35 | 8.2286 | 8.051 | 7 | 6.2653 | 4.6449 | 9.1357 | 9.0673 | 9 | 8.9184 | 8.8245 | 8.7592 | 8.5898 | 8.399 | 8.2571 | 8.0724 | 7.1633 | 7.0408 | 6.95
|  | EDZELL STREET | CF |  |  |  |  | 9.1837 | 9.1571 | 9.1296 | 9.0878 | 9.049 | 8.999 | 8.9571 | 8.8653 | 8.7776 | 8.7255 | 8.0898 | 7.65 | 7.0224 | 9.0816 | 9.0296 | 8.9786 | 8.898 | 8.8163 | 8.7082 | 8.6092 | 8.4602 | 8.3133 | 8.199 | 7.148 | 5.2939 | 1.7102 | 9.1684 | 9.1296 | 9.0918 | 9.0388 | 8.9888 | 8.9255 | 8.8827 | 8.7949 | 8.7133 | 8.6633 | 8.0684 | 7.6765 | 7.1245
| ELGIN | ELGIN | MINIMUM HEADROOM | NJ 21256 64664 | NO | YES | 2.373 | 6.4022 | 5.7593 | 5.095 | 4.4563 | 3.8154 | 3.095 | 2.1859 | 1.1859 | -0.069245 | -1.4988 | -7.859 | -11.0386 | -11.7121 | 8.2012 | 7.7685 | 7.3175 | 6.893 | 6.4746 | 6.0328 | 5.5114 | 5.0277 | 4.3573 | 3.5685 | -0.61006 | -1.9978 | -2.9856 | 7.2634 | 6.6991 | 6.095 | 5.5103 | 4.9236 | 4.2879 | 3.493 | 2.6073 | 1.5236 | 0.31239 | -5.2315 | -7.8356 | -8.3846
|  | ELGIN | EE |  |  |  |  | 6.4022 | 5.7593 | 5.095 | 4.4563 | 3.8154 | 3.095 | 2.1859 | 1.4195 | 0.36953 | -0.69271 | -7.3284 | -10.5417 | -11.7121 | 8.2012 | 7.7685 | 7.3175 | 6.893 | 6.4746 | 6.0328 | 5.5114 | 5.0277 | 4.3879 | 3.7797 | -0.33251 | -1.9978 | -2.9856 | 7.2634 | 6.6991 | 6.095 | 5.5103 | 4.9236 | 4.2879 | 3.493 | 2.7828 | 1.8542 | 0.92259 | -4.8805 | -7.4652 | -8.3846
|  | ELGIN | HT |  |  |  |  | 6.5001 | 5.893 | 5.2052 | 4.6114 | 4.041 | 3.4001 | 2.3654 | 1.1859 | -0.069245 | -1.4988 | -7.859 | -11.0386 | -11.6529 | 8.2736 | 7.8685 | 7.394 | 7.0144 | 6.6695 | 6.3073 | 5.744 | 5.0654 | 4.3573 | 3.5685 | -0.22741 | -1.7509 | -2.0407 | 7.3665 | 6.8114 | 6.1654 | 5.6144 | 5.092 | 4.5246 | 3.6359 | 2.6073 | 1.5236 | 0.31239 | -5.2315 | -7.8356 | -8.3254
|  | ELGIN | HE |  |  |  |  | 6.5124 | 6.0073 | 5.4603 | 4.9532 | 4.4481 | 3.8491 | 3.1563 | 2.2154 | 1.245 | 0.21035 | -5.6223 | -8.4876 | -10.0203 | 8.2818 | 7.9185 | 7.5185 | 7.1654 | 6.8134 | 6.4297 | 5.9532 | 5.2869 | 4.6063 | 3.8797 | -0.61006 | -1.9611 | -2.5448 | 7.3818 | 6.9226 | 6.4154 | 5.945 | 5.4777 | 4.9461 | 4.3359 | 3.5144 | 2.6634 | 1.7573 | -3.5478 | -5.9682 | -7.2029
|  | ELGIN | CF |  |  |  |  | 6.6563 | 6.3246 | 5.9552 | 5.6032 | 5.2777 | 4.8624 | 4.4246 | 3.9726 | 3.4593 | 2.8797 | -1.0907 | -5.4407 | -8.3499 | 8.393 | 8.1624 | 7.891 | 7.6471 | 7.4185 | 7.1399 | 6.8461 | 6.5348 | 6.1869 | 5.795 | 2.7124 | -0.34782 | -2.6509 | 7.5134 | 7.2297 | 6.9073 | 6.594 | 6.294 | 5.9287 | 5.5552 | 5.1603 | 4.7103 | 4.1961 | 0.6328 | -3.2631 | -5.7131
| ARBROATH | ELLIOT DEPOT | MINIMUM HEADROOM | NO 62251 40381 | YES | YES | 4.539 | -7.8143 | -8.2133 | -8.5847 | -8.9225 | -9.1613 | -9.3633 | -9.5541 | -9.7684 | -9.9786 | -10.1419 | -11.0011 | -11.4735 | -11.5654 | -7.1021 | -7.3827 | -7.6062 | -7.799 | -7.9286 | -8.0347 | -8.1582 | -8.3052 | -8.4368 | -8.5439 | -8.998 | -9.2562 | -9.5541 | -7.5245 | -7.8368 | -8.1154 | -8.348 | -8.5072 | -8.6684 | -8.8388 | -9.0225 | -9.2307 | -9.3827 | -10.1347 | -10.5531 | -10.6358
|  | ELLIOT DEPOT | EE |  |  |  |  | -7.7664 | -8.1592 | -8.5113 | -8.8582 | -9.1215 | -9.3378 | -9.5521 | -9.7684 | -9.9786 | -10.1419 | -10.9541 | -11.446 | -11.5368 | -7.045 | -7.3194 | -7.5266 | -7.7327 | -7.8898 | -8.0184 | -8.1582 | -8.3052 | -8.4368 | -8.5439 | -8.998 | -9.2562 | -9.5103 | -7.4745 | -7.7807 | -8.0429 | -8.2909 | -8.4766 | -8.6327 | -8.8276 | -9.0225 | -9.2307 | -9.3827 | -10.1123 | -10.5317 | -10.6092
|  | ELLIOT DEPOT | HT |  |  |  |  | -7.8143 | -8.2133 | -8.5847 | -8.9225 | -9.1613 | -9.3633 | -9.5541 | -9.7531 | -9.9327 | -10.1296 | -11.0011 | -11.4735 | -11.5654 | -7.1021 | -7.3827 | -7.6062 | -7.799 | -7.9286 | -8.0347 | -8.1256 | -8.246 | -8.3501 | -8.4633 | -8.9715 | -9.198 | -9.2643 | -7.5245 | -7.8368 | -8.1154 | -8.348 | -8.5072 | -8.6684 | -8.8388 | -9.0194 | -9.1766 | -9.3521 | -10.1347 | -10.5531 | -10.6358
|  | ELLIOT DEPOT | HE |  |  |  |  | -7.746 | -8.097 | -8.4154 | -8.7194 | -8.9296 | -9.1082 | -9.2613 | -9.4103 | -9.5409 | -9.6837 | -10.445 | -10.9398 | -11.1368 | -7.0286 | -7.295 | -7.4868 | -7.6674 | -7.8001 | -7.9154 | -8.0296 | -8.1541 | -8.2592 | -8.3756 | -8.8888 | -9.0878 | -9.297 | -7.4541 | -7.746 | -7.9817 | -8.2041 | -8.3592 | -8.4909 | -8.6072 | -8.7398 | -8.8756 | -9.0235 | -9.7041 | -10.1052 | -10.2807
|  | ELLIOT DEPOT | CF |  |  |  |  | -7.5501 | -7.797 | -8.0501 | -8.2807 | -8.4541 | -8.5878 | -8.6776 | -8.7684 | -8.8562 | -8.946 | -9.5205 | -10.1582 | -10.6684 | -6.8307 | -7.0041 | -7.1582 | -7.2796 | -7.397 | -7.495 | -7.5776 | -7.6623 | -7.7368 | -7.8235 | -8.3286 | -8.8837 | -9.5541 | -7.2582 | -7.4541 | -7.645 | -7.8103 | -7.9409 | -8.0439 | -8.1296 | -8.2164 | -8.295 | -8.3919 | -8.9756 | -9.5633 | -9.9521
| DYCE | ELLON | MINIMUM HEADROOM | NJ 95510 30054 | NO | YES | 2.393 | -0.61842 | 24.6862 | 23.8209 | 22.7158 | 21.7586 | 19.6454 | 18.1596 | 16.1933 | 14.1178 | 11.6841 | 6.0535 | 1.3994 | -1.2444 | 2.28 | 27.1576 | 26.6433 | 25.8647 | 25.328 | 23.5443 | 22.578 | 21.176 | 19.6933 | 17.7596 | 11.7096 | 7.8494 | 4.23 | 0.93438 | 26.2994 | 25.5239 | 24.4617 | 23.6178 | 21.4943 | 20.1433 | 18.3229 | 16.3749 | 14.0637 | 8.678 | 3.6841 | 0.26474
|  | ELLON | EE |  |  |  |  | -0.61842 | 24.6862 | 23.9545 | 23.1076 | 22.3056 | 20.7454 | 18.8005 | 17.0607 | 15.078 | 13.0433 | 6.6362 | 2.3117 | 1.0586 | 2.28 | 27.1576 | 26.7137 | 26.1862 | 25.678 | 24.4413 | 23.0729 | 21.8423 | 20.3219 | 18.7851 | 14.1372 | 10.2637 | 8.2566 | 0.93438 | 26.2994 | 25.6382 | 24.8658 | 24.1402 | 22.6209 | 20.8362 | 19.2362 | 17.3505 | 15.4382 | 9.4668 | 5.0433 | 3.6607
|  | ELLON | HT |  |  |  |  | -0.53067 | 24.7811 | 23.8209 | 22.7158 | 21.7586 | 19.6454 | 18.1596 | 16.1933 | 14.1178 | 11.6841 | 6.0535 | 1.3994 | -0.94649 | 2.3811 | 27.3076 | 26.6433 | 25.8647 | 25.328 | 23.5443 | 22.578 | 21.176 | 19.6933 | 17.7596 | 14.03 | 10.0617 | 7.4178 | 1.0456 | 26.4423 | 25.5239 | 24.4617 | 23.6178 | 21.4943 | 20.1433 | 18.3229 | 16.3749 | 14.0637 | 8.8402 | 3.9739 | 1.1933
|  | ELLON | HE |  |  |  |  | -0.48985 | 25.0607 | 24.3943 | 23.5882 | 22.7739 | 21.0535 | 19.6045 | 17.9882 | 16.2627 | 14.1229 | 6.579 | 1.7586 | -1.2444 | 2.3994 | 27.4025 | 26.8617 | 26.2035 | 25.6229 | 24.0831 | 23.0209 | 21.726 | 20.3351 | 18.3096 | 11.7096 | 7.8494 | 4.23 | 1.0823 | 26.6719 | 26.0076 | 25.2056 | 24.4413 | 22.6841 | 21.38 | 19.8372 | 18.1933 | 16.0709 | 8.678 | 3.6841 | 0.26474
|  | ELLON | CF |  |  |  |  | -0.30006 | 25.4137 | 25.126 | 24.7923 | 24.3096 | 23.577 | 22.778 | 22.1474 | 21.3351 | 20.3321 | 14.6137 | 9.277 | 6.7474 | 2.526 | 27.6209 | 27.4066 | 27.1525 | 26.7658 | 26.1147 | 25.4372 | 24.9076 | 24.1913 | 23.3086 | 18.6209 | 13.9943 | 10.8556 | 1.2568 | 26.9902 | 26.7198 | 26.4025 | 25.9362 | 25.2005 | 24.4341 | 23.8698 | 23.0913 | 22.1321 | 16.8423 | 11.9086 | 9.5443
| TAYNUILT | EREDINE | MINIMUM HEADROOM | NM 97142 09376 | YES | YES | 0 | 0.14314 | 0.13192 | 0.1309 | 0.12988 | 0.12478 | 0.12273 | 0.11865 | 0.11049 | 0.10539 | 0.095184 | 0.083959 | 0.086 | 0.086 | 0.15269 | 0.14453 | 0.14453 | 0.14453 | 0.14453 | 0.14453 | 0.14147 | 0.13433 | 0.13127 | 0.12616 | 0.11596 | 0.118 | 0.1078 | 0.15353 | 0.14333 | 0.14129 | 0.14027 | 0.13516 | 0.13312 | 0.12904 | 0.1219 | 0.11782 | 0.10761 | 0.096388 | 0.098429 | 0.097408
|  | EREDINE | EE |  |  |  |  | 0.14314 | 0.13192 | 0.136 | 0.1309 | 0.12478 | 0.12273 | 0.11865 | 0.11049 | 0.10539 | 0.095184 | 0.083959 | 0.088041 | 0.088041 | 0.15269 | 0.14453 | 0.15371 | 0.15065 | 0.14453 | 0.14453 | 0.14147 | 0.13433 | 0.13127 | 0.12616 | 0.11596 | 0.11902 | 0.1129 | 0.15353 | 0.14333 | 0.14741 | 0.14231 | 0.13516 | 0.13312 | 0.12904 | 0.1219 | 0.11782 | 0.10761 | 0.096388 | 0.10149 | 0.10047
|  | EREDINE | HT |  |  |  |  | 0.15029 | 0.14008 | 0.1309 | 0.12988 | 0.13294 | 0.12886 | 0.12478 | 0.12273 | 0.11253 | 0.11151 | 0.088041 | 0.086 | 0.086 | 0.16086 | 0.15167 | 0.14453 | 0.14759 | 0.15167 | 0.14861 | 0.14555 | 0.14453 | 0.13739 | 0.13637 | 0.12106 | 0.12106 | 0.12004 | 0.16067 | 0.15047 | 0.14129 | 0.14027 | 0.14435 | 0.13924 | 0.13516 | 0.13414 | 0.12394 | 0.12394 | 0.10047 | 0.098429 | 0.097408
|  | EREDINE | HE |  |  |  |  | 0.15029 | 0.14008 | 0.13192 | 0.1309 | 0.13498 | 0.1309 | 0.12784 | 0.12682 | 0.11967 | 0.11661 | 0.090082 | 0.089061 | 0.089061 | 0.16086 | 0.15269 | 0.14453 | 0.14861 | 0.15269 | 0.14963 | 0.14657 | 0.14657 | 0.14147 | 0.14045 | 0.11902 | 0.12004 | 0.11494 | 0.16067 | 0.15149 | 0.14333 | 0.14129 | 0.14639 | 0.14231 | 0.13822 | 0.1372 | 0.13006 | 0.12802 | 0.10251 | 0.10149 | 0.10149
|  | EREDINE | CF |  |  |  |  | 0.15029 | 0.14927 | 0.1411 | 0.13192 | 0.1309 | 0.136 | 0.12988 | 0.12682 | 0.12376 | 0.12273 | 0.10845 | 0.097224 | 0.091102 | 0.16086 | 0.15984 | 0.15167 | 0.14453 | 0.14861 | 0.15371 | 0.14963 | 0.14759 | 0.14453 | 0.14453 | 0.13229 | 0.118 | 0.1078 | 0.16067 | 0.15965 | 0.15251 | 0.14231 | 0.14129 | 0.14741 | 0.14231 | 0.13924 | 0.13516 | 0.13414 | 0.11986 | 0.10863 | 0.10353
| INVERNESS | ERROGIE | MINIMUM HEADROOM | NH 56674 22810 | YES | NO | 0.036 | 0.86837 | 0.8602 | 0.8602 | 0.85306 | 0.84286 | 0.83469 | 0.82857 | 0.81327 | 0.79898 | 0.78878 | 0.77959 | 0.77551 | 0.77245 | 0.9051 | 0.89796 | 0.9051 | 0.9 | 0.89286 | 0.88673 | 0.88265 | 0.87041 | 0.86122 | 0.85 | 0.84898 | 0.84082 | 0.82143 | 0.88469 | 0.87653 | 0.87857 | 0.87041 | 0.86224 | 0.85408 | 0.84898 | 0.83367 | 0.82041 | 0.8102 | 0.80102 | 0.79898 | 0.79694
|  | ERROGIE | EE |  |  |  |  | 0.86837 | 0.86735 | 0.8602 | 0.85306 | 0.84286 | 0.83469 | 0.82857 | 0.81327 | 0.79898 | 0.78878 | 0.77959 | 0.77551 | 0.77347 | 0.90714 | 0.90918 | 0.9051 | 0.9 | 0.89286 | 0.88673 | 0.88265 | 0.87041 | 0.86122 | 0.85 | 0.84898 | 0.84286 | 0.83571 | 0.88469 | 0.88367 | 0.87857 | 0.87041 | 0.86224 | 0.85408 | 0.84898 | 0.83367 | 0.82041 | 0.8102 | 0.80102 | 0.79898 | 0.79694
|  | ERROGIE | HT |  |  |  |  | 0.86837 | 0.86531 | 0.86327 | 0.85918 | 0.85408 | 0.84592 | 0.83776 | 0.83061 | 0.82245 | 0.81633 | 0.78673 | 0.77551 | 0.77245 | 0.9051 | 0.90612 | 0.90612 | 0.90408 | 0.90204 | 0.89592 | 0.89286 | 0.88776 | 0.87857 | 0.87551 | 0.85612 | 0.85 | 0.84796 | 0.88571 | 0.88163 | 0.88061 | 0.87653 | 0.87245 | 0.86429 | 0.85714 | 0.85 | 0.84286 | 0.83776 | 0.8102 | 0.8 | 0.79694
|  | ERROGIE | HE |  |  |  |  | 0.86939 | 0.86429 | 0.86531 | 0.86224 | 0.85918 | 0.85102 | 0.8449 | 0.83878 | 0.82857 | 0.82551 | 0.78878 | 0.78061 | 0.77857 | 0.90612 | 0.90612 | 0.90816 | 0.90612 | 0.90408 | 0.89694 | 0.89388 | 0.8898 | 0.88163 | 0.87653 | 0.85408 | 0.84592 | 0.83878 | 0.88673 | 0.88061 | 0.88265 | 0.88061 | 0.87653 | 0.86837 | 0.86327 | 0.85714 | 0.84796 | 0.84694 | 0.81122 | 0.80408 | 0.80204
|  | ERROGIE | CF |  |  |  |  | 0.86939 | 0.8602 | 0.86837 | 0.86429 | 0.85918 | 0.85816 | 0.85408 | 0.84592 | 0.84184 | 0.83571 | 0.80408 | 0.78673 | 0.77653 | 0.90612 | 0.89796 | 0.90918 | 0.90816 | 0.90408 | 0.90306 | 0.90102 | 0.89286 | 0.89082 | 0.88469 | 0.8602 | 0.84082 | 0.82143 | 0.88673 | 0.87653 | 0.88469 | 0.88163 | 0.87755 | 0.87551 | 0.87143 | 0.86531 | 0.8602 | 0.8551 | 0.82551 | 0.8102 | 0.80102
| ABERNETHY | ERROL | MINIMUM HEADROOM | NO 23206 23038 | NO | YES | 0.259 | 3.6541 | 3.4949 | 3.2418 | 2.801 | 2.5418 | 1.8061 | 1.4663 | 1.103 | 0.78161 | 0.3714 | -2.1908 | -4.1878 | -6.1755 | 4.6653 | 4.5724 | 4.35 | 3.9551 | 3.8132 | 3.0734 | 2.8336 | 2.5102 | 2.2214 | 1.702 | -0.63982 | -2.9194 | -5.348 | 4.2765 | 4.1245 | 3.8388 | 3.3663 | 3.1347 | 2.3 | 1.9806 | 1.6347 | 1.3571 | 0.76222 | -2.0296 | -4.4408 | -6.8878
|  | ERROL | EE |  |  |  |  | 3.6541 | 3.4949 | 3.2734 | 3.0592 | 2.6428 | 2.0796 | 1.6704 | 1.303 | 0.78161 | 0.3714 | -0.7939 | -2.9429 | -3.7337 | 4.6653 | 4.5724 | 4.4367 | 4.3132 | 3.9847 | 3.4847 | 3.1959 | 2.9765 | 2.5643 | 2.2734 | 1.4245 | -0.94288 | -1.9643 | 4.2765 | 4.1245 | 3.9143 | 3.7153 | 3.2939 | 2.6939 | 2.2928 | 1.9479 | 1.4163 | 1.0122 | -0.16839 | -2.7521 | -3.7072
|  | ERROL | HT |  |  |  |  | 3.7245 | 3.5704 | 3.2418 | 2.801 | 2.5418 | 1.8061 | 1.4663 | 1.103 | 0.83365 | 0.4714 | -1.4878 | -3.6439 | -5.4429 | 4.7071 | 4.6398 | 4.35 | 3.9551 | 3.8132 | 3.0734 | 2.8663 | 2.6367 | 2.4918 | 2.2571 | 0.751 | -1.6664 | -3.8347 | 4.3459 | 4.199 | 3.8388 | 3.3663 | 3.1347 | 2.3 | 1.9806 | 1.6347 | 1.3857 | 1.0398 | -0.95615 | -3.6021 | -5.8225
|  | ERROL | HE |  |  |  |  | 3.7234 | 3.6194 | 3.3602 | 2.9979 | 2.7224 | 2.0449 | 1.6714 | 1.2836 | 0.94079 | 0.39793 | -2.1908 | -4.1878 | -6.1755 | 4.7061 | 4.653 | 4.4132 | 4.0663 | 3.8469 | 3.1326 | 2.8336 | 2.5102 | 2.2214 | 1.702 | -0.63982 | -2.9194 | -5.348 | 4.3439 | 4.2459 | 3.9622 | 3.5622 | 3.2816 | 2.503 | 2.1214 | 1.7173 | 1.3571 | 0.76222 | -2.0296 | -4.4408 | -6.8878
|  | ERROL | CF |  |  |  |  | 3.751 | 3.6745 | 3.5714 | 3.4357 | 3.2092 | 2.8908 | 2.703 | 2.4928 | 2.2857 | 2.0418 | 0.92753 | 0.19896 | -0.60207 | 4.7173 | 4.6888 | 4.6214 | 4.5357 | 4.3439 | 4.0469 | 3.8826 | 3.7081 | 3.5326 | 3.3183 | 2.4428 | 1.8102 | 1.0377 | 4.3745 | 4.299 | 4.2041 | 4.0806 | 3.8459 | 3.4979 | 3.299 | 3.0847 | 2.8704 | 2.6112 | 1.4969 | 0.77242 | -0.027576
| FASNAKYLE | FASNAKYLE | MINIMUM HEADROOM | NH 31948 29998 | YES | YES | 0.019 | 0.57636 | 0.56105 | 0.5386 | 0.51309 | 0.50084 | 0.47125 | 0.44574 | 0.41207 | 0.37533 | 0.34574 | 0.31105 | 0.29574 | 0.29064 | 0.64574 | 0.63452 | 0.62023 | 0.5988 | 0.58962 | 0.57023 | 0.55595 | 0.53146 | 0.50493 | 0.48554 | 0.46207 | 0.43962 | 0.37023 | 0.6437 | 0.6284 | 0.60799 | 0.58248 | 0.57023 | 0.5437 | 0.51921 | 0.48656 | 0.45289 | 0.42533 | 0.38962 | 0.37636 | 0.37227
|  | FASNAKYLE | EE |  |  |  |  | 0.57636 | 0.56105 | 0.5386 | 0.51309 | 0.50084 | 0.47125 | 0.44574 | 0.41207 | 0.37533 | 0.34574 | 0.31105 | 0.29982 | 0.29574 | 0.64574 | 0.63452 | 0.62023 | 0.5988 | 0.58962 | 0.57023 | 0.55595 | 0.53146 | 0.50493 | 0.48554 | 0.46207 | 0.44064 | 0.41513 | 0.6437 | 0.6284 | 0.60799 | 0.58248 | 0.57023 | 0.5437 | 0.51921 | 0.48656 | 0.45289 | 0.42533 | 0.38962 | 0.38146 | 0.37636
|  | FASNAKYLE | HT |  |  |  |  | 0.5886 | 0.57431 | 0.55799 | 0.5386 | 0.52329 | 0.4988 | 0.49064 | 0.46003 | 0.43146 | 0.41513 | 0.33248 | 0.29574 | 0.29064 | 0.65289 | 0.64574 | 0.63452 | 0.62125 | 0.61309 | 0.59778 | 0.59268 | 0.57227 | 0.55595 | 0.5437 | 0.48962 | 0.46819 | 0.46309 | 0.65493 | 0.64064 | 0.62533 | 0.60799 | 0.59166 | 0.57125 | 0.56003 | 0.53248 | 0.50697 | 0.49166 | 0.41207 | 0.37636 | 0.37227
|  | FASNAKYLE | HE |  |  |  |  | 0.5886 | 0.5784 | 0.56717 | 0.54676 | 0.53656 | 0.51411 | 0.50697 | 0.47942 | 0.45391 | 0.44166 | 0.34166 | 0.31411 | 0.31003 | 0.65289 | 0.64676 | 0.6386 | 0.62329 | 0.61615 | 0.60187 | 0.59574 | 0.5784 | 0.55697 | 0.55084 | 0.48248 | 0.45084 | 0.42636 | 0.65493 | 0.64472 | 0.63248 | 0.61411 | 0.60391 | 0.58452 | 0.57636 | 0.55289 | 0.52636 | 0.51411 | 0.42125 | 0.39268 | 0.38962
|  | FASNAKYLE | CF |  |  |  |  | 0.59064 | 0.5784 | 0.57023 | 0.55697 | 0.54778 | 0.53044 | 0.51309 | 0.50697 | 0.49064 | 0.47227 | 0.3886 | 0.33758 | 0.30697 | 0.65493 | 0.64676 | 0.6386 | 0.63044 | 0.62329 | 0.61309 | 0.5988 | 0.5937 | 0.57942 | 0.56513 | 0.49778 | 0.43962 | 0.37023 | 0.65697 | 0.64676 | 0.6386 | 0.62738 | 0.61717 | 0.60187 | 0.58554 | 0.5784 | 0.56411 | 0.54472 | 0.46717 | 0.41819 | 0.3886
| TUMMEL BRIDGE | FINCASTLE | MINIMUM HEADROOM | NN 87976 61147 | YES | YES | 0 | 0.068 | 0.059837 | 0.049633 | 0.047592 | 0.046571 | 0.046571 | 0.041469 | 0.039429 | 0.033306 | 0.031265 | 0.021061 | 0.01902 | 0.018 | 0.072265 | 0.064102 | 0.056959 | 0.06002 | 0.055939 | 0.056959 | 0.054918 | 0.055939 | 0.050837 | 0.050837 | 0.044714 | 0.040633 | 0.036551 | 0.072684 | 0.065541 | 0.054316 | 0.054316 | 0.053296 | 0.053296 | 0.049214 | 0.048194 | 0.041051 | 0.03901 | 0.029827 | 0.026765 | 0.025745
|  | FINCASTLE | EE |  |  |  |  | 0.068 | 0.059837 | 0.049633 | 0.047592 | 0.052694 | 0.047592 | 0.041469 | 0.039429 | 0.033306 | 0.031265 | 0.021061 | 0.021061 | 0.020041 | 0.072265 | 0.064102 | 0.056959 | 0.06002 | 0.064102 | 0.061041 | 0.055939 | 0.055939 | 0.050837 | 0.050837 | 0.044714 | 0.040633 | 0.038592 | 0.072684 | 0.065541 | 0.054316 | 0.054316 | 0.059418 | 0.054316 | 0.049214 | 0.048194 | 0.041051 | 0.03901 | 0.029827 | 0.028806 | 0.027786
|  | FINCASTLE | HT |  |  |  |  | 0.068 | 0.068 | 0.057796 | 0.054735 | 0.046571 | 0.046571 | 0.049633 | 0.044531 | 0.04249 | 0.038408 | 0.025143 | 0.01902 | 0.018 | 0.072265 | 0.072265 | 0.064102 | 0.063082 | 0.055939 | 0.059 | 0.062061 | 0.05798 | 0.05798 | 0.054918 | 0.046755 | 0.043694 | 0.043694 | 0.072684 | 0.072684 | 0.06248 | 0.061459 | 0.053296 | 0.053296 | 0.056357 | 0.052276 | 0.050235 | 0.047173 | 0.033908 | 0.026765 | 0.025745
|  | FINCASTLE | HE |  |  |  |  | 0.06902 | 0.068 | 0.065959 | 0.056776 | 0.049633 | 0.047592 | 0.046571 | 0.048612 | 0.047592 | 0.04351 | 0.030245 | 0.024122 | 0.023102 | 0.072265 | 0.072265 | 0.071245 | 0.064102 | 0.055939 | 0.06002 | 0.059 | 0.06002 | 0.06002 | 0.05798 | 0.050837 | 0.044714 | 0.041653 | 0.072684 | 0.072684 | 0.070643 | 0.06248 | 0.054316 | 0.053296 | 0.052276 | 0.055337 | 0.054316 | 0.051255 | 0.03799 | 0.032888 | 0.031867
|  | FINCASTLE | CF |  |  |  |  | 0.077184 | 0.068 | 0.068 | 0.058816 | 0.057796 | 0.050653 | 0.048612 | 0.047592 | 0.053714 | 0.047592 | 0.038408 | 0.031265 | 0.024122 | 0.080429 | 0.072265 | 0.072265 | 0.064102 | 0.064102 | 0.056959 | 0.054918 | 0.059 | 0.064102 | 0.06002 | 0.054918 | 0.044714 | 0.036551 | 0.079827 | 0.072684 | 0.072684 | 0.0635 | 0.06248 | 0.055337 | 0.054316 | 0.054316 | 0.059418 | 0.054316 | 0.045133 | 0.03799 | 0.032888
| SHETLAND | FIRTH | MINIMUM HEADROOM | HU4396874166 | YES | YES | 0.15 | -2.0216 | -2.8839 | -3.7594 | -4.638 | -5.539 | -6.4431 | -7.3563 | -8.2696 | -9.1727 | -9.2237 | -9.3757 | -9.4369 | -9.4665 | -1.7186 | -2.6655 | -3.6216 | -4.5788 | -5.5471 | -6.5186 | -7.4982 | -8.4788 | -9.4482 | -9.4696 | -9.5196 | -9.5502 | -9.5859 | -1.8441 | -2.7033 | -3.5727 | -4.4431 | -5.3278 | -6.2206 | -7.1196 | -8.0155 | -8.9033 | -8.9349 | -9.0084 | -9.041 | -9.0522
|  | FIRTH | EE |  |  |  |  | -2.0216 | -2.8839 | -3.7594 | -4.638 | -5.539 | -6.4431 | -7.3563 | -8.2696 | -9.1727 | -9.2237 | -9.3461 | -9.3543 | -9.3553 | -1.7186 | -2.6655 | -3.6216 | -4.5788 | -5.5471 | -6.5186 | -7.4982 | -8.4788 | -9.4482 | -9.4696 | -9.5196 | -9.5329 | -9.5604 | -1.8441 | -2.7033 | -3.5727 | -4.4431 | -5.3278 | -6.2206 | -7.1196 | -8.0155 | -8.9033 | -8.9349 | -9.0022 | -9.0084 | -9.0104
|  | FIRTH | HT |  |  |  |  | -2.0135 | -2.8686 | -3.7349 | -4.6094 | -5.5063 | -6.4043 | -7.3043 | -8.2084 | -9.1176 | -9.1727 | -9.3278 | -9.3798 | -9.4043 | -1.7094 | -2.6573 | -3.6043 | -4.5604 | -5.5278 | -6.4941 | -7.4655 | -8.4369 | -9.4135 | -9.4349 | -9.4961 | -9.5206 | -9.5278 | -1.8369 | -2.6931 | -3.5584 | -4.4257 | -5.3114 | -6.1992 | -7.0859 | -7.9778 | -8.8716 | -8.9094 | -8.9941 | -9.0206 | -9.0308
|  | FIRTH | HE |  |  |  |  | -2.0135 | -2.8676 | -3.7329 | -4.6063 | -5.4982 | -6.3961 | -7.3063 | -8.2155 | -9.1267 | -9.1798 | -9.3757 | -9.4369 | -9.4665 | -1.7104 | -2.6594 | -3.6094 | -4.5645 | -5.5329 | -6.5002 | -7.4767 | -8.4512 | -9.4227 | -9.4461 | -9.5176 | -9.5502 | -9.5859 | -1.838 | -2.692 | -3.5543 | -4.4216 | -5.3043 | -6.19 | -7.0849 | -7.9788 | -8.8727 | -8.9043 | -9.0084 | -9.041 | -9.0522
|  | FIRTH | CF |  |  |  |  | -2.0053 | -2.8482 | -3.6982 | -4.5563 | -5.4186 | -6.29 | -7.1655 | -8.041 | -8.9186 | -8.9502 | -9.1349 | -9.2747 | -9.3614 | -1.7104 | -2.6533 | -3.6012 | -4.5553 | -5.5104 | -6.4737 | -7.4369 | -8.4012 | -9.3645 | -9.3849 | -9.4604 | -9.5216 | -9.5839 | -1.8308 | -2.6747 | -3.5267 | -4.3839 | -5.2451 | -6.1135 | -6.9859 | -7.8584 | -8.7329 | -8.7553 | -8.8624 | -8.9359 | -8.9829
| FORT WILLIAM | FISHNISH | MINIMUM HEADROOM | NM 66623 42191 | YES | NO | 0 | 0.23192 | 0.2309 | 0.2309 | 0.2309 | 0.2309 | 0.22886 | 0.22886 | 0.22784 | 0.22784 | 0.22784 | 0.22478 | 0.22376 | 0.22376 | 0.21494 | 0.21392 | 0.21392 | 0.21392 | 0.21392 | 0.2129 | 0.2129 | 0.21188 | 0.21188 | 0.21188 | 0.20984 | 0.20882 | 0.20882 | 0.22394 | 0.22292 | 0.22292 | 0.22292 | 0.22292 | 0.22088 | 0.22088 | 0.21986 | 0.21986 | 0.21986 | 0.21782 | 0.21578 | 0.21578
|  | FISHNISH | EE |  |  |  |  | 0.23192 | 0.2309 | 0.2309 | 0.2309 | 0.2309 | 0.22886 | 0.22886 | 0.22784 | 0.22784 | 0.22784 | 0.22682 | 0.22682 | 0.22682 | 0.21494 | 0.21392 | 0.21392 | 0.21392 | 0.21392 | 0.2129 | 0.2129 | 0.21188 | 0.21188 | 0.21188 | 0.21086 | 0.21086 | 0.21086 | 0.22394 | 0.22292 | 0.22292 | 0.22292 | 0.22292 | 0.22088 | 0.22088 | 0.21986 | 0.21986 | 0.21986 | 0.21884 | 0.21884 | 0.21884
|  | FISHNISH | HT |  |  |  |  | 0.23192 | 0.23192 | 0.2309 | 0.2309 | 0.2309 | 0.2309 | 0.22886 | 0.22886 | 0.22886 | 0.22784 | 0.22682 | 0.22478 | 0.22478 | 0.21494 | 0.21494 | 0.21392 | 0.21392 | 0.21392 | 0.21392 | 0.2129 | 0.2129 | 0.2129 | 0.21188 | 0.21086 | 0.20984 | 0.20984 | 0.22394 | 0.22394 | 0.22292 | 0.22292 | 0.22292 | 0.22292 | 0.22088 | 0.22088 | 0.22088 | 0.21986 | 0.21884 | 0.21782 | 0.21782
|  | FISHNISH | HE |  |  |  |  | 0.23192 | 0.23192 | 0.2309 | 0.2309 | 0.2309 | 0.2309 | 0.22886 | 0.22886 | 0.22784 | 0.22784 | 0.22478 | 0.22376 | 0.22376 | 0.21494 | 0.21494 | 0.21392 | 0.21392 | 0.21392 | 0.21392 | 0.2129 | 0.2129 | 0.21188 | 0.21188 | 0.20984 | 0.20882 | 0.20882 | 0.22394 | 0.22394 | 0.22292 | 0.22292 | 0.22292 | 0.22292 | 0.22088 | 0.22088 | 0.21986 | 0.21986 | 0.21782 | 0.21578 | 0.21578
|  | FISHNISH | CF |  |  |  |  | 0.23192 | 0.23192 | 0.23192 | 0.2309 | 0.2309 | 0.2309 | 0.2309 | 0.2309 | 0.22886 | 0.22886 | 0.22784 | 0.22478 | 0.22478 | 0.21494 | 0.21494 | 0.21494 | 0.21392 | 0.21392 | 0.21392 | 0.21392 | 0.21392 | 0.2129 | 0.2129 | 0.21188 | 0.20984 | 0.20984 | 0.22394 | 0.22394 | 0.22394 | 0.22292 | 0.22292 | 0.22292 | 0.22292 | 0.22292 | 0.22088 | 0.22088 | 0.21986 | 0.21782 | 0.21782
| THURSO | FLOTTA | MINIMUM HEADROOM | NC 94318 95432 | YES | NO | 0 | 0.67245 | 0.66531 | 0.66531 | 0.66122 | 0.65612 | 0.64592 | 0.63571 | 0.63061 | 0.61735 | 0.60714 | 0.58571 | 0.57959 | 0.57551 | 0.13367 | 0.12653 | 0.13163 | 0.12755 | 0.12347 | 0.11735 | 0.11122 | 0.10612 | 0.096939 | 0.089796 | 0.072449 | 0.071429 | 0.066327 | 0.81735 | 0.8102 | 0.8051 | 0.80204 | 0.7949 | 0.78776 | 0.77857 | 0.77245 | 0.75918 | 0.75 | 0.73367 | 0.73163 | 0.72755
|  | FLOTTA | EE |  |  |  |  | 0.67245 | 0.67245 | 0.66531 | 0.66122 | 0.65612 | 0.64592 | 0.63571 | 0.63061 | 0.61735 | 0.60714 | 0.58571 | 0.58265 | 0.57959 | 0.13367 | 0.13673 | 0.13163 | 0.12755 | 0.12347 | 0.11735 | 0.11122 | 0.10612 | 0.096939 | 0.089796 | 0.072449 | 0.071429 | 0.066327 | 0.81735 | 0.81224 | 0.8051 | 0.80204 | 0.7949 | 0.78776 | 0.77857 | 0.77245 | 0.75918 | 0.75 | 0.73367 | 0.73265 | 0.73061
|  | FLOTTA | HT |  |  |  |  | 0.67755 | 0.66531 | 0.67347 | 0.66837 | 0.66122 | 0.6602 | 0.6551 | 0.64388 | 0.63776 | 0.62959 | 0.59286 | 0.57959 | 0.57755 | 0.13367 | 0.12653 | 0.13878 | 0.13571 | 0.12755 | 0.12755 | 0.12551 | 0.11837 | 0.11224 | 0.10612 | 0.078571 | 0.071429 | 0.070408 | 0.82041 | 0.8102 | 0.81531 | 0.81122 | 0.80306 | 0.80204 | 0.79796 | 0.78878 | 0.77959 | 0.77143 | 0.7398 | 0.73163 | 0.72755
|  | FLOTTA | HE |  |  |  |  | 0.67755 | 0.66735 | 0.67449 | 0.66939 | 0.66735 | 0.66327 | 0.65714 | 0.64796 | 0.64082 | 0.62959 | 0.59184 | 0.58061 | 0.57551 | 0.13367 | 0.12653 | 0.13878 | 0.13571 | 0.13163 | 0.12959 | 0.12653 | 0.12143 | 0.11429 | 0.10918 | 0.081633 | 0.07551 | 0.069388 | 0.82041 | 0.81327 | 0.81633 | 0.81122 | 0.80816 | 0.80408 | 0.8 | 0.79082 | 0.78265 | 0.77653 | 0.7449 | 0.73878 | 0.73571
|  | FLOTTA | CF |  |  |  |  | 0.68571 | 0.67653 | 0.67245 | 0.67653 | 0.67041 | 0.66633 | 0.66531 | 0.65918 | 0.65714 | 0.64898 | 0.62653 | 0.59898 | 0.58061 | 0.14286 | 0.13367 | 0.13367 | 0.13878 | 0.13571 | 0.13265 | 0.13163 | 0.12551 | 0.12347 | 0.12041 | 0.10204 | 0.078571 | 0.069388 | 0.82857 | 0.81939 | 0.81735 | 0.81633 | 0.81224 | 0.80918 | 0.80816 | 0.80306 | 0.80102 | 0.79388 | 0.77041 | 0.74592 | 0.7398
| ELGIN | FOCHABERS | MINIMUM HEADROOM | NC 94318 95432 | NO | YES | 3.14 | 5.5474 | 5.2607 | 4.93 | 4.5739 | 4.1749 | 3.4433 | 2.3709 | 1.3617 | 0.42188 | -0.66282 | -5.0465 | -6.2853 | -6.5608 | 6.3464 | 6.1545 | 5.9341 | 5.6902 | 5.4198 | 4.7974 | 3.8719 | 2.978 | 2.1198 | 1.2117 | -2.422 | -3.2802 | -3.4557 | 6.1367 | 5.8714 | 5.5591 | 5.2183 | 4.8397 | 4.1152 | 3.0928 | 2.1142 | 1.2152 | 0.25402 | -4.0878 | -5.2541 | -5.5011
|  | FOCHABERS | EE |  |  |  |  | 5.5474 | 5.2607 | 4.93 | 4.5739 | 4.1749 | 3.4433 | 2.3709 | 1.3617 | 0.42188 | -0.37506 | -4.6189 | -5.0832 | -5.1832 | 6.3464 | 6.1545 | 5.9341 | 5.6902 | 5.4198 | 4.7974 | 3.8719 | 3.0362 | 2.2668 | 1.6137 | -1.9057 | -2.1363 | -2.1975 | 6.1367 | 5.8714 | 5.5591 | 5.2183 | 4.8397 | 4.1152 | 3.0928 | 2.1142 | 1.2152 | 0.4479 | -3.5246 | -3.9439 | -4.0348
|  | FOCHABERS | HT |  |  |  |  | 5.6994 | 5.476 | 5.2249 | 4.9515 | 4.6453 | 3.7831 | 2.5688 | 1.479 | 0.44739 | -0.66282 | -4.0342 | -4.9689 | -5.1169 | 6.4637 | 6.3219 | 6.1678 | 5.9923 | 5.7964 | 5.0117 | 3.9198 | 2.978 | 2.1198 | 1.2117 | -1.4526 | -2.0332 | -2.1251 | 6.2979 | 6.0928 | 5.8652 | 5.6101 | 5.3469 | 4.5152 | 3.3469 | 2.2969 | 1.3112 | 0.25402 | -2.9592 | -3.8307 | -3.9684
|  | FOCHABERS | HE |  |  |  |  | 5.6596 | 5.4239 | 5.176 | 4.8902 | 4.5607 | 3.8596 | 2.8362 | 1.8525 | 0.91473 | -0.09649 | -5.0465 | -6.2853 | -6.5608 | 6.4331 | 6.2678 | 6.0953 | 5.8943 | 5.6637 | 5.0494 | 4.1556 | 3.3474 | 2.5586 | 1.7096 | -2.422 | -3.2802 | -3.4557 | 6.255 | 6.0275 | 5.7816 | 5.4989 | 5.1683 | 4.4632 | 3.4724 | 2.5326 | 1.6326 | 0.66422 | -4.0878 | -5.2541 | -5.5011
|  | FOCHABERS | CF |  |  |  |  | 5.7402 | 5.6025 | 5.4423 | 5.2698 | 5.0729 | 4.7525 | 4.3096 | 3.8239 | 3.3678 | 2.8351 | -0.9618 | -4.4169 | -5.7169 | 6.4872 | 6.3913 | 6.2821 | 6.1637 | 6.0209 | 5.7545 | 5.3678 | 4.9545 | 4.5678 | 4.1351 | 0.93106 | -1.9975 | -2.9057 | 6.3306 | 6.205 | 6.053 | 5.8867 | 5.6908 | 5.3693 | 4.9316 | 4.4408 | 3.9826 | 3.4663 | -0.17659 | -3.4837 | -4.7062
| NAIRN | FORRES | MINIMUM HEADROOM | NJ 03362 59425 | NO | YES | 1.82 | 2.4131 | 1.5744 | 0.70089 | -0.38176 | 21.9744 | 21.008 | 19.504 | 17.9386 | 16.4131 | 14.955 | 8.2672 | 5.3672 | 4.8846 | 6.107 | 5.7274 | 5.1427 | 4.357 | 26.4376 | 25.5448 | 24.4509 | 23.2019 | 22.0182 | 20.9427 | 15.4846 | 13.5142 | 13.2162 | 4.4504 | 3.683 | 2.8167 | 1.8126 | 24.3162 | 23.2325 | 21.8744 | 20.3284 | 18.8744 | 17.5407 | 10.9274 | 8.2009 | 7.7672
|  | FORRES | EE |  |  |  |  | 2.4131 | 1.5744 | 0.70089 | -0.38176 | 21.9744 | 21.008 | 19.504 | 17.9386 | 16.4131 | 14.955 | 8.3856 | 6.2142 | 5.7825 | 6.107 | 5.7274 | 5.1427 | 4.357 | 26.4376 | 25.5448 | 24.4509 | 23.2019 | 22.0182 | 20.9427 | 16.9019 | 16.3121 | 15.6601 | 4.4504 | 3.683 | 2.8167 | 1.8126 | 24.3162 | 23.2325 | 21.8744 | 20.3284 | 18.8744 | 17.5407 | 12.254 | 10.507 | 10.1193
|  | FORRES | HT |  |  |  |  | 2.6009 | 1.8356 | 1.0254 | 0.013135 | 22.4488 | 21.2203 | 19.7142 | 18.3795 | 16.7397 | 15.0193 | 8.8846 | 6.2723 | 5.9376 | 6.2876 | 5.9519 | 5.4284 | 4.7744 | 27.0591 | 26.2468 | 25.2621 | 24.2142 | 23.054 | 21.9223 | 18.0713 | 16.6529 | 16.5142 | 4.7575 | 4.079 | 3.3412 | 2.4269 | 25.0488 | 23.9356 | 22.5733 | 21.3937 | 19.9142 | 18.3897 | 12.8866 | 10.5611 | 10.2774
|  | FORRES | HE |  |  |  |  | 2.6162 | 1.9652 | 1.3091 | 0.44579 | 23.0458 | 21.8744 | 20.4856 | 19.0131 | 17.456 | 15.8478 | 8.2672 | 5.3672 | 4.8846 | 6.3162 | 5.9795 | 5.5131 | 4.805 | 26.9509 | 25.9795 | 24.8958 | 23.7417 | 22.5091 | 21.2437 | 15.4846 | 13.5142 | 13.2162 | 4.7106 | 4.0218 | 3.3177 | 2.4361 | 25.0499 | 23.8876 | 22.5703 | 21.1693 | 19.6866 | 18.1468 | 10.9274 | 8.2009 | 7.7672
|  | FORRES | CF |  |  |  |  | 2.9091 | 2.4968 | 2.0642 | 1.5223 | 24.4866 | 23.8305 | 23.1805 | 22.4642 | 21.7162 | 20.9468 | 15.0601 | 9.6111 | 6.6529 | 6.4448 | 6.2488 | 6.0315 | 5.6703 | 28.2448 | 27.7723 | 27.2233 | 26.5101 | 25.8295 | 25.2009 | 20.5437 | 16.3295 | 14.2621 | 5.0494 | 4.6463 | 4.2055 | 3.6902 | 26.7284 | 26.057 | 25.3642 | 24.5203 | 23.7244 | 22.9907 | 17.3835 | 12.206 | 9.4213
| DOUNREAY | FORSS | MINIMUM HEADROOM | ND 02614 69148 | YES | NO | 0.681 | -0.91521 | -0.98256 | -1.055 | -1.1326 | -1.2101 | -1.2948 | -1.3866 | -1.4856 | -1.5866 | -1.6775 | -2.0499 | -2.2142 | -2.306 | -0.70194 | -0.75704 | -0.81521 | -0.87235 | -0.92847 | -0.99072 | -1.057 | -1.1264 | -1.1917 | -1.2468 | -1.5101 | -1.6326 | -1.706 | -1.1897 | -1.2264 | -1.2856 | -1.355 | -1.4285 | -1.507 | -1.5989 | -1.703 | -1.8019 | -1.8887 | -2.2448 | -2.4019 | -2.4907
|  | FORSS | EE |  |  |  |  | -0.91521 | -0.98256 | -1.055 | -1.1326 | -1.2101 | -1.2948 | -1.3866 | -1.4856 | -1.5866 | -1.6775 | -1.953 | -1.9866 | -1.9928 | -0.70194 | -0.75704 | -0.81521 | -0.87235 | -0.92847 | -0.99072 | -1.057 | -1.1264 | -1.1917 | -1.2468 | -1.4264 | -1.4509 | -1.4581 | -1.1897 | -1.2264 | -1.2856 | -1.355 | -1.4285 | -1.507 | -1.5989 | -1.703 | -1.8019 | -1.8887 | -2.1489 | -2.1815 | -2.1877
|  | FORSS | HT |  |  |  |  | -0.89786 | -0.96011 | -1.0162 | -1.0805 | -1.1407 | -1.207 | -1.2764 | -1.3621 | -1.4397 | -1.5162 | -1.8989 | -2.056 | -2.1356 | -0.6846 | -0.73256 | -0.78562 | -0.83562 | -0.87847 | -0.92643 | -0.97337 | -1.0326 | -1.0887 | -1.1387 | -1.3917 | -1.505 | -1.5632 | -1.1713 | -1.205 | -1.2509 | -1.304 | -1.3611 | -1.4234 | -1.4907 | -1.5683 | -1.6468 | -1.7234 | -2.0989 | -2.2479 | -2.3224
|  | FORSS | HE |  |  |  |  | -0.89786 | -0.94888 | -1.007 | -1.0683 | -1.1275 | -1.1979 | -1.2734 | -1.3662 | -1.457 | -1.556 | -2.0499 | -2.2142 | -2.306 | -0.6846 | -0.73256 | -0.78051 | -0.83051 | -0.87439 | -0.92745 | -0.98051 | -1.0499 | -1.1121 | -1.1713 | -1.5101 | -1.6326 | -1.706 | -1.1724 | -1.2009 | -1.2407 | -1.2989 | -1.356 | -1.4224 | -1.4928 | -1.5877 | -1.6815 | -1.7744 | -2.2448 | -2.4019 | -2.4907
|  | FORSS | CF |  |  |  |  | -0.89582 | -0.92541 | -0.95704 | -0.98868 | -1.0326 | -1.0744 | -1.1254 | -1.1836 | -1.2407 | -1.2989 | -1.6611 | -1.9928 | -2.1989 | -0.68562 | -0.70296 | -0.72745 | -0.75909 | -0.79276 | -0.82337 | -0.86215 | -0.90398 | -0.9448 | -0.98868 | -1.2356 | -1.4764 | -1.6244 | -1.1724 | -1.1866 | -1.207 | -1.2295 | -1.2591 | -1.2979 | -1.3468 | -1.3999 | -1.454 | -1.5111 | -1.8734 | -2.1907 | -2.3877
| BRACO | FORTEVIOT | MINIMUM HEADROOM | NO 04539 18092 | YES | YES | 0.841 | 4.4979 | 4.1703 | 3.9448 | 3.7693 | 3.6172 | 3.4979 | 3.3234 | 3.1815 | 3.0224 | 2.8815 | 2.3846 | 2.1183 | 2.0652 | 4.6156 | 4.3502 | 4.1615 | 4.0247 | 3.9125 | 3.8135 | 3.6951 | 3.5951 | 3.4992 | 3.4115 | 3.1298 | 3.0421 | 2.8319 | 4.6715 | 4.3746 | 4.1664 | 4.0072 | 3.8664 | 3.7225 | 3.5664 | 3.4256 | 3.2868 | 3.1603 | 2.7184 | 2.4868 | 2.4389
|  | FORTEVIOT | EE |  |  |  |  | 4.5836 | 4.2642 | 4.0326 | 3.8397 | 3.6601 | 3.4979 | 3.3234 | 3.1815 | 3.0224 | 2.8815 | 2.3846 | 2.1387 | 2.0866 | 4.6829 | 4.4288 | 4.236 | 4.0788 | 3.94 | 3.8135 | 3.6951 | 3.5951 | 3.4992 | 3.4115 | 3.1298 | 3.0421 | 2.8911 | 4.746 | 4.4511 | 4.2358 | 4.0511 | 3.8817 | 3.7225 | 3.5664 | 3.4256 | 3.2868 | 3.1603 | 2.7184 | 2.5052 | 2.4582
|  | FORTEVIOT | HT |  |  |  |  | 4.4979 | 4.1703 | 3.9448 | 3.7693 | 3.6172 | 3.5009 | 3.3734 | 3.2438 | 3.1121 | 3.0101 | 2.4295 | 2.1183 | 2.0652 | 4.6156 | 4.3502 | 4.1615 | 4.0247 | 3.9125 | 3.8319 | 3.7594 | 3.6788 | 3.6064 | 3.54 | 3.2125 | 3.0727 | 3.0278 | 4.6715 | 4.3746 | 4.1664 | 4.0072 | 3.8664 | 3.7593 | 3.644 | 3.5205 | 3.3991 | 3.3031 | 2.7623 | 2.4868 | 2.4389
|  | FORTEVIOT | HE |  |  |  |  | 4.5989 | 4.303 | 4.1091 | 3.9468 | 3.8009 | 3.6897 | 3.5693 | 3.4591 | 3.3499 | 3.2683 | 2.706 | 2.4203 | 2.304 | 4.6962 | 4.4523 | 4.2829 | 4.139 | 4.0156 | 3.9186 | 3.8227 | 3.7319 | 3.6492 | 3.5768 | 3.2084 | 3.0717 | 2.989 | 4.7623 | 4.4868 | 4.3021 | 4.1419 | 3.9991 | 3.8827 | 3.7603 | 3.6399 | 3.5276 | 3.4297 | 2.895 | 2.6705 | 2.5664
|  | FORTEVIOT | CF |  |  |  |  | 4.8275 | 4.6672 | 4.5326 | 4.4101 | 4.2826 | 4.1621 | 4.0672 | 3.957 | 3.8724 | 3.7805 | 3.3101 | 2.8285 | 2.5479 | 4.889 | 4.7554 | 4.6431 | 4.5492 | 4.4523 | 4.3543 | 4.2727 | 4.1788 | 4.1043 | 4.0247 | 3.6125 | 3.2217 | 2.8319 | 4.9725 | 4.8225 | 4.695 | 4.5858 | 4.4695 | 4.3552 | 4.2603 | 4.1531 | 4.0654 | 3.9715 | 3.4654 | 2.996 | 2.7327
| INVERNESS | FOYERS | MINIMUM HEADROOM | NH 49740 21044 | YES | NO | 0.298 | 0.56624 | 0.55808 | 0.55196 | 0.53971 | 0.51931 | 0.51216 | 0.49073 | 0.46727 | 0.46522 | 0.44584 | 0.40706 | 0.39278 | 0.38767 | 0.63053 | 0.62849 | 0.62543 | 0.61727 | 0.604 | 0.59992 | 0.58767 | 0.56522 | 0.56624 | 0.55604 | 0.52747 | 0.51829 | 0.48257 | 0.59073 | 0.58563 | 0.57849 | 0.56522 | 0.54686 | 0.54176 | 0.52339 | 0.4989 | 0.49482 | 0.47849 | 0.44278 | 0.42849 | 0.42441
|  | FOYERS | EE |  |  |  |  | 0.56829 | 0.55808 | 0.55196 | 0.53971 | 0.51931 | 0.51216 | 0.49073 | 0.46727 | 0.46522 | 0.44584 | 0.40706 | 0.39686 | 0.39482 | 0.63461 | 0.62849 | 0.62543 | 0.61727 | 0.604 | 0.59992 | 0.58767 | 0.56522 | 0.56624 | 0.55604 | 0.52747 | 0.51829 | 0.504 | 0.5938 | 0.58563 | 0.57849 | 0.56522 | 0.54686 | 0.54176 | 0.52339 | 0.4989 | 0.49482 | 0.47849 | 0.44278 | 0.43257 | 0.43053
|  | FOYERS | HT |  |  |  |  | 0.56624 | 0.56727 | 0.55706 | 0.54788 | 0.54176 | 0.52645 | 0.51216 | 0.50298 | 0.48563 | 0.46829 | 0.41727 | 0.39278 | 0.38767 | 0.63053 | 0.63563 | 0.62951 | 0.62441 | 0.62135 | 0.61216 | 0.604 | 0.59686 | 0.58563 | 0.57645 | 0.54278 | 0.52951 | 0.52645 | 0.59176 | 0.59278 | 0.58359 | 0.57441 | 0.56931 | 0.55706 | 0.5438 | 0.53359 | 0.51624 | 0.50196 | 0.45094 | 0.42849 | 0.42441
|  | FOYERS | HE |  |  |  |  | 0.56624 | 0.56931 | 0.55808 | 0.55502 | 0.55094 | 0.53767 | 0.52543 | 0.51727 | 0.50094 | 0.48563 | 0.42543 | 0.40502 | 0.39992 | 0.63053 | 0.63563 | 0.62951 | 0.62645 | 0.62441 | 0.61522 | 0.60706 | 0.59992 | 0.58971 | 0.57951 | 0.53767 | 0.52339 | 0.50808 | 0.59073 | 0.59584 | 0.58665 | 0.58257 | 0.57645 | 0.56318 | 0.55298 | 0.54686 | 0.53053 | 0.51727 | 0.4591 | 0.44176 | 0.43665
|  | FOYERS | CF |  |  |  |  | 0.57543 | 0.5642 | 0.56522 | 0.55604 | 0.54992 | 0.54788 | 0.53767 | 0.52747 | 0.52339 | 0.5142 | 0.47339 | 0.42543 | 0.404 | 0.63869 | 0.63257 | 0.63461 | 0.62849 | 0.62339 | 0.61931 | 0.61522 | 0.60604 | 0.604 | 0.59482 | 0.56216 | 0.51931 | 0.48257 | 0.60094 | 0.59073 | 0.59176 | 0.58359 | 0.57849 | 0.57543 | 0.56624 | 0.55502 | 0.55298 | 0.54482 | 0.504 | 0.4591 | 0.43971
| FRASERBURGH | FRASERBURGH | MINIMUM HEADROOM | NH 51502 69028 | NO | YES | 4.535 | 16.602 | 15.5234 | 14.3959 | 13.1602 | 11.7714 | 10.2367 | 8.7449 | 6.8887 | 4.853 | 2.6081 | -3.2306 | -6.1102 | -6.6082 | 20.803 | 20.0459 | 19.2336 | 18.3265 | 17.2918 | 16.101 | 15.1132 | 13.8194 | 12.3704 | 10.704 | 7.1051 | 5.4938 | 3.9092 | 18.8234 | 17.8489 | 16.8122 | 15.6561 | 14.351 | 12.8908 | 11.5204 | 9.7949 | 7.9132 | 5.8255 | 0.65201 | -1.849 | -2.2755
|  | FRASERBURGH | EE |  |  |  |  | 16.6102 | 15.5632 | 14.5469 | 13.3377 | 12.2479 | 10.85 | 9.1306 | 7.3724 | 5.5581 | 3.6132 | -3.2011 | -5.8408 | -6.3725 | 20.8092 | 20.0632 | 19.3306 | 18.4408 | 17.6449 | 16.5724 | 15.3255 | 14.0755 | 12.803 | 11.3918 | 7.1051 | 5.4938 | 4.2673 | 18.8234 | 17.8571 | 16.8979 | 15.7632 | 14.7989 | 13.4796 | 11.8612 | 10.2173 | 8.551 | 6.7561 | 0.67548 | -1.6062 | -2.0572
|  | FRASERBURGH | HT |  |  |  |  | 16.602 | 15.5234 | 14.3959 | 13.1602 | 11.7714 | 10.2367 | 8.7449 | 6.8887 | 4.853 | 2.6081 | -3.2306 | -6.1102 | -6.6082 | 20.803 | 20.0459 | 19.2336 | 18.3265 | 17.2918 | 16.101 | 15.1132 | 13.8194 | 12.3704 | 10.704 | 7.5367 | 6.3306 | 6.0081 | 18.8367 | 17.8489 | 16.8122 | 15.6561 | 14.351 | 12.8908 | 11.5204 | 9.7949 | 7.9132 | 5.8255 | 0.65201 | -1.849 | -2.2755
|  | FRASERBURGH | HE |  |  |  |  | 16.7234 | 15.8979 | 15.1194 | 14.1449 | 13.054 | 11.8643 | 10.4592 | 9.2643 | 7.7857 | 6.1398 | -0.33881 | -3.4051 | -4.3796 | 20.901 | 20.2622 | 19.6449 | 18.8867 | 18.0224 | 17.0418 | 15.9112 | 14.8255 | 13.5918 | 12.1938 | 7.7714 | 6.3898 | 5.003 | 18.9459 | 18.1877 | 17.4643 | 16.5581 | 15.5306 | 14.3959 | 13.0571 | 11.9489 | 10.5581 | 9.0112 | 3.1061 | 0.45201 | -0.41126
|  | FRASERBURGH | CF |  |  |  |  | 17.0122 | 16.5153 | 16.0367 | 15.4847 | 14.8551 | 14.1163 | 13.3847 | 12.5449 | 11.9877 | 11.0928 | 5.5163 | 0.55405 | -2.147 | 21.1336 | 20.752 | 20.3612 | 19.9306 | 19.4245 | 18.8102 | 18.1724 | 17.4326 | 16.9265 | 16.1387 | 11.5959 | 7.2234 | 3.9092 | 19.2163 | 18.7622 | 18.3194 | 17.8102 | 17.2255 | 16.5357 | 15.8428 | 15.0459 | 14.5255 | 13.6796 | 8.5143 | 3.9704 | 1.5653
| LUNANHEAD | FRIOCKHEIM | MINIMUM HEADROOM | NO 58834 49317 | YES | YES | 0.132 | 2.6065 | 2.4932 | 2.3586 | 2.2004 | 2.0626 | 1.8984 | 1.6708 | 1.4728 | 1.2473 | 1.0422 | 0.40549 | 0.034065 | -0.046547 | 3.9565 | 3.8902 | 3.8055 | 3.7024 | 3.6218 | 3.5116 | 3.3677 | 3.2555 | 3.1126 | 2.9881 | 2.631 | 2.4463 | 2.1024 | 3.2198 | 3.1177 | 2.9902 | 2.8422 | 2.7167 | 2.5616 | 2.3432 | 2.1657 | 1.9484 | 1.7565 | 1.1861 | 0.881 | 0.81774
|  | FRIOCKHEIM | EE |  |  |  |  | 2.6065 | 2.4932 | 2.3586 | 2.2004 | 2.0626 | 1.8984 | 1.6708 | 1.4728 | 1.2473 | 1.0422 | 0.40549 | 0.091208 | 0.02182 | 3.9565 | 3.8902 | 3.8055 | 3.7024 | 3.6218 | 3.5116 | 3.3677 | 3.2555 | 3.1126 | 2.9881 | 2.631 | 2.4463 | 2.2432 | 3.2198 | 3.1177 | 2.9902 | 2.8422 | 2.7167 | 2.5616 | 2.3432 | 2.1657 | 1.9484 | 1.7565 | 1.1861 | 0.93407 | 0.87182
|  | FRIOCKHEIM | HT |  |  |  |  | 2.6453 | 2.5371 | 2.4269 | 2.2984 | 2.1535 | 2.0157 | 1.8565 | 1.6647 | 1.4708 | 1.2718 | 0.45958 | 0.034065 | -0.046547 | 3.9953 | 3.9392 | 3.8759 | 3.8096 | 3.731 | 3.6432 | 3.5698 | 3.4555 | 3.3402 | 3.2208 | 2.7514 | 2.5555 | 2.5198 | 3.2596 | 3.1626 | 3.0596 | 2.9484 | 2.8167 | 2.6851 | 2.5494 | 2.3688 | 2.1881 | 2.0014 | 1.2453 | 0.881 | 0.81774
|  | FRIOCKHEIM | HE |  |  |  |  | 2.6463 | 2.5871 | 2.5035 | 2.4198 | 2.3106 | 2.2035 | 2.0963 | 1.9443 | 1.7932 | 1.6371 | 0.83611 | 0.42692 | 0.23917 | 3.9922 | 3.9565 | 3.8973 | 3.8463 | 3.7769 | 3.7014 | 3.631 | 3.5259 | 3.4269 | 3.3239 | 2.833 | 2.5861 | 2.3535 | 3.2596 | 3.1922 | 3.1177 | 3.0351 | 2.9371 | 2.8361 | 2.7188 | 2.5677 | 2.4269 | 2.2779 | 1.5341 | 1.1555 | 0.98509
|  | FRIOCKHEIM | CF |  |  |  |  | 2.6667 | 2.6198 | 2.5626 | 2.4912 | 2.4371 | 2.3647 | 2.279 | 2.2147 | 2.129 | 2.0422 | 1.5392 | 0.96774 | 0.59121 | 4.0045 | 3.9698 | 3.931 | 3.8769 | 3.8402 | 3.7861 | 3.7208 | 3.6728 | 3.6065 | 3.5351 | 3.1524 | 2.6535 | 2.1024 | 3.279 | 3.2361 | 3.181 | 3.1147 | 3.0637 | 2.9953 | 2.9147 | 2.8504 | 2.7657 | 2.6769 | 2.1922 | 1.6555 | 1.3024
| KINTORE | FYVIE | MINIMUM HEADROOM | NJ 76759 37635 | NO | YES | 0.328 | 3.1691 | 3.0701 | 2.9385 | 2.7874 | 2.6589 | 2.4987 | 2.315 | 2.1629 | 1.9885 | 1.8364 | 1.3885 | 1.266 | 1.2089 | 4.5487 | 4.465 | 4.3599 | 4.2272 | 4.116 | 3.9793 | 3.8293 | 3.716 | 3.5823 | 3.465 | 3.1874 | 3.0854 | 2.7895 | 3.9599 | 3.8283 | 3.6772 | 3.5038 | 3.3446 | 3.1629 | 2.9354 | 2.7599 | 2.5558 | 2.3793 | 1.9803 | 1.8793 | 1.8354
|  | FYVIE | EE |  |  |  |  | 3.1691 | 3.0701 | 2.9385 | 2.7874 | 2.6589 | 2.4987 | 2.315 | 2.1629 | 1.9885 | 1.8364 | 1.3885 | 1.315 | 1.2823 | 4.5487 | 4.465 | 4.3599 | 4.2272 | 4.116 | 3.9793 | 3.8293 | 3.716 | 3.5823 | 3.465 | 3.1874 | 3.0854 | 2.9425 | 3.9599 | 3.8283 | 3.6772 | 3.5038 | 3.3446 | 3.1629 | 2.9354 | 2.7599 | 2.5558 | 2.3793 | 1.9803 | 1.917 | 1.8844
|  | FYVIE | HT |  |  |  |  | 3.215 | 3.1385 | 3.0211 | 2.916 | 2.7813 | 2.6538 | 2.566 | 2.418 | 2.2599 | 2.0976 | 1.5303 | 1.266 | 1.2089 | 4.5823 | 4.5089 | 4.4027 | 4.3027 | 4.1803 | 4.0711 | 3.9997 | 3.8946 | 3.7956 | 3.6956 | 3.3272 | 3.1874 | 3.1609 | 3.9793 | 3.8609 | 3.7089 | 3.5527 | 3.3711 | 3.217 | 3.0915 | 2.9446 | 2.8017 | 2.6578 | 2.115 | 1.8793 | 1.8354
|  | FYVIE | HE |  |  |  |  | 3.218 | 3.1517 | 3.0548 | 2.968 | 2.8527 | 2.7344 | 2.6395 | 2.5089 | 2.3854 | 2.2538 | 1.5762 | 1.3864 | 1.3476 | 4.5854 | 4.5232 | 4.4385 | 4.3568 | 4.2527 | 4.1497 | 4.065 | 3.9619 | 3.868 | 3.765 | 3.2976 | 3.1283 | 2.9885 | 3.9854 | 3.8966 | 3.7823 | 3.668 | 3.5354 | 3.3987 | 3.266 | 3.1313 | 3.0027 | 2.867 | 2.1609 | 1.9905 | 1.9578
|  | FYVIE | CF |  |  |  |  | 3.2395 | 3.1864 | 3.1221 | 3.065 | 2.9864 | 2.9048 | 2.8129 | 2.7436 | 2.6538 | 2.5599 | 2.0997 | 1.6466 | 1.4211 | 4.6027 | 4.5527 | 4.4966 | 4.4405 | 4.367 | 4.2925 | 4.2089 | 4.1476 | 4.0711 | 3.9925 | 3.5885 | 3.1415 | 2.7895 | 4.0068 | 3.9334 | 3.8527 | 3.7742 | 3.6772 | 3.5823 | 3.4732 | 3.3864 | 3.2925 | 3.1936 | 2.6742 | 2.1976 | 2.0089
| GRUDIE BRIDGE | GARBAT FOREST | MINIMUM HEADROOM | NH 41255 67993 | YES | NO | 0 | 0.11698 | 0.11596 | 0.11596 | 0.11596 | 0.11392 | 0.11392 | 0.11392 | 0.1129 | 0.1129 | 0.11188 | 0.10984 | 0.10882 | 0.1078 | 0.10798 | 0.10696 | 0.10696 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.10288 | 0.10186 | 0.10084 | 0.11248 | 0.11146 | 0.11146 | 0.11146 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.10738 | 0.10636 | 0.10432 | 0.1033
|  | GARBAT FOREST | EE |  |  |  |  | 0.11698 | 0.11596 | 0.11596 | 0.11596 | 0.11392 | 0.11392 | 0.11392 | 0.1129 | 0.1129 | 0.11188 | 0.10984 | 0.10984 | 0.10984 | 0.10798 | 0.10696 | 0.10696 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.10288 | 0.10288 | 0.10288 | 0.11248 | 0.11146 | 0.11146 | 0.11146 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.10738 | 0.10636 | 0.10636 | 0.10636
|  | GARBAT FOREST | HT |  |  |  |  | 0.11698 | 0.11698 | 0.11596 | 0.11596 | 0.11596 | 0.11596 | 0.11392 | 0.11392 | 0.11392 | 0.1129 | 0.10984 | 0.10984 | 0.10984 | 0.10798 | 0.10798 | 0.10696 | 0.10696 | 0.10696 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10288 | 0.10288 | 0.10288 | 0.11248 | 0.11248 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.10636 | 0.10636 | 0.10636
|  | GARBAT FOREST | HE |  |  |  |  | 0.11698 | 0.11698 | 0.11596 | 0.11596 | 0.11596 | 0.11392 | 0.11392 | 0.11392 | 0.1129 | 0.1129 | 0.10984 | 0.10882 | 0.1078 | 0.10798 | 0.10798 | 0.10696 | 0.10696 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10288 | 0.10186 | 0.10084 | 0.11248 | 0.11248 | 0.11146 | 0.11146 | 0.11146 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.10636 | 0.10432 | 0.1033
|  | GARBAT FOREST | CF |  |  |  |  | 0.11698 | 0.11698 | 0.11698 | 0.11596 | 0.11596 | 0.11596 | 0.11596 | 0.11596 | 0.11392 | 0.11392 | 0.11188 | 0.10984 | 0.10882 | 0.10798 | 0.10798 | 0.10798 | 0.10696 | 0.10696 | 0.10696 | 0.10696 | 0.10696 | 0.10594 | 0.10594 | 0.1039 | 0.10288 | 0.10186 | 0.11248 | 0.11248 | 0.11248 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.11146 | 0.10942 | 0.10942 | 0.10738 | 0.10636 | 0.10432
| STORNOWAY | GISLA | MINIMUM HEADROOM | NB 12846 25823 | YES | YES | 0.112 | -0.74285 | -0.76122 | -0.80204 | -0.82142 | 1.3969 | 1.3725 | 1.3316 | 1.3061 | 1.2663 | 1.2306 | 1.0704 | 1.0133 | 0.9949 | -0.3551 | -0.37244 | -0.40918 | -0.42449 | 1.798 | 1.7796 | 1.7449 | 1.7245 | 1.6929 | 1.6622 | 1.5694 | 1.5316 | 1.4969 | -0.66938 | -0.69489 | -0.73163 | -0.75714 | 1.4653 | 1.4357 | 1.3929 | 1.3571 | 1.3112 | 1.2653 | 1.1378 | 1.0969 | 1.0786
|  | GISLA | EE |  |  |  |  | -0.74285 | -0.76122 | -0.80204 | -0.82142 | 1.3969 | 1.3725 | 1.3316 | 1.3061 | 1.2663 | 1.2306 | 1.0704 | 1.0174 | 1.0112 | -0.3551 | -0.37244 | -0.40918 | -0.42449 | 1.798 | 1.7796 | 1.7449 | 1.7245 | 1.6929 | 1.6622 | 1.5694 | 1.5347 | 1.5286 | -0.66938 | -0.68673 | -0.73163 | -0.75714 | 1.4653 | 1.4357 | 1.3929 | 1.3571 | 1.3112 | 1.2653 | 1.1378 | 1.1031 | 1.0969
|  | GISLA | HT |  |  |  |  | -0.72857 | -0.75204 | -0.77142 | -0.78877 | 1.4347 | 1.4214 | 1.3918 | 1.3684 | 1.3327 | 1.2867 | 1.0969 | 1.0133 | 0.9949 | -0.34387 | -0.36326 | -0.38061 | -0.39387 | 1.8347 | 1.8265 | 1.8 | 1.7735 | 1.7418 | 1.7122 | 1.5878 | 1.5316 | 1.5194 | -0.65918 | -0.69489 | -0.71734 | -0.74183 | 1.4816 | 1.4582 | 1.4235 | 1.3908 | 1.3541 | 1.3174 | 1.1714 | 1.0969 | 1.0786
|  | GISLA | HE |  |  |  |  | -0.72857 | -0.73979 | -0.76938 | -0.78367 | 1.4429 | 1.4327 | 1.4061 | 1.3827 | 1.3531 | 1.3071 | 1.099 | 1.0541 | 1.0439 | -0.34387 | -0.35204 | -0.37857 | -0.39183 | 1.8388 | 1.8316 | 1.8082 | 1.7816 | 1.7531 | 1.7194 | 1.5857 | 1.552 | 1.5429 | -0.65918 | -0.66938 | -0.70612 | -0.72551 | 1.5031 | 1.4857 | 1.4561 | 1.4255 | 1.3908 | 1.3561 | 1.1725 | 1.1276 | 1.1153
|  | GISLA | CF |  |  |  |  | -0.72347 | -0.73673 | -0.74591 | -0.7653 | 1.4674 | 1.449 | 1.4418 | 1.4204 | 1.398 | 1.3878 | 1.2898 | 1.1378 | 1.0214 | -0.33979 | -0.35102 | -0.35918 | -0.37653 | 1.8571 | 1.8398 | 1.8347 | 1.8153 | 1.7969 | 1.7898 | 1.7051 | 1.6031 | 1.4969 | -0.65408 | -0.66632 | -0.67857 | -0.70918 | 1.5225 | 1.5061 | 1.4929 | 1.4725 | 1.448 | 1.4327 | 1.3245 | 1.2082 | 1.1041
| ALNESS | GLASTULLICH | MINIMUM HEADROOM | NH 78509 76508 | YES | NO | 0.056 | -0.71013 | -0.7836 | -0.87442 | -0.94482 | -1.0346 | -1.1418 | -1.2285 | -1.3683 | -1.503 | -1.6214 | -1.8877 | -1.9805 | -1.953 | 0.61436 | 0.56742 | 0.50926 | 0.4664 | 0.40722 | 0.33783 | 0.28783 | 0.19395 | 0.10416 | 0.029665 | -0.14993 | -0.21421 | -0.43054 | -0.34687 | -0.41319 | -0.49891 | -0.56727 | -0.64993 | -0.74891 | -0.83054 | -0.96319 | -1.0887 | -1.1979 | -1.4438 | -1.5305 | -1.5071
|  | GLASTULLICH | EE |  |  |  |  | -0.71013 | -0.7836 | -0.87442 | -0.94482 | -1.0346 | -1.1418 | -1.2285 | -1.3683 | -1.503 | -1.6214 | -1.8877 | -1.9326 | -1.8999 | 0.61436 | 0.56742 | 0.50926 | 0.4664 | 0.40722 | 0.33783 | 0.28783 | 0.19395 | 0.10416 | 0.029665 | -0.14993 | -0.21421 | -0.28666 | -0.34687 | -0.41319 | -0.49891 | -0.56727 | -0.64993 | -0.74891 | -0.83054 | -0.96319 | -1.0887 | -1.1979 | -1.4438 | -1.4856 | -1.4622
|  | GLASTULLICH | HT |  |  |  |  | -0.68156 | -0.74482 | -0.80707 | -0.87238 | -0.94891 | -1.0142 | -1.102 | -1.204 | -1.306 | -1.3683 | -1.805 | -1.9805 | -1.953 | 0.63885 | 0.60109 | 0.56742 | 0.52762 | 0.47762 | 0.44293 | 0.39191 | 0.32354 | 0.25518 | 0.22456 | -0.070335 | -0.17136 | -0.13768 | -0.31829 | -0.37748 | -0.43564 | -0.49687 | -0.56931 | -0.62952 | -0.71013 | -0.80707 | -0.90299 | -0.96115 | -1.3673 | -1.5305 | -1.5071
|  | GLASTULLICH | HE |  |  |  |  | -0.68156 | -0.7336 | -0.78054 | -0.8285 | -0.89074 | -0.93666 | -1.0101 | -1.102 | -1.1948 | -1.2458 | -1.7326 | -1.8438 | -1.8601 | 0.63681 | 0.60518 | 0.57456 | 0.54497 | 0.49803 | 0.47252 | 0.42558 | 0.3613 | 0.30007 | 0.2715 | -0.044824 | -0.15197 | -0.25197 | -0.31829 | -0.36625 | -0.41115 | -0.45809 | -0.51523 | -0.55911 | -0.6285 | -0.71727 | -0.80095 | -0.84993 | -1.2958 | -1.4009 | -1.4152
|  | GLASTULLICH | CF |  |  |  |  | -0.67136 | -0.71523 | -0.75299 | -0.79278 | -0.84891 | -0.90401 | -0.93768 | -1.005 | -1.0601 | -1.1224 | -1.4193 | -1.7132 | -1.8418 | 0.64497 | 0.6164 | 0.59497 | 0.56538 | 0.53273 | 0.49089 | 0.47354 | 0.42252 | 0.38375 | 0.33885 | 0.11742 | -0.16217 | -0.43054 | -0.30911 | -0.34789 | -0.38462 | -0.42238 | -0.47238 | -0.52646 | -0.55503 | -0.61829 | -0.67136 | -0.73156 | -1.0101 | -1.2867 | -1.402
| SHIN | GLEDFIELD | MINIMUM HEADROOM | NH 58876 90837 | YES | NO | 0.457 | 1.3396 | 1.2927 | 1.2427 | 1.1763 | 1.1335 | 1.0192 | 0.92021 | 0.82327 | 0.73449 | 0.69572 | 0.52327 | 0.45796 | 0.4396 | 1.7013 | 1.6768 | 1.6442 | 1.6034 | 1.5758 | 1.5095 | 1.4493 | 1.3891 | 1.3299 | 1.3085 | 1.185 | 1.1268 | 0.94011 | 1.5271 | 1.4822 | 1.4342 | 1.374 | 1.3312 | 1.2261 | 1.1363 | 1.0485 | 0.96485 | 0.92812 | 0.76587 | 0.70771 | 0.68934
|  | GLEDFIELD | EE |  |  |  |  | 1.3396 | 1.2927 | 1.2427 | 1.1763 | 1.1335 | 1.0192 | 0.92021 | 0.82327 | 0.73449 | 0.69572 | 0.52327 | 0.49062 | 0.47021 | 1.7013 | 1.6768 | 1.6442 | 1.6034 | 1.5758 | 1.5095 | 1.4493 | 1.3891 | 1.3299 | 1.3085 | 1.185 | 1.1268 | 1.035 | 1.5271 | 1.4822 | 1.4342 | 1.374 | 1.3312 | 1.2261 | 1.1363 | 1.0485 | 0.96485 | 0.92812 | 0.76587 | 0.73526 | 0.71791
|  | GLEDFIELD | HT |  |  |  |  | 1.3651 | 1.3274 | 1.2722 | 1.2345 | 1.1927 | 1.0876 | 0.9998 | 0.94878 | 0.88245 | 0.82123 | 0.57429 | 0.45796 | 0.4396 | 1.7146 | 1.6952 | 1.6697 | 1.6472 | 1.6228 | 1.5666 | 1.5156 | 1.4891 | 1.4493 | 1.4085 | 1.2564 | 1.186 | 1.1748 | 1.5485 | 1.5118 | 1.4618 | 1.4261 | 1.3863 | 1.2924 | 1.2128 | 1.1669 | 1.1036 | 1.0434 | 0.81383 | 0.70771 | 0.68934
|  | GLEDFIELD | HE |  |  |  |  | 1.3651 | 1.3355 | 1.2886 | 1.2631 | 1.2294 | 1.1406 | 1.058 | 1.0202 | 0.96307 | 0.91102 | 0.61817 | 0.5498 | 0.53756 | 1.7146 | 1.7003 | 1.6748 | 1.6575 | 1.6381 | 1.585 | 1.533 | 1.5126 | 1.4717 | 1.436 | 1.2472 | 1.1626 | 1.0809 | 1.5485 | 1.5189 | 1.4812 | 1.4536 | 1.423 | 1.3393 | 1.2679 | 1.2291 | 1.174 | 1.1261 | 0.85465 | 0.79036 | 0.78016
|  | GLEDFIELD | CF |  |  |  |  | 1.3661 | 1.3416 | 1.31 | 1.2865 | 1.2498 | 1.1845 | 1.1263 | 1.0763 | 1.058 | 1.0161 | 0.7947 | 0.6447 | 0.5549 | 1.7146 | 1.7034 | 1.685 | 1.6738 | 1.6493 | 1.6126 | 1.5768 | 1.5401 | 1.5279 | 1.4962 | 1.3217 | 1.1472 | 0.94011 | 1.5506 | 1.5281 | 1.4995 | 1.4781 | 1.4455 | 1.3853 | 1.3332 | 1.2904 | 1.27 | 1.2332 | 1.0291 | 0.8873 | 0.79852
| FORT AUGUSTUS | GLEN LAOGH | MINIMUM HEADROOM | NH 27430 00910 | YES | YES | 0 | 0.1129 | 0.1129 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10984 | 0.10984 | 0.10984 | 0.10882 | 0.1078 | 0.1078 | 0.10576 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10492 | 0.1039 | 0.10288 | 0.10288 | 0.10186 | 0.11044 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10738 | 0.10738 | 0.10738 | 0.10636 | 0.10534 | 0.10534 | 0.10432
|  | GLEN LAOGH | EE |  |  |  |  | 0.1129 | 0.1129 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10984 | 0.10984 | 0.10984 | 0.10882 | 0.10882 | 0.10882 | 0.10882 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10492 | 0.1039 | 0.1039 | 0.1039 | 0.1039 | 0.11044 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10738 | 0.10738 | 0.10738 | 0.10636 | 0.10636 | 0.10636 | 0.10636
|  | GLEN LAOGH | HT |  |  |  |  | 0.1129 | 0.1129 | 0.1129 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10984 | 0.10984 | 0.10984 | 0.10882 | 0.1078 | 0.1078 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10492 | 0.1039 | 0.10288 | 0.10288 | 0.11044 | 0.11044 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10738 | 0.10738 | 0.10738 | 0.10636 | 0.10534 | 0.10534
|  | GLEN LAOGH | HE |  |  |  |  | 0.1129 | 0.1129 | 0.1129 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10984 | 0.10984 | 0.10984 | 0.1078 | 0.1078 | 0.10576 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10492 | 0.10288 | 0.10288 | 0.10186 | 0.11044 | 0.11044 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10738 | 0.10738 | 0.10738 | 0.10534 | 0.10534 | 0.10432
|  | GLEN LAOGH | CF |  |  |  |  | 0.1129 | 0.1129 | 0.1129 | 0.1129 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10882 | 0.1078 | 0.1078 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.1039 | 0.10288 | 0.10288 | 0.11044 | 0.11044 | 0.11044 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10636 | 0.10534 | 0.10534
| KINLOCHLEVEN | GLENCOE | MINIMUM HEADROOM | NN 10658 58797 | YES | YES | 0.375 | 1.0753 | 1.0223 | 0.96105 | 0.88248 | 0.80084 | 0.74064 | 0.6488 | 0.53656 | 0.43044 | 0.37227 | 0.11105 | 0.012069 | -0.023645 | 1.7304 | 1.6978 | 1.6631 | 1.6141 | 1.561 | 1.5284 | 1.4743 | 1.4008 | 1.3315 | 1.307 | 1.1304 | 1.0396 | 0.80391 | 1.4672 | 1.4151 | 1.358 | 1.2876 | 1.2121 | 1.1539 | 1.0692 | 0.96411 | 0.86309 | 0.80901 | 0.56717 | 0.47329 | 0.4386
|  | GLENCOE | EE |  |  |  |  | 1.0753 | 1.0223 | 0.96105 | 0.88248 | 0.80084 | 0.74064 | 0.6488 | 0.53656 | 0.43044 | 0.37227 | 0.11105 | 0.045743 | 0.018192 | 1.7304 | 1.6978 | 1.6631 | 1.6141 | 1.561 | 1.5284 | 1.4743 | 1.4008 | 1.3315 | 1.307 | 1.1304 | 1.0396 | 0.92942 | 1.4672 | 1.4151 | 1.358 | 1.2876 | 1.2121 | 1.1539 | 1.0692 | 0.96411 | 0.86309 | 0.80901 | 0.56717 | 0.50697 | 0.47942
|  | GLENCOE | HT |  |  |  |  | 1.1019 | 1.0498 | 0.98758 | 0.93452 | 0.8784 | 0.80697 | 0.72942 | 0.66207 | 0.5784 | 0.49982 | 0.17227 | 0.012069 | -0.023645 | 1.7519 | 1.7243 | 1.6866 | 1.6621 | 1.6315 | 1.5917 | 1.5406 | 1.509 | 1.458 | 1.4121 | 1.207 | 1.111 | 1.0876 | 1.4896 | 1.4396 | 1.3835 | 1.3355 | 1.2815 | 1.2162 | 1.1417 | 1.0815 | 1.0029 | 0.92942 | 0.62533 | 0.47329 | 0.4386
|  | GLENCOE | HE |  |  |  |  | 1.1019 | 1.0631 | 1.011 | 0.97125 | 0.9284 | 0.86819 | 0.79982 | 0.74166 | 0.67023 | 0.59982 | 0.22942 | 0.13452 | 0.12023 | 1.7519 | 1.7264 | 1.6927 | 1.6743 | 1.6478 | 1.609 | 1.5651 | 1.5366 | 1.4886 | 1.4457 | 1.2019 | 1.0978 | 1.0019 | 1.4896 | 1.4519 | 1.4039 | 1.3682 | 1.3284 | 1.2733 | 1.21 | 1.1539 | 1.0855 | 1.0213 | 0.67533 | 0.58656 | 0.57329
|  | GLENCOE | CF |  |  |  |  | 1.1233 | 1.0774 | 1.0366 | 1.009 | 0.96513 | 0.93044 | 0.8886 | 0.83554 | 0.80697 | 0.75493 | 0.48554 | 0.26921 | 0.10391 | 1.7651 | 1.7355 | 1.711 | 1.6947 | 1.6662 | 1.6457 | 1.6141 | 1.5743 | 1.561 | 1.5253 | 1.3202 | 1.0906 | 0.80391 | 1.507 | 1.4651 | 1.4294 | 1.4029 | 1.3621 | 1.3304 | 1.2917 | 1.2417 | 1.2141 | 1.1682 | 0.91513 | 0.70901 | 0.55289
| DUNOON | GLENDARUEL | MINIMUM HEADROOM | NN 03067 59147 | YES | YES | 0.023 | 0.24366 | 0.23243 | 0.21917 | 0.21305 | 0.2008 | 0.1906 | 0.17121 | 0.15386 | 0.14876 | 0.1355 | 0.10386 | 0.09468 | 0.092639 | 0.29876 | 0.29774 | 0.28856 | 0.28346 | 0.27427 | 0.27019 | 0.2559 | 0.24162 | 0.23754 | 0.22733 | 0.20488 | 0.19672 | 0.16917 | 0.27223 | 0.26203 | 0.24876 | 0.24366 | 0.23141 | 0.22325 | 0.20386 | 0.18652 | 0.18346 | 0.17019 | 0.13856 | 0.13039 | 0.12733
|  | GLENDARUEL | EE |  |  |  |  | 0.24366 | 0.23243 | 0.21917 | 0.21305 | 0.2008 | 0.1906 | 0.17121 | 0.15386 | 0.14876 | 0.1355 | 0.10386 | 0.097741 | 0.0957 | 0.30284 | 0.29774 | 0.28856 | 0.28346 | 0.27427 | 0.27019 | 0.2559 | 0.24162 | 0.23754 | 0.22733 | 0.20488 | 0.19672 | 0.18448 | 0.27223 | 0.26203 | 0.24876 | 0.24366 | 0.23141 | 0.22325 | 0.20386 | 0.18652 | 0.18346 | 0.17019 | 0.13856 | 0.13346 | 0.13039
|  | GLENDARUEL | HT |  |  |  |  | 0.24468 | 0.23448 | 0.23039 | 0.22019 | 0.21203 | 0.20692 | 0.19672 | 0.18039 | 0.17223 | 0.15692 | 0.11509 | 0.09468 | 0.092639 | 0.29876 | 0.29774 | 0.2957 | 0.2906 | 0.28448 | 0.28141 | 0.27427 | 0.26203 | 0.25897 | 0.24774 | 0.21917 | 0.2059 | 0.20386 | 0.27325 | 0.26203 | 0.25999 | 0.2508 | 0.24468 | 0.23754 | 0.22937 | 0.20999 | 0.2059 | 0.19264 | 0.1508 | 0.13039 | 0.12733
|  | GLENDARUEL | HE |  |  |  |  | 0.24468 | 0.23448 | 0.23346 | 0.22427 | 0.22019 | 0.21407 | 0.20284 | 0.18958 | 0.18346 | 0.17121 | 0.12019 | 0.10794 | 0.10488 | 0.29876 | 0.29774 | 0.29774 | 0.29162 | 0.28856 | 0.28448 | 0.27733 | 0.26815 | 0.25999 | 0.25182 | 0.21713 | 0.20386 | 0.19162 | 0.27325 | 0.26305 | 0.26203 | 0.25386 | 0.24876 | 0.24468 | 0.23448 | 0.22121 | 0.21611 | 0.20182 | 0.1559 | 0.14366 | 0.1406
|  | GLENDARUEL | CF |  |  |  |  | 0.24468 | 0.23448 | 0.2355 | 0.22937 | 0.22631 | 0.21611 | 0.21305 | 0.20488 | 0.19468 | 0.19264 | 0.14264 | 0.12121 | 0.10284 | 0.29876 | 0.29876 | 0.29978 | 0.29672 | 0.29468 | 0.28754 | 0.28141 | 0.27733 | 0.26917 | 0.26815 | 0.22631 | 0.2008 | 0.16917 | 0.27325 | 0.26407 | 0.26509 | 0.25999 | 0.25692 | 0.24672 | 0.24366 | 0.2355 | 0.22631 | 0.22427 | 0.17529 | 0.15386 | 0.13856
| ABERNETHY | GLENDEVON | MINIMUM HEADROOM | NO 00101 02760 | YES | YES | 0.891 | 3.1309 | 3.0656 | 2.988 | 2.9074 | 2.7992 | 2.6788 | 2.5554 | 2.486 | 2.3492 | 2.2013 | 1.7809 | 1.7299 | 1.7094 | 3.2137 | 3.178 | 3.1331 | 3.0892 | 3.0301 | 2.9627 | 2.8872 | 2.8494 | 2.7556 | 2.6494 | 2.3352 | 2.2943 | 2.1586 | 3.1784 | 3.1203 | 3.0488 | 2.9794 | 2.8815 | 2.7754 | 2.6601 | 2.5948 | 2.4713 | 2.3294 | 1.955 | 1.907 | 1.8897
|  | GLENDEVON | EE |  |  |  |  | 3.1309 | 3.0656 | 2.988 | 2.9074 | 2.7992 | 2.6788 | 2.5554 | 2.486 | 2.3492 | 2.2013 | 1.7809 | 1.7503 | 1.7431 | 3.2137 | 3.178 | 3.1331 | 3.0892 | 3.0301 | 2.9627 | 2.8872 | 2.8494 | 2.7556 | 2.6494 | 2.3352 | 2.2943 | 2.2392 | 3.1784 | 3.1203 | 3.0488 | 2.9794 | 2.8815 | 2.7754 | 2.6601 | 2.5948 | 2.4713 | 2.3294 | 1.955 | 1.9264 | 1.9182
|  | GLENDEVON | HT |  |  |  |  | 3.1554 | 3.0788 | 3.0023 | 2.9135 | 2.8094 | 2.735 | 2.6646 | 2.5931 | 2.4523 | 2.2523 | 1.8492 | 1.7299 | 1.7094 | 3.2331 | 3.1933 | 3.1525 | 3.1107 | 3.0556 | 3.0219 | 2.979 | 2.9372 | 2.8352 | 2.678 | 2.3964 | 2.3341 | 2.3219 | 3.206 | 3.1376 | 3.0682 | 2.9937 | 2.9009 | 2.8397 | 2.7703 | 2.6999 | 2.5682 | 2.3917 | 2.0141 | 1.907 | 1.8897
|  | GLENDEVON | HE |  |  |  |  | 3.1564 | 3.1003 | 3.0462 | 2.9748 | 2.8819 | 2.7992 | 2.7248 | 2.6594 | 2.5523 | 2.4135 | 1.8574 | 1.7717 | 1.7564 | 3.2331 | 3.2005 | 3.1688 | 3.129 | 3.0801 | 3.0372 | 2.9954 | 2.9566 | 2.876 | 2.7719 | 2.3699 | 2.3005 | 2.2423 | 3.206 | 3.1529 | 3.105 | 3.0437 | 2.9601 | 2.8927 | 2.8233 | 2.759 | 2.6621 | 2.5305 | 2.0223 | 1.9417 | 1.9315
|  | GLENDEVON | CF |  |  |  |  | 3.1676 | 3.1329 | 3.0972 | 3.0462 | 3.0013 | 2.939 | 2.8788 | 2.7972 | 2.735 | 2.6462 | 2.238 | 1.9023 | 1.7839 | 3.2392 | 3.2188 | 3.1954 | 3.1648 | 3.1433 | 3.1035 | 3.0719 | 3.025 | 2.979 | 2.9219 | 2.6025 | 2.3148 | 2.1586 | 3.2152 | 3.1825 | 3.1499 | 3.1019 | 3.0631 | 3.005 | 2.955 | 2.8815 | 2.8223 | 2.7417 | 2.3621 | 2.0427 | 1.9458
| FORT AUGUSTUS | GLENDOE | MINIMUM HEADROOM | NH 40060 08894 | YES | YES | 0.062 | 7.6215 | 7.6021 | 7.5776 | 7.5542 | 7.5235 | 7.3623 | 7.3286 | 7.2868 | 7.2572 | 7.2256 | 7.1388 | 7.1113 | 7.1052 | 7.4322 | 7.421 | 7.4036 | 7.3904 | 7.372 | 7.2934 | 7.2679 | 7.2424 | 7.2271 | 7.2047 | 7.1475 | 7.12 | 7.0445 | 7.5656 | 7.5493 | 7.5269 | 7.5044 | 7.4769 | 7.3452 | 7.3105 | 7.2718 | 7.2452 | 7.2156 | 7.135 | 7.1085 | 7.1024
|  | GLENDOE | EE |  |  |  |  | 7.6215 | 7.6021 | 7.5776 | 7.5542 | 7.5235 | 7.3623 | 7.3286 | 7.2868 | 7.2572 | 7.2256 | 7.1388 | 7.1246 | 7.1154 | 7.4322 | 7.421 | 7.4036 | 7.3904 | 7.372 | 7.2934 | 7.2679 | 7.2424 | 7.2271 | 7.2047 | 7.1475 | 7.12 | 7.0761 | 7.5656 | 7.5493 | 7.5269 | 7.5044 | 7.4769 | 7.3452 | 7.3105 | 7.2718 | 7.2452 | 7.2156 | 7.135 | 7.1207 | 7.1105
|  | GLENDOE | HT |  |  |  |  | 7.6286 | 7.6123 | 7.596 | 7.5786 | 7.5562 | 7.3909 | 7.3633 | 7.3317 | 7.3123 | 7.2848 | 7.1695 | 7.1113 | 7.1052 | 7.4363 | 7.4302 | 7.42 | 7.4108 | 7.3975 | 7.3189 | 7.3016 | 7.2832 | 7.273 | 7.2557 | 7.1792 | 7.1455 | 7.1445 | 7.5728 | 7.5585 | 7.5432 | 7.5289 | 7.5064 | 7.3748 | 7.3473 | 7.3187 | 7.3003 | 7.2728 | 7.1626 | 7.1085 | 7.1024
|  | GLENDOE | HE |  |  |  |  | 7.6286 | 7.6174 | 7.6042 | 7.5919 | 7.5725 | 7.4144 | 7.3909 | 7.3684 | 7.3521 | 7.3266 | 7.199 | 7.1613 | 7.1542 | 7.4363 | 7.4322 | 7.421 | 7.4128 | 7.4016 | 7.3261 | 7.3077 | 7.2924 | 7.2843 | 7.2649 | 7.1843 | 7.1434 | 7.1036 | 7.5728 | 7.5626 | 7.5503 | 7.5391 | 7.5228 | 7.3952 | 7.3728 | 7.3493 | 7.334 | 7.3115 | 7.1922 | 7.1544 | 7.1473
|  | GLENDOE | CF |  |  |  |  | 7.6307 | 7.6225 | 7.6144 | 7.6021 | 7.5868 | 7.4439 | 7.4327 | 7.4123 | 7.397 | 7.3797 | 7.3021 | 7.2154 | 7.1644 | 7.4373 | 7.4322 | 7.4261 | 7.4189 | 7.4108 | 7.3394 | 7.3312 | 7.3169 | 7.3047 | 7.2904 | 7.2302 | 7.1414 | 7.0445 | 7.5748 | 7.5677 | 7.5595 | 7.5493 | 7.535 | 7.4238 | 7.4115 | 7.3932 | 7.3758 | 7.3595 | 7.2881 | 7.2085 | 7.1585
| BRACO | GLENEAGLES | MINIMUM HEADROOM | NN 91540 11582 | NO | YES | 4.071 | 0.090359 | -0.25658 | -0.6127 | -1.1862 | -1.5994 | -2.576 | -3.0903 | -3.6831 | -4.2811 | -5.0168 | -7.9556 | -11.0127 | -13.3903 | 2.8536 | 2.6414 | 2.3689 | 1.9016 | 1.6802 | 0.75362 | 0.43526 | -0.029029 | -0.5178 | -1.2454 | -3.9974 | -7.1862 | -10.2556 | 1.9388 | 1.6256 | 1.2052 | 0.61026 | 0.24393 | -0.82852 | -1.2908 | -1.8469 | -2.3846 | -3.0785 | -6.3969 | -9.8183 | -12.6234
|  | GLENEAGLES | EE |  |  |  |  | 0.090359 | -0.25658 | -0.6127 | -1.0168 | -1.5443 | -2.2994 | -3.0239 | -3.2709 | -3.9913 | -4.677 | -7.327 | -10.1576 | -11.1566 | 2.8536 | 2.6414 | 2.4281 | 2.1771 | 1.7648 | 1.1189 | 0.61281 | 0.5526 | 0.014849 | -0.42393 | -2.2698 | -5.2209 | -6.7698 | 1.9388 | 1.6256 | 1.296 | 0.93373 | 0.39903 | -0.37852 | -1.0775 | -1.303 | -2.0061 | -2.6459 | -5.1918 | -8.352 | -9.5234
|  | GLENEAGLES | HT |  |  |  |  | 0.20056 | -0.087192 | -0.6127 | -1.1862 | -1.5994 | -2.576 | -3.0903 | -3.6831 | -4.2811 | -5.0168 | -7.6637 | -10.9137 | -13.026 | 2.9393 | 2.7791 | 2.3689 | 1.9016 | 1.6802 | 0.75362 | 0.47097 | 0.10362 | -0.23107 | -0.66882 | -2.4515 | -5.6535 | -8.1107 | 2.0143 | 1.7429 | 1.2052 | 0.61026 | 0.24393 | -0.82852 | -1.2908 | -1.8469 | -2.3846 | -3.053 | -5.6214 | -9.2846 | -11.8357
|  | GLENEAGLES | HE |  |  |  |  | 0.2026 | -0.017804 | -0.42903 | -0.87903 | -1.2719 | -2.1668 | -2.7056 | -3.3045 | -3.9382 | -4.7984 | -7.9556 | -11.0127 | -13.3903 | 2.9353 | 2.7965 | 2.4536 | 2.0383 | 1.7393 | 0.8424 | 0.43526 | -0.029029 | -0.5178 | -1.2454 | -3.9974 | -7.1862 | -10.2556 | 2.0184 | 1.8215 | 1.4031 | 0.9174 | 0.53169 | -0.46117 | -1.005 | -1.5897 | -2.2071 | -3.0785 | -6.3969 | -9.8183 | -12.6234
|  | GLENEAGLES | CF |  |  |  |  | 0.24852 | 0.074033 | -0.14025 | -0.36066 | -0.62801 | -1.0168 | -1.327 | -1.6147 | -1.926 | -2.3147 | -3.8954 | -5.5596 | -6.9576 | 2.9638 | 2.8516 | 2.7159 | 2.574 | 2.3485 | 1.9832 | 1.7128 | 1.473 | 1.2108 | 0.8822 | -0.42087 | -2.0903 | -3.9331 | 2.0654 | 1.9164 | 1.7337 | 1.548 | 1.2715 | 0.86842 | 0.57046 | 0.30005 | 0.0010735 | -0.38974 | -1.9224 | -3.5408 | -4.9316
| RANNOCH | GLENETIVE | MINIMUM HEADROOM | NN 25850 54886 | YES | YES | 0 | 0.29584 | 0.29584 | 0.2938 | 0.2938 | 0.2938 | 0.2938 | 0.29176 | 0.28971 | 0.28869 | 0.28665 | 0.28053 | 0.27645 | 0.27543 | 0.29741 | 0.29741 | 0.29741 | 0.29639 | 0.29537 | 0.29537 | 0.29537 | 0.29435 | 0.29231 | 0.29129 | 0.28618 | 0.28414 | 0.28312 | 0.29356 | 0.29356 | 0.29254 | 0.29254 | 0.2905 | 0.2905 | 0.28948 | 0.28744 | 0.2854 | 0.28438 | 0.27723 | 0.27417 | 0.27315
|  | GLENETIVE | EE |  |  |  |  | 0.29584 | 0.29584 | 0.2938 | 0.2938 | 0.2938 | 0.2938 | 0.29176 | 0.28971 | 0.28869 | 0.28665 | 0.28155 | 0.28155 | 0.28155 | 0.29741 | 0.29741 | 0.29741 | 0.29639 | 0.29537 | 0.29537 | 0.29537 | 0.29435 | 0.29231 | 0.29129 | 0.2872 | 0.2872 | 0.2872 | 0.29356 | 0.29356 | 0.29254 | 0.29254 | 0.2905 | 0.2905 | 0.28948 | 0.28744 | 0.2854 | 0.28438 | 0.27928 | 0.27928 | 0.27928
|  | GLENETIVE | HT |  |  |  |  | 0.29584 | 0.29584 | 0.29584 | 0.29482 | 0.2938 | 0.2938 | 0.2938 | 0.29278 | 0.29073 | 0.28971 | 0.28359 | 0.28053 | 0.27849 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29639 | 0.29639 | 0.29639 | 0.29537 | 0.29537 | 0.29333 | 0.28924 | 0.2872 | 0.28618 | 0.29356 | 0.29356 | 0.29356 | 0.29356 | 0.29254 | 0.29254 | 0.29152 | 0.28948 | 0.28846 | 0.28642 | 0.28132 | 0.27723 | 0.27621
|  | GLENETIVE | HE |  |  |  |  | 0.29584 | 0.29584 | 0.29482 | 0.29482 | 0.2938 | 0.2938 | 0.2938 | 0.29073 | 0.28971 | 0.28767 | 0.28053 | 0.27645 | 0.27543 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29639 | 0.29639 | 0.29537 | 0.29537 | 0.29333 | 0.29231 | 0.28618 | 0.28414 | 0.28312 | 0.29356 | 0.29356 | 0.29356 | 0.29356 | 0.29254 | 0.29152 | 0.2905 | 0.28846 | 0.28642 | 0.2854 | 0.27723 | 0.27417 | 0.27315
|  | GLENETIVE | CF |  |  |  |  | 0.29584 | 0.29584 | 0.29584 | 0.29584 | 0.29482 | 0.2938 | 0.2938 | 0.2938 | 0.2938 | 0.29278 | 0.28665 | 0.28155 | 0.27747 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29741 | 0.29639 | 0.29639 | 0.29537 | 0.29537 | 0.29027 | 0.28618 | 0.28414 | 0.29356 | 0.29356 | 0.29356 | 0.29356 | 0.29356 | 0.29254 | 0.29254 | 0.29254 | 0.2905 | 0.28948 | 0.28336 | 0.27826 | 0.27519
| FORT WILLIAM | GLENUIG | MINIMUM HEADROOM | NM 67224 77119 | YES | NO | 0 | 0.048612 | 0.039429 | 0.037388 | 0.029224 | 0.027184 | 0.026163 | 0.026163 | 0.025143 | 0.024122 | 0.01902 | 0.0098367 | 0.0098367 | 0.0098367 | 0.055939 | 0.047776 | 0.046755 | 0.038592 | 0.044714 | 0.037571 | 0.038592 | 0.043694 | 0.042673 | 0.038592 | 0.03349 | 0.030429 | 0.023286 | 0.056357 | 0.048194 | 0.045133 | 0.036969 | 0.036969 | 0.034929 | 0.035949 | 0.034929 | 0.032888 | 0.027786 | 0.019622 | 0.018602 | 0.018602
|  | GLENUIG | EE |  |  |  |  | 0.048612 | 0.039429 | 0.037388 | 0.029224 | 0.027184 | 0.032286 | 0.029224 | 0.025143 | 0.024122 | 0.01902 | 0.0098367 | 0.010857 | 0.0098367 | 0.055939 | 0.047776 | 0.046755 | 0.038592 | 0.044714 | 0.047776 | 0.045735 | 0.043694 | 0.042673 | 0.038592 | 0.03349 | 0.030429 | 0.028388 | 0.056357 | 0.048194 | 0.045133 | 0.036969 | 0.036969 | 0.042071 | 0.03799 | 0.034929 | 0.032888 | 0.027786 | 0.019622 | 0.020643 | 0.018602
|  | GLENUIG | HT |  |  |  |  | 0.055755 | 0.047592 | 0.045551 | 0.037388 | 0.036367 | 0.027184 | 0.026163 | 0.032286 | 0.026163 | 0.026163 | 0.012898 | 0.0098367 | 0.0098367 | 0.063082 | 0.055939 | 0.053898 | 0.046755 | 0.046755 | 0.037571 | 0.043694 | 0.048796 | 0.043694 | 0.043694 | 0.035531 | 0.032469 | 0.031449 | 0.0635 | 0.056357 | 0.052276 | 0.044112 | 0.043092 | 0.034929 | 0.035949 | 0.042071 | 0.035949 | 0.034929 | 0.022684 | 0.018602 | 0.018602
|  | GLENUIG | HE |  |  |  |  | 0.055755 | 0.047592 | 0.046571 | 0.037388 | 0.036367 | 0.026163 | 0.027184 | 0.032286 | 0.028204 | 0.029224 | 0.013918 | 0.0098367 | 0.011878 | 0.063082 | 0.054918 | 0.054918 | 0.046755 | 0.045735 | 0.037571 | 0.043694 | 0.047776 | 0.045735 | 0.045735 | 0.035531 | 0.030429 | 0.029408 | 0.0635 | 0.055337 | 0.055337 | 0.045133 | 0.044112 | 0.035949 | 0.036969 | 0.042071 | 0.03901 | 0.03799 | 0.023704 | 0.019622 | 0.020643
|  | GLENUIG | CF |  |  |  |  | 0.055755 | 0.047592 | 0.047592 | 0.045551 | 0.037388 | 0.037388 | 0.029224 | 0.027184 | 0.027184 | 0.032286 | 0.022082 | 0.014939 | 0.010857 | 0.063082 | 0.054918 | 0.054918 | 0.054918 | 0.046755 | 0.046755 | 0.038592 | 0.044714 | 0.044714 | 0.047776 | 0.039612 | 0.031449 | 0.023286 | 0.0635 | 0.055337 | 0.055337 | 0.054316 | 0.045133 | 0.044112 | 0.036969 | 0.036969 | 0.036969 | 0.042071 | 0.031867 | 0.023704 | 0.020643
| BRORA | GOLSPIE | MINIMUM HEADROOM | NC 82996 00240 | YES | NO | 0.392 | 0.88462 | 0.81625 | 0.73462 | 0.66727 | 0.5989 | 0.52645 | 0.41829 | 0.30604 | 0.16115 | 0.027473 | -0.21232 | -0.296 | -0.32253 | 1.5469 | 1.4897 | 1.4142 | 1.3662 | 1.305 | 1.2356 | 1.155 | 1.0856 | 0.99176 | 0.90911 | 0.74278 | 0.67237 | 0.4387 | 1.3336 | 1.2571 | 1.1734 | 1.102 | 1.0203 | 0.93258 | 0.82747 | 0.72033 | 0.58462 | 0.46115 | 0.23666 | 0.15911 | 0.13666
|  | GOLSPIE | EE |  |  |  |  | 0.88462 | 0.81931 | 0.73462 | 0.66727 | 0.5989 | 0.52645 | 0.41829 | 0.30604 | 0.16115 | 0.027473 | -0.21232 | -0.25314 | -0.27355 | 1.5469 | 1.4897 | 1.4142 | 1.3662 | 1.305 | 1.2356 | 1.155 | 1.0856 | 0.99176 | 0.90911 | 0.74278 | 0.67237 | 0.56217 | 1.3336 | 1.2632 | 1.1734 | 1.102 | 1.0203 | 0.93258 | 0.82747 | 0.72033 | 0.58462 | 0.46115 | 0.23666 | 0.19788 | 0.17849
|  | GOLSPIE | HT |  |  |  |  | 0.90298 | 0.81625 | 0.74992 | 0.68666 | 0.62543 | 0.54992 | 0.46421 | 0.37543 | 0.2989 | 0.24074 | -0.14191 | -0.296 | -0.32253 | 1.5611 | 1.4918 | 1.4448 | 1.404 | 1.3601 | 1.3162 | 1.255 | 1.1856 | 1.1275 | 1.0958 | 0.82543 | 0.7336 | 0.72033 | 1.3356 | 1.2571 | 1.1969 | 1.1397 | 1.0785 | 1.0009 | 0.89992 | 0.79788 | 0.71625 | 0.66115 | 0.304 | 0.15911 | 0.13666
|  | GOLSPIE | HE |  |  |  |  | 0.90911 | 0.84686 | 0.78666 | 0.7387 | 0.6887 | 0.6438 | 0.58666 | 0.51421 | 0.44176 | 0.36319 | -0.073547 | -0.17253 | -0.18783 | 1.5683 | 1.5173 | 1.4683 | 1.4295 | 1.3887 | 1.3591 | 1.3122 | 1.2499 | 1.1856 | 1.1203 | 0.83666 | 0.73156 | 0.62951 | 1.3448 | 1.2856 | 1.2305 | 1.1836 | 1.1346 | 1.0969 | 1.0275 | 0.94482 | 0.85911 | 0.77135 | 0.37135 | 0.27849 | 0.26523
|  | GOLSPIE | CF |  |  |  |  | 0.92543 | 0.88258 | 0.84278 | 0.79482 | 0.75502 | 0.71217 | 0.66727 | 0.62951 | 0.57747 | 0.52645 | 0.22849 | -0.039873 | -0.15824 | 1.5846 | 1.553 | 1.5203 | 1.4765 | 1.4469 | 1.4081 | 1.3622 | 1.3356 | 1.2856 | 1.2438 | 0.99584 | 0.71421 | 0.4387 | 1.3611 | 1.3214 | 1.2846 | 1.2346 | 1.2009 | 1.1591 | 1.1081 | 1.0724 | 1.0071 | 0.954 | 0.65196 | 0.39788 | 0.2938
| BURGHMUIR | GOODLYBURN | MINIMUM HEADROOM | NO 10084 24586 | NO | YES | 1.14 | 1.1023 | 0.79724 | 0.06969 | -1.0221 | -1.416 | -3.516 | -4.3528 | -5.3466 | -6.1558 | -7.5007 | -13.6813 | -20.7711 | -26.9334 | 4.3508 | 4.2335 | 3.5161 | 2.4335 | 2.2069 | -0.12368 | -1.0084 | -2.0778 | -3.1196 | -4.5676 | -11.5941 | -20.5502 | -29.5584 | 3.3133 | 3.1327 | 2.3531 | 1.1919 | 0.93474 | -1.5306 | -2.3591 | -3.4734 | -4.55 | -6.153 | -13.2581 | -21.8479 | -29.5704
|  | GOODLYBURN | EE |  |  |  |  | 1.1023 | 0.79724 | 0.4401 | 0.071731 | -0.80888 | -2.1609 | -3.2732 | -3.8221 | -5.0742 | -5.9966 | -9.6875 | -15.1732 | -17.4824 | 4.3508 | 4.2335 | 4.0671 | 3.8518 | 2.9733 | 1.5233 | 0.55898 | 0.23653 | -0.95327 | -1.7574 | -5.4247 | -13.4104 | -17.6992 | 3.3133 | 3.1327 | 2.8827 | 2.6103 | 1.7388 | 0.19392 | -0.96934 | -1.45 | -2.8102 | -3.7744 | -7.7571 | -14.8051 | -17.7775
|  | GOODLYBURN | HT |  |  |  |  | 1.1789 | 0.9054 | 0.06969 | -1.0221 | -1.416 | -3.516 | -4.3528 | -5.3466 | -6.0987 | -6.6977 | -10.9619 | -18.0456 | -23.9283 | 4.3998 | 4.3069 | 3.5161 | 2.4335 | 2.2631 | -0.12368 | -0.73286 | -1.49 | -2.0002 | -2.389 | -6.3267 | -15.1665 | -22.5716 | 3.3633 | 3.2215 | 2.3531 | 1.1919 | 0.93474 | -1.5306 | -2.3591 | -3.3469 | -4.0724 | -4.6469 | -9.3326 | -18.1683 | -25.5336
|  | GOODLYBURN | HE |  |  |  |  | 1.186 | 1.036 | 0.42683 | -0.45174 | -0.97011 | -2.9272 | -3.9681 | -5.0895 | -6.1558 | -7.5007 | -13.6813 | -20.7711 | -26.9334 | 4.3988 | 4.3131 | 3.6631 | 2.6926 | 2.2069 | -0.083882 | -1.0084 | -2.0778 | -3.1196 | -4.5676 | -11.5941 | -20.5502 | -29.5584 | 3.3654 | 3.2613 | 2.5603 | 1.5388 | 0.99494 | -1.3663 | -2.3581 | -3.4734 | -4.55 | -6.153 | -13.2581 | -21.8479 | -29.5704
|  | GOODLYBURN | CF |  |  |  |  | 1.2717 | 1.2074 | 1.1248 | 1.0401 | 0.63908 | -0.034392 | -0.50072 | -0.99766 | -1.4477 | -1.9977 | -4.0395 | -6.8038 | -9.2538 | 4.4345 | 4.3855 | 4.3294 | 4.2682 | 3.8345 | 3.062 | 2.5396 | 1.9906 | 1.4661 | 0.81408 | -1.6747 | -5.2971 | -9.7257 | 3.4103 | 3.3643 | 3.3082 | 3.2449 | 2.7827 | 1.9817 | 1.4562 | 0.94903 | 0.46535 | -0.15199 | -2.4591 | -4.9857 | -7.4244
| CHARLESTON | GOURDIE | MINIMUM HEADROOM | NO 34573 32203 | YES | YES | 0.966 | 3.6116 | 3.0952 | 2.6248 | 2.1748 | 1.6728 | 1.1769 | 0.71258 | 0.34727 | -0.078237 | -0.38946 | -1.3201 | -1.7548 | -1.8986 | 4.1282 | 3.6874 | 3.2915 | 2.915 | 2.6201 | 2.2333 | 1.8854 | 1.6568 | 1.4517 | 1.2752 | 0.67517 | 0.38129 | -0.071767 | 3.9525 | 3.4638 | 3.0158 | 2.5862 | 2.1434 | 1.6668 | 1.2281 | 0.88622 | 0.5199 | 0.24439 | -0.58521 | -0.97092 | -1.1056
|  | GOURDIE | EE |  |  |  |  | 3.6646 | 3.1738 | 2.7636 | 2.3442 | 1.9197 | 1.4299 | 0.84013 | 0.43197 | 0.076865 | -0.27007 | -1.3201 | -1.7333 | -1.8446 | 4.1966 | 3.7813 | 3.4374 | 3.0956 | 2.8007 | 2.4405 | 2.0293 | 1.7497 | 1.5354 | 1.3272 | 0.67517 | 0.38129 | 0.12517 | 4.0128 | 3.5485 | 3.1577 | 2.7617 | 2.3699 | 1.9097 | 1.3628 | 0.98622 | 0.66479 | 0.35357 | -0.58521 | -0.95561 | -1.0597
|  | GOURDIE | HT |  |  |  |  | 3.6116 | 3.0952 | 2.6248 | 2.1748 | 1.6728 | 1.1769 | 0.71258 | 0.34727 | -0.078237 | -0.38946 | -1.2772 | -1.7548 | -1.8986 | 4.1282 | 3.6874 | 3.2915 | 2.915 | 2.6201 | 2.2333 | 1.8854 | 1.6568 | 1.4517 | 1.2752 | 0.81497 | 0.57211 | 0.46089 | 3.9525 | 3.4638 | 3.0158 | 2.5862 | 2.1434 | 1.6668 | 1.2281 | 0.88622 | 0.5199 | 0.24439 | -0.54439 | -0.97092 | -1.1056
|  | GOURDIE | HE |  |  |  |  | 3.6932 | 3.2565 | 2.885 | 2.5167 | 2.0901 | 1.632 | 1.1309 | 0.76258 | 0.38809 | 0.12687 | -0.85375 | -1.3354 | -1.5048 | 4.216 | 3.815 | 3.4864 | 3.1609 | 2.8619 | 2.516 | 2.1272 | 1.8537 | 1.6201 | 1.4313 | 0.78538 | 0.52925 | 0.27109 | 4.0332 | 3.6199 | 3.2679 | 2.9138 | 2.5281 | 2.1015 | 1.6281 | 1.2872 | 0.95357 | 0.71173 | -0.18214 | -0.61174 | -0.7648
|  | GOURDIE | CF |  |  |  |  | 3.8779 | 3.635 | 3.3738 | 3.1616 | 2.933 | 2.6738 | 2.3912 | 2.085 | 1.836 | 1.5422 | 0.33503 | -0.67109 | -1.3048 | 4.4088 | 4.2007 | 3.9833 | 3.7966 | 3.6099 | 3.3874 | 3.1527 | 2.9139 | 2.7242 | 2.5201 | 1.5639 | 0.6415 | -0.071767 | 4.2342 | 3.9944 | 3.7505 | 3.5495 | 3.3321 | 3.0832 | 2.8168 | 2.5342 | 2.3097 | 2.0485 | 0.92602 | -0.021941 | -0.59337
| BOAT OF GARTEN | GRANTOWN | MINIMUM HEADROOM | NJ 03670 26311 | NO | YES | 0.822 | 8.5671 | 8.4039 | 8.2161 | 8.0477 | 7.8304 | 7.5937 | 7.3732 | 7.0569 | 6.759 | 6.4967 | 5.8651 | 5.6243 | 5.5569 | 10.2957 | 10.1998 | 10.0886 | 9.9906 | 9.8569 | 9.7141 | 9.5722 | 9.361 | 9.1539 | 8.9722 | 8.4947 | 8.2702 | 7.4039 | 9.5503 | 9.3982 | 9.2125 | 9.0482 | 8.8329 | 8.6044 | 8.386 | 8.087 | 7.8023 | 7.5533 | 6.9391 | 6.7125 | 6.6462
|  | GRANTOWN | EE |  |  |  |  | 8.5671 | 8.4039 | 8.2161 | 8.0477 | 7.8304 | 7.5937 | 7.3732 | 7.0569 | 6.759 | 6.4967 | 5.8651 | 5.7457 | 5.6661 | 10.2957 | 10.1998 | 10.0886 | 9.9906 | 9.8569 | 9.7141 | 9.5722 | 9.361 | 9.1539 | 8.9722 | 8.4947 | 8.2702 | 7.8753 | 9.5503 | 9.3982 | 9.2125 | 9.0482 | 8.8329 | 8.6044 | 8.386 | 8.087 | 7.8023 | 7.5533 | 6.9391 | 6.8268 | 6.7533
|  | GRANTOWN | HT |  |  |  |  | 8.6559 | 8.511 | 8.3773 | 8.2232 | 8.0518 | 7.8957 | 7.6977 | 7.46 | 7.2906 | 7.06 | 6.0559 | 5.6243 | 5.5569 | 10.3467 | 10.2661 | 10.1916 | 10.1079 | 10.0079 | 9.9232 | 9.811 | 9.6763 | 9.5773 | 9.4334 | 8.76 | 8.4926 | 8.4539 | 9.638 | 9.4942 | 9.3595 | 9.2044 | 9.035 | 8.886 | 8.6911 | 8.4625 | 8.2921 | 8.0697 | 7.1238 | 6.7125 | 6.6462
|  | GRANTOWN | HE |  |  |  |  | 8.6549 | 8.5345 | 8.4314 | 8.3079 | 8.1641 | 8.0518 | 7.8763 | 7.6671 | 7.5253 | 7.3273 | 6.2396 | 5.9763 | 5.9324 | 10.3437 | 10.2732 | 10.2069 | 10.1334 | 10.0467 | 9.9712 | 9.861 | 9.7345 | 9.6437 | 9.512 | 8.7539 | 8.4253 | 8.063 | 9.637 | 9.5217 | 9.4176 | 9.2931 | 9.1554 | 9.0421 | 8.8697 | 8.6707 | 8.5248 | 8.3329 | 7.2993 | 7.0493 | 7.0074
|  | GRANTOWN | CF |  |  |  |  | 8.6845 | 8.5753 | 8.4539 | 8.3661 | 8.2539 | 8.1294 | 8.0437 | 7.8967 | 7.7579 | 7.6141 | 6.9171 | 6.263 | 5.9416 | 10.363 | 10.2977 | 10.2263 | 10.1732 | 10.1018 | 10.0243 | 9.959 | 9.8569 | 9.761 | 9.6641 | 9.0834 | 8.3079 | 7.4039 | 9.6625 | 9.5646 | 9.4482 | 9.3636 | 9.2605 | 9.1411 | 9.0595 | 8.9176 | 8.787 | 8.6482 | 7.9789 | 7.3513 | 7.0197
| SHETLAND | GREMISTA | MINIMUM HEADROOM | HU4646842756 | NO | YES | 3.825 | 20.5589 | 19.4528 | 18.2834 | 17.0865 | 15.9334 | 14.7191 | 13.4028 | 12.215 | 10.9293 | 10.263 | 7.8885 | 7.0446 | 6.6875 | 23.5712 | 22.5365 | 21.4497 | 20.3405 | 19.314 | 18.2416 | 17.1048 | 16.064 | 14.9467 | 14.4844 | 12.9079 | 12.3436 | 11.7763 | 21.5589 | 20.4854 | 19.3487 | 18.1885 | 17.0773 | 15.9089 | 14.6436 | 13.5018 | 12.2681 | 11.6416 | 9.4324 | 8.6477 | 8.3099
|  | GREMISTA | EE |  |  |  |  | 20.5589 | 19.4528 | 18.2834 | 17.0865 | 15.9334 | 14.7191 | 13.4028 | 12.215 | 10.9293 | 10.263 | 7.8885 | 7.261 | 7.1252 | 23.5712 | 22.5365 | 21.4497 | 20.3405 | 19.314 | 18.2416 | 17.1048 | 16.064 | 14.9467 | 14.4844 | 12.9079 | 12.5528 | 12.4569 | 21.5589 | 20.4854 | 19.3487 | 18.1885 | 17.0773 | 15.9089 | 14.6436 | 13.5018 | 12.2681 | 11.6416 | 9.4324 | 8.8538 | 8.7273
|  | GREMISTA | HT |  |  |  |  | 20.6385 | 19.5661 | 18.4497 | 17.2977 | 16.1538 | 14.9793 | 13.7834 | 12.4865 | 11.1773 | 10.4416 | 8.0518 | 7.0446 | 6.6875 | 23.6303 | 22.6252 | 21.5793 | 20.5069 | 19.4936 | 18.4487 | 17.4038 | 16.2742 | 15.1375 | 14.6334 | 13.0548 | 12.4069 | 12.1507 | 21.6375 | 20.5946 | 19.5099 | 18.3956 | 17.2977 | 16.165 | 15.015 | 13.7691 | 12.5099 | 11.8242 | 9.5916 | 8.6477 | 8.3099
|  | GREMISTA | HE |  |  |  |  | 20.6518 | 19.6263 | 18.5834 | 17.4987 | 16.4456 | 15.3181 | 14.1048 | 12.8303 | 11.5467 | 10.8191 | 8.1038 | 7.1987 | 6.815 | 23.6467 | 22.6538 | 21.6426 | 20.5997 | 19.6365 | 18.614 | 17.5416 | 16.415 | 15.2905 | 14.7701 | 12.9161 | 12.3436 | 12.0752 | 21.6497 | 20.6497 | 19.6324 | 18.5752 | 17.5569 | 16.4722 | 15.3038 | 14.0712 | 12.8385 | 12.1558 | 9.6079 | 8.7661 | 8.4089
|  | GREMISTA | CF |  |  |  |  | 20.8191 | 19.9487 | 19.0446 | 18.1212 | 17.3212 | 16.4671 | 15.5854 | 14.6344 | 13.6997 | 13.2865 | 10.8405 | 8.7446 | 7.263 | 23.7661 | 22.8793 | 21.9589 | 21.0283 | 20.2405 | 19.4099 | 18.5599 | 17.6538 | 16.761 | 16.4426 | 14.6803 | 13.2028 | 11.7763 | 21.8079 | 20.9538 | 20.0671 | 19.1589 | 18.3793 | 17.5436 | 16.6865 | 15.762 | 14.8518 | 14.4579 | 12.163 | 10.1834 | 8.8058
| WILLOWDALE | GREYFRIARS | MINIMUM HEADROOM | NJ 94327 07070 | NO | NO | 4.686 | 10.5741 | 10.0894 | 9.5384 | 8.919 | 8.2251 | 7.4629 | 6.5608 | 5.6925 | 4.8802 | 4.117 | 0.70881 | -1.9126 | -2.33 | 13.0092 | 12.7011 | 12.3327 | 11.9276 | 11.4643 | 10.9511 | 10.3786 | 9.7674 | 9.1898 | 8.646 | 5.8123 | 3.0347 | -5.5632 | 12.1878 | 11.7511 | 11.246 | 10.6847 | 10.048 | 9.3439 | 8.5082 | 7.6857 | 6.9174 | 6.1949 | 2.9949 | 0.54187 | 0.1786
|  | GREYFRIARS | EE |  |  |  |  | 10.5741 | 10.0894 | 9.5384 | 8.919 | 8.2251 | 7.4629 | 6.5608 | 5.6925 | 4.8802 | 4.117 | 0.70881 | -1.5065 | -2.2218 | 13.0092 | 12.7011 | 12.3327 | 11.9276 | 11.4643 | 10.9511 | 10.3786 | 9.7674 | 9.1898 | 8.646 | 5.8123 | 3.0347 | -0.94282 | 12.1878 | 11.7511 | 11.246 | 10.6847 | 10.048 | 9.3439 | 8.5082 | 7.6857 | 6.9174 | 6.1949 | 2.9949 | 0.93269 | 0.27554
|  | GREYFRIARS | HT |  |  |  |  | 10.7068 | 10.166 | 9.6864 | 9.1445 | 8.5578 | 7.8894 | 7.2057 | 6.4343 | 5.6925 | 4.8802 | 0.88636 | -1.9126 | -2.33 | 13.148 | 12.8725 | 12.6123 | 12.3164 | 12.0011 | 11.6317 | 11.2653 | 10.8286 | 10.4225 | 9.9684 | 7.7776 | 6.3449 | 6.1398 | 12.3143 | 11.848 | 11.4153 | 10.9245 | 10.3929 | 9.7817 | 9.1388 | 8.4113 | 7.7143 | 6.9551 | 3.1806 | 0.54187 | 0.1786
|  | GREYFRIARS | HE |  |  |  |  | 10.6935 | 10.366 | 10.0935 | 9.7884 | 9.4639 | 9.0894 | 8.57 | 7.9629 | 7.3711 | 6.7853 | 3.5945 | 1.4496 | 0.82411 | 13.1102 | 12.8868 | 12.6725 | 12.4347 | 12.1735 | 11.8745 | 11.5113 | 11.0715 | 10.6408 | 10.2 | 7.3919 | 4.5021 | 0.67044 | 12.3021 | 12.0113 | 11.7572 | 11.4755 | 11.1715 | 10.8225 | 10.3317 | 9.7664 | 9.2133 | 8.6653 | 5.6878 | 3.6868 | 3.1092
|  | GREYFRIARS | CF |  |  |  |  | 10.7864 | 10.5537 | 10.4078 | 10.217 | 9.9904 | 9.7619 | 9.5425 | 9.2762 | 9.02 | 8.7415 | 6.8517 | 4.9302 | 2.9557 | 13.149 | 12.9643 | 12.8051 | 12.6113 | 12.3827 | 12.1174 | 11.8113 | 11.4592 | 11.1041 | 10.7276 | 8.0266 | 3.0674 | -5.5632 | 12.3857 | 12.1898 | 12.0511 | 11.8735 | 11.6643 | 11.45 | 11.2449 | 10.997 | 10.7582 | 10.5 | 8.7592 | 6.9562 | 5.098
| SHETLAND | GUTCHER | MINIMUM HEADROOM | HU5453899599 | YES | YES | 0.404 | 0.084131 | 0.068824 | 0.047396 | 0.031069 | 0.0065796 | -0.0077061 | -0.033216 | -0.06689 | -0.087298 | -0.11179 | -0.16893 | -0.18934 | -0.19444 | 0.26168 | 0.2525 | 0.24025 | 0.22903 | 0.21168 | 0.2025 | 0.18821 | 0.16372 | 0.15148 | 0.13515 | 0.092294 | 0.080049 | 0.03209 | 0.14536 | 0.13617 | 0.11882 | 0.1025 | 0.079029 | 0.065763 | 0.041273 | 0.0065796 | -0.0097469 | -0.034237 | -0.087298 | -0.10464 | -0.10873
|  | GUTCHER | EE |  |  |  |  | 0.084131 | 0.068824 | 0.047396 | 0.031069 | 0.0065796 | -0.0077061 | -0.033216 | -0.06689 | -0.087298 | -0.11179 | -0.16893 | -0.17709 | -0.18322 | 0.26168 | 0.2525 | 0.24025 | 0.22903 | 0.21168 | 0.2025 | 0.18821 | 0.16372 | 0.15148 | 0.13515 | 0.092294 | 0.080049 | 0.053518 | 0.14536 | 0.13617 | 0.11882 | 0.1025 | 0.079029 | 0.065763 | 0.041273 | 0.0065796 | -0.0097469 | -0.034237 | -0.087298 | -0.094441 | -0.10056
|  | GUTCHER | HT |  |  |  |  | 0.088212 | 0.078008 | 0.064743 | 0.049437 | 0.035151 | 0.018824 | -0.0026041 | -0.029135 | -0.039339 | -0.060767 | -0.14954 | -0.18934 | -0.19444 | 0.2627 | 0.25658 | 0.25148 | 0.24229 | 0.23515 | 0.22699 | 0.2127 | 0.19536 | 0.18923 | 0.17393 | 0.11474 | 0.090253 | 0.088212 | 0.14842 | 0.14127 | 0.13311 | 0.11984 | 0.10862 | 0.098416 | 0.074947 | 0.049437 | 0.042294 | 0.019845 | -0.069951 | -0.10464 | -0.10873
|  | GUTCHER | HE |  |  |  |  | 0.088212 | 0.079029 | 0.070865 | 0.059641 | 0.043314 | 0.031069 | 0.012702 | -0.0097469 | -0.018931 | -0.040359 | -0.13322 | -0.15771 | -0.16179 | 0.2627 | 0.2576 | 0.25352 | 0.24842 | 0.23719 | 0.22903 | 0.2178 | 0.2025 | 0.19638 | 0.18209 | 0.11678 | 0.094335 | 0.069845 | 0.1474 | 0.14127 | 0.13515 | 0.12903 | 0.11678 | 0.10556 | 0.088212 | 0.064743 | 0.0576 | 0.036171 | -0.052604 | -0.074033 | -0.077094
|  | GUTCHER | CF |  |  |  |  | 0.089233 | 0.085151 | 0.078008 | 0.069845 | 0.0576 | 0.045355 | 0.038212 | 0.021886 | 0.0065796 | -0.0087265 | -0.064849 | -0.13016 | -0.15771 | 0.2627 | 0.26066 | 0.25862 | 0.25046 | 0.24331 | 0.23719 | 0.23311 | 0.21882 | 0.20862 | 0.19944 | 0.15556 | 0.089233 | 0.03209 | 0.14842 | 0.14331 | 0.14025 | 0.13209 | 0.12291 | 0.11474 | 0.1076 | 0.091273 | 0.074947 | 0.061682 | 0.0076 | -0.053624 | -0.076073
| THURSO | HALKIRK | MINIMUM HEADROOM | ND 13246 58223 | YES | NO | 0.149 | 0.057967 | -0.027747 | -0.1104 | -0.20938 | -0.30632 | -0.41652 | -0.52469 | -0.69611 | -0.86958 | -1.0288 | -1.3522 | -1.4675 | -1.5124 | 0.73654 | 0.68552 | 0.6345 | 0.56307 | 0.49674 | 0.41613 | 0.35593 | 0.23756 | 0.12531 | 0.026335 | -0.14611 | -0.23081 | -0.56346 | 0.49266 | 0.41307 | 0.33348 | 0.2345 | 0.13858 | 0.028376 | -0.071624 | -0.23693 | -0.39509 | -0.54203 | -0.83693 | -0.93795 | -0.97673
|  | HALKIRK | EE |  |  |  |  | 0.057967 | -0.027747 | -0.1104 | -0.20938 | -0.30632 | -0.41652 | -0.52469 | -0.69611 | -0.86958 | -1.0288 | -1.3522 | -1.4247 | -1.4471 | 0.73654 | 0.68552 | 0.6345 | 0.56307 | 0.49674 | 0.41613 | 0.35593 | 0.23756 | 0.12531 | 0.026335 | -0.14611 | -0.23081 | -0.35836 | 0.49266 | 0.41307 | 0.33348 | 0.2345 | 0.13858 | 0.028376 | -0.071624 | -0.23693 | -0.39509 | -0.54203 | -0.83693 | -0.90326 | -0.92673
|  | HALKIRK | HT |  |  |  |  | 0.080416 | 0.0079673 | -0.071624 | -0.15938 | -0.23285 | -0.35224 | -0.47775 | -0.62469 | -0.71346 | -0.82571 | -1.2563 | -1.4675 | -1.5124 | 0.76715 | 0.73042 | 0.6845 | 0.63144 | 0.5947 | 0.52327 | 0.45491 | 0.36307 | 0.31715 | 0.24164 | -0.041012 | -0.1553 | -0.17673 | 0.52225 | 0.45593 | 0.38144 | 0.2998 | 0.23042 | 0.12021 | 0.0069469 | -0.12979 | -0.21346 | -0.32264 | -0.74509 | -0.93795 | -0.97673
|  | HALKIRK | HE |  |  |  |  | 0.082457 | 0.025314 | -0.031829 | -0.096114 | -0.15122 | -0.22469 | -0.31652 | -0.43897 | -0.53489 | -0.65428 | -1.2328 | -1.3665 | -1.39 | 0.76613 | 0.7345 | 0.69776 | 0.64674 | 0.61511 | 0.56205 | 0.50389 | 0.41919 | 0.36817 | 0.28654 | -0.06142 | -0.18387 | -0.31346 | 0.52327 | 0.47123 | 0.41613 | 0.3498 | 0.29878 | 0.22531 | 0.13756 | 0.017151 | -0.064482 | -0.18183 | -0.71448 | -0.84611 | -0.89305
|  | HALKIRK | CF |  |  |  |  | 0.085518 | 0.03858 | -0.0093796 | -0.05938 | -0.1155 | -0.1604 | -0.22367 | -0.28693 | -0.37367 | -0.46346 | -0.83489 | -1.1328 | -1.3614 | 0.76919 | 0.73654 | 0.71001 | 0.67633 | 0.6345 | 0.60797 | 0.55797 | 0.50797 | 0.44776 | 0.3794 | 0.093682 | -0.18693 | -0.56346 | 0.52736 | 0.48144 | 0.43654 | 0.39062 | 0.33552 | 0.29572 | 0.23246 | 0.16715 | 0.085518 | 0.0018449 | -0.35938 | -0.65122 | -0.84816
| ABERNETHY | HARBOUR | MINIMUM HEADROOM | NO 11948 22049 | NO | YES | 2.613 | 16.88 | 16.4004 | 15.3678 | 14.2035 | 13.6678 | 11.7933 | 11.1923 | 10.5392 | 9.8443 | 8.5535 | 3.2525 | -2.6996 | -7.9802 | 19.2535 | 18.9504 | 18.0494 | 16.978 | 16.6739 | 14.6708 | 13.9535 | 13.1464 | 12.3382 | 10.9739 | 5.3811 | -1.4343 | -7.8812 | 18.2402 | 17.8045 | 16.7525 | 15.5004 | 15.0341 | 12.8668 | 12.2953 | 11.5341 | 10.5708 | 9.0413 | 2.8362 | -4.323 | -10.8322
|  | HARBOUR | EE |  |  |  |  | 16.88 | 16.4004 | 15.828 | 15.2443 | 14.3066 | 13.0321 | 12.1004 | 11.478 | 10.7647 | 9.9943 | 6.8208 | 1.8117 | -0.17201 | 19.2535 | 18.9504 | 18.5851 | 18.1933 | 17.3647 | 16.1096 | 15.3943 | 14.9913 | 14.2015 | 13.5984 | 10.8453 | 4.7453 | 1.7606 | 18.2402 | 17.8045 | 17.3025 | 16.778 | 15.8157 | 14.4208 | 13.4902 | 12.9025 | 12.0708 | 11.278 | 7.8964 | 1.7096 | -0.72201
|  | HARBOUR | HT |  |  |  |  | 16.9208 | 16.4413 | 15.3678 | 14.2035 | 13.6678 | 11.7933 | 11.1923 | 10.5392 | 9.9902 | 9.279 | 5.8923 | -0.21895 | -5.0445 | 19.277 | 18.978 | 18.0494 | 16.978 | 16.6739 | 14.6708 | 14.2851 | 13.8443 | 13.5311 | 13.0545 | 9.8811 | 2.6106 | -3.4751 | 18.28 | 17.8566 | 16.7525 | 15.5004 | 15.0341 | 12.8668 | 12.2953 | 11.6657 | 11.1657 | 10.4811 | 6.8657 | -0.55262 | -6.6373
|  | HARBOUR | HE |  |  |  |  | 16.9627 | 16.6096 | 15.7851 | 14.7902 | 14.1341 | 12.3402 | 11.5168 | 10.678 | 9.8443 | 8.5535 | 3.2525 | -2.6996 | -7.9802 | 19.3066 | 19.0311 | 18.2678 | 17.2913 | 16.7127 | 14.7025 | 13.9535 | 13.1464 | 12.3382 | 10.9739 | 5.3811 | -1.4343 | -7.8812 | 18.3198 | 18.0015 | 17.1443 | 16.0668 | 15.4147 | 13.3229 | 12.4668 | 11.5341 | 10.5708 | 9.0413 | 2.8362 | -4.323 | -10.8322
|  | HARBOUR | CF |  |  |  |  | 17.0678 | 16.8862 | 16.6168 | 16.3525 | 15.8372 | 15.1198 | 14.6219 | 14.1811 | 13.8239 | 13.327 | 11.1025 | 8.7157 | 6.6811 | 19.3964 | 19.2494 | 19.0566 | 18.8892 | 18.426 | 17.7055 | 17.2208 | 16.7953 | 16.3923 | 15.8698 | 13.8127 | 11.7311 | 9.079 | 18.426 | 18.2515 | 18.0178 | 17.7872 | 17.2515 | 16.4555 | 15.9321 | 15.4811 | 15.0504 | 14.4708 | 12.078 | 9.4964 | 7.3913
| ARDMORE | HARRIS GRID | MINIMUM HEADROOM | NG 13500 94249 | YES | YES | 0 | 35.3704 | 35.2092 | 35.1908 | 35.1745 | 35.1582 | 35.1429 | 35.1224 | 35.1 | 35.0786 | 35.0571 | 34.9796 | 34.952 | 34.9316 | 32.6724 | 32.5092 | 32.498 | 32.4888 | 32.4755 | 32.4653 | 32.45 | 32.4357 | 32.4204 | 32.4061 | 32.349 | 32.3286 | 32.3112 | 34.0204 | 33.8582 | 33.8429 | 33.8306 | 33.8133 | 33.799 | 33.7796 | 33.7571 | 33.7367 | 33.7173 | 33.6429 | 33.6173 | 33.599
|  | HARRIS GRID | EE |  |  |  |  | 35.3724 | 35.3633 | 35.1908 | 35.1745 | 35.1582 | 35.1429 | 35.1224 | 35.1 | 35.0786 | 35.0571 | 34.9796 | 34.9561 | 34.95 | 32.6776 | 32.6714 | 32.498 | 32.4888 | 32.4755 | 32.4653 | 32.45 | 32.4357 | 32.4204 | 32.4061 | 32.349 | 32.3316 | 32.3276 | 34.0224 | 34.0133 | 33.8429 | 33.8306 | 33.8133 | 33.799 | 33.7796 | 33.7571 | 33.7367 | 33.7173 | 33.6429 | 33.6224 | 33.6153
|  | HARRIS GRID | HT |  |  |  |  | 35.3704 | 35.2092 | 35.199 | 35.1867 | 35.1755 | 35.1612 | 35.1439 | 35.1235 | 35.1031 | 35.0827 | 34.9949 | 34.952 | 34.9367 | 32.6724 | 32.5092 | 32.5031 | 32.498 | 32.4898 | 32.4786 | 32.4673 | 32.4541 | 32.4367 | 32.4245 | 32.3602 | 32.3296 | 32.3173 | 34.0204 | 33.8582 | 33.85 | 33.8418 | 33.8306 | 33.8163 | 33.8 | 33.7806 | 33.7612 | 33.7408 | 33.6571 | 33.6173 | 33.601
|  | HARRIS GRID | HE |  |  |  |  | 35.3714 | 35.3735 | 35.199 | 35.1878 | 35.1786 | 35.1633 | 35.1469 | 35.1265 | 35.1061 | 35.0827 | 34.9816 | 34.9541 | 34.9429 | 32.6735 | 32.6796 | 32.5051 | 32.498 | 32.4898 | 32.4786 | 32.4673 | 32.451 | 32.4378 | 32.4204 | 32.349 | 32.3286 | 32.3204 | 34.0214 | 34.0235 | 33.851 | 33.8408 | 33.8316 | 33.8184 | 33.802 | 33.7827 | 33.7633 | 33.7398 | 33.6459 | 33.6184 | 33.6082
|  | HARRIS GRID | CF |  |  |  |  | 35.3806 | 35.3694 | 35.3673 | 35.2031 | 35.1959 | 35.1878 | 35.1786 | 35.1663 | 35.1551 | 35.1439 | 35.0684 | 34.9939 | 34.9316 | 32.6827 | 32.6776 | 32.6765 | 32.5041 | 32.502 | 32.4969 | 32.4898 | 32.4806 | 32.4724 | 32.4643 | 32.4092 | 32.3561 | 32.3112 | 34.0306 | 34.0204 | 34.0184 | 33.8531 | 33.849 | 33.8398 | 33.8316 | 33.8204 | 33.8092 | 33.799 | 33.7276 | 33.6571 | 33.599
| DYCE | HARVEST AVENUE | MINIMUM HEADROOM | NJ 86978 11769 | NO | YES | 1.258 | 18.9041 | 18.898 | 18.8898 | 18.8847 | 18.8776 | 18.8714 | 18.8622 | 18.852 | 18.8459 | 18.8337 | 18.7969 | 18.7878 | 18.7857 | 19.3347 | 19.3296 | 19.3224 | 19.3163 | 19.3051 | 19.302 | 19.2908 | 19.2806 | 19.2735 | 19.2633 | 19.2408 | 19.2337 | 19.2327 | 19.5561 | 19.55 | 19.5449 | 19.5408 | 19.5337 | 19.5286 | 19.5224 | 19.5133 | 19.5082 | 19.499 | 19.4776 | 19.4704 | 19.4714
|  | HARVEST AVENUE | EE |  |  |  |  | 18.9041 | 18.898 | 18.8898 | 18.8847 | 18.8776 | 18.8714 | 18.8622 | 18.852 | 18.8459 | 18.8337 | 18.7969 | 18.7878 | 18.7857 | 19.3347 | 19.3296 | 19.3224 | 19.3163 | 19.3051 | 19.302 | 19.2908 | 19.2806 | 19.2735 | 19.2633 | 19.2408 | 19.2337 | 19.2327 | 19.5561 | 19.55 | 19.5449 | 19.5408 | 19.5337 | 19.5286 | 19.5224 | 19.5133 | 19.5082 | 19.499 | 19.4776 | 19.4704 | 19.4714
|  | HARVEST AVENUE | HT |  |  |  |  | 18.9061 | 18.901 | 18.8939 | 18.8898 | 18.8837 | 18.8776 | 18.8694 | 18.8653 | 18.8571 | 18.849 | 18.8122 | 18.7918 | 18.7878 | 19.3378 | 19.3327 | 19.3276 | 19.3235 | 19.3163 | 19.3112 | 19.302 | 19.299 | 19.2918 | 19.2837 | 19.2582 | 19.2449 | 19.2418 | 19.5571 | 19.552 | 19.549 | 19.5459 | 19.5398 | 19.5357 | 19.5296 | 19.5255 | 19.5184 | 19.5112 | 19.4898 | 19.4765 | 19.4745
|  | HARVEST AVENUE | HE |  |  |  |  | 18.9061 | 18.902 | 18.898 | 18.8939 | 18.8878 | 18.8847 | 18.8776 | 18.8745 | 18.8663 | 18.8592 | 18.8194 | 18.8031 | 18.7969 | 19.3378 | 19.3337 | 19.3296 | 19.3255 | 19.3204 | 19.3163 | 19.3082 | 19.3061 | 19.299 | 19.2918 | 19.2592 | 19.251 | 19.2459 | 19.5571 | 19.5531 | 19.55 | 19.5469 | 19.5418 | 19.5398 | 19.5337 | 19.5306 | 19.5255 | 19.5194 | 19.4898 | 19.4786 | 19.4755
|  | HARVEST AVENUE | CF |  |  |  |  | 18.9051 | 18.9031 | 18.9 | 18.898 | 18.8929 | 18.8888 | 18.8857 | 18.8806 | 18.8786 | 18.8755 | 18.8561 | 18.8286 | 18.8051 | 19.3367 | 19.3347 | 19.3316 | 19.3265 | 19.3224 | 19.3214 | 19.3153 | 19.3092 | 19.3082 | 19.3051 | 19.2857 | 19.2622 | 19.249 | 19.5561 | 19.5541 | 19.552 | 19.549 | 19.5439 | 19.5429 | 19.5408 | 19.5367 | 19.5357 | 19.5316 | 19.5173 | 19.4969 | 19.4857
| THURSO | HASTIGROW | MINIMUM HEADROOM | ND 26576 60773 | YES | NO | 0.454 | -0.025384 | -0.14273 | -0.2764 | -0.42436 | -0.54375 | -0.69783 | -0.89783 | -1.0764 | -1.2805 | -1.4642 | -1.9233 | -2.0723 | -2.1264 | 0.85319 | 0.78992 | 0.71237 | 0.61951 | 0.55217 | 0.45319 | 0.33074 | 0.22972 | 0.10523 | -0.0049755 | -0.28151 | -0.38559 | -0.6662 | 0.34196 | 0.2389 | 0.12053 | -0.0080367 | -0.11212 | -0.24681 | -0.41926 | -0.57334 | -0.75396 | -0.92436 | -1.3407 | -1.4713 | -1.5172
|  | HASTIGROW | EE |  |  |  |  | -0.025384 | -0.14273 | -0.2764 | -0.42436 | -0.54375 | -0.69783 | -0.89783 | -1.0764 | -1.2805 | -1.4642 | -1.9233 | -2.005 | -2.0335 | 0.85319 | 0.78992 | 0.71237 | 0.61951 | 0.55217 | 0.45319 | 0.33074 | 0.22972 | 0.10523 | -0.0049755 | -0.28151 | -0.38559 | -0.52538 | 0.34196 | 0.2389 | 0.12053 | -0.0080367 | -0.11212 | -0.24681 | -0.41926 | -0.57334 | -0.75396 | -0.92436 | -1.3407 | -1.4121 | -1.4397
|  | HASTIGROW | HT |  |  |  |  | 0.0011469 | -0.10498 | -0.21518 | -0.3213 | -0.44273 | -0.57947 | -0.70089 | -0.86212 | -1.0203 | -1.1835 | -1.7805 | -2.0723 | -2.1264 | 0.86135 | 0.83074 | 0.77156 | 0.71951 | 0.65115 | 0.57462 | 0.51441 | 0.41849 | 0.32462 | 0.2236 | -0.14477 | -0.29375 | -0.32028 | 0.36747 | 0.26747 | 0.16645 | 0.069514 | -0.039669 | -0.16008 | -0.2662 | -0.406 | -0.54579 | -0.68559 | -1.2091 | -1.4713 | -1.5172
|  | HASTIGROW | HE |  |  |  |  | 0.0011469 | -0.071302 | -0.15498 | -0.23049 | -0.31926 | -0.4213 | -0.52232 | -0.66314 | -0.80191 | -0.94375 | -1.7101 | -1.8927 | -1.9172 | 0.86033 | 0.83992 | 0.78992 | 0.74707 | 0.6889 | 0.62053 | 0.56849 | 0.4787 | 0.39298 | 0.29911 | -0.14987 | -0.31416 | -0.44681 | 0.36543 | 0.29809 | 0.2236 | 0.15727 | 0.079718 | -0.0080367 | -0.097833 | -0.21926 | -0.33559 | -0.46008 | -1.1438 | -1.3121 | -1.3335
|  | HASTIGROW | CF |  |  |  |  | 0.011351 | -0.052935 | -0.12028 | -0.18457 | -0.26722 | -0.34579 | -0.43763 | -0.50498 | -0.59885 | -0.69273 | -1.158 | -1.605 | -1.8611 | 0.86339 | 0.85421 | 0.81237 | 0.77462 | 0.72258 | 0.67258 | 0.61339 | 0.57053 | 0.50523 | 0.43686 | 0.096045 | -0.31008 | -0.6662 | 0.37768 | 0.31645 | 0.25013 | 0.19298 | 0.12053 | 0.050127 | -0.028445 | -0.088649 | -0.16824 | -0.24987 | -0.64477 | -1.0529 | -1.2876
| STRICHEN | HATTON | MINIMUM HEADROOM | NK 06441 37348 | NO | YES | 0.444 | 4.3548 | 4.1109 | 3.8262 | 3.5548 | 3.2293 | 2.9344 | 2.5528 | 2.1232 | 1.7721 | 1.4038 | 0.26908 | -0.29929 | -0.34214 | 5.8374 | 5.6905 | 5.5109 | 5.3517 | 5.1385 | 4.9303 | 4.7313 | 4.4752 | 4.2507 | 4.0395 | 3.4538 | 3.1517 | 2.8446 | 5.0191 | 4.8068 | 4.5507 | 4.3191 | 4.0242 | 3.7364 | 3.4191 | 3.0293 | 2.6864 | 2.3558 | 1.4201 | 0.91296 | 0.87929
|  | HATTON | EE |  |  |  |  | 4.3548 | 4.1109 | 3.8262 | 3.565 | 3.2477 | 2.9344 | 2.566 | 2.1436 | 1.7732 | 1.4038 | 0.28235 | -0.23194 | -0.34214 | 5.8374 | 5.6905 | 5.5109 | 5.3517 | 5.1385 | 4.9303 | 4.7313 | 4.4752 | 4.2507 | 4.0395 | 3.4538 | 3.1517 | 2.8446 | 5.0191 | 4.8068 | 4.5507 | 4.3191 | 4.0242 | 3.7364 | 3.4191 | 3.0293 | 2.6864 | 2.3558 | 1.4242 | 0.97622 | 0.87929
|  | HATTON | HT |  |  |  |  | 4.3885 | 4.1313 | 3.8466 | 3.5548 | 3.2293 | 2.9548 | 2.5528 | 2.1232 | 1.7721 | 1.4211 | 0.26908 | -0.29929 | -0.13908 | 5.8823 | 5.7354 | 5.566 | 5.3844 | 5.1772 | 5.0221 | 4.814 | 4.5936 | 4.4262 | 4.2405 | 3.616 | 3.3619 | 3.5589 | 5.0752 | 4.8609 | 4.6099 | 4.3497 | 4.0548 | 3.8099 | 3.4599 | 3.0895 | 2.7874 | 2.4732 | 1.4201 | 0.91296 | 1.0885
|  | HATTON | HE |  |  |  |  | 4.3997 | 4.2181 | 4.015 | 3.8068 | 3.564 | 3.3528 | 3.0579 | 2.7385 | 2.5038 | 2.2272 | 0.93949 | 0.59255 | 0.34051 | 5.8895 | 5.767 | 5.6374 | 5.4926 | 5.3252 | 5.1854 | 5.0079 | 4.8221 | 4.6874 | 4.5191 | 3.7181 | 3.5926 | 3.2395 | 5.0854 | 4.9201 | 4.7466 | 4.5589 | 4.3354 | 4.1579 | 3.8946 | 3.6048 | 3.4017 | 3.1466 | 1.9681 | 1.7303 | 1.5109
|  | HATTON | CF |  |  |  |  | 4.4497 | 4.317 | 4.1619 | 4.0334 | 3.8783 | 3.7038 | 3.5426 | 3.3548 | 3.2119 | 3.0517 | 2.065 | 1.5017 | 0.88031 | 5.916 | 5.8334 | 5.7211 | 5.6354 | 5.5262 | 5.4007 | 5.2987 | 5.1599 | 5.0466 | 4.9201 | 4.2079 | 3.7272 | 2.9426 | 5.1262 | 5.0099 | 4.864 | 4.7507 | 4.6058 | 4.4446 | 4.3109 | 4.1334 | 3.9915 | 3.8344 | 2.9364 | 2.513 | 1.9823
| PERSLEY | HAUDAGAIN | MINIMUM HEADROOM | NJ 91425 09066 | NO | NO | 4.793 | 8.6444 | 8.221 | 7.772 | 7.2751 | 6.724 | 6.1751 | 5.3087 | 4.3465 | 3.4322 | 2.9342 | -0.59944 | -3.2025 | -3.6056 | 10.174 | 9.9138 | 9.6302 | 9.3046 | 8.9363 | 8.5751 | 8.0618 | 7.47 | 6.9097 | 6.6873 | 4.6802 | 3.2434 | 1.8893 | 9.5659 | 9.1669 | 8.7434 | 8.2608 | 7.7322 | 7.22 | 6.424 | 5.5281 | 4.6781 | 4.2434 | 1.1067 | -1.1556 | -1.5178
|  | HAUDAGAIN | EE |  |  |  |  | 8.6444 | 8.221 | 7.772 | 7.2751 | 6.724 | 6.1751 | 5.3087 | 4.3465 | 3.4322 | 2.9342 | -0.5627 | -2.9852 | -3.6056 | 10.174 | 9.9138 | 9.6302 | 9.3046 | 8.9363 | 8.5751 | 8.0618 | 7.47 | 6.9097 | 6.6873 | 4.6802 | 3.2434 | 1.922 | 9.5659 | 9.1669 | 8.7434 | 8.2608 | 7.7322 | 7.22 | 6.424 | 5.5281 | 4.6781 | 4.2434 | 1.1067 | -0.9576 | -1.5178
|  | HAUDAGAIN | HT |  |  |  |  | 8.7638 | 8.3853 | 7.9944 | 7.5751 | 7.1495 | 6.672 | 5.8679 | 5.0424 | 4.1985 | 3.3302 | -0.59944 | -3.2025 | -3.579 | 10.2863 | 10.0883 | 9.8853 | 9.6485 | 9.4128 | 9.123 | 8.7097 | 8.2781 | 7.8251 | 7.3567 | 5.3842 | 4.1383 | 3.9822 | 9.7097 | 9.3659 | 9.0087 | 8.6189 | 8.2271 | 7.77 | 7.0444 | 6.2893 | 5.5169 | 4.72 | 1.1802 | -1.1556 | -1.4852
|  | HAUDAGAIN | HE |  |  |  |  | 8.7485 | 8.4944 | 8.2342 | 7.9424 | 7.6495 | 7.3067 | 6.7393 | 6.1444 | 5.5373 | 4.9077 | 1.7404 | -0.63923 | -1.2933 | 10.2669 | 10.1046 | 9.9302 | 9.7251 | 9.5179 | 9.2577 | 8.9128 | 8.5363 | 8.1475 | 7.7414 | 5.7648 | 4.1863 | 2.9506 | 9.6975 | 9.4536 | 9.2026 | 8.9189 | 8.6383 | 8.2944 | 7.773 | 7.2148 | 6.6495 | 6.0638 | 3.1812 | 1.1332 | 0.56077
|  | HAUDAGAIN | CF |  |  |  |  | 8.8618 | 8.723 | 8.5761 | 8.4057 | 8.2169 | 8.0414 | 7.8363 | 7.5689 | 7.323 | 7.1046 | 5.2353 | 3.3975 | 1.2802 | 10.322 | 10.2189 | 10.1067 | 9.9638 | 9.7995 | 9.6404 | 9.4404 | 9.1995 | 8.9689 | 8.7536 | 7.0802 | 5.0097 | 1.8893 | 9.7975 | 9.6577 | 9.5097 | 9.3363 | 9.1404 | 8.9628 | 8.7546 | 8.4893 | 8.2444 | 8.0353 | 6.2536 | 4.624 | 2.7169
| WILLOWDALE | HAYTON | MINIMUM HEADROOM | NJ 92753 08909 | NO | NO | 0.76 | 17.5131 | 17.0182 | 16.4457 | 15.8161 | 15.1702 | 14.4376 | 13.4467 | 12.3325 | 11.2692 | 10.3018 | 5.2008 | 2.659 | 2.461 | 17.9804 | 17.6498 | 17.2437 | 16.7967 | 16.2733 | 15.5967 | 14.8539 | 13.959 | 13.1722 | 12.4957 | 8.5651 | 6.7988 | 6.4549 | 17.1309 | 16.7289 | 16.186 | 15.5432 | 14.8564 | 14.0972 | 13.1626 | 12.0809 | 11.0962 | 10.2258 | 5.6595 | 3.2493 | 3.0758
|  | HAYTON | EE |  |  |  |  | 17.5131 | 17.0182 | 16.4457 | 15.8161 | 15.1702 | 14.4376 | 13.4467 | 12.3325 | 11.2692 | 10.3018 | 6.5274 | 4.6263 | 4.11 | 17.9804 | 17.6498 | 17.2437 | 16.7967 | 16.2733 | 15.5967 | 14.8539 | 13.959 | 13.1722 | 12.4957 | 10.312 | 9.162 | 7.6488 | 17.1309 | 16.7289 | 16.186 | 15.5432 | 14.8564 | 14.0972 | 13.1626 | 12.0809 | 11.0962 | 10.2258 | 7.0748 | 5.8085 | 5.4442
|  | HAYTON | HT |  |  |  |  | 17.7957 | 17.411 | 16.9876 | 16.5498 | 16.059 | 15.5039 | 14.6651 | 13.6927 | 12.7202 | 11.7467 | 7.3518 | 4.908 | 4.6263 | 18.1988 | 17.9753 | 17.7243 | 17.4488 | 17.1284 | 16.762 | 16.2916 | 15.7141 | 15.1467 | 14.5865 | 11.9294 | 10.6804 | 10.5508 | 17.3717 | 17.0687 | 16.737 | 16.3932 | 15.9983 | 15.4595 | 14.735 | 13.8819 | 13.0585 | 12.2207 | 8.434 | 6.1891 | 5.9442
|  | HAYTON | HE |  |  |  |  | 17.7212 | 17.3569 | 16.9631 | 16.5325 | 16.0345 | 15.3202 | 14.4202 | 13.2753 | 12.0896 | 10.8498 | 5.2008 | 2.659 | 2.461 | 18.1284 | 17.8753 | 17.5896 | 17.2671 | 16.7569 | 16.0886 | 15.3641 | 14.4447 | 13.5733 | 12.6671 | 8.5651 | 6.7988 | 6.6488 | 17.2921 | 16.9779 | 16.6289 | 16.1044 | 15.4942 | 14.7697 | 13.8972 | 12.8034 | 11.7677 | 10.6819 | 5.6595 | 3.2493 | 3.0758
|  | HAYTON | CF |  |  |  |  | 17.862 | 17.6671 | 17.4447 | 17.1988 | 16.9049 | 16.5835 | 16.2416 | 15.7722 | 15.2182 | 14.6212 | 10.9631 | 7.659 | 5.8498 | 18.2131 | 18.0631 | 17.8886 | 17.6865 | 17.4355 | 17.1498 | 16.8427 | 16.4386 | 15.9814 | 15.4896 | 12.61 | 10.1222 | 6.4549 | 17.4217 | 17.2554 | 17.0666 | 16.8544 | 16.5534 | 16.1646 | 15.7595 | 15.2197 | 14.6942 | 14.133 | 10.7952 | 7.9034 | 6.2809
| BRORA | HELMSDALE | MINIMUM HEADROOM | ND 02372 15376 | YES | NO | 0.012 | 0.36015 | 0.29688 | 0.2479 | 0.19178 | 0.12545 | 0.083616 | 0.0019837 | -0.089853 | -0.18985 | -0.27965 | -0.41434 | -0.4674 | -0.48067 | 0.71219 | 0.67035 | 0.63974 | 0.60811 | 0.56423 | 0.53668 | 0.48668 | 0.42953 | 0.37239 | 0.31627 | 0.22749 | 0.17239 | -5.7143e-05 | 0.55709 | 0.4979 | 0.453 | 0.39994 | 0.33872 | 0.2979 | 0.22137 | 0.13566 | 0.0428 | -0.041894 | -0.15924 | -0.20924 | -0.22149
|  | HELMSDALE | EE |  |  |  |  | 0.36015 | 0.29688 | 0.2479 | 0.19178 | 0.12545 | 0.083616 | 0.0019837 | -0.089853 | -0.18985 | -0.27965 | -0.41434 | -0.43883 | -0.4521 | 0.71219 | 0.67035 | 0.63974 | 0.60811 | 0.56423 | 0.53668 | 0.48668 | 0.42953 | 0.37239 | 0.31627 | 0.22749 | 0.17239 | 0.087698 | 0.55709 | 0.4979 | 0.453 | 0.39994 | 0.33872 | 0.2979 | 0.22137 | 0.13566 | 0.0428 | -0.041894 | -0.15924 | -0.18271 | -0.19496
|  | HELMSDALE | HT |  |  |  |  | 0.37341 | 0.32341 | 0.27647 | 0.23872 | 0.18872 | 0.13158 | 0.059127 | -0.028629 | -0.071486 | -0.13577 | -0.4021 | -0.4674 | -0.48067 | 0.72749 | 0.69382 | 0.66423 | 0.6377 | 0.60607 | 0.57239 | 0.53158 | 0.4826 | 0.46117 | 0.42647 | 0.25709 | 0.22953 | 0.22137 | 0.57647 | 0.52953 | 0.48362 | 0.44892 | 0.39892 | 0.34994 | 0.27953 | 0.19484 | 0.16423 | 0.10198 | -0.1521 | -0.20924 | -0.22149
|  | HELMSDALE | HE |  |  |  |  | 0.37239 | 0.33464 | 0.30402 | 0.27239 | 0.22953 | 0.19688 | 0.14076 | 0.06729 | 0.021371 | -0.052098 | -0.35516 | -0.38373 | -0.39189 | 0.72341 | 0.69586 | 0.67341 | 0.65402 | 0.62443 | 0.603 | 0.56627 | 0.52137 | 0.49688 | 0.453 | 0.26321 | 0.21015 | 0.13158 | 0.57647 | 0.5377 | 0.50607 | 0.47647 | 0.43566 | 0.40504 | 0.353 | 0.28464 | 0.2428 | 0.17545 | -0.10924 | -0.12965 | -0.13781
|  | HELMSDALE | CF |  |  |  |  | 0.37647 | 0.34892 | 0.32443 | 0.28974 | 0.26831 | 0.22953 | 0.20402 | 0.15913 | 0.10504 | 0.049943 | -0.14393 | -0.32965 | -0.37455 | 0.72647 | 0.70913 | 0.6928 | 0.66627 | 0.65198 | 0.62851 | 0.61015 | 0.57851 | 0.54586 | 0.51117 | 0.36015 | 0.17341 | -5.7143e-05 | 0.5826 | 0.55709 | 0.52545 | 0.49076 | 0.47239 | 0.43566 | 0.41219 | 0.37137 | 0.32137 | 0.27035 | 0.088718 | -0.088833 | -0.12353
| INVERNESS | HILTON | MINIMUM HEADROOM | NH 67326 43262 | NO | NO | 4.817 | 6.6093 | 6.0665 | 5.4461 | 4.7563 | 4.4461 | 3.7777 | 2.7297 | 1.6001 | 0.50422 | -0.51109 | -4.7652 | -7.2417 | -7.6703 | 10.3444 | 10.0495 | 9.7036 | 9.325 | 9.1822 | 8.7587 | 8.172 | 7.5169 | 6.8801 | 6.3067 | 4.0179 | 2.3648 | -0.2464 | 7.7546 | 7.2679 | 6.725 | 6.1505 | 5.8087 | 5.2169 | 4.2883 | 3.2444 | 2.2373 | 1.3087 | -2.4413 | -4.6607 | -5.025
|  | HILTON | EE |  |  |  |  | 6.6093 | 6.0665 | 5.4461 | 4.7563 | 4.4481 | 3.7818 | 2.7297 | 1.6001 | 0.50422 | -0.51109 | -4.4876 | -6.8172 | -7.3723 | 10.3444 | 10.0495 | 9.7036 | 9.325 | 9.1822 | 8.7587 | 8.172 | 7.5169 | 6.8801 | 6.3067 | 4.0179 | 2.3648 | 0.60258 | 7.7546 | 7.2679 | 6.725 | 6.1505 | 5.8689 | 5.2536 | 4.2883 | 3.2444 | 2.2373 | 1.3087 | -2.2515 | -4.2882 | -4.777
|  | HILTON | HT |  |  |  |  | 6.694 | 6.1807 | 5.6185 | 5.0665 | 4.4461 | 3.7777 | 3.0634 | 2.0369 | 1.0205 | -0.01109 | -4.7652 | -7.2417 | -7.6703 | 10.4291 | 10.1822 | 9.9067 | 9.6393 | 9.3281 | 8.9863 | 8.7332 | 8.2526 | 7.7495 | 7.223 | 4.7791 | 3.6169 | 3.425 | 7.8363 | 7.3669 | 6.8587 | 6.3597 | 5.8087 | 5.2169 | 4.5761 | 3.6505 | 2.7373 | 1.8107 | -2.4413 | -4.6607 | -5.025
|  | HILTON | HE |  |  |  |  | 6.7471 | 6.4807 | 6.1624 | 5.8665 | 5.4716 | 5.0318 | 4.7389 | 4.0685 | 3.4124 | 2.745 | -1.0203 | -3.6427 | -4.7244 | 10.4485 | 10.275 | 10.071 | 9.8842 | 9.6485 | 9.3812 | 9.2546 | 8.8475 | 8.4454 | 8.024 | 5.5934 | 3.7026 | 1.8352 | 7.8842 | 7.6383 | 7.3556 | 7.0934 | 6.774 | 6.4128 | 6.1281 | 5.524 | 4.9199 | 4.3005 | 0.85462 | -1.4648 | -2.4413
|  | HILTON | CF |  |  |  |  | 6.9593 | 6.7981 | 6.6267 | 6.4583 | 6.195 | 5.9103 | 5.594 | 5.6501 | 5.3746 | 5.092 | 2.8103 | -0.091702 | -2.4846 | 10.6005 | 10.4546 | 10.3179 | 10.1791 | 9.9944 | 9.7893 | 9.5281 | 9.4985 | 9.2414 | 8.971 | 6.9812 | 3.8658 | -0.2464 | 8.0883 | 7.9261 | 7.7761 | 7.6281 | 7.4271 | 7.2138 | 6.9373 | 6.9699 | 6.7199 | 6.4628 | 4.373 | 1.6944 | -0.47905
| ARBROATH | HUME STREET | MINIMUM HEADROOM | NO 64067 41180 | NO | YES | 0.526 | 14.0721 | 13.6833 | 13.3119 | 12.9017 | 12.5068 | 12.064 | 11.3987 | 10.9191 | 10.2742 | 9.6731 | 6.8915 | 4.9364 | 4.5793 | 16.2603 | 16.0491 | 15.8399 | 15.6052 | 15.3715 | 15.0827 | 14.6736 | 14.4654 | 14.0725 | 13.7174 | 11.9562 | 10.9103 | 9.745 | 15.5593 | 15.1909 | 14.8358 | 14.4368 | 14.045 | 13.6062 | 12.9378 | 12.5521 | 11.9389 | 11.3572 | 8.8684 | 7.144 | 6.8256
|  | HUME STREET | EE |  |  |  |  | 14.0721 | 13.6833 | 13.3119 | 12.9017 | 12.5068 | 12.064 | 11.3987 | 10.9191 | 10.2742 | 9.6731 | 6.8915 | 5.0262 | 4.5793 | 16.2603 | 16.0491 | 15.8399 | 15.6052 | 15.3715 | 15.0827 | 14.6736 | 14.4654 | 14.0725 | 13.7174 | 12.197 | 11.0705 | 10.0593 | 15.5593 | 15.1909 | 14.8358 | 14.4368 | 14.045 | 13.6062 | 12.9378 | 12.5521 | 11.9389 | 11.3572 | 8.8684 | 7.2276 | 6.8256
|  | HUME STREET | HT |  |  |  |  | 14.1884 | 13.8487 | 13.518 | 13.1987 | 12.8384 | 12.465 | 11.8946 | 11.2599 | 10.6293 | 9.9864 | 6.9752 | 4.9364 | 4.5987 | 16.3613 | 16.197 | 16.0327 | 15.8766 | 15.694 | 15.495 | 15.2266 | 14.898 | 14.5501 | 14.1909 | 12.7521 | 11.8144 | 11.6705 | 15.6817 | 15.3684 | 15.0531 | 14.7491 | 14.4031 | 14.0399 | 13.5031 | 12.898 | 12.3021 | 11.6889 | 8.9725 | 7.144 | 6.848
|  | HUME STREET | HE |  |  |  |  | 14.1487 | 13.8895 | 13.6384 | 13.3691 | 13.1058 | 12.8017 | 12.3844 | 11.8936 | 11.416 | 10.9201 | 7.8374 | 6.0078 | 5.6874 | 16.3287 | 16.1756 | 16.0266 | 15.8633 | 15.697 | 15.4991 | 15.2582 | 14.9572 | 14.5174 | 14.048 | 11.9562 | 10.9103 | 10.6236 | 15.6501 | 15.4082 | 15.1664 | 14.9052 | 14.6593 | 14.3644 | 13.9674 | 13.498 | 13.0419 | 12.4419 | 9.3838 | 7.7031 | 7.4205
|  | HUME STREET | CF |  |  |  |  | 14.2436 | 14.0721 | 13.918 | 13.7497 | 13.5629 | 13.3895 | 13.2129 | 13.0017 | 12.8384 | 12.6354 | 11.0211 | 8.6262 | 6.6262 | 16.3776 | 16.2695 | 16.1674 | 16.0562 | 15.9215 | 15.7929 | 15.6429 | 15.4603 | 15.3103 | 15.1317 | 13.7807 | 12.196 | 9.745 | 15.7389 | 15.5797 | 15.4327 | 15.2684 | 15.0868 | 14.9256 | 14.7542 | 14.5419 | 14.3787 | 14.1776 | 12.3093 | 10.0684 | 8.2215
| KEITH 2 | HUNTLY | MINIMUM HEADROOM | NJ 52762 39217 | NO | YES | 0.913 | 8.2254 | 7.7234 | 7.1775 | 6.5673 | 5.9142 | 5.4285 | 4.9642 | 4.4397 | 3.9305 | 3.6714 | 2.0662 | 1.0356 | 0.81931 | 9.5867 | 9.1714 | 8.7224 | 8.2285 | 7.6928 | 7.3571 | 7.0918 | 6.7418 | 6.4428 | 6.304 | 5.4805 | 4.954 | 4.4356 | 8.9566 | 8.4841 | 7.9749 | 7.4106 | 6.7994 | 6.3494 | 5.931 | 5.4515 | 5.031 | 4.8015 | 3.4627 | 2.5617 | 2.378
|  | HUNTLY | EE |  |  |  |  | 8.2448 | 7.7785 | 7.2958 | 6.7326 | 6.1101 | 5.602 | 4.9928 | 4.4397 | 3.9305 | 3.756 | 2.0826 | 1.152 | 0.93156 | 9.6448 | 9.2438 | 8.8652 | 8.4162 | 7.9101 | 7.4877 | 7.0918 | 6.7418 | 6.4428 | 6.304 | 5.4805 | 4.954 | 4.4836 | 8.981 | 8.5066 | 8.0402 | 7.5076 | 6.9229 | 6.4372 | 5.931 | 5.4515 | 5.031 | 4.8015 | 3.4627 | 2.6749 | 2.477
|  | HUNTLY | HT |  |  |  |  | 8.2254 | 7.7234 | 7.1775 | 6.5673 | 5.9142 | 5.4285 | 4.9642 | 4.5326 | 4.102 | 3.6714 | 2.0662 | 1.0356 | 0.81931 | 9.5867 | 9.1714 | 8.7224 | 8.2285 | 7.6928 | 7.3571 | 7.0918 | 6.8448 | 6.6142 | 6.3877 | 5.5397 | 5.0999 | 4.9265 | 8.9566 | 8.4841 | 7.9749 | 7.4106 | 6.7994 | 6.3494 | 5.9739 | 5.6086 | 5.2586 | 4.8841 | 3.4678 | 2.5617 | 2.378
|  | HUNTLY | HE |  |  |  |  | 8.306 | 7.8907 | 7.4958 | 7.0285 | 6.5173 | 6.0826 | 5.6805 | 5.3346 | 4.9683 | 4.5999 | 2.9938 | 2.1377 | 1.7642 | 9.6816 | 9.2979 | 8.9418 | 8.5203 | 8.0642 | 7.7081 | 7.3744 | 7.0867 | 6.8265 | 6.5693 | 5.5724 | 5.1438 | 4.7958 | 9.0423 | 8.627 | 8.2321 | 7.7657 | 7.2606 | 6.8239 | 6.4004 | 6.03 | 5.6851 | 5.3382 | 3.8484 | 3.1086 | 2.7872
|  | HUNTLY | CF |  |  |  |  | 8.5111 | 8.2816 | 8.0326 | 7.7867 | 7.4877 | 7.2091 | 6.9438 | 6.6581 | 6.4183 | 6.1887 | 4.6969 | 3.3999 | 2.4438 | 9.8775 | 9.6652 | 9.4356 | 9.2142 | 8.9458 | 8.6989 | 8.4775 | 8.2581 | 8.0591 | 7.8652 | 6.6479 | 5.653 | 4.4356 | 9.231 | 9.0127 | 8.7657 | 8.5178 | 8.2219 | 7.9433 | 7.6719 | 7.3821 | 7.1361 | 6.8994 | 5.4239 | 4.2117 | 3.3372
| BRIDGE OF DUN | INCHBARE | MINIMUM HEADROOM | NO 60684 65379 | YES | NO | 0.533 | 1.618 | 1.5884 | 1.5465 | 1.5098 | 1.4659 | 1.419 | 1.3618 | 1.3006 | 1.2373 | 1.1812 | 0.95061 | 0.83326 | 0.73224 | 1.795 | 1.7766 | 1.7501 | 1.7266 | 1.7011 | 1.6695 | 1.6307 | 1.5868 | 1.543 | 1.5062 | 1.3307 | 1.2501 | 1.1685 | 1.6963 | 1.6708 | 1.6361 | 1.6024 | 1.5646 | 1.5238 | 1.4687 | 1.4106 | 1.3514 | 1.2983 | 1.0779 | 0.96668 | 0.86566
|  | INCHBARE | EE |  |  |  |  | 1.618 | 1.5884 | 1.5465 | 1.5098 | 1.4659 | 1.419 | 1.3618 | 1.3006 | 1.2373 | 1.1812 | 0.98632 | 0.91489 | 0.8802 | 1.795 | 1.7766 | 1.7501 | 1.7266 | 1.7011 | 1.6695 | 1.6307 | 1.5868 | 1.543 | 1.5062 | 1.3705 | 1.3215 | 1.296 | 1.6963 | 1.6708 | 1.6361 | 1.6024 | 1.5646 | 1.5238 | 1.4687 | 1.4106 | 1.3514 | 1.2983 | 1.1146 | 1.0453 | 1.0126
|  | INCHBARE | HT |  |  |  |  | 1.6312 | 1.6078 | 1.5822 | 1.5516 | 1.5139 | 1.4792 | 1.4363 | 1.3792 | 1.3261 | 1.269 | 1.019 | 0.8853 | 0.79959 | 1.8062 | 1.793 | 1.7776 | 1.7583 | 1.7358 | 1.7154 | 1.6868 | 1.6511 | 1.6123 | 1.5705 | 1.393 | 1.3021 | 1.2379 | 1.7095 | 1.6912 | 1.6646 | 1.6361 | 1.6034 | 1.5728 | 1.535 | 1.4871 | 1.4361 | 1.381 | 1.1453 | 1.0177 | 0.93709
|  | INCHBARE | HE |  |  |  |  | 1.6312 | 1.6098 | 1.5843 | 1.5547 | 1.519 | 1.4853 | 1.4394 | 1.3822 | 1.3251 | 1.2598 | 0.95061 | 0.83326 | 0.77918 | 1.8062 | 1.7909 | 1.7746 | 1.7552 | 1.7307 | 1.7083 | 1.6776 | 1.6389 | 1.595 | 1.5511 | 1.3307 | 1.2501 | 1.2123 | 1.7095 | 1.6912 | 1.6697 | 1.6442 | 1.6116 | 1.584 | 1.5401 | 1.4871 | 1.4299 | 1.3718 | 1.0779 | 0.96668 | 0.9177
|  | INCHBARE | CF |  |  |  |  | 1.6343 | 1.621 | 1.6078 | 1.5904 | 1.568 | 1.5435 | 1.519 | 1.4822 | 1.4465 | 1.4129 | 1.1853 | 0.95571 | 0.73224 | 1.8083 | 1.796 | 1.7889 | 1.7797 | 1.7644 | 1.7501 | 1.7328 | 1.7072 | 1.6838 | 1.6593 | 1.495 | 1.3276 | 1.1685 | 1.7136 | 1.7004 | 1.6891 | 1.6738 | 1.6524 | 1.633 | 1.6126 | 1.5799 | 1.5493 | 1.5146 | 1.2993 | 1.081 | 0.86566
| DUNOON | INNELLAN | MINIMUM HEADROOM | NS 15129 70875 | YES | YES | 0 | 1.8561 | 1.802 | 1.7418 | 1.6837 | 1.599 | 1.5184 | 1.3673 | 1.2602 | 1.1245 | 0.99796 | 0.56633 | 0.28673 | 0.24184 | 2.0617 | 2.027 | 1.9862 | 1.9464 | 1.8852 | 1.8311 | 1.7403 | 1.677 | 1.5893 | 1.5128 | 1.2811 | 1.1485 | 1.0087 | 1.9538 | 1.9028 | 1.8406 | 1.7875 | 1.7038 | 1.6242 | 1.4865 | 1.3885 | 1.261 | 1.1446 | 0.77628 | 0.54362 | 0.50485
|  | INNELLAN | EE |  |  |  |  | 1.8561 | 1.802 | 1.7418 | 1.6837 | 1.599 | 1.5184 | 1.3673 | 1.2602 | 1.1245 | 0.99796 | 0.56633 | 0.30918 | 0.24898 | 2.0617 | 2.027 | 1.9862 | 1.9464 | 1.8852 | 1.8311 | 1.7403 | 1.677 | 1.5893 | 1.5128 | 1.2811 | 1.1485 | 1.0117 | 1.9538 | 1.9028 | 1.8406 | 1.7875 | 1.7038 | 1.6242 | 1.4865 | 1.3885 | 1.261 | 1.1446 | 0.77628 | 0.56403 | 0.51097
|  | INNELLAN | HT |  |  |  |  | 1.8867 | 1.8347 | 1.7827 | 1.7276 | 1.651 | 1.5898 | 1.4694 | 1.3418 | 1.2082 | 1.0878 | 0.58367 | 0.28673 | 0.24184 | 2.0934 | 2.0617 | 2.0321 | 1.9995 | 1.9505 | 1.9209 | 1.8515 | 1.7811 | 1.7036 | 1.6301 | 1.3536 | 1.2189 | 1.2005 | 1.9926 | 1.9457 | 1.8957 | 1.8477 | 1.7742 | 1.7232 | 1.6099 | 1.4967 | 1.3773 | 1.262 | 0.80281 | 0.54362 | 0.50485
|  | INNELLAN | HE |  |  |  |  | 1.8867 | 1.8531 | 1.8173 | 1.7837 | 1.7286 | 1.6827 | 1.5735 | 1.4755 | 1.3867 | 1.299 | 0.89082 | 0.62959 | 0.52653 | 2.0934 | 2.0658 | 2.0423 | 2.0158 | 1.973 | 1.9485 | 1.8842 | 1.8219 | 1.7587 | 1.6985 | 1.4342 | 1.2811 | 1.1372 | 1.9926 | 1.9589 | 1.9222 | 1.8895 | 1.8324 | 1.7926 | 1.6936 | 1.6038 | 1.5191 | 1.4324 | 1.0548 | 0.83546 | 0.75077
|  | INNELLAN | CF |  |  |  |  | 1.898 | 1.8765 | 1.8551 | 1.8276 | 1.8031 | 1.7704 | 1.7408 | 1.6806 | 1.6347 | 1.5724 | 1.3071 | 0.99694 | 0.78673 | 2.1005 | 2.0791 | 2.0628 | 2.0372 | 2.0158 | 1.9832 | 1.9607 | 1.9128 | 1.877 | 1.8301 | 1.6168 | 1.325 | 1.0087 | 2.0028 | 1.9783 | 1.9569 | 1.9212 | 1.8946 | 1.8569 | 1.8314 | 1.7712 | 1.7253 | 1.6661 | 1.4089 | 1.1171 | 0.94974
| KEITH 2 | INSCH | MINIMUM HEADROOM | NJ 63100 28651 | NO | YES | 0.724 | 0.63006 | 0.14333 | 6.8183 | 6.1479 | 5.4214 | 4.8806 | 4.4183 | 3.8989 | 3.7704 | 3.3836 | 2.3663 | 2.0744 | 1.952 | 2.3704 | 2.0377 | 8.5796 | 8.0857 | 7.5306 | 7.152 | 6.8489 | 6.4806 | 6.4744 | 6.2418 | 5.5704 | 5.2949 | 4.3551 | 1.5211 | 1.0711 | 7.626 | 7.0158 | 6.3443 | 5.8413 | 5.4046 | 4.9209 | 4.8229 | 4.4678 | 3.5413 | 3.2811 | 3.176
|  | INSCH | EE |  |  |  |  | 0.63006 | 0.14333 | 6.8867 | 6.2408 | 5.5704 | 4.9877 | 4.4183 | 3.8989 | 3.7704 | 3.3836 | 2.3663 | 2.1938 | 2.1377 | 2.3704 | 2.0377 | 8.5826 | 8.1234 | 7.6591 | 7.2316 | 6.8489 | 6.4806 | 6.4744 | 6.2418 | 5.5704 | 5.2949 | 4.9132 | 1.5211 | 1.0711 | 7.677 | 7.0852 | 6.4699 | 5.9301 | 5.4046 | 4.9209 | 4.8229 | 4.4678 | 3.5413 | 3.3882 | 3.3392
|  | INSCH | HT |  |  |  |  | 0.64843 | 0.15149 | 6.8183 | 6.1479 | 5.4214 | 4.8806 | 4.5316 | 4.1632 | 3.8132 | 3.4612 | 2.6183 | 2.0744 | 1.952 | 2.4132 | 2.0938 | 8.5796 | 8.0857 | 7.5306 | 7.152 | 6.9408 | 6.7091 | 6.4989 | 6.2928 | 5.8663 | 5.5898 | 5.5051 | 1.5426 | 1.0926 | 7.626 | 7.0158 | 6.3443 | 5.8413 | 5.5229 | 5.1801 | 4.8566 | 4.5341 | 3.7699 | 3.2811 | 3.176
|  | INSCH | HE |  |  |  |  | 0.69027 | 0.29741 | 7.1153 | 6.5969 | 6.004 | 5.4867 | 5.0744 | 4.6887 | 4.3377 | 3.9938 | 2.6663 | 2.3051 | 2.2316 | 2.4418 | 2.1683 | 8.7428 | 8.3622 | 7.8969 | 7.5091 | 7.2204 | 6.9551 | 6.7153 | 6.4857 | 5.7234 | 5.3581 | 4.9755 | 1.5793 | 1.2191 | 7.8892 | 7.4158 | 6.8658 | 6.3923 | 6.0137 | 5.6556 | 5.328 | 5.0086 | 3.8188 | 3.4964 | 3.4352
|  | INSCH | CF |  |  |  |  | 0.79231 | 0.51782 | 7.4989 | 7.1581 | 6.8081 | 6.4377 | 6.0826 | 5.7826 | 5.4938 | 5.201 | 4.0612 | 2.9561 | 2.3724 | 2.5204 | 2.3255 | 9.0275 | 8.7877 | 8.5469 | 8.2765 | 8.0204 | 7.7979 | 7.5785 | 7.3581 | 6.4449 | 5.3438 | 4.3551 | 1.6752 | 1.4242 | 8.2443 | 7.9341 | 7.6117 | 7.2729 | 6.9484 | 6.6739 | 6.4056 | 6.1321 | 5.0892 | 4.0658 | 3.5433
| BURGHMUIR | INVERALMOND | MINIMUM HEADROOM | NO 08721 25807 | NO | YES | 9.592 | 8.4162 | 7.9683 | 7.3183 | 6.603 | 5.9172 | 5.2478 | 4.7152 | 4.1438 | 3.6621 | 3.2427 | 1.7774 | 0.82642 | 0.24989 | 8.456 | 8.0407 | 7.4081 | 6.7325 | 6.2519 | 5.9346 | 5.6876 | 5.2183 | 4.8254 | 4.4795 | 3.2458 | 2.5295 | 2.103 | 8.8591 | 8.4376 | 7.8091 | 7.1397 | 6.5672 | 5.9519 | 5.4489 | 4.9142 | 4.4611 | 4.0632 | 2.6407 | 1.7632 | 1.2448
|  | INVERALMOND | EE |  |  |  |  | 8.4519 | 7.9927 | 7.3621 | 6.603 | 5.9172 | 5.2478 | 4.7152 | 4.1438 | 3.6621 | 3.2427 | 1.9244 | 1.4111 | 1.0448 | 8.5274 | 8.1132 | 7.5723 | 6.9591 | 6.4662 | 6.0458 | 5.6876 | 5.2183 | 4.8254 | 4.4795 | 3.3581 | 2.9876 | 2.7438 | 8.9081 | 8.4825 | 7.9111 | 7.203 | 6.5672 | 5.9519 | 5.4489 | 4.9142 | 4.4611 | 4.0632 | 2.7876 | 2.3305 | 2.0172
|  | INVERALMOND | HT |  |  |  |  | 8.4162 | 7.9683 | 7.3183 | 6.6162 | 5.9948 | 5.4825 | 5.0785 | 4.6652 | 4.3009 | 3.9427 | 2.4805 | 1.5978 | 1.0642 | 8.456 | 8.0407 | 7.4081 | 6.7325 | 6.2519 | 5.9346 | 5.6897 | 5.4683 | 5.2836 | 5.004 | 3.7999 | 3.1346 | 2.7468 | 8.8591 | 8.4376 | 7.8091 | 7.1397 | 6.6315 | 6.1693 | 5.7897 | 5.4019 | 5.0591 | 4.7213 | 3.3172 | 2.507 | 2.0325
|  | INVERALMOND | HE |  |  |  |  | 8.4948 | 8.0468 | 7.4968 | 6.8234 | 6.1866 | 5.5968 | 5.1091 | 4.5846 | 4.1234 | 3.6611 | 1.7774 | 0.82642 | 0.24989 | 8.555 | 8.1478 | 7.6336 | 7.0407 | 6.556 | 6.1754 | 5.8642 | 5.5611 | 5.1836 | 4.807 | 3.2458 | 2.5295 | 2.103 | 8.9417 | 8.5244 | 7.9999 | 7.4019 | 6.8162 | 6.2764 | 5.8162 | 5.3264 | 4.8876 | 4.4489 | 2.6407 | 1.7632 | 1.2448
|  | INVERALMOND | CF |  |  |  |  | 8.755 | 8.4478 | 8.0632 | 7.6774 | 7.2866 | 6.8611 | 6.4785 | 6.0601 | 5.6764 | 5.2815 | 3.1632 | 1.3764 | 0.38969 | 8.855 | 8.5856 | 8.2448 | 7.9111 | 7.5805 | 7.2774 | 7.005 | 6.7315 | 6.4856 | 6.2356 | 4.5142 | 3.0387 | 2.2601 | 9.2019 | 8.9183 | 8.5581 | 8.2009 | 7.8397 | 7.4621 | 7.104 | 6.7132 | 6.3581 | 5.9887 | 3.9917 | 2.3091 | 1.3825
| CLACHAN | INVERARAY | MINIMUM HEADROOM | NN 09172 09746 | YES | YES | 0 | 1.902 | 1.8643 | 1.8388 | 1.7969 | 1.798 | 1.7582 | 1.5622 | 1.4367 | 1.3439 | 1.2571 | 1.1459 | 1.1265 | 1.1173 | 2.1372 | 2.1179 | 2.1199 | 2.1046 | 2.3582 | 2.3378 | 2.101 | 1.9541 | 1.8653 | 1.799 | 1.7214 | 1.702 | 1.6429 | 2.063 | 2.0395 | 2.0365 | 2.0161 | 2.1541 | 2.1337 | 1.9061 | 1.7673 | 1.6684 | 1.5908 | 1.4888 | 1.4684 | 1.4592
|  | INVERARAY | EE |  |  |  |  | 1.9092 | 1.8898 | 1.8643 | 1.8337 | 1.849 | 1.8041 | 1.7531 | 1.6143 | 1.5051 | 1.4051 | 1.1459 | 1.1357 | 1.1255 | 2.1495 | 2.1413 | 2.1301 | 2.1168 | 2.3724 | 2.3469 | 2.3194 | 2.1745 | 2.051 | 1.952 | 1.7214 | 1.702 | 1.6786 | 2.0773 | 2.0651 | 2.0518 | 2.0355 | 2.1816 | 2.1592 | 2.1327 | 1.9786 | 1.8531 | 1.7449 | 1.4888 | 1.4786 | 1.4684
|  | INVERARAY | HT |  |  |  |  | 1.902 | 1.8643 | 1.8388 | 1.7969 | 1.798 | 1.7582 | 1.5622 | 1.4367 | 1.3439 | 1.2571 | 1.1541 | 1.1265 | 1.1173 | 2.1372 | 2.1179 | 2.1199 | 2.1046 | 2.3582 | 2.3378 | 2.101 | 1.9541 | 1.8653 | 1.799 | 1.7357 | 1.7224 | 1.7143 | 2.063 | 2.0395 | 2.0365 | 2.0161 | 2.1541 | 2.1337 | 1.9061 | 1.7673 | 1.6684 | 1.5908 | 1.4939 | 1.4684 | 1.4592
|  | INVERARAY | HE |  |  |  |  | 1.9184 | 1.8888 | 1.8735 | 1.8459 | 1.8561 | 1.8184 | 1.7786 | 1.6367 | 1.5255 | 1.4173 | 1.1694 | 1.1582 | 1.1561 | 2.1444 | 2.1281 | 2.1342 | 2.1209 | 2.3786 | 2.3633 | 2.3418 | 2.1867 | 2.0622 | 1.9602 | 1.7316 | 1.7143 | 1.6929 | 2.0722 | 2.0528 | 2.0538 | 2.0395 | 2.1816 | 2.1633 | 2.1429 | 1.9898 | 1.8714 | 1.7612 | 1.5122 | 1.501 | 1.499
|  | INVERARAY | CF |  |  |  |  | 1.9357 | 1.9204 | 1.9051 | 1.898 | 1.9296 | 1.9133 | 1.8969 | 1.8694 | 1.8092 | 1.7378 | 1.3571 | 1.1806 | 1.1337 | 2.1556 | 2.1454 | 2.1485 | 2.1434 | 2.4092 | 2.4031 | 2.3929 | 2.3806 | 2.3204 | 2.2551 | 1.9224 | 1.7071 | 1.6429 | 2.0844 | 2.0742 | 2.0763 | 2.0702 | 2.2224 | 2.2143 | 2.2051 | 2.1878 | 2.1306 | 2.0673 | 1.7194 | 1.5235 | 1.4796
| LUNANHEAD | INVERARITY | MINIMUM HEADROOM | NO 44549 44200 | YES | YES | 0 | 0.18061 | 0.15204 | 0.12143 | 0.084694 | 0.028571 | -0.030612 | -0.1051 | -0.1949 | -0.26429 | -0.3398 | -0.60612 | -0.71327 | -0.76327 | 0.53061 | 0.50204 | 0.47143 | 0.43673 | 0.39592 | 0.35306 | 0.3 | 0.23673 | 0.18673 | 0.13367 | -0.067347 | -0.1449 | -0.17959 | 0.34796 | 0.31327 | 0.27041 | 0.22755 | 0.17959 | 0.12449 | 0.057143 | -0.020408 | -0.087755 | -0.15306 | -0.40816 | -0.50102 | -0.53776
|  | INVERARITY | EE |  |  |  |  | 0.18061 | 0.15204 | 0.12143 | 0.084694 | 0.028571 | -0.030612 | -0.1051 | -0.1949 | -0.26429 | -0.3398 | -0.60102 | -0.66429 | -0.67143 | 0.53061 | 0.50204 | 0.47143 | 0.43673 | 0.39592 | 0.35306 | 0.3 | 0.23673 | 0.18673 | 0.13367 | -0.054082 | -0.097959 | -0.10306 | 0.34796 | 0.31327 | 0.27041 | 0.22755 | 0.17959 | 0.12449 | 0.057143 | -0.020408 | -0.087755 | -0.15306 | -0.40612 | -0.47041 | -0.47653
|  | INVERARITY | HT |  |  |  |  | 0.18673 | 0.16224 | 0.1398 | 0.11122 | 0.078571 | 0.032653 | -0.026531 | -0.10306 | -0.17041 | -0.24388 | -0.56122 | -0.69286 | -0.73878 | 0.5398 | 0.51837 | 0.49694 | 0.46837 | 0.43571 | 0.40102 | 0.35816 | 0.30612 | 0.25714 | 0.2051 | -0.02551 | -0.11939 | -0.15204 | 0.35816 | 0.33163 | 0.30204 | 0.26531 | 0.22347 | 0.17959 | 0.12653 | 0.056122 | -0.0081633 | -0.072449 | -0.37041 | -0.49082 | -0.53265
|  | INVERARITY | HE |  |  |  |  | 0.18776 | 0.16837 | 0.14898 | 0.12653 | 0.089796 | 0.039796 | -0.021429 | -0.097959 | -0.16939 | -0.24694 | -0.60612 | -0.71327 | -0.76327 | 0.5398 | 0.51735 | 0.4949 | 0.46837 | 0.43673 | 0.4 | 0.35714 | 0.29898 | 0.24694 | 0.18878 | -0.067347 | -0.1449 | -0.17959 | 0.35816 | 0.33163 | 0.30408 | 0.26735 | 0.22755 | 0.18367 | 0.12653 | 0.055102 | -0.011224 | -0.082653 | -0.40816 | -0.50102 | -0.53776
|  | INVERARITY | CF |  |  |  |  | 0.19184 | 0.17857 | 0.16531 | 0.14898 | 0.13571 | 0.11735 | 0.090816 | 0.05102 | 0.0091837 | -0.038776 | -0.30816 | -0.55204 | -0.72755 | 0.54082 | 0.53367 | 0.52347 | 0.5051 | 0.48776 | 0.46633 | 0.44082 | 0.41122 | 0.37959 | 0.34388 | 0.1449 | -0.033673 | -0.15714 | 0.35918 | 0.35102 | 0.33673 | 0.31633 | 0.29286 | 0.26531 | 0.23469 | 0.19796 | 0.1602 | 0.11633 | -0.13163 | -0.36122 | -0.52653
| INVERNESS | INVERARNIE | MINIMUM HEADROOM | NH 68830 34971 | YES | NO | 0.605 | 1.2345 | 1.1528 | 1.0518 | 0.93651 | 0.80896 | 0.65794 | 0.48651 | 0.27325 | 0.07631 | -0.13491 | -1.0849 | -1.4574 | -1.5472 | 1.4243 | 1.362 | 1.2855 | 1.1947 | 1.0998 | 0.98549 | 0.85386 | 0.6906 | 0.53856 | 0.37937 | -0.34002 | -0.62573 | -0.70124 | 1.3263 | 1.2477 | 1.1528 | 1.0396 | 0.91815 | 0.77427 | 0.611 | 0.4059 | 0.21815 | 0.016106 | -0.89104 | -1.2482 | -1.3359
|  | INVERARNIE | EE |  |  |  |  | 1.2345 | 1.1569 | 1.0661 | 0.97325 | 0.86611 | 0.75794 | 0.63039 | 0.48856 | 0.36407 | 0.26611 | 0.053861 | 0.038555 | 0.035494 | 1.4243 | 1.3671 | 1.2988 | 1.2314 | 1.1539 | 1.0702 | 0.97835 | 0.87223 | 0.78141 | 0.71202 | 0.56304 | 0.55386 | 0.5508 | 1.3263 | 1.2528 | 1.1651 | 1.0753 | 0.97631 | 0.87121 | 0.7508 | 0.61509 | 0.49672 | 0.40488 | 0.20488 | 0.18958 | 0.18753
|  | INVERARNIE | HT |  |  |  |  | 1.2977 | 1.2753 | 1.2263 | 1.21 | 1.1528 | 1.0896 | 1.0171 | 0.93447 | 0.85692 | 0.77733 | 0.47835 | 0.38549 | 0.37937 | 1.4926 | 1.462 | 1.4253 | 1.4192 | 1.3784 | 1.3304 | 1.2814 | 1.2192 | 1.1651 | 1.1079 | 0.88958 | 0.82937 | 0.82631 | 1.411 | 1.3681 | 1.3192 | 1.3059 | 1.2518 | 1.1906 | 1.1212 | 1.0437 | 0.97019 | 0.8957 | 0.61202 | 0.52325 | 0.51917
|  | INVERARNIE | HE |  |  |  |  | 1.2508 | 1.1528 | 1.0518 | 0.93651 | 0.80896 | 0.65794 | 0.48651 | 0.27325 | 0.07631 | -0.13491 | -1.0849 | -1.4574 | -1.4614 | 1.4375 | 1.362 | 1.2855 | 1.1947 | 1.0998 | 0.98549 | 0.85386 | 0.6906 | 0.53856 | 0.37937 | -0.34002 | -0.62573 | -0.62879 | 1.3426 | 1.2477 | 1.1528 | 1.0396 | 0.91815 | 0.77427 | 0.611 | 0.4059 | 0.21815 | 0.016106 | -0.89104 | -1.2482 | -1.2523
|  | INVERARNIE | CF |  |  |  |  | 1.3018 | 1.2437 | 1.1692 | 1.0886 | 0.99876 | 0.90284 | 0.7957 | 0.64978 | 0.52733 | 0.3906 | -0.40328 | -1.0921 | -1.5472 | 1.4784 | 1.4314 | 1.3763 | 1.3151 | 1.2457 | 1.1743 | 1.0916 | 0.98141 | 0.88549 | 0.78243 | 0.17121 | -0.35634 | -0.70124 | 1.3937 | 1.3345 | 1.2651 | 1.1886 | 1.1008 | 1.01 | 0.90692 | 0.76917 | 0.64978 | 0.51917 | -0.24104 | -0.90022 | -1.3359
| FIDDES | INVERBERVIE | MINIMUM HEADROOM | NO 82850 72935 | NO | NO | 0.641 | 3.7751 | 3.4455 | 3.1506 | 2.8333 | 2.4925 | 2.2384 | 1.919 | 1.571 | 1.2149 | 0.79756 | -0.51877 | -1.0218 | -1.1239 | 4.6282 | 4.3884 | 4.1598 | 3.9149 | 3.6537 | 3.4935 | 3.3353 | 3.1006 | 2.871 | 2.6557 | 1.9547 | 1.6394 | 1.0843 | 4.2129 | 3.9353 | 3.6557 | 3.3588 | 3.0394 | 2.8139 | 2.5333 | 2.1996 | 1.869 | 1.5384 | 0.38429 | -0.04938 | -0.13407
|  | INVERBERVIE | EE |  |  |  |  | 3.7761 | 3.4598 | 3.1659 | 2.872 | 2.5363 | 2.2384 | 1.9425 | 1.5772 | 1.222 | 0.85572 | -0.51877 | -0.94224 | -1.0504 | 4.6282 | 4.4169 | 4.2047 | 3.9976 | 3.7506 | 3.5282 | 3.3445 | 3.1006 | 2.871 | 2.6557 | 1.9547 | 1.6394 | 1.2976 | 4.2129 | 3.9445 | 3.6751 | 3.4108 | 3.0996 | 2.818 | 2.5414 | 2.1996 | 1.869 | 1.5384 | 0.38429 | 0.028171 | -0.068767
|  | INVERBERVIE | HT |  |  |  |  | 3.7751 | 3.4455 | 3.1506 | 2.8333 | 2.4925 | 2.2465 | 1.919 | 1.571 | 1.2149 | 0.79756 | -0.48203 | -1.0218 | -1.1239 | 4.6323 | 4.3884 | 4.1598 | 3.9149 | 3.6537 | 3.4935 | 3.3353 | 3.1812 | 3.0169 | 2.82 | 2.1149 | 1.8496 | 1.8047 | 4.2394 | 3.9353 | 3.6557 | 3.3588 | 3.0394 | 2.8139 | 2.5333 | 2.2353 | 1.9414 | 1.5935 | 0.43327 | -0.04938 | -0.13407
|  | INVERBERVIE | HE |  |  |  |  | 3.8231 | 3.5588 | 3.3435 | 3.1006 | 2.8353 | 2.6384 | 2.4016 | 2.1292 | 1.8904 | 1.6047 | 0.21287 | -0.45652 | -0.63611 | 4.6823 | 4.47 | 4.2904 | 4.0884 | 3.869 | 3.7149 | 3.5608 | 3.4159 | 3.2823 | 3.1241 | 2.2874 | 1.8506 | 1.4884 | 4.2823 | 4.0455 | 3.8404 | 3.6139 | 3.3629 | 3.1761 | 2.9649 | 2.7323 | 2.522 | 2.2639 | 1.0139 | 0.4547 | 0.3047
|  | INVERBERVIE | CF |  |  |  |  | 3.9394 | 3.7588 | 3.5976 | 3.4588 | 3.2914 | 3.121 | 2.9945 | 2.8384 | 2.6823 | 2.5088 | 1.4343 | 0.30572 | -0.22183 | 4.769 | 4.6425 | 4.5139 | 4.4098 | 4.2741 | 4.1394 | 4.0333 | 3.9027 | 3.7731 | 3.6353 | 2.8547 | 1.9047 | 1.0843 | 4.3782 | 4.222 | 4.0669 | 3.9435 | 3.7925 | 3.6282 | 3.5159 | 3.3567 | 3.2016 | 3.0302 | 2.0537 | 1.0547 | 0.63123
| GRUDIE BRIDGE | INVERBROOM | MINIMUM HEADROOM | NH 17885 84667 | YES | NO | 0 | 0.14722 | 0.14314 | 0.14008 | 0.13294 | 0.12273 | 0.11253 | 0.10539 | 0.088041 | 0.072735 | 0.073755 | 0.050286 | 0.041102 | 0.038041 | 0.15576 | 0.15371 | 0.15269 | 0.14759 | 0.14147 | 0.13433 | 0.1282 | 0.11698 | 0.10678 | 0.10473 | 0.089429 | 0.080245 | 0.058816 | 0.14435 | 0.14129 | 0.13924 | 0.1321 | 0.1219 | 0.11271 | 0.10353 | 0.088224 | 0.071898 | 0.073939 | 0.05149 | 0.042306 | 0.040265
|  | INVERBROOM | EE |  |  |  |  | 0.14722 | 0.1462 | 0.14008 | 0.13294 | 0.12273 | 0.11253 | 0.10539 | 0.088041 | 0.072735 | 0.073755 | 0.050286 | 0.045184 | 0.044163 | 0.15576 | 0.15678 | 0.15269 | 0.14759 | 0.14147 | 0.13433 | 0.1282 | 0.11698 | 0.10678 | 0.10473 | 0.089429 | 0.082286 | 0.073102 | 0.14435 | 0.14435 | 0.13924 | 0.1321 | 0.1219 | 0.11271 | 0.10353 | 0.088224 | 0.071898 | 0.073939 | 0.05149 | 0.046388 | 0.045367
|  | INVERBROOM | HT |  |  |  |  | 0.15641 | 0.14314 | 0.14416 | 0.13804 | 0.13294 | 0.12886 | 0.11763 | 0.10641 | 0.10335 | 0.091102 | 0.055388 | 0.041102 | 0.038041 | 0.16086 | 0.15371 | 0.15576 | 0.15167 | 0.14963 | 0.14657 | 0.13841 | 0.13127 | 0.13024 | 0.12106 | 0.096571 | 0.088408 | 0.087388 | 0.15455 | 0.14129 | 0.14231 | 0.1372 | 0.1321 | 0.12802 | 0.11578 | 0.10659 | 0.10149 | 0.090265 | 0.057612 | 0.042306 | 0.040265
|  | INVERBROOM | HE |  |  |  |  | 0.15641 | 0.14416 | 0.14518 | 0.14212 | 0.13498 | 0.13294 | 0.12273 | 0.11355 | 0.11151 | 0.098245 | 0.06049 | 0.050286 | 0.048245 | 0.16086 | 0.15473 | 0.15678 | 0.15371 | 0.14963 | 0.14759 | 0.14147 | 0.13433 | 0.13433 | 0.1231 | 0.096571 | 0.086367 | 0.076163 | 0.15455 | 0.14231 | 0.14333 | 0.14027 | 0.13312 | 0.1321 | 0.1219 | 0.11271 | 0.11067 | 0.097408 | 0.062714 | 0.05251 | 0.049449
|  | INVERBROOM | CF |  |  |  |  | 0.15641 | 0.14722 | 0.14927 | 0.14518 | 0.13906 | 0.13498 | 0.13396 | 0.12273 | 0.11763 | 0.11151 | 0.076816 | 0.058449 | 0.049265 | 0.16086 | 0.15371 | 0.15984 | 0.15678 | 0.15269 | 0.14861 | 0.14963 | 0.14045 | 0.13739 | 0.13127 | 0.10167 | 0.080245 | 0.058816 | 0.15455 | 0.14639 | 0.14741 | 0.14333 | 0.1372 | 0.13312 | 0.1321 | 0.12088 | 0.1168 | 0.10965 | 0.07598 | 0.059653 | 0.049449
| FORT AUGUSTUS | INVERGARRY | MINIMUM HEADROOM | NH 29862 01000 | YES | YES | 0 | 0.6949 | 0.69184 | 0.68163 | 0.67143 | 0.65306 | 0.63061 | 0.62551 | 0.60204 | 0.57653 | 0.57143 | 0.53469 | 0.52143 | 0.51735 | 0.82755 | 0.82449 | 0.81939 | 0.81224 | 0.80204 | 0.78776 | 0.78163 | 0.76633 | 0.75 | 0.74694 | 0.71735 | 0.7051 | 0.6602 | 0.78061 | 0.76837 | 0.7602 | 0.75 | 0.73265 | 0.71122 | 0.70714 | 0.68367 | 0.65816 | 0.6551 | 0.62041 | 0.60816 | 0.6051
|  | INVERGARRY | EE |  |  |  |  | 0.7051 | 0.69184 | 0.68163 | 0.67143 | 0.65306 | 0.63061 | 0.62551 | 0.60204 | 0.57653 | 0.57143 | 0.53469 | 0.52755 | 0.52551 | 0.83367 | 0.82449 | 0.81939 | 0.81224 | 0.80204 | 0.78776 | 0.78163 | 0.76633 | 0.75 | 0.74694 | 0.71735 | 0.7051 | 0.68673 | 0.78265 | 0.76837 | 0.7602 | 0.75 | 0.73265 | 0.71122 | 0.70714 | 0.68367 | 0.65816 | 0.6551 | 0.62041 | 0.61327 | 0.61224
|  | INVERGARRY | HT |  |  |  |  | 0.70408 | 0.70204 | 0.69286 | 0.68469 | 0.67449 | 0.65816 | 0.65 | 0.62653 | 0.62245 | 0.60816 | 0.54694 | 0.52143 | 0.51735 | 0.83265 | 0.83469 | 0.82551 | 0.82347 | 0.81735 | 0.8051 | 0.79898 | 0.78673 | 0.78469 | 0.77347 | 0.73367 | 0.71837 | 0.71633 | 0.78265 | 0.78163 | 0.77041 | 0.76327 | 0.75306 | 0.73878 | 0.72959 | 0.70816 | 0.7051 | 0.6898 | 0.63061 | 0.60816 | 0.6051
|  | INVERGARRY | HE |  |  |  |  | 0.70408 | 0.70204 | 0.69592 | 0.69082 | 0.68061 | 0.66633 | 0.65918 | 0.63878 | 0.63776 | 0.62041 | 0.55306 | 0.53571 | 0.53163 | 0.83265 | 0.83469 | 0.82857 | 0.82449 | 0.81939 | 0.8102 | 0.80102 | 0.78878 | 0.78878 | 0.77653 | 0.72959 | 0.7102 | 0.6898 | 0.78265 | 0.78265 | 0.77347 | 0.76837 | 0.75816 | 0.7449 | 0.73776 | 0.71939 | 0.71837 | 0.70102 | 0.63673 | 0.62041 | 0.61633
|  | INVERGARRY | CF |  |  |  |  | 0.6949 | 0.70204 | 0.69592 | 0.69388 | 0.68571 | 0.67653 | 0.66735 | 0.66122 | 0.65 | 0.63469 | 0.58776 | 0.55306 | 0.53571 | 0.82755 | 0.83469 | 0.83061 | 0.82755 | 0.82245 | 0.81429 | 0.80816 | 0.80306 | 0.79184 | 0.78469 | 0.7449 | 0.7051 | 0.6602 | 0.78061 | 0.78265 | 0.77653 | 0.77143 | 0.76531 | 0.75612 | 0.74694 | 0.74082 | 0.72959 | 0.71633 | 0.67143 | 0.63776 | 0.62143
| ALNESS | INVERGORDON | MINIMUM HEADROOM | NH 70756 69177 | NO | NO | 3.452 | 5.6232 | 5.3079 | 4.9038 | 4.3967 | 3.914 | 3.115 | 2.2936 | 1.3885 | 0.41913 | -0.50536 | -2.7737 | -3.5503 | -3.7064 | 5.5906 | 5.3181 | 4.9548 | 4.5038 | 4.0783 | 3.6977 | 3.311 | 2.8028 | 2.262 | 1.713 | -0.3574 | -1.1115 | -1.239 | 5.6349 | 5.3502 | 4.9554 | 4.4819 | 4.0043 | 3.3472 | 2.636 | 1.8268 | 0.97066 | 0.15739 | -2.0375 | -2.713 | -2.8446
|  | INVERGORDON | EE |  |  |  |  | 5.6232 | 5.3079 | 4.9038 | 4.4099 | 3.914 | 3.4467 | 3.0069 | 2.0926 | 1.1069 | 0.19158 | -2.7737 | -3.5115 | -3.6788 | 5.5906 | 5.3181 | 4.9548 | 4.5038 | 4.0783 | 3.6977 | 3.3406 | 2.8048 | 2.262 | 1.7406 | -0.15944 | -0.40128 | -0.49618 | 5.6349 | 5.3502 | 4.9554 | 4.4819 | 4.0043 | 3.5574 | 3.137 | 2.3135 | 1.4329 | 0.61453 | -2.0375 | -2.6732 | -2.8314
|  | INVERGORDON | HT |  |  |  |  | 5.6957 | 5.3732 | 4.9385 | 4.3967 | 3.9161 | 3.115 | 2.2936 | 1.3885 | 0.41913 | -0.50536 | -2.6094 | -3.5503 | -3.7064 | 5.6752 | 5.413 | 5.0293 | 4.5395 | 4.1538 | 3.7344 | 3.311 | 2.8028 | 2.2712 | 1.713 | 0.14872 | -0.38393 | -0.48087 | 5.6849 | 5.4298 | 5.0166 | 4.5002 | 4.0513 | 3.3472 | 2.636 | 1.8268 | 0.97066 | 0.15739 | -1.8518 | -2.713 | -2.8446
|  | INVERGORDON | HE |  |  |  |  | 5.6844 | 5.4201 | 5.0671 | 4.6069 | 4.165 | 3.7477 | 3.3661 | 2.8028 | 2.2008 | 1.5946 | -1.7013 | -3.1615 | -3.4564 | 5.6559 | 5.4018 | 5.0783 | 4.6559 | 4.265 | 3.9028 | 3.5732 | 3.112 | 2.6222 | 2.113 | -0.3574 | -1.1115 | -1.239 | 5.6829 | 5.4747 | 5.1329 | 4.6717 | 4.2339 | 3.8247 | 3.4533 | 2.889 | 2.2666 | 1.6319 | -1.4569 | -2.5222 | -2.7446
|  | INVERGORDON | CF |  |  |  |  | 5.7344 | 5.5906 | 5.4048 | 5.1926 | 4.9304 | 4.6579 | 4.4191 | 4.1538 | 3.7732 | 3.3691 | 0.78443 | -1.5982 | -2.687 | 5.6997 | 5.5712 | 5.3916 | 5.1875 | 4.9579 | 4.7212 | 4.5089 | 4.2742 | 3.9701 | 3.6518 | 1.5916 | -0.24006 | -1.0441 | 5.687 | 5.6064 | 5.4482 | 5.2543 | 4.9951 | 4.7298 | 4.4951 | 4.2319 | 3.8737 | 3.5002 | 1.0145 | -1.2426 | -2.3202
| FORT WILLIAM | INVERLOCHY | MINIMUM HEADROOM | NN 11653 74987 | NO | NO | 7.861 | -1.4173 | -1.6418 | 12.6837 | 12.4266 | 12.1521 | 11.7756 | 11.1582 | 10.5297 | 9.9817 | 9.4123 | 8.1786 | 7.749 | 7.546 | 0.78374 | 0.65415 | 14.3266 | 14.1705 | 13.998 | 13.8368 | 13.5695 | 13.2113 | 12.8072 | 12.6317 | 11.7144 | 11.3092 | 10.0807 | 0.49241 | 0.322 | 14.3092 | 14.1031 | 13.8654 | 13.599 | 13.1225 | 12.5603 | 11.9062 | 11.5695 | 10.398 | 10.0031 | 9.7797
|  | INVERLOCHY | EE |  |  |  |  | -1.4173 | -1.6418 | 12.6837 | 12.4266 | 12.1521 | 11.8899 | 11.5195 | 10.7603 | 10.0266 | 9.6827 | 8.1786 | 7.898 | 7.7531 | 0.78374 | 0.65415 | 14.3266 | 14.1705 | 13.998 | 13.8368 | 13.6235 | 13.2113 | 12.8072 | 12.6603 | 11.7144 | 11.3092 | 10.7878 | 0.49241 | 0.322 | 14.3092 | 14.1031 | 13.8654 | 13.599 | 13.2358 | 12.5603 | 11.9062 | 11.699 | 10.398 | 10.146 | 9.996
|  | INVERLOCHY | HT |  |  |  |  | -1.3622 | -1.5581 | 12.795 | 12.5786 | 12.3725 | 11.7756 | 11.1582 | 10.5297 | 9.9817 | 9.4123 | 8.4031 | 7.749 | 7.546 | 0.83272 | 0.73068 | 14.4286 | 14.3062 | 14.197 | 13.8899 | 13.5695 | 13.2419 | 12.9409 | 12.6317 | 12.0439 | 11.6582 | 11.5195 | 0.54037 | 0.39956 | 14.4235 | 14.2521 | 14.0756 | 13.6582 | 13.1225 | 12.5858 | 12.0899 | 11.5695 | 10.6103 | 10.0031 | 9.8307
|  | INVERLOCHY | HE |  |  |  |  | -1.3632 | -1.5163 | 12.8837 | 12.7133 | 12.5531 | 12.3531 | 12.1154 | 11.6786 | 11.2184 | 10.7327 | 8.8174 | 8.1899 | 8.1215 | 0.82864 | 0.73884 | 14.4501 | 14.347 | 14.247 | 14.1174 | 13.9644 | 13.7154 | 13.445 | 13.1633 | 12.0501 | 11.4827 | 11.0246 | 0.53731 | 0.41078 | 14.4521 | 14.3011 | 14.1378 | 13.947 | 13.7154 | 13.3256 | 12.9297 | 12.5103 | 10.7154 | 10.1133 | 9.946
|  | INVERLOCHY | CF |  |  |  |  | -1.3152 | -1.4479 | 12.9695 | 12.8286 | 12.6746 | 12.5439 | 12.3878 | 12.2072 | 11.8531 | 11.5276 | 9.748 | 8.795 | 8.0103 | 0.85823 | 0.77966 | 14.5021 | 14.4184 | 14.3195 | 14.2348 | 14.1205 | 13.9868 | 13.7746 | 13.5756 | 12.3746 | 11.4205 | 10.0807 | 0.58833 | 0.5169 | 14.6072 | 14.5133 | 14.4072 | 14.3041 | 14.1705 | 13.9868 | 13.6797 | 13.4041 | 11.7562 | 10.7868 | 9.7797
| PORT ANN | INVERNEIL | MINIMUM HEADROOM | NR 84790 80580 | YES | YES | 0.018 | 2.33 | 2.3096 | 2.278 | 2.2545 | 2.2147 | 2.1719 | 2.1035 | 2.0402 | 2.0014 | 1.9514 | 1.8443 | 1.8106 | 1.8127 | 2.5759 | 2.5627 | 2.5402 | 2.527 | 2.5035 | 2.477 | 2.4361 | 2.3933 | 2.3688 | 2.3351 | 2.2535 | 2.2147 | 2.0933 | 2.479 | 2.4606 | 2.429 | 2.4116 | 2.38 | 2.3535 | 2.3045 | 2.2433 | 2.2065 | 2.1596 | 2.0545 | 2.0188 | 2.0188
|  | INVERNEIL | EE |  |  |  |  | 2.33 | 2.3096 | 2.278 | 2.2545 | 2.2147 | 2.1719 | 2.1035 | 2.0402 | 2.0014 | 1.9514 | 1.8443 | 1.83 | 1.8168 | 2.5759 | 2.5627 | 2.5402 | 2.527 | 2.5035 | 2.477 | 2.4361 | 2.3933 | 2.3688 | 2.3351 | 2.2535 | 2.2147 | 2.1535 | 2.479 | 2.4606 | 2.429 | 2.4116 | 2.38 | 2.3535 | 2.3045 | 2.2433 | 2.2065 | 2.1596 | 2.0545 | 2.0402 | 2.0259
|  | INVERNEIL | HT |  |  |  |  | 2.3433 | 2.329 | 2.3076 | 2.2892 | 2.2555 | 2.2208 | 2.1759 | 2.1331 | 2.0657 | 2.0127 | 1.8739 | 1.8106 | 1.8127 | 2.5872 | 2.579 | 2.5657 | 2.5525 | 2.5351 | 2.5198 | 2.4923 | 2.4647 | 2.427 | 2.3953 | 2.2963 | 2.2525 | 2.2545 | 2.4923 | 2.48 | 2.4586 | 2.4402 | 2.4157 | 2.3974 | 2.3678 | 2.331 | 2.2729 | 2.2229 | 2.0841 | 2.0188 | 2.0188
|  | INVERNEIL | HE |  |  |  |  | 2.3433 | 2.3321 | 2.3137 | 2.2994 | 2.277 | 2.2443 | 2.1923 | 2.1504 | 2.0963 | 2.0565 | 1.9096 | 1.8698 | 1.8657 | 2.5882 | 2.58 | 2.5688 | 2.5576 | 2.5423 | 2.5229 | 2.4933 | 2.4657 | 2.4351 | 2.4065 | 2.3035 | 2.2484 | 2.1963 | 2.4923 | 2.4821 | 2.4647 | 2.4504 | 2.427 | 2.4116 | 2.3821 | 2.3504 | 2.3014 | 2.2637 | 2.1239 | 2.0872 | 2.0831
|  | INVERNEIL | CF |  |  |  |  | 2.3494 | 2.3382 | 2.328 | 2.3157 | 2.3035 | 2.2739 | 2.2586 | 2.2208 | 2.1872 | 2.1596 | 2.031 | 1.9147 | 1.8627 | 2.5912 | 2.5831 | 2.5759 | 2.5657 | 2.5565 | 2.5402 | 2.527 | 2.5014 | 2.478 | 2.4586 | 2.3514 | 2.227 | 2.0933 | 2.4984 | 2.4892 | 2.478 | 2.4657 | 2.4576 | 2.4402 | 2.4331 | 2.4096 | 2.381 | 2.3555 | 2.23 | 2.1239 | 2.0759
| INVERNESS | INVERNESS | MINIMUM HEADROOM | NH 65302 42625 | NO | NO | 4.519 | 2.707 | 2.0642 | 1.3009 | 0.49071 | -0.4144 | -1.3981 | -2.0868 | -2.946 | -3.7695 | -4.3236 | -6.4093 | -7.446 | -7.6175 | 4.9438 | 4.6152 | 4.2121 | 3.8009 | 3.3346 | 2.8234 | 2.5805 | 2.104 | 1.6438 | 1.3223 | 0.17642 | -0.45215 | -1.6654 | 3.8545 | 3.3249 | 2.6739 | 1.9871 | 1.2096 | 0.35652 | -0.14552 | -0.90878 | -1.6547 | -2.1751 | -3.9629 | -4.8986 | -5.0414
|  | INVERNESS | EE |  |  |  |  | 2.707 | 2.0642 | 1.3009 | 0.49071 | -0.4144 | -1.3981 | -2.046 | -2.9083 | -3.7542 | -4.3236 | -6.3511 | -7.1001 | -7.2868 | 4.9438 | 4.6152 | 4.2121 | 3.8009 | 3.3346 | 2.8234 | 2.5805 | 2.104 | 1.6438 | 1.3223 | 0.17642 | -0.45215 | -1.1736 | 3.8545 | 3.3249 | 2.6739 | 1.9871 | 1.2096 | 0.35652 | -0.14552 | -0.90878 | -1.6547 | -2.1751 | -3.9537 | -4.5874 | -4.7557
|  | INVERNESS | HT |  |  |  |  | 2.7876 | 2.1519 | 1.4172 | 0.6305 | -0.23684 | -1.1736 | -2.0868 | -2.946 | -3.7695 | -4.0246 | -6.4093 | -7.446 | -7.6175 | 5.0285 | 4.7264 | 4.3683 | 4.0101 | 3.5989 | 3.1672 | 2.7213 | 2.2774 | 1.854 | 1.8162 | 0.52744 | -0.012355 | -0.10113 | 3.9524 | 3.4331 | 2.8198 | 2.178 | 1.4484 | 0.66775 | -0.11695 | -0.86899 | -1.5904 | -1.7976 | -3.9629 | -4.8986 | -5.0414
|  | INVERNESS | HE |  |  |  |  | 2.8009 | 2.305 | 1.7081 | 1.0581 | 0.33152 | -0.43787 | -1.1613 | -1.8532 | -2.5348 | -2.644 | -4.6715 | -5.9175 | -6.3317 | 5.0264 | 4.7652 | 4.4509 | 4.1315 | 3.7642 | 3.3897 | 3.0019 | 2.606 | 2.2223 | 2.2234 | 0.91418 | 0.053971 | -0.71031 | 3.9616 | 3.5586 | 3.0596 | 2.531 | 1.9208 | 1.2769 | 0.65652 | 0.048359 | -0.55266 | -0.61184 | -2.4925 | -3.5578 | -3.9149
|  | INVERNESS | CF |  |  |  |  | 2.9846 | 2.6866 | 2.1989 | 1.6713 | 1.0785 | 0.41622 | -0.080722 | -0.5297 | -0.99195 | -1.2532 | -2.3236 | -4.0389 | -5.5848 | 5.1254 | 4.9468 | 4.6795 | 4.4081 | 4.0958 | 3.7448 | 3.4642 | 3.1703 | 2.8774 | 2.6723 | 1.8111 | 0.25295 | -1.6654 | 4.1177 | 3.8596 | 3.4677 | 3.0453 | 2.5565 | 2.0116 | 1.6004 | 1.2055 | 0.8055 | 0.55244 | -0.44348 | -2.0118 | -3.3231
| KINTORE | INVERURIE | MINIMUM HEADROOM | NJ 75665 21688 | NO | YES | 2.313 | 12.4778 | 11.188 | 9.6288 | 7.8635 | 6.1145 | 3.6574 | 1.4553 | -0.85487 | -3.2732 | -5.462 | -15.1212 | -20.2845 | -22.8589 | 16.9115 | 15.9227 | 14.7717 | 13.5278 | 12.1227 | 10.2911 | 8.4686 | 6.4257 | 4.29 | 1.7737 | -6.9855 | -11.6426 | -14.4906 | 14.4584 | 13.2972 | 11.9186 | 10.3574 | 8.7574 | 6.3043 | 4.4411 | 2.3411 | 0.076767 | -2.0355 | -12.1875 | -17.6794 | -20.6936
|  | INVERURIE | EE |  |  |  |  | 12.4778 | 11.188 | 9.6288 | 7.8635 | 6.1145 | 3.8115 | 1.4553 | -0.85487 | -3.2732 | -5.462 | -11.8467 | -16.1651 | -17.5385 | 16.9115 | 15.9227 | 14.7717 | 13.5278 | 12.1227 | 10.3298 | 8.4686 | 6.536 | 4.4462 | 2.4717 | -2.9192 | -5.9283 | -7.0896 | 14.4584 | 13.2972 | 11.9186 | 10.3574 | 8.7574 | 6.6033 | 4.4411 | 2.3411 | 0.076767 | -1.9783 | -8.211 | -12.6069 | -14.0926
|  | INVERURIE | HT |  |  |  |  | 12.7747 | 11.5747 | 9.9125 | 8.0655 | 6.2727 | 3.6574 | 1.8125 | -0.56915 | -2.9834 | -5.4436 | -11.5753 | -16.6498 | -19.012 | 17.1462 | 16.3808 | 15.2543 | 13.9941 | 12.9257 | 10.888 | 9.4196 | 7.5166 | 5.5788 | 3.3849 | -1.7375 | -6.06 | -8.6538 | 14.7298 | 13.6604 | 12.1441 | 10.4288 | 8.8533 | 6.3043 | 4.6145 | 2.4349 | 0.24718 | -2.0355 | -7.9181 | -13.2538 | -16.013
|  | INVERURIE | HE |  |  |  |  | 12.738 | 11.736 | 10.3094 | 8.6666 | 6.939 | 4.589 | 2.8278 | 0.47371 | -2.0447 | -4.8681 | -15.1212 | -20.2845 | -22.8589 | 17.1023 | 16.3043 | 15.1176 | 13.7339 | 12.3839 | 10.2911 | 8.5268 | 6.4257 | 4.29 | 1.7737 | -6.9855 | -11.6426 | -14.4906 | 14.6951 | 13.7962 | 12.4931 | 10.9686 | 9.4125 | 7.1227 | 5.4798 | 3.2615 | 0.81962 | -1.9743 | -12.1875 | -17.6794 | -20.6936
|  | INVERURIE | CF |  |  |  |  | 12.9788 | 12.2002 | 11.2717 | 10.1686 | 8.8972 | 7.5911 | 6.4513 | 5.4482 | 4.3176 | 3.2104 | -4.2906 | -10.5579 | -13.4885 | 17.2523 | 16.6686 | 16.0043 | 15.2104 | 14.2074 | 13.2115 | 12.238 | 11.1411 | 10.0186 | 8.7615 | 2.3727 | -2.7855 | -4.9824 | 14.9176 | 14.2298 | 13.4206 | 12.4635 | 11.3186 | 10.1186 | 9.0921 | 8.189 | 7.1604 | 5.9043 | -1.1947 | -7.2692 | -10.113
| BROADFORD | KALNAKIL | MINIMUM HEADROOM | NG 69146 53941 | YES | YES | 0.06 | 0.56837 | 0.55102 | 0.53469 | 0.51429 | 0.49592 | 0.46939 | 0.4398 | 0.42347 | 0.39388 | 0.36837 | 0.31939 | 0.29898 | 0.29592 | 0.67653 | 0.67245 | 0.6602 | 0.64796 | 0.63367 | 0.61633 | 0.59592 | 0.58673 | 0.56735 | 0.55 | 0.51531 | 0.50306 | 0.4551 | 0.63878 | 0.62449 | 0.60714 | 0.58776 | 0.57143 | 0.54694 | 0.51735 | 0.50102 | 0.47245 | 0.44796 | 0.40204 | 0.38265 | 0.37857
|  | KALNAKIL | EE |  |  |  |  | 0.56837 | 0.55102 | 0.53469 | 0.51429 | 0.49592 | 0.46939 | 0.4398 | 0.42347 | 0.39388 | 0.36837 | 0.31939 | 0.3102 | 0.30408 | 0.68265 | 0.67245 | 0.6602 | 0.64796 | 0.63367 | 0.61633 | 0.59592 | 0.58673 | 0.56735 | 0.55 | 0.51531 | 0.50306 | 0.47857 | 0.6398 | 0.62449 | 0.60714 | 0.58776 | 0.57143 | 0.54694 | 0.51735 | 0.50102 | 0.47245 | 0.44796 | 0.40204 | 0.3949 | 0.38673
|  | KALNAKIL | HT |  |  |  |  | 0.56939 | 0.55918 | 0.5449 | 0.52959 | 0.51735 | 0.49898 | 0.48265 | 0.4602 | 0.43469 | 0.42653 | 0.33776 | 0.29898 | 0.29592 | 0.67755 | 0.67857 | 0.66837 | 0.66122 | 0.65408 | 0.64286 | 0.63163 | 0.61531 | 0.6 | 0.59592 | 0.53776 | 0.51224 | 0.5102 | 0.63878 | 0.63265 | 0.61837 | 0.6051 | 0.59286 | 0.57653 | 0.55918 | 0.53571 | 0.51429 | 0.5051 | 0.42143 | 0.38265 | 0.37857
|  | KALNAKIL | HE |  |  |  |  | 0.57041 | 0.56122 | 0.55102 | 0.5398 | 0.52959 | 0.51429 | 0.50306 | 0.47857 | 0.45816 | 0.45306 | 0.35816 | 0.33061 | 0.32755 | 0.67653 | 0.67857 | 0.67143 | 0.66531 | 0.65714 | 0.64592 | 0.63878 | 0.62347 | 0.6102 | 0.60714 | 0.54286 | 0.51939 | 0.49898 | 0.63878 | 0.63469 | 0.62347 | 0.61327 | 0.60306 | 0.5898 | 0.57857 | 0.5551 | 0.53571 | 0.53061 | 0.44082 | 0.41531 | 0.41224
|  | KALNAKIL | CF |  |  |  |  | 0.56939 | 0.56837 | 0.55408 | 0.54694 | 0.54082 | 0.52551 | 0.51429 | 0.50612 | 0.4898 | 0.47551 | 0.41224 | 0.35714 | 0.32449 | 0.67857 | 0.68469 | 0.67653 | 0.67041 | 0.66429 | 0.6551 | 0.64694 | 0.6398 | 0.62959 | 0.61939 | 0.57041 | 0.51327 | 0.4551 | 0.63878 | 0.64082 | 0.62857 | 0.62041 | 0.61327 | 0.59898 | 0.5898 | 0.57959 | 0.56531 | 0.55 | 0.49082 | 0.44082 | 0.4102
| DUNOON | KAMES | MINIMUM HEADROOM | NR 96305 71237 | YES | YES | 0.053 | 2.3525 | 2.3138 | 2.276 | 2.2229 | 2.177 | 2.1005 | 2.0056 | 1.9444 | 1.8658 | 1.8046 | 1.6372 | 1.5821 | 1.5709 | 2.4153 | 2.3888 | 2.3622 | 2.3255 | 2.2959 | 2.2469 | 2.1857 | 2.149 | 2.0949 | 2.053 | 1.9316 | 1.8908 | 1.7949 | 2.3961 | 2.3594 | 2.3237 | 2.2706 | 2.2257 | 2.1553 | 2.0655 | 2.0053 | 1.9308 | 1.8727 | 1.7135 | 1.6615 | 1.6533
|  | KAMES | EE |  |  |  |  | 2.3525 | 2.3138 | 2.276 | 2.2229 | 2.177 | 2.1005 | 2.0056 | 1.9444 | 1.8658 | 1.8046 | 1.6372 | 1.6117 | 1.5913 | 2.4153 | 2.3888 | 2.3622 | 2.3255 | 2.2959 | 2.2469 | 2.1857 | 2.149 | 2.0949 | 2.053 | 1.9316 | 1.8908 | 1.8224 | 2.3961 | 2.3594 | 2.3237 | 2.2706 | 2.2257 | 2.1553 | 2.0655 | 2.0053 | 1.9308 | 1.8727 | 1.7135 | 1.6921 | 1.6706
|  | KAMES | HT |  |  |  |  | 2.3729 | 2.3413 | 2.3097 | 2.2627 | 2.228 | 2.1658 | 2.1066 | 2.0321 | 1.9668 | 1.9219 | 1.6852 | 1.5821 | 1.5709 | 2.4326 | 2.4122 | 2.3939 | 2.3622 | 2.3428 | 2.3061 | 2.2724 | 2.2234 | 2.1816 | 2.1571 | 1.9918 | 1.9204 | 1.9163 | 2.4155 | 2.3849 | 2.3553 | 2.3115 | 2.2778 | 2.2176 | 2.1666 | 2.0951 | 2.0308 | 1.989 | 1.7615 | 1.6615 | 1.6533
|  | KAMES | HE |  |  |  |  | 2.3729 | 2.3464 | 2.324 | 2.2882 | 2.2607 | 2.2046 | 2.1393 | 2.0791 | 2.028 | 1.9719 | 1.7566 | 1.6944 | 1.6913 | 2.4326 | 2.4153 | 2.3979 | 2.3724 | 2.3551 | 2.3204 | 2.2847 | 2.2449 | 2.2092 | 2.1683 | 2.0194 | 1.9551 | 1.899 | 2.4155 | 2.391 | 2.3676 | 2.3339 | 2.3074 | 2.2553 | 2.1961 | 2.139 | 2.089 | 2.0359 | 1.8329 | 1.7727 | 1.7686
|  | KAMES | CF |  |  |  |  | 2.377 | 2.3576 | 2.3321 | 2.3148 | 2.2882 | 2.2648 | 2.227 | 2.1719 | 2.1403 | 2.0974 | 1.9229 | 1.774 | 1.6913 | 2.4347 | 2.4224 | 2.4051 | 2.3928 | 2.3724 | 2.3581 | 2.3326 | 2.2949 | 2.2755 | 2.2439 | 2.1051 | 1.9479 | 1.7949 | 2.4206 | 2.4043 | 2.3819 | 2.3645 | 2.337 | 2.3135 | 2.2788 | 2.2278 | 2.1992 | 2.1574 | 1.9859 | 1.8451 | 1.7696
| KEITH 2 | KEITH | MINIMUM HEADROOM | NJ 43925 50405 | NO | YES | 2.361 | 6.0371 | 5.7677 | 5.484 | 5.135 | 4.7779 | 4.4126 | 3.8779 | 3.3238 | 3.0585 | 2.5881 | 0.81461 | -0.28233 | -0.4762 | 5.5932 | 5.4279 | 5.2646 | 5.036 | 4.8177 | 4.6024 | 4.3207 | 4.0085 | 3.9156 | 3.6799 | 2.7218 | 2.1034 | 1.636 | 6.2386 | 6.008 | 5.7702 | 5.4672 | 5.16 | 4.858 | 4.4386 | 3.9661 | 3.709 | 3.3376 | 1.7814 | 0.80594 | 0.63655
|  | KEITH | EE |  |  |  |  | 6.0371 | 5.7677 | 5.484 | 5.135 | 4.7779 | 4.4126 | 3.8779 | 3.3238 | 3.1269 | 2.683 | 0.86461 | -0.19049 | -0.40171 | 5.5932 | 5.4279 | 5.2646 | 5.036 | 4.8177 | 4.6024 | 4.3207 | 4.0085 | 3.9156 | 3.6799 | 2.7218 | 2.1034 | 1.636 | 6.2386 | 6.008 | 5.7702 | 5.4672 | 5.16 | 4.858 | 4.4386 | 3.9661 | 3.709 | 3.3376 | 1.8131 | 0.89165 | 0.70186
|  | KEITH | HT |  |  |  |  | 6.0922 | 5.8289 | 5.5595 | 5.2044 | 4.8452 | 4.5136 | 3.9901 | 3.5289 | 3.0585 | 2.5881 | 0.81461 | -0.28233 | -0.4762 | 5.632 | 5.4697 | 5.3187 | 5.086 | 4.8738 | 4.6911 | 4.4034 | 4.1667 | 3.9309 | 3.6993 | 2.9136 | 2.4442 | 2.3524 | 6.2845 | 6.0559 | 5.8294 | 5.5141 | 5.2161 | 4.9355 | 4.5019 | 4.1049 | 3.7202 | 3.3406 | 1.7814 | 0.80594 | 0.63655
|  | KEITH | HE |  |  |  |  | 6.1013 | 5.9228 | 5.7411 | 5.5034 | 5.2432 | 4.984 | 4.5962 | 4.2646 | 3.9095 | 3.5544 | 2.0197 | 0.92992 | 0.49829 | 5.634 | 5.5075 | 5.3922 | 5.2156 | 5.0432 | 4.8748 | 4.6616 | 4.4391 | 4.2116 | 3.985 | 3.1095 | 2.5218 | 1.9687 | 6.2866 | 6.1192 | 5.96 | 5.7355 | 5.5049 | 5.2723 | 4.9498 | 4.6243 | 4.3059 | 3.9866 | 2.5335 | 1.659 | 1.2876
|  | KEITH | CF |  |  |  |  | 6.1452 | 6.0462 | 5.9207 | 5.7922 | 5.6156 | 5.4881 | 5.3218 | 5.1177 | 4.9769 | 4.7881 | 3.5054 | 2.532 | 1.5636 | 5.6544 | 5.584 | 5.5013 | 5.4095 | 5.284 | 5.186 | 5.0656 | 4.9258 | 4.8136 | 4.6758 | 3.7616 | 2.8646 | 1.6524 | 6.3304 | 6.2437 | 6.1406 | 6.0263 | 5.8774 | 5.759 | 5.6141 | 5.4427 | 5.2978 | 5.1243 | 3.9866 | 2.9753 | 2.108
| KINTORE | KEMNAY | MINIMUM HEADROOM | NJ 73180 16804 | NO | YES | 0.276 | 10.6907 | 10.5326 | 10.3356 | 10.1346 | 9.9366 | 9.6499 | 9.2264 | 8.7438 | 8.2621 | 7.6989 | 6.3224 | 5.6948 | 5.5724 | 11.4377 | 11.3519 | 11.2356 | 11.1275 | 10.9999 | 10.7979 | 10.5407 | 10.2305 | 9.903 | 9.5591 | 8.6295 | 8.2499 | 7.8438 | 11.1035 | 10.9565 | 10.7739 | 10.5912 | 10.3912 | 10.1188 | 9.7525 | 9.3249 | 8.8882 | 8.3718 | 7.0769 | 6.5178 | 6.4157
|  | KEMNAY | EE |  |  |  |  | 10.6907 | 10.5326 | 10.3417 | 10.1417 | 9.9366 | 9.6519 | 9.257 | 8.8101 | 8.3468 | 7.8632 | 6.3907 | 5.7652 | 5.6336 | 11.4377 | 11.3519 | 11.2356 | 11.1275 | 10.9999 | 10.7979 | 10.5407 | 10.2305 | 9.903 | 9.5591 | 8.6295 | 8.2499 | 7.9081 | 11.1035 | 10.9565 | 10.7739 | 10.5912 | 10.3912 | 10.1188 | 9.7525 | 9.3249 | 8.8882 | 8.4341 | 7.1147 | 6.5871 | 6.4678
|  | KEMNAY | HT |  |  |  |  | 10.7254 | 10.5519 | 10.3356 | 10.1346 | 9.954 | 9.6499 | 9.2264 | 8.7438 | 8.2621 | 7.6989 | 6.3224 | 5.6948 | 5.5724 | 11.4805 | 11.3958 | 11.2887 | 11.1866 | 11.0907 | 10.8846 | 10.6132 | 10.2887 | 9.9642 | 9.5601 | 8.7785 | 8.4907 | 8.4336 | 11.1474 | 10.9922 | 10.8055 | 10.6208 | 10.4504 | 10.1708 | 9.781 | 9.331 | 8.8963 | 8.3718 | 7.0769 | 6.5178 | 6.4157
|  | KEMNAY | HE |  |  |  |  | 10.7305 | 10.6336 | 10.5111 | 10.3662 | 10.2387 | 10.053 | 9.7407 | 9.404 | 9.0805 | 8.6815 | 7.1499 | 6.4336 | 6.1377 | 11.4785 | 11.4183 | 11.3448 | 11.2581 | 11.1724 | 11.0366 | 10.8101 | 10.5611 | 10.3183 | 10.0121 | 8.956 | 8.5101 | 8.1193 | 11.1514 | 11.0606 | 10.9484 | 10.8137 | 10.6902 | 10.5198 | 10.2259 | 9.9045 | 9.6055 | 9.231 | 7.7984 | 7.178 | 6.9341
|  | KEMNAY | CF |  |  |  |  | 10.7632 | 10.7152 | 10.6499 | 10.5795 | 10.4968 | 10.3815 | 10.255 | 10.0805 | 9.9172 | 9.7224 | 8.6152 | 7.4866 | 6.8366 | 11.4948 | 11.4591 | 11.406 | 11.3591 | 11.2989 | 11.205 | 11.107 | 10.955 | 10.8091 | 10.6346 | 9.7019 | 8.6805 | 7.8438 | 11.1831 | 11.1361 | 11.0657 | 11.0014 | 10.9218 | 10.8076 | 10.6912 | 10.5218 | 10.3606 | 10.1718 | 9.1157 | 8.0616 | 7.5045
| TAYNUILT | KENMORE | MINIMUM HEADROOM | NN 00325 34042 | YES | YES | 0 | 0.79694 | 0.79082 | 0.79286 | 0.78061 | 0.77551 | 0.76429 | 0.75918 | 0.7449 | 0.73163 | 0.72041 | 0.69796 | 0.68776 | 0.68061 | 0.86735 | 0.86122 | 0.86531 | 0.85816 | 0.85408 | 0.84796 | 0.84388 | 0.83571 | 0.82551 | 0.81327 | 0.80408 | 0.80204 | 0.77857 | 0.84184 | 0.83878 | 0.83776 | 0.82551 | 0.82143 | 0.81327 | 0.80612 | 0.79082 | 0.77857 | 0.76735 | 0.75 | 0.74082 | 0.73367
|  | KENMORE | EE |  |  |  |  | 0.79694 | 0.79694 | 0.79286 | 0.78061 | 0.77551 | 0.76429 | 0.75918 | 0.7449 | 0.73163 | 0.72041 | 0.70612 | 0.70408 | 0.70408 | 0.86735 | 0.86939 | 0.86531 | 0.85816 | 0.85408 | 0.84796 | 0.84388 | 0.83571 | 0.82551 | 0.81327 | 0.80714 | 0.80306 | 0.7898 | 0.84184 | 0.84184 | 0.83776 | 0.82551 | 0.82143 | 0.81327 | 0.80612 | 0.79082 | 0.77857 | 0.76735 | 0.75714 | 0.7551 | 0.7551
|  | KENMORE | HT |  |  |  |  | 0.80408 | 0.79184 | 0.79796 | 0.79184 | 0.78878 | 0.77653 | 0.77347 | 0.76429 | 0.75408 | 0.74694 | 0.71122 | 0.69694 | 0.69184 | 0.87041 | 0.86122 | 0.86939 | 0.86735 | 0.86327 | 0.85714 | 0.8551 | 0.84898 | 0.84184 | 0.83776 | 0.81531 | 0.80714 | 0.80612 | 0.85 | 0.83878 | 0.84388 | 0.83776 | 0.83469 | 0.82347 | 0.82041 | 0.81224 | 0.80102 | 0.79388 | 0.76327 | 0.74796 | 0.74286
|  | KENMORE | HE |  |  |  |  | 0.80306 | 0.79082 | 0.80102 | 0.7949 | 0.7898 | 0.78367 | 0.77755 | 0.76735 | 0.75612 | 0.74898 | 0.69796 | 0.68776 | 0.68061 | 0.86939 | 0.86122 | 0.87041 | 0.86837 | 0.86327 | 0.8602 | 0.85612 | 0.85204 | 0.84388 | 0.84082 | 0.80408 | 0.80612 | 0.79082 | 0.84898 | 0.83878 | 0.8449 | 0.84082 | 0.83469 | 0.82857 | 0.82449 | 0.81531 | 0.8051 | 0.79694 | 0.75 | 0.74082 | 0.73367
|  | KENMORE | CF |  |  |  |  | 0.80408 | 0.7949 | 0.79286 | 0.79592 | 0.79286 | 0.79082 | 0.78265 | 0.78061 | 0.77449 | 0.76837 | 0.73776 | 0.70918 | 0.6898 | 0.87041 | 0.86122 | 0.86633 | 0.86837 | 0.86633 | 0.86633 | 0.8602 | 0.8551 | 0.85204 | 0.84796 | 0.82653 | 0.80204 | 0.77857 | 0.84898 | 0.8398 | 0.83776 | 0.84184 | 0.83878 | 0.83776 | 0.82857 | 0.82653 | 0.82041 | 0.81531 | 0.78673 | 0.76122 | 0.74388
| STRATHLEVEN | KEPCULLOCH | MINIMUM HEADROOM | NS 53864 91598 | NO | YES | 1.283 | 1.8203 | 1.7009 | 1.555 | 1.3856 | 9.4898 | 9.3061 | 9.0653 | 8.8367 | 8.5796 | 8.3489 | 7.5183 | 6.9316 | 6.7 | 2.8177 | 2.7483 | 2.6534 | 2.5443 | 10.2785 | 10.1551 | 10.003 | 9.8734 | 9.7092 | 9.5683 | 9.1204 | 8.8367 | 8.4714 | 2.1965 | 2.0925 | 1.9649 | 1.8221 | 9.734 | 9.581 | 9.3708 | 9.1708 | 8.9483 | 8.7483 | 8.0187 | 7.5269 | 7.3565
|  | KEPCULLOCH | EE |  |  |  |  | 1.8203 | 1.7009 | 1.555 | 1.3856 | 9.4898 | 9.3061 | 9.0653 | 8.8367 | 8.5796 | 8.3489 | 7.552 | 7.0806 | 6.8592 | 2.8177 | 2.7483 | 2.6534 | 2.5443 | 10.2785 | 10.1551 | 10.003 | 9.8734 | 9.7092 | 9.5683 | 9.1204 | 8.8367 | 8.5459 | 2.1965 | 2.0925 | 1.9649 | 1.8221 | 9.734 | 9.581 | 9.3708 | 9.1708 | 8.9483 | 8.7483 | 8.0381 | 7.6392 | 7.4749
|  | KEPCULLOCH | HT |  |  |  |  | 1.857 | 1.7386 | 1.609 | 1.4764 | 9.5714 | 9.4102 | 9.2245 | 8.9898 | 8.7632 | 8.5275 | 7.5183 | 6.9316 | 6.7 | 2.8555 | 2.7932 | 2.7208 | 2.6514 | 10.3877 | 10.2847 | 10.1918 | 10.0561 | 9.9234 | 9.7847 | 9.2092 | 8.9194 | 8.801 | 2.2282 | 2.1231 | 2.0108 | 1.8976 | 9.8045 | 9.6667 | 9.4994 | 9.2943 | 9.0973 | 8.8881 | 8.0187 | 7.5269 | 7.3565
|  | KEPCULLOCH | HE |  |  |  |  | 1.858 | 1.7774 | 1.6917 | 1.5999 | 9.7377 | 9.6143 | 9.4847 | 9.302 | 9.1224 | 8.9367 | 7.9938 | 7.4469 | 7.1602 | 2.8514 | 2.8034 | 2.7422 | 2.6871 | 10.4347 | 10.3489 | 10.2734 | 10.1561 | 10.0367 | 9.9132 | 9.3255 | 8.9755 | 8.6734 | 2.2292 | 2.1608 | 2.0843 | 2.0088 | 9.9575 | 9.8575 | 9.7371 | 9.583 | 9.43 | 9.2738 | 8.4524 | 7.9738 | 7.7443
|  | KEPCULLOCH | CF |  |  |  |  | 1.8795 | 1.8244 | 1.759 | 1.6723 | 9.852 | 9.7673 | 9.6683 | 9.5479 | 9.4826 | 9.3694 | 8.751 | 8.0612 | 7.5683 | 2.8657 | 2.83 | 2.781 | 2.7177 | 10.4949 | 10.4296 | 10.3571 | 10.2663 | 10.2173 | 10.1316 | 9.6551 | 9.052 | 8.4714 | 2.2486 | 2.2017 | 2.1465 | 2.0751 | 10.0585 | 9.9922 | 9.9116 | 9.8177 | 9.7585 | 9.6708 | 9.131 | 8.4994 | 8.1014
| TAYNUILT | KERRERA | MINIMUM HEADROOM | NM 82340 27997 | YES | YES | 0 | 0.27543 | 0.2642 | 0.2591 | 0.24788 | 0.25502 | 0.2438 | 0.24482 | 0.23563 | 0.22951 | 0.22237 | 0.19788 | 0.18563 | 0.17849 | 0.27496 | 0.2668 | 0.26373 | 0.25353 | 0.26067 | 0.25047 | 0.25353 | 0.25047 | 0.24537 | 0.24129 | 0.2219 | 0.21373 | 0.20863 | 0.27826 | 0.26703 | 0.26295 | 0.25172 | 0.25887 | 0.24866 | 0.24968 | 0.2405 | 0.23438 | 0.22826 | 0.20479 | 0.19254 | 0.1854
|  | KERRERA | EE |  |  |  |  | 0.27543 | 0.2642 | 0.2591 | 0.24788 | 0.25604 | 0.25196 | 0.24482 | 0.23563 | 0.22951 | 0.22237 | 0.20298 | 0.20196 | 0.20094 | 0.27496 | 0.2668 | 0.26373 | 0.25353 | 0.26169 | 0.26373 | 0.25863 | 0.25047 | 0.24537 | 0.24129 | 0.227 | 0.227 | 0.227 | 0.27826 | 0.26703 | 0.26295 | 0.25172 | 0.25887 | 0.25785 | 0.24968 | 0.2405 | 0.23438 | 0.22826 | 0.20989 | 0.20785 | 0.20683
|  | KERRERA | HT |  |  |  |  | 0.28461 | 0.27441 | 0.27033 | 0.26012 | 0.25502 | 0.2438 | 0.25196 | 0.24788 | 0.24176 | 0.23461 | 0.2091 | 0.19482 | 0.18971 | 0.28312 | 0.27394 | 0.27496 | 0.26578 | 0.26169 | 0.25251 | 0.25965 | 0.26169 | 0.25557 | 0.25047 | 0.23006 | 0.22292 | 0.21884 | 0.28744 | 0.27723 | 0.27519 | 0.26499 | 0.26091 | 0.24968 | 0.25581 | 0.25274 | 0.24662 | 0.2405 | 0.21499 | 0.20274 | 0.19764
|  | KERRERA | HE |  |  |  |  | 0.28461 | 0.27339 | 0.27033 | 0.26012 | 0.25502 | 0.2438 | 0.25094 | 0.24686 | 0.23869 | 0.23155 | 0.19788 | 0.18563 | 0.17849 | 0.28312 | 0.27496 | 0.27394 | 0.26476 | 0.26067 | 0.25047 | 0.26169 | 0.25965 | 0.25251 | 0.24741 | 0.2219 | 0.21373 | 0.20863 | 0.28744 | 0.27723 | 0.27315 | 0.26397 | 0.25887 | 0.24866 | 0.25683 | 0.25274 | 0.2456 | 0.23642 | 0.20479 | 0.19254 | 0.1854
|  | KERRERA | CF |  |  |  |  | 0.28461 | 0.27645 | 0.27441 | 0.27135 | 0.26114 | 0.2591 | 0.24788 | 0.25706 | 0.254 | 0.25094 | 0.22237 | 0.19992 | 0.18767 | 0.28414 | 0.27496 | 0.27394 | 0.27394 | 0.2668 | 0.26373 | 0.25353 | 0.26271 | 0.26169 | 0.26271 | 0.24129 | 0.22394 | 0.21476 | 0.28744 | 0.27928 | 0.27723 | 0.27417 | 0.26499 | 0.26193 | 0.2507 | 0.25989 | 0.25887 | 0.25581 | 0.22826 | 0.20683 | 0.19458
| GRUDIE BRIDGE | KERRY FALLS | MINIMUM HEADROOM | NG 82909 71978 | YES | NO | 0.253 | 1.7116 | 1.6697 | 1.6187 | 1.5636 | 1.5177 | 1.4626 | 1.3871 | 1.2871 | 1.2075 | 1.1177 | 0.93299 | 0.87177 | 0.84218 | 1.782 | 1.7677 | 1.7483 | 1.7187 | 1.7065 | 1.682 | 1.6289 | 1.5432 | 1.4932 | 1.4218 | 1.2646 | 1.1901 | 0.93911 | 1.6483 | 1.6156 | 1.5738 | 1.5279 | 1.4942 | 1.4524 | 1.3912 | 1.3105 | 1.2565 | 1.1861 | 1.0401 | 0.99013 | 0.96871
|  | KERRY FALLS | EE |  |  |  |  | 1.7116 | 1.6697 | 1.6187 | 1.5636 | 1.5177 | 1.4626 | 1.3871 | 1.2871 | 1.2075 | 1.1177 | 0.93299 | 0.8983 | 0.88503 | 1.782 | 1.7677 | 1.7483 | 1.7187 | 1.7065 | 1.682 | 1.6289 | 1.5432 | 1.4932 | 1.4218 | 1.2646 | 1.1901 | 1.0677 | 1.6483 | 1.6156 | 1.5738 | 1.5279 | 1.4942 | 1.4524 | 1.3912 | 1.3105 | 1.2565 | 1.1861 | 1.0401 | 1.0085 | 1.0014
|  | KERRY FALLS | HT |  |  |  |  | 1.7258 | 1.684 | 1.6422 | 1.5963 | 1.5514 | 1.482 | 1.4126 | 1.3248 | 1.2687 | 1.2105 | 0.98707 | 0.87177 | 0.84218 | 1.7973 | 1.784 | 1.7718 | 1.7514 | 1.7381 | 1.7105 | 1.6922 | 1.6483 | 1.6034 | 1.5503 | 1.3514 | 1.2656 | 1.2524 | 1.6636 | 1.631 | 1.5983 | 1.5616 | 1.5269 | 1.4728 | 1.4228 | 1.3575 | 1.3136 | 1.2646 | 1.085 | 0.99013 | 0.96871
|  | KERRY FALLS | HE |  |  |  |  | 1.7258 | 1.6942 | 1.6667 | 1.633 | 1.5993 | 1.5616 | 1.5218 | 1.4493 | 1.384 | 1.3116 | 1.0024 | 0.91973 | 0.90544 | 1.7983 | 1.7861 | 1.7748 | 1.7565 | 1.7452 | 1.7248 | 1.7156 | 1.685 | 1.6452 | 1.5861 | 1.3473 | 1.2391 | 1.1279 | 1.6646 | 1.6381 | 1.6146 | 1.5861 | 1.5605 | 1.5279 | 1.5003 | 1.4463 | 1.3973 | 1.3432 | 1.0922 | 1.0228 | 1.0065
|  | KERRY FALLS | CF |  |  |  |  | 1.7299 | 1.7054 | 1.6738 | 1.6473 | 1.6156 | 1.5901 | 1.5554 | 1.5299 | 1.4799 | 1.4299 | 1.233 | 1.0687 | 0.94728 | 1.8003 | 1.7891 | 1.7738 | 1.7636 | 1.7473 | 1.7381 | 1.7218 | 1.7126 | 1.6912 | 1.6697 | 1.4687 | 1.2116 | 0.93911 | 1.6646 | 1.6452 | 1.6177 | 1.5963 | 1.5687 | 1.5483 | 1.5177 | 1.4973 | 1.4565 | 1.4177 | 1.2595 | 1.1187 | 1.0258
| TAYNUILT | KILCHRENAN | MINIMUM HEADROOM | NN 03495 23835 | YES | YES | 0.038 | 0.17702 | 0.16069 | 0.14028 | 0.11579 | 0.089261 | 0.071914 | 0.043343 | 0.014771 | -0.016861 | -0.047473 | -0.11278 | -0.13727 | -0.14237 | 0.43008 | 0.41987 | 0.40457 | 0.38926 | 0.37396 | 0.36579 | 0.34436 | 0.326 | 0.30661 | 0.28926 | 0.23722 | 0.21681 | 0.14844 | 0.31987 | 0.30253 | 0.28416 | 0.26171 | 0.23416 | 0.22089 | 0.1913 | 0.16579 | 0.13416 | 0.10457 | 0.044363 | 0.022935 | 0.016812
|  | KILCHRENAN | EE |  |  |  |  | 0.17702 | 0.16069 | 0.14028 | 0.11579 | 0.089261 | 0.071914 | 0.043343 | 0.014771 | -0.016861 | -0.047473 | -0.11278 | -0.124 | -0.12911 | 0.43008 | 0.41987 | 0.40457 | 0.38926 | 0.37396 | 0.36579 | 0.34436 | 0.326 | 0.30661 | 0.28926 | 0.23722 | 0.21681 | 0.1811 | 0.31987 | 0.30253 | 0.28416 | 0.26171 | 0.23416 | 0.22089 | 0.1913 | 0.16579 | 0.13416 | 0.10457 | 0.044363 | 0.03518 | 0.028037
|  | KILCHRENAN | HT |  |  |  |  | 0.1862 | 0.17089 | 0.15661 | 0.13518 | 0.12089 | 0.098445 | 0.074976 | 0.058649 | 0.033139 | 0.0066082 | -0.094412 | -0.13727 | -0.14237 | 0.43722 | 0.42702 | 0.41987 | 0.40967 | 0.40049 | 0.3862 | 0.37089 | 0.36273 | 0.34742 | 0.33008 | 0.26375 | 0.23926 | 0.2362 | 0.32396 | 0.31273 | 0.30049 | 0.28212 | 0.26579 | 0.24742 | 0.22396 | 0.20763 | 0.18518 | 0.15865 | 0.062731 | 0.022935 | 0.016812
|  | KILCHRENAN | HE |  |  |  |  | 0.1862 | 0.17191 | 0.16273 | 0.1464 | 0.13518 | 0.11579 | 0.094363 | 0.081098 | 0.057629 | 0.034159 | -0.079106 | -0.10666 | -0.1087 | 0.43722 | 0.42804 | 0.41987 | 0.41069 | 0.40151 | 0.39028 | 0.37702 | 0.36681 | 0.35253 | 0.3362 | 0.26069 | 0.23008 | 0.19538 | 0.32396 | 0.31375 | 0.30457 | 0.29232 | 0.28008 | 0.26171 | 0.23926 | 0.2311 | 0.20661 | 0.18416 | 0.078037 | 0.051506 | 0.048445
|  | KILCHRENAN | CF |  |  |  |  | 0.18722 | 0.17702 | 0.16477 | 0.15457 | 0.1413 | 0.13314 | 0.11681 | 0.097424 | 0.093343 | 0.078037 | 0.00048571 | -0.075024 | -0.087269 | 0.43926 | 0.43008 | 0.42191 | 0.41579 | 0.40967 | 0.40049 | 0.38926 | 0.37191 | 0.37089 | 0.35967 | 0.29947 | 0.21681 | 0.14844 | 0.32498 | 0.31885 | 0.30763 | 0.29844 | 0.28824 | 0.27804 | 0.26375 | 0.24538 | 0.24028 | 0.226 | 0.15151 | 0.079057 | 0.068853
| STRATHLEVEN | KILLEARN | MINIMUM HEADROOM | NS 51313 86758 | YES | YES | 0.549 | -1.3614 | -1.4655 | -1.5727 | -1.7053 | -1.8573 | -2.0165 | -2.1992 | -2.4073 | -2.6053 | -2.789 | -3.4992 | -4.0043 | -4.2584 | -0.50224 | -0.56449 | -0.62776 | -0.71245 | -0.80429 | -0.9002 | -0.99612 | -1.1278 | -1.2441 | -1.3533 | -1.6931 | -1.9594 | -2.2124 | -0.87265 | -0.96143 | -1.0543 | -1.1706 | -1.3073 | -1.4502 | -1.6053 | -1.792 | -1.9686 | -2.1308 | -2.7043 | -3.1104 | -3.3002
|  | KILLEARN | EE |  |  |  |  | -1.3614 | -1.4655 | -1.5727 | -1.7053 | -1.8573 | -2.0165 | -2.1992 | -2.4073 | -2.6053 | -2.789 | -3.4206 | -3.8716 | -4.1022 | -0.50224 | -0.56449 | -0.62776 | -0.71245 | -0.80429 | -0.9002 | -0.99612 | -1.1278 | -1.2441 | -1.3533 | -1.6931 | -1.9594 | -2.2002 | -0.87265 | -0.96143 | -1.0543 | -1.1706 | -1.3073 | -1.4502 | -1.6053 | -1.792 | -1.9686 | -2.1308 | -2.6543 | -3.0104 | -3.1849
|  | KILLEARN | HT |  |  |  |  | -1.341 | -1.439 | -1.5553 | -1.6982 | -1.8267 | -1.9757 | -2.1502 | -2.3461 | -2.5002 | -2.6859 | -3.4992 | -4.0043 | -4.2584 | -0.47878 | -0.52878 | -0.59306 | -0.67163 | -0.73898 | -0.82163 | -0.91449 | -1.0267 | -1.1012 | -1.2043 | -1.6522 | -1.9084 | -2.0431 | -0.84612 | -0.93184 | -1.0329 | -1.1533 | -1.2614 | -1.388 | -1.539 | -1.7094 | -1.838 | -2.0002 | -2.7043 | -3.1104 | -3.3002
|  | KILLEARN | HE |  |  |  |  | -1.3298 | -1.3961 | -1.4767 | -1.5829 | -1.6727 | -1.792 | -1.9451 | -2.0941 | -2.2002 | -2.34 | -3.0655 | -3.5645 | -3.8696 | -0.47673 | -0.51857 | -0.56755 | -0.63898 | -0.69408 | -0.76347 | -0.85224 | -0.94918 | -1.0084 | -1.0961 | -1.5431 | -1.8461 | -2.1114 | -0.83796 | -0.89612 | -0.96551 | -1.0573 | -1.1359 | -1.24 | -1.3727 | -1.5073 | -1.5971 | -1.7216 | -2.3492 | -2.7563 | -2.9931
|  | KILLEARN | CF |  |  |  |  | -1.3094 | -1.3502 | -1.4124 | -1.4767 | -1.5573 | -1.6135 | -1.7043 | -1.8135 | -1.9104 | -2.0155 | -2.5369 | -3.0788 | -3.5206 | -0.46551 | -0.49408 | -0.54 | -0.5849 | -0.63694 | -0.67776 | -0.73898 | -0.81245 | -0.8798 | -0.95122 | -1.3227 | -1.7533 | -2.2124 | -0.81959 | -0.85633 | -0.91347 | -0.96857 | -1.042 | -1.089 | -1.1696 | -1.2676 | -1.3543 | -1.4482 | -1.9094 | -2.3665 | -2.7155
| KILLIN | KILLIN TOWN | MINIMUM HEADROOM | NN 56931 32662 | YES | YES | 0.024 | 1.9801 | 1.9484 | 1.9148 | 1.8617 | 1.8117 | 1.7505 | 1.6984 | 1.6189 | 1.5515 | 1.4842 | 1.2964 | 1.1974 | 1.1464 | 2.0388 | 2.0122 | 1.9888 | 1.9479 | 1.9204 | 1.8785 | 1.8469 | 1.7908 | 1.7479 | 1.703 | 1.5653 | 1.4928 | 1.3102 | 1.9982 | 1.9625 | 1.9278 | 1.8788 | 1.8359 | 1.7819 | 1.7319 | 1.6615 | 1.6002 | 1.5421 | 1.3717 | 1.291 | 1.2513
|  | KILLIN TOWN | EE |  |  |  |  | 1.9801 | 1.9484 | 1.9148 | 1.8617 | 1.8117 | 1.7505 | 1.6984 | 1.6189 | 1.5515 | 1.4842 | 1.2964 | 1.2321 | 1.1831 | 2.0388 | 2.0122 | 1.9888 | 1.9479 | 1.9204 | 1.8785 | 1.8469 | 1.7908 | 1.7479 | 1.703 | 1.5653 | 1.4928 | 1.3979 | 1.9982 | 1.9625 | 1.9278 | 1.8788 | 1.8359 | 1.7819 | 1.7319 | 1.6615 | 1.6002 | 1.5421 | 1.3717 | 1.3196 | 1.2798
|  | KILLIN TOWN | HT |  |  |  |  | 2.0035 | 1.9801 | 1.9413 | 1.8974 | 1.8617 | 1.8097 | 1.7627 | 1.6974 | 1.6342 | 1.5923 | 1.3311 | 1.1974 | 1.1464 | 2.0571 | 2.0398 | 2.0112 | 1.9826 | 1.9632 | 1.9316 | 1.903 | 1.8612 | 1.8194 | 1.7959 | 1.6245 | 1.5428 | 1.5102 | 2.0176 | 1.9859 | 1.9533 | 1.9125 | 1.8808 | 1.8349 | 1.7951 | 1.7349 | 1.6808 | 1.641 | 1.4104 | 1.291 | 1.2513
|  | KILLIN TOWN | HE |  |  |  |  | 2.0035 | 1.9811 | 1.9525 | 1.9158 | 1.8842 | 1.8433 | 1.7984 | 1.7372 | 1.6801 | 1.6301 | 1.3484 | 1.2423 | 1.2229 | 2.053 | 2.0367 | 2.0183 | 1.9888 | 1.9683 | 1.9367 | 1.903 | 1.8571 | 1.8132 | 1.7796 | 1.5755 | 1.5 | 1.4285 | 2.0166 | 1.99 | 1.9645 | 1.9308 | 1.9043 | 1.8655 | 1.8278 | 1.7747 | 1.7247 | 1.6819 | 1.4023 | 1.3033 | 1.2849
|  | KILLIN TOWN | CF |  |  |  |  | 2.0076 | 1.9974 | 1.9689 | 1.9444 | 1.9117 | 1.8903 | 1.8535 | 1.8229 | 1.7842 | 1.7423 | 1.5505 | 1.3648 | 1.2168 | 2.0551 | 2.0449 | 2.0265 | 2.0061 | 1.9867 | 1.9724 | 1.9459 | 1.9194 | 1.8918 | 1.8622 | 1.7061 | 1.5122 | 1.3102 | 2.0176 | 2.0023 | 1.9747 | 1.9543 | 1.9268 | 1.9043 | 1.8747 | 1.8461 | 1.8104 | 1.7768 | 1.6023 | 1.4206 | 1.2788
| TAYNUILT | KILMELFORD | MINIMUM HEADROOM | NM 84056 14437 | YES | YES | 0.309 | -1.4968 | -1.5142 | -1.5315 | -1.5519 | -1.5795 | -1.6284 | 2.4389 | 2.3716 | 2.3114 | 2.2552 | 2.1287 | 2.0991 | 2.092 | -1.1152 | -1.1376 | -1.1631 | -1.1897 | -1.2295 | -1.2733 | 2.7991 | 2.745 | 2.7032 | 2.6593 | 2.545 | 2.5073 | 2.3358 | -1.9284 | -1.954 | -1.9805 | -2.0142 | -2.056 | -2.104 | 1.9644 | 1.9073 | 1.8552 | 1.8083 | 1.7165 | 1.6981 | 1.692
|  | KILMELFORD | EE |  |  |  |  | -1.4968 | -1.5142 | -1.5315 | -1.5519 | -1.5795 | -1.6284 | 2.4389 | 2.3716 | 2.3114 | 2.2552 | 2.1287 | 2.1144 | 2.1032 | -1.1152 | -1.1376 | -1.1631 | -1.1897 | -1.2295 | -1.2733 | 2.7991 | 2.745 | 2.7032 | 2.6593 | 2.545 | 2.5073 | 2.4307 | -1.9284 | -1.954 | -1.9805 | -2.0142 | -2.056 | -2.104 | 1.9644 | 1.9073 | 1.8552 | 1.8083 | 1.7165 | 1.7073 | 1.6991
|  | KILMELFORD | HT |  |  |  |  | -1.4866 | -1.5019 | -1.5162 | -1.5315 | -1.5519 | -1.5733 | 2.5032 | 2.4532 | 2.4195 | 2.3675 | 2.1562 | 2.0991 | 2.092 | -1.0958 | -1.1111 | -1.1346 | -1.1519 | -1.1825 | -1.207 | 2.8583 | 2.8154 | 2.7981 | 2.7593 | 2.595 | 2.544 | 2.5338 | -1.906 | -1.9264 | -1.9499 | -1.9703 | -2.0019 | -2.0295 | 2.0318 | 1.9879 | 1.9654 | 1.9205 | 1.742 | 1.6981 | 1.692
|  | KILMELFORD | HE |  |  |  |  | -1.4866 | -1.5009 | -1.5142 | -1.5295 | -1.5509 | -1.5693 | 2.5073 | 2.4787 | 2.4511 | 2.4052 | 2.1787 | 2.1185 | 2.0971 | -1.0978 | -1.1131 | -1.1335 | -1.1489 | -1.1774 | -1.1978 | 2.8675 | 2.8256 | 2.8124 | 2.7746 | 2.595 | 2.5348 | 2.4603 | -1.906 | -1.9254 | -1.9458 | -1.9642 | -1.9927 | -2.0162 | 2.0471 | 2.0042 | 1.9838 | 1.944 | 1.7562 | 1.7195 | 1.7144
|  | KILMELFORD | CF |  |  |  |  | -1.4856 | -1.4948 | -1.505 | -1.5213 | -1.5335 | -1.5499 | 2.5318 | 2.5154 | 2.495 | 2.4756 | 2.3409 | 2.196 | 2.1287 | -1.0927 | -1.107 | -1.1203 | -1.1448 | -1.1591 | -1.1825 | 2.8889 | 2.8685 | 2.8358 | 2.8052 | 2.6716 | 2.5073 | 2.3358 | -1.8989 | -1.9152 | -1.9295 | -1.9519 | -1.9642 | -1.9876 | 2.0858 | 2.0644 | 2.0358 | 2.0062 | 1.8746 | 1.7481 | 1.7175
| TAYNUILT | KILNINVER | MINIMUM HEADROOM | NM 83049 22251 | YES | YES | 0.042 | -0.64681 | -0.70498 | -0.75191 | -0.806 | -0.87334 | -0.94477 | -1.005 | -1.0917 | -1.1784 | -1.258 | -1.4499 | -1.5172 | -1.4968 | 0.0838 | 0.049106 | 0.016453 | -0.0162 | -0.060078 | -0.11008 | -0.14885 | -0.20396 | -0.26518 | -0.31518 | -0.45396 | -0.51212 | -0.6764 | -0.12947 | -0.18253 | -0.22742 | -0.27844 | -0.34069 | -0.40906 | -0.46824 | -0.54987 | -0.63151 | -0.706 | -0.88559 | -0.95396 | -0.93355
|  | KILNINVER | EE |  |  |  |  | -0.64681 | -0.70498 | -0.75191 | -0.806 | -0.87334 | -0.94477 | -1.005 | -1.0917 | -1.1784 | -1.258 | -1.4499 | -1.4774 | -1.4968 | 0.0838 | 0.049106 | 0.016453 | -0.0162 | -0.060078 | -0.11008 | -0.14885 | -0.20396 | -0.26518 | -0.31518 | -0.45396 | -0.51212 | -0.59885 | -0.12947 | -0.18253 | -0.22742 | -0.27844 | -0.34069 | -0.40906 | -0.46824 | -0.54987 | -0.63151 | -0.706 | -0.88559 | -0.91416 | -0.93355
|  | KILNINVER | HT |  |  |  |  | -0.62844 | -0.67232 | -0.7111 | -0.75293 | -0.80702 | -0.85396 | -0.9162 | -0.98865 | -1.0356 | -1.107 | -1.3897 | -1.5172 | -1.4968 | 0.099106 | 0.074616 | 0.050127 | 0.027678 | -0.0049755 | -0.033547 | -0.073343 | -0.11824 | -0.14681 | -0.19273 | -0.38457 | -0.4662 | -0.44477 | -0.1111 | -0.14783 | -0.18661 | -0.2264 | -0.27538 | -0.32028 | -0.37947 | -0.44783 | -0.49069 | -0.56008 | -0.83355 | -0.95396 | -0.93049
|  | KILNINVER | HE |  |  |  |  | -0.63049 | -0.6611 | -0.69579 | -0.72436 | -0.76416 | -0.80089 | -0.85702 | -0.92028 | -0.95702 | -1.0182 | -1.3284 | -1.4029 | -1.4142 | 0.097065 | 0.078698 | 0.055229 | 0.037882 | 0.011351 | -0.014159 | -0.051914 | -0.093751 | -0.11824 | -0.1611 | -0.3713 | -0.45498 | -0.53253 | -0.11314 | -0.13967 | -0.17232 | -0.19885 | -0.23865 | -0.27232 | -0.32436 | -0.38457 | -0.4213 | -0.47947 | -0.77028 | -0.83967 | -0.85089
|  | KILNINVER | CF |  |  |  |  | -0.62334 | -0.64885 | -0.67538 | -0.70804 | -0.73151 | -0.76722 | -0.79579 | -0.83763 | -0.87947 | -0.92028 | -1.1111 | -1.305 | -1.4101 | 0.10217 | 0.089922 | 0.069514 | 0.047065 | 0.03278 | 0.006249 | -0.014159 | -0.044771 | -0.079465 | -0.10906 | -0.26416 | -0.47028 | -0.6764 | -0.10498 | -0.12742 | -0.15089 | -0.18457 | -0.20702 | -0.23967 | -0.2662 | -0.30804 | -0.34681 | -0.38559 | -0.56824 | -0.75293 | -0.84885
| BEAULY | KILTARLITY | MINIMUM HEADROOM | NH 50271 41265 | YES | NO | 0.358 | 4.0362 | 3.9842 | 3.923 | 3.8485 | 3.7964 | 3.727 | 3.6291 | 3.5372 | 3.4168 | 3.3046 | 3.1076 | 3.0362 | 3.0148 | 4.7179 | 4.6872 | 4.6464 | 4.5964 | 4.5628 | 4.5179 | 4.4525 | 4.3985 | 4.3199 | 4.2505 | 4.1128 | 4.0556 | 3.8199 | 4.4536 | 4.4056 | 4.3474 | 4.275 | 4.224 | 4.1576 | 4.0648 | 3.977 | 3.8617 | 3.7556 | 3.5709 | 3.5046 | 3.4862
|  | KILTARLITY | EE |  |  |  |  | 4.0362 | 3.9842 | 3.923 | 3.8485 | 3.7964 | 3.727 | 3.6291 | 3.5372 | 3.4168 | 3.3046 | 3.1076 | 3.073 | 3.0546 | 4.7179 | 4.6872 | 4.6464 | 4.5964 | 4.5628 | 4.5179 | 4.4525 | 4.3985 | 4.3199 | 4.2505 | 4.1128 | 4.0556 | 3.9576 | 4.4536 | 4.4056 | 4.3474 | 4.275 | 4.224 | 4.1576 | 4.0648 | 3.977 | 3.8617 | 3.7556 | 3.5709 | 3.5383 | 3.5219
|  | KILTARLITY | HT |  |  |  |  | 4.0607 | 4.0128 | 3.9668 | 3.9158 | 3.8566 | 3.7719 | 3.6995 | 3.5995 | 3.527 | 3.4515 | 3.1648 | 3.0362 | 3.0148 | 4.7464 | 4.7179 | 4.6923 | 4.6617 | 4.624 | 4.5699 | 4.5332 | 4.475 | 4.424 | 4.3709 | 4.1811 | 4.1076 | 4.0954 | 4.4872 | 4.4413 | 4.3985 | 4.3505 | 4.2923 | 4.2107 | 4.1485 | 4.0546 | 3.9801 | 3.9025 | 3.625 | 3.5046 | 3.4862
|  | KILTARLITY | HE |  |  |  |  | 4.0597 | 4.025 | 3.9903 | 3.9525 | 3.9056 | 3.8495 | 3.8087 | 3.7281 | 3.6423 | 3.5525 | 3.2015 | 3.1148 | 3.1015 | 4.7434 | 4.7209 | 4.6964 | 4.6709 | 4.6362 | 4.5985 | 4.5719 | 4.5209 | 4.4648 | 4.4046 | 4.1719 | 4.0821 | 3.9913 | 4.4862 | 4.4505 | 4.4148 | 4.3791 | 4.3301 | 4.276 | 4.2372 | 4.1607 | 4.0821 | 3.9974 | 3.6587 | 3.5801 | 3.5679
|  | KILTARLITY | CF |  |  |  |  | 4.0658 | 4.0342 | 4.0046 | 3.9689 | 3.9383 | 3.8934 | 3.8454 | 3.8189 | 3.7515 | 3.6964 | 3.4413 | 3.2168 | 3.1138 | 4.7485 | 4.727 | 4.7097 | 4.6791 | 4.6597 | 4.6291 | 4.5913 | 4.5699 | 4.526 | 4.4893 | 4.2934 | 4.0556 | 3.8199 | 4.4923 | 4.4628 | 4.4332 | 4.3954 | 4.3638 | 4.3189 | 4.2719 | 4.2464 | 4.1842 | 4.1332 | 3.8883 | 3.6689 | 3.5781
| REDMOSS | KINCORTH | MINIMUM HEADROOM | NJ 94445 03252 | NO | NO | 6.583 | 1.4981 | 0.97769 | 0.16647 | -0.60088 | -1.3213 | -2.0346 | -2.5886 | -3.1662 | -3.6488 | -4.1529 | -6.0927 | -7.4601 | -7.6988 | 1.6741 | 1.3721 | 0.8782 | 0.29147 | -0.2769 | -0.84221 | -1.1575 | -1.5126 | -1.7034 | -1.9483 | -3.0381 | -3.8912 | -4.5963 | 1.6193 | 1.205 | 0.50192 | -0.19603 | -0.85114 | -1.5164 | -2.0164 | -2.5909 | -2.9797 | -3.4369 | -5.1552 | -6.3715 | -6.5817
|  | KINCORTH | EE |  |  |  |  | 1.5216 | 1.041 | 0.40728 | -0.3917 | -1.1039 | -1.8213 | -2.5295 | -3.1662 | -3.4141 | -3.908 | -5.9397 | -7.3774 | -7.6876 | 1.6741 | 1.3721 | 0.97004 | 0.41698 | -0.10139 | -0.64527 | -1.1238 | -1.5126 | -1.6483 | -1.933 | -3.0381 | -3.8912 | -4.5963 | 1.6376 | 1.2325 | 0.67641 | -0.041953 | -0.68889 | -1.3501 | -2.0001 | -2.5909 | -2.7909 | -3.242 | -5.044 | -6.3062 | -6.5817
|  | KINCORTH | HT |  |  |  |  | 1.4981 | 0.97769 | 0.16647 | -0.60088 | -1.3213 | -2.0346 | -2.5886 | -3.1356 | -3.6488 | -4.1529 | -6.0927 | -7.4601 | -7.6988 | 1.6915 | 1.3792 | 0.8782 | 0.29147 | -0.2769 | -0.84221 | -1.1575 | -1.4473 | -1.7034 | -1.9483 | -2.7575 | -3.3238 | -3.4289 | 1.6193 | 1.205 | 0.50192 | -0.19603 | -0.85114 | -1.5164 | -2.0164 | -2.5134 | -2.9797 | -3.4369 | -5.1552 | -6.3715 | -6.5817
|  | KINCORTH | HE |  |  |  |  | 1.5634 | 1.2226 | 0.61953 | -0.035576 | -0.59884 | -1.1611 | -1.6488 | -2.0295 | -2.3978 | -2.7631 | -4.3203 | -5.6988 | -6.2192 | 1.7231 | 1.4853 | 1.0976 | 0.60473 | 0.13636 | -0.33404 | -0.7116 | -0.97486 | -1.2167 | -1.4534 | -2.3647 | -3.2075 | -3.9708 | 1.6621 | 1.405 | 0.88968 | 0.29988 | -0.21644 | -0.73685 | -1.1889 | -1.5399 | -1.8787 | -2.2164 | -3.593 | -4.8022 | -5.2603
|  | KINCORTH | CF |  |  |  |  | 1.6267 | 1.5297 | 1.3348 | 1.0093 | 0.65524 | 0.28177 | -0.059045 | -0.39476 | -0.59374 | -0.84272 | -2.0448 | -3.5315 | -4.6876 | 1.7721 | 1.669 | 1.5027 | 1.2568 | 0.9833 | 0.67208 | 0.39453 | 0.11596 | -0.068739 | -0.28404 | -1.3555 | -2.832 | -4.582 | 1.706 | 1.6193 | 1.4642 | 1.1958 | 0.88152 | 0.54172 | 0.2356 | -0.064402 | -0.24501 | -0.47461 | -1.5634 | -2.9175 | -3.9317
| FORT WILLIAM | KINGAIRLOCH | MINIMUM HEADROOM | NM 76917 56652 | YES | NO | 0.082 | 0.0021102 | -0.0019714 | -0.0060531 | -0.016257 | -0.021359 | -0.033604 | -0.025441 | -0.031563 | -0.043808 | -0.049931 | -0.060135 | -0.070339 | -0.076461 | 0.012498 | 0.010457 | 0.0073959 | -0.0017878 | -0.004849 | -0.015053 | -0.0089306 | -0.013012 | -0.023216 | -0.028318 | -0.03138 | -0.038522 | -0.042604 | 0.010876 | 0.0078143 | 0.0047531 | -0.0044306 | -0.0095327 | -0.020757 | -0.013614 | -0.019737 | -0.030961 | -0.036063 | -0.045247 | -0.054431 | -0.060553
|  | KINGAIRLOCH | EE |  |  |  |  | 0.0021102 | -0.0019714 | -0.0060531 | -0.016257 | -0.021359 | -0.033604 | -0.025441 | -0.029522 | -0.034624 | -0.039727 | -0.054012 | -0.056053 | -0.056053 | 0.012498 | 0.010457 | 0.0073959 | -0.0017878 | -0.004849 | -0.015053 | -0.0038286 | -0.0079102 | -0.010971 | -0.015053 | -0.025257 | -0.027298 | -0.027298 | 0.010876 | 0.0078143 | 0.0047531 | -0.0044306 | -0.0095327 | -0.020757 | -0.011573 | -0.015655 | -0.019737 | -0.024839 | -0.039124 | -0.041165 | -0.041165
|  | KINGAIRLOCH | HT |  |  |  |  | 0.010273 | 0.0072122 | -0.0019714 | -0.0040122 | -0.0070735 | -0.019318 | -0.0234 | -0.029522 | -0.039727 | -0.044829 | -0.050951 | -0.059114 | -0.064216 | 0.020661 | 0.01862 | 0.010457 | 0.0084163 | 0.0063755 | -0.0038286 | -0.0058694 | -0.010971 | -0.021176 | -0.024237 | -0.023216 | -0.029339 | -0.03342 | 0.019039 | 0.015978 | 0.0078143 | 0.0057735 | 0.0037327 | -0.0085122 | -0.010553 | -0.015655 | -0.025859 | -0.030961 | -0.036063 | -0.044227 | -0.049329
|  | KINGAIRLOCH | HE |  |  |  |  | 0.010273 | 0.0082327 | -0.0029918 | -0.0060531 | -0.0091143 | -0.013196 | -0.025441 | -0.031563 | -0.043808 | -0.049931 | -0.060135 | -0.070339 | -0.076461 | 0.020661 | 0.01862 | 0.0094367 | 0.0073959 | 0.0053551 | 0.0022939 | -0.0089306 | -0.013012 | -0.023216 | -0.028318 | -0.03138 | -0.038522 | -0.042604 | 0.019039 | 0.015978 | 0.0067939 | 0.0047531 | 0.0027122 | -0.0013694 | -0.013614 | -0.019737 | -0.030961 | -0.036063 | -0.045247 | -0.054431 | -0.060553
|  | KINGAIRLOCH | CF |  |  |  |  | 0.010273 | 0.0092531 | 0.0010898 | -0.0019714 | -0.0040122 | -0.0060531 | -0.0091143 | -0.020339 | -0.02238 | -0.026461 | -0.040747 | -0.057073 | -0.068298 | 0.020661 | 0.019641 | 0.011478 | 0.010457 | 0.0084163 | 0.0073959 | 0.0053551 | -0.004849 | -0.0068898 | -0.0089306 | -0.017094 | -0.029339 | -0.037502 | 0.019039 | 0.018018 | 0.0088347 | 0.0078143 | 0.0057735 | 0.0047531 | 0.0027122 | -0.0085122 | -0.010553 | -0.014635 | -0.0279 | -0.043206 | -0.05341
| DYCE | KINGSEAT | MINIMUM HEADROOM | NJ 89545 19709 | NO | YES | 2.067 | 9.3873 | 9.1404 | 8.8118 | 8.4465 | 8.0281 | 7.5016 | 6.922 | 6.2914 | 5.6455 | 4.8832 | 3.7516 | 3.5771 | 3.4669 | 10.3118 | 10.1802 | 9.9965 | 9.8179 | 9.5822 | 9.2761 | 8.8781 | 8.4485 | 7.9455 | 7.3128 | 6.5853 | 6.3128 | 5.8067 | 9.8899 | 9.6868 | 9.395 | 9.1092 | 8.7337 | 8.2929 | 7.7715 | 7.1909 | 6.6011 | 5.895 | 4.847 | 4.698 | 4.6021
|  | KINGSEAT | EE |  |  |  |  | 9.3873 | 9.1404 | 8.8118 | 8.4669 | 8.0281 | 7.5128 | 6.922 | 6.322 | 5.7098 | 5.07 | 4.0689 | 3.6649 | 3.5557 | 10.3118 | 10.1802 | 9.9965 | 9.8179 | 9.5822 | 9.2761 | 8.8781 | 8.4485 | 8.0098 | 7.523 | 6.6271 | 6.3128 | 5.9985 | 9.8899 | 9.6868 | 9.395 | 9.1092 | 8.7337 | 8.3021 | 7.7715 | 7.2266 | 6.6705 | 6.0807 | 5.145 | 4.7746 | 4.6807
|  | KINGSEAT | HT |  |  |  |  | 9.4434 | 9.1689 | 8.8291 | 8.4465 | 8.0547 | 7.5016 | 6.9383 | 6.2914 | 5.6455 | 4.8832 | 3.7516 | 3.5771 | 3.4669 | 10.3689 | 10.2291 | 10.0679 | 9.8771 | 9.6832 | 9.3373 | 8.9363 | 8.4506 | 7.9455 | 7.3128 | 6.5853 | 6.5424 | 6.4689 | 9.9654 | 9.7399 | 9.4592 | 9.1337 | 8.799 | 8.2929 | 7.7827 | 7.1909 | 6.6011 | 5.895 | 4.847 | 4.698 | 4.6021
|  | KINGSEAT | HE |  |  |  |  | 9.4455 | 9.2485 | 9.0016 | 8.6894 | 8.3261 | 7.9036 | 7.4332 | 6.9485 | 6.4802 | 5.922 | 4.6853 | 4.1842 | 3.9618 | 10.3649 | 10.2506 | 10.121 | 9.9516 | 9.7608 | 9.5036 | 9.1689 | 8.7924 | 8.4138 | 7.9383 | 6.8159 | 6.5087 | 6.1475 | 9.9664 | 9.797 | 9.5929 | 9.3327 | 9.0276 | 8.6644 | 8.2439 | 7.799 | 7.3695 | 6.8501 | 5.7041 | 5.246 | 5.0429
|  | KINGSEAT | CF |  |  |  |  | 9.4761 | 9.3424 | 9.174 | 8.9669 | 8.7036 | 8.421 | 8.122 | 7.7832 | 7.4689 | 7.1536 | 5.724 | 4.8608 | 4.3863 | 10.3822 | 10.3016 | 10.2026 | 10.0842 | 9.9404 | 9.7781 | 9.571 | 9.321 | 9.0853 | 8.8475 | 7.5771 | 6.5842 | 5.8067 | 9.9919 | 9.8735 | 9.7276 | 9.5521 | 9.3266 | 9.096 | 8.8358 | 8.5307 | 8.245 | 7.9807 | 6.647 | 5.8654 | 5.4297
| BOAT OF GARTEN | KINGUSSIE | MINIMUM HEADROOM | NH 75429 00426 | NO | YES | 2.492 | 0.58 | 0.39837 | 0.16776 | -0.090408 | -0.33837 | -0.63735 | -0.9649 | -1.27 | -1.5904 | -1.8547 | -2.5935 | -2.8598 | -2.9435 | 2.079 | 1.9647 | 1.8218 | 1.6678 | 1.5218 | 1.3402 | 1.1341 | 0.93714 | 0.73204 | 0.55857 | 0.02898 | -0.2802 | -1.0231 | 1.4009 | 1.2346 | 1.0326 | 0.80194 | 0.59173 | 0.32439 | 0.03051 | -0.23582 | -0.53173 | -0.77153 | -1.4552 | -1.9113 | -1.9899
|  | KINGUSSIE | EE |  |  |  |  | 0.58 | 0.39837 | 0.16776 | -0.090408 | -0.33837 | -0.63735 | -0.9649 | -1.27 | -1.5904 | -1.8547 | -2.5935 | -2.7363 | -2.8129 | 2.079 | 1.9647 | 1.8218 | 1.6678 | 1.5218 | 1.3402 | 1.1341 | 0.93714 | 0.73204 | 0.55857 | 0.02898 | -0.18633 | -0.49857 | 1.4009 | 1.2346 | 1.0326 | 0.80194 | 0.59173 | 0.32439 | 0.03051 | -0.23582 | -0.53173 | -0.77153 | -1.4358 | -1.5623 | -1.6358
|  | KINGUSSIE | HT |  |  |  |  | 0.65041 | 0.49735 | 0.29837 | 0.10041 | -0.12714 | -0.38735 | -0.6149 | -0.8751 | -1.1322 | -1.37 | -2.3455 | -2.8363 | -2.8986 | 2.131 | 2.0433 | 1.932 | 1.828 | 1.7014 | 1.5545 | 1.4269 | 1.2667 | 1.1106 | 0.95653 | 0.31265 | 0.0085714 | -0.025102 | 1.4703 | 1.3377 | 1.1672 | 1.006 | 0.81622 | 0.59071 | 0.405 | 0.16724 | -0.062347 | -0.28378 | -1.2042 | -1.6552 | -1.7113
|  | KINGUSSIE | HE |  |  |  |  | 0.64327 | 0.51265 | 0.33612 | 0.16163 | -0.043469 | -0.2802 | -0.49857 | -0.75571 | -1.0016 | -1.2373 | -2.4322 | -2.8598 | -2.9435 | 2.1259 | 2.0412 | 1.93 | 1.831 | 1.7035 | 1.5606 | 1.43 | 1.2565 | 1.0953 | 0.92898 | 0.10857 | -0.2802 | -0.55673 | 1.4601 | 1.3438 | 1.1938 | 1.0509 | 0.87643 | 0.66929 | 0.48255 | 0.23459 | -0.0082653 | -0.24908 | -1.4552 | -1.9113 | -1.9899
|  | KINGUSSIE | CF |  |  |  |  | 0.68408 | 0.57796 | 0.44531 | 0.30551 | 0.12898 | -0.050612 | -0.22408 | -0.37204 | -0.54041 | -0.68939 | -1.4945 | -2.27 | -2.7965 | 2.1484 | 2.0841 | 2.0024 | 1.9188 | 1.8137 | 1.7035 | 1.5871 | 1.4841 | 1.3688 | 1.2545 | 0.60143 | -0.18633 | -1.0231 | 1.4999 | 1.405 | 1.2826 | 1.1621 | 1.0101 | 0.855 | 0.6999 | 0.57235 | 0.41827 | 0.27949 | -0.45214 | -1.2481 | -1.8593
| TAYNUILT | KINLOCH | MINIMUM HEADROOM | NM 52465 27215 | YES | YES | 0.953 | -0.88088 | -0.92067 | -0.95843 | -1.0084 | -1.0543 | -1.1125 | -1.1788 | -1.2329 | -1.3003 | -1.3554 | -1.5043 | -1.5564 | -1.5666 | -0.58394 | -0.60741 | -0.62986 | -0.66761 | -0.69516 | -0.73394 | -0.77782 | -0.81353 | -0.85945 | -0.89618 | -0.99822 | -1.035 | -1.1237 | -1.0401 | -1.0564 | -1.0707 | -1.0931 | -1.1125 | -1.1635 | -1.2278 | -1.2778 | -1.3421 | -1.3952 | -1.5339 | -1.585 | -1.5952
|  | KINLOCH | EE |  |  |  |  | -0.88088 | -0.92067 | -0.95843 | -1.0084 | -1.0543 | -1.1125 | -1.1788 | -1.2329 | -1.3003 | -1.3554 | -1.5043 | -1.5288 | -1.5462 | -0.58394 | -0.60741 | -0.62986 | -0.66761 | -0.69516 | -0.73394 | -0.77782 | -0.81353 | -0.85945 | -0.89618 | -0.99822 | -1.035 | -1.088 | -1.0401 | -1.0564 | -1.0707 | -1.0931 | -1.1125 | -1.1635 | -1.2278 | -1.2778 | -1.3421 | -1.3952 | -1.5339 | -1.5574 | -1.5748
|  | KINLOCH | HT |  |  |  |  | -0.86251 | -0.89516 | -0.9268 | -0.96863 | -0.99924 | -1.0431 | -1.0829 | -1.1421 | -1.1952 | -1.2319 | -1.4533 | -1.5564 | -1.5666 | -0.56761 | -0.58598 | -0.60537 | -0.63088 | -0.64924 | -0.67782 | -0.70231 | -0.74108 | -0.77476 | -0.79618 | -0.94822 | -1.0115 | -1.0197 | -1.0309 | -1.0472 | -1.0584 | -1.0748 | -1.0901 | -1.1074 | -1.1329 | -1.187 | -1.239 | -1.2748 | -1.489 | -1.585 | -1.5952
|  | KINLOCH | HE |  |  |  |  | -0.86251 | -0.88904 | -0.91353 | -0.94618 | -0.96863 | -1.0033 | -1.0411 | -1.0901 | -1.139 | -1.188 | -1.4094 | -1.4707 | -1.4778 | -0.56761 | -0.58496 | -0.60027 | -0.62476 | -0.63802 | -0.66353 | -0.68496 | -0.72169 | -0.75333 | -0.79006 | -0.93292 | -0.99414 | -1.036 | -1.0329 | -1.0462 | -1.0574 | -1.0727 | -1.0839 | -1.1023 | -1.1217 | -1.1482 | -1.187 | -1.236 | -1.4431 | -1.5023 | -1.5084
|  | KINLOCH | CF |  |  |  |  | -0.85945 | -0.87884 | -0.90333 | -0.92476 | -0.95333 | -0.97067 | -0.99924 | -1.036 | -1.0564 | -1.0901 | -1.2492 | -1.3972 | -1.4788 | -0.56557 | -0.5768 | -0.5921 | -0.60945 | -0.62782 | -0.6421 | -0.66047 | -0.68904 | -0.70435 | -0.72884 | -0.85333 | -0.99618 | -1.1237 | -1.0288 | -1.036 | -1.0452 | -1.0543 | -1.0666 | -1.0737 | -1.087 | -1.1033 | -1.1146 | -1.1431 | -1.2931 | -1.4339 | -1.5094
| TUMMEL BRIDGE | KINLOCH RANNOCH | MINIMUM HEADROOM | NN 65927 58500 | YES | YES | 0 | -0.0091837 | -0.02449 | -0.039796 | -0.054082 | -0.07449 | -0.083673 | -0.11327 | -0.13673 | -0.17143 | -0.19796 | -0.26939 | -0.29286 | -0.29796 | 0.46122 | 0.44898 | 0.43776 | 0.42245 | 0.40306 | 0.39592 | 0.37551 | 0.35918 | 0.33571 | 0.31735 | 0.26531 | 0.24286 | 0.17041 | 0.18571 | 0.16939 | 0.1551 | 0.14082 | 0.11429 | 0.10306 | 0.07449 | 0.05 | 0.016327 | -0.0081633 | -0.078571 | -0.10102 | -0.10306
|  | KINLOCH RANNOCH | EE |  |  |  |  | -0.0091837 | -0.02449 | -0.039796 | -0.054082 | -0.07449 | -0.083673 | -0.11327 | -0.13673 | -0.17143 | -0.19796 | -0.26939 | -0.28469 | -0.29184 | 0.46122 | 0.44898 | 0.43776 | 0.42245 | 0.40306 | 0.39592 | 0.37551 | 0.35918 | 0.33571 | 0.31735 | 0.26531 | 0.24286 | 0.21224 | 0.18571 | 0.16939 | 0.1551 | 0.14082 | 0.11429 | 0.10306 | 0.07449 | 0.05 | 0.016327 | -0.0081633 | -0.078571 | -0.091837 | -0.1
|  | KINLOCH RANNOCH | HT |  |  |  |  | -0.0040816 | -0.013265 | -0.023469 | -0.031633 | -0.04898 | -0.059184 | -0.082653 | -0.09898 | -0.12143 | -0.14796 | -0.24694 | -0.29286 | -0.29796 | 0.46735 | 0.45816 | 0.45 | 0.44082 | 0.42959 | 0.42041 | 0.40408 | 0.39694 | 0.37959 | 0.36327 | 0.29286 | 0.26429 | 0.25918 | 0.19184 | 0.18265 | 0.17041 | 0.1602 | 0.14082 | 0.12857 | 0.10408 | 0.089796 | 0.067347 | 0.039796 | -0.057143 | -0.10102 | -0.10306
|  | KINLOCH RANNOCH | HE |  |  |  |  | -0.0040816 | -0.012245 | -0.021429 | -0.028571 | -0.042857 | -0.05102 | -0.066327 | -0.07551 | -0.09898 | -0.12041 | -0.23163 | -0.26735 | -0.27347 | 0.46735 | 0.45714 | 0.45102 | 0.44286 | 0.43163 | 0.42245 | 0.4102 | 0.40204 | 0.38469 | 0.36837 | 0.28878 | 0.25204 | 0.22653 | 0.19184 | 0.18265 | 0.17347 | 0.16735 | 0.15306 | 0.14082 | 0.12245 | 0.1102 | 0.086735 | 0.066327 | -0.043878 | -0.076531 | -0.081633
|  | KINLOCH RANNOCH | CF |  |  |  |  | -0.0091837 | -0.0071429 | -0.013265 | -0.020408 | -0.027551 | -0.038776 | -0.042857 | -0.058163 | -0.072449 | -0.076531 | -0.15306 | -0.23163 | -0.27857 | 0.46327 | 0.46429 | 0.45714 | 0.44796 | 0.44082 | 0.43265 | 0.42551 | 0.41224 | 0.39796 | 0.39694 | 0.33265 | 0.24898 | 0.17041 | 0.19286 | 0.18878 | 0.18163 | 0.17449 | 0.16531 | 0.15408 | 0.14694 | 0.12959 | 0.11429 | 0.11122 | 0.034694 | -0.043878 | -0.087755
| GRUDIE BRIDGE | KINLOCHEWE | MINIMUM HEADROOM | NH 03723 62321 | YES | NO | 0.361 | 0.49871 | 0.47932 | 0.45993 | 0.42728 | 0.40993 | 0.38136 | 0.35381 | 0.31095 | 0.2732 | 0.2385 | 0.19156 | 0.1732 | 0.16605 | 0.58952 | 0.5783 | 0.56401 | 0.54258 | 0.53034 | 0.50687 | 0.49054 | 0.46095 | 0.43034 | 0.40789 | 0.37116 | 0.34667 | 0.26401 | 0.5232 | 0.50687 | 0.48748 | 0.45687 | 0.44258 | 0.41197 | 0.38952 | 0.34769 | 0.30789 | 0.27728 | 0.23442 | 0.21503 | 0.20993
|  | KINLOCHEWE | EE |  |  |  |  | 0.49871 | 0.47932 | 0.45993 | 0.42728 | 0.40993 | 0.38136 | 0.35381 | 0.31095 | 0.2732 | 0.2385 | 0.19156 | 0.18034 | 0.1732 | 0.58952 | 0.5783 | 0.56401 | 0.54258 | 0.53034 | 0.50687 | 0.49054 | 0.46095 | 0.43034 | 0.40789 | 0.37116 | 0.34667 | 0.31095 | 0.5232 | 0.50687 | 0.48748 | 0.45687 | 0.44258 | 0.41197 | 0.38952 | 0.34769 | 0.30789 | 0.27728 | 0.23442 | 0.2232 | 0.21605
|  | KINLOCHEWE | HT |  |  |  |  | 0.50993 | 0.49564 | 0.47932 | 0.45891 | 0.44258 | 0.41809 | 0.40381 | 0.37218 | 0.34054 | 0.32218 | 0.21911 | 0.1732 | 0.16605 | 0.60279 | 0.5936 | 0.58238 | 0.56707 | 0.55585 | 0.53952 | 0.53136 | 0.50993 | 0.48748 | 0.47626 | 0.40483 | 0.37524 | 0.37116 | 0.53646 | 0.52422 | 0.50687 | 0.4885 | 0.47116 | 0.44769 | 0.43544 | 0.40585 | 0.3732 | 0.35993 | 0.25891 | 0.21503 | 0.20993
|  | KINLOCHEWE | HE |  |  |  |  | 0.50993 | 0.49973 | 0.48544 | 0.47013 | 0.45483 | 0.43136 | 0.42218 | 0.39462 | 0.36299 | 0.35177 | 0.23748 | 0.20585 | 0.20075 | 0.60075 | 0.59156 | 0.58238 | 0.57218 | 0.56095 | 0.5436 | 0.53646 | 0.51911 | 0.49462 | 0.48544 | 0.40177 | 0.36503 | 0.33136 | 0.53646 | 0.52728 | 0.51299 | 0.49667 | 0.48238 | 0.46197 | 0.45177 | 0.42524 | 0.39769 | 0.38442 | 0.2783 | 0.24769 | 0.24156
|  | KINLOCHEWE | CF |  |  |  |  | 0.51401 | 0.50177 | 0.4936 | 0.48136 | 0.46197 | 0.45381 | 0.4334 | 0.42626 | 0.40585 | 0.38646 | 0.29769 | 0.23544 | 0.20177 | 0.60381 | 0.59462 | 0.5885 | 0.58136 | 0.56605 | 0.56095 | 0.54258 | 0.53748 | 0.5232 | 0.50891 | 0.43034 | 0.35483 | 0.26401 | 0.54156 | 0.53034 | 0.52116 | 0.50993 | 0.49054 | 0.48238 | 0.45993 | 0.45483 | 0.4385 | 0.42013 | 0.33034 | 0.27422 | 0.24462
| KINLOCHLEVEN | KINLOCHLEVEN | MINIMUM HEADROOM | NN 19285 62002 | NO | YES | 0.053 | 2.0519 | 2.008 | 1.9529 | 1.907 | 1.8488 | 1.808 | 1.7417 | 1.6488 | 1.5529 | 1.4651 | 1.36 | 1.31 | 1.2947 | 2.5029 | 2.4733 | 2.4366 | 2.4029 | 2.36 | 2.3335 | 2.2866 | 2.2274 | 2.1631 | 2.1049 | 2.0274 | 1.9723 | 1.8019 | 2.3325 | 2.2917 | 2.2396 | 2.1947 | 2.1396 | 2.1019 | 2.0366 | 1.9498 | 1.8621 | 1.7794 | 1.6866 | 1.6386 | 1.6264
|  | KINLOCHLEVEN | EE |  |  |  |  | 2.0519 | 2.008 | 1.9529 | 1.907 | 1.8488 | 1.808 | 1.7417 | 1.6488 | 1.5529 | 1.4651 | 1.36 | 1.3376 | 1.3253 | 2.5029 | 2.4733 | 2.4366 | 2.4029 | 2.36 | 2.3335 | 2.2866 | 2.2274 | 2.1631 | 2.1049 | 2.0274 | 1.9723 | 1.8876 | 2.3325 | 2.2917 | 2.2396 | 2.1947 | 2.1396 | 2.1019 | 2.0366 | 1.9498 | 1.8621 | 1.7794 | 1.6866 | 1.6662 | 1.6519
|  | KINLOCHLEVEN | HT |  |  |  |  | 2.0753 | 2.0264 | 1.9835 | 1.9519 | 1.907 | 1.8458 | 1.7713 | 1.709 | 1.6549 | 1.607 | 1.3998 | 1.31 | 1.2947 | 2.5213 | 2.4906 | 2.4621 | 2.4396 | 2.41 | 2.3743 | 2.3325 | 2.2968 | 2.2611 | 2.2294 | 2.0876 | 2.0284 | 2.0192 | 2.356 | 2.31 | 2.2702 | 2.2386 | 2.1978 | 2.1427 | 2.0733 | 2.0192 | 1.9692 | 1.9223 | 1.7243 | 1.6386 | 1.6264
|  | KINLOCHLEVEN | HE |  |  |  |  | 2.0753 | 2.0376 | 2.0009 | 1.9743 | 1.9386 | 1.91 | 1.8651 | 1.8172 | 1.756 | 1.6927 | 1.4529 | 1.3998 | 1.3927 | 2.5213 | 2.4937 | 2.4692 | 2.4509 | 2.4213 | 2.4019 | 2.3682 | 2.3406 | 2.3019 | 2.258 | 2.0896 | 2.0172 | 1.9386 | 2.356 | 2.3182 | 2.2855 | 2.2621 | 2.2253 | 2.1988 | 2.1539 | 2.1121 | 2.056 | 1.9978 | 1.7764 | 1.7264 | 1.7182
|  | KINLOCHLEVEN | CF |  |  |  |  | 2.0774 | 2.0549 | 2.0274 | 1.9978 | 1.9825 | 1.9498 | 1.9264 | 1.8906 | 1.8447 | 1.8182 | 1.5978 | 1.4774 | 1.409 | 2.5243 | 2.508 | 2.4886 | 2.4662 | 2.4539 | 2.4315 | 2.4131 | 2.3845 | 2.3488 | 2.3325 | 2.1549 | 1.9937 | 1.8019 | 2.357 | 2.3366 | 2.3121 | 2.2815 | 2.2672 | 2.2366 | 2.2141 | 2.1774 | 2.1335 | 2.1131 | 1.9039 | 1.7896 | 1.7345
| FORT WILLIAM | KINLOCHMOIDART | MINIMUM HEADROOM | NM 71407 72091 | YES | NO | 0 | 0.93776 | 0.93571 | 0.92857 | 0.92755 | 0.91939 | 0.91735 | 0.91735 | 0.91735 | 0.91531 | 0.91327 | 0.9102 | 0.90918 | 0.90918 | 0.95204 | 0.95102 | 0.9449 | 0.94286 | 0.93571 | 0.94082 | 0.93571 | 0.93571 | 0.93571 | 0.94082 | 0.93673 | 0.93571 | 0.93469 | 0.94796 | 0.94694 | 0.9398 | 0.93776 | 0.93061 | 0.92959 | 0.92959 | 0.92959 | 0.92857 | 0.92755 | 0.92245 | 0.92041 | 0.92041
|  | KINLOCHMOIDART | EE |  |  |  |  | 0.93776 | 0.93673 | 0.92857 | 0.92755 | 0.91939 | 0.91735 | 0.92347 | 0.91735 | 0.91531 | 0.91327 | 0.9102 | 0.90918 | 0.91122 | 0.95204 | 0.95204 | 0.9449 | 0.94286 | 0.93571 | 0.94082 | 0.94592 | 0.94184 | 0.94286 | 0.94082 | 0.93673 | 0.93673 | 0.93571 | 0.94796 | 0.94796 | 0.9398 | 0.93776 | 0.93061 | 0.92959 | 0.93571 | 0.93061 | 0.92959 | 0.92755 | 0.92245 | 0.92041 | 0.92347
|  | KINLOCHMOIDART | HT |  |  |  |  | 0.9449 | 0.93571 | 0.93673 | 0.93571 | 0.92755 | 0.92653 | 0.91735 | 0.91735 | 0.91633 | 0.92143 | 0.9102 | 0.90918 | 0.90918 | 0.95918 | 0.95102 | 0.95204 | 0.95102 | 0.94286 | 0.94286 | 0.93571 | 0.94082 | 0.9398 | 0.9449 | 0.93673 | 0.93571 | 0.93571 | 0.9551 | 0.94694 | 0.94796 | 0.94694 | 0.93776 | 0.93776 | 0.92959 | 0.92959 | 0.92857 | 0.93469 | 0.92245 | 0.92041 | 0.92041
|  | KINLOCHMOIDART | HE |  |  |  |  | 0.9449 | 0.93571 | 0.93673 | 0.93673 | 0.92959 | 0.92755 | 0.91939 | 0.91837 | 0.91735 | 0.92245 | 0.91122 | 0.91327 | 0.91224 | 0.95918 | 0.95102 | 0.95204 | 0.95204 | 0.9449 | 0.94286 | 0.93571 | 0.94082 | 0.94082 | 0.94592 | 0.93776 | 0.9398 | 0.93673 | 0.9551 | 0.94694 | 0.94796 | 0.94796 | 0.94082 | 0.93776 | 0.93061 | 0.93061 | 0.92959 | 0.93469 | 0.92449 | 0.92653 | 0.92449
|  | KINLOCHMOIDART | CF |  |  |  |  | 0.9449 | 0.93776 | 0.93571 | 0.93571 | 0.93571 | 0.92857 | 0.92653 | 0.91837 | 0.91837 | 0.91837 | 0.91939 | 0.91327 | 0.91327 | 0.95918 | 0.95204 | 0.95102 | 0.95102 | 0.95102 | 0.94388 | 0.94286 | 0.93571 | 0.93571 | 0.94082 | 0.94286 | 0.93673 | 0.93469 | 0.9551 | 0.94796 | 0.94694 | 0.94694 | 0.94694 | 0.9398 | 0.93776 | 0.93061 | 0.93061 | 0.93061 | 0.93163 | 0.92755 | 0.92551
| ELGIN | KINLOSS | MINIMUM HEADROOM | NJ 06695 61740 | NO | YES | 0.088 | 11.17 | 11.0098 | 10.7874 | 10.5415 | 10.268 | 9.9782 | 9.6292 | 9.2068 | 8.8405 | 8.5098 | 6.7129 | 5.868 | 5.7374 | 12.47 | 12.3343 | 12.1803 | 12.0078 | 11.819 | 11.6119 | 11.3578 | 11.0456 | 10.7762 | 10.5384 | 9.1649 | 8.5496 | 8.4527 | 12.3593 | 12.194 | 11.9828 | 11.745 | 11.4838 | 11.2073 | 10.8726 | 10.4675 | 10.1175 | 9.8022 | 8.0706 | 7.2624 | 7.1399
|  | KINLOSS | EE |  |  |  |  | 11.17 | 11.0098 | 10.7874 | 10.5415 | 10.268 | 9.9782 | 9.6292 | 9.2068 | 8.8405 | 8.5098 | 7.3986 | 7.168 | 7.1058 | 12.47 | 12.3343 | 12.1803 | 12.0078 | 11.819 | 11.6119 | 11.3578 | 11.0456 | 10.7762 | 10.5384 | 9.7384 | 9.5915 | 9.5405 | 12.3593 | 12.194 | 11.9828 | 11.745 | 11.4838 | 11.2073 | 10.8726 | 10.4675 | 10.1175 | 9.8022 | 8.744 | 8.5267 | 8.4685
|  | KINLOSS | HT |  |  |  |  | 11.2476 | 11.1405 | 11.0211 | 10.8547 | 10.669 | 10.4456 | 10.1782 | 9.8772 | 9.5762 | 9.266 | 7.8803 | 7.2313 | 7.1211 | 12.5578 | 12.4609 | 12.3547 | 12.2323 | 12.1047 | 11.9496 | 11.769 | 11.5598 | 11.3527 | 11.1374 | 10.117 | 9.6517 | 9.5792 | 12.4695 | 12.3542 | 12.2216 | 12.0522 | 11.8746 | 11.6665 | 11.4134 | 11.1277 | 10.843 | 10.5471 | 9.2073 | 8.5889 | 8.4981
|  | KINLOSS | HE |  |  |  |  | 11.2343 | 11.1282 | 10.9496 | 10.7445 | 10.5098 | 10.2323 | 9.9007 | 9.5007 | 9.1078 | 8.6915 | 6.7129 | 5.868 | 5.7374 | 12.5333 | 12.418 | 12.2945 | 12.1507 | 11.9905 | 11.7854 | 11.5394 | 11.2415 | 10.9445 | 10.6354 | 9.1649 | 8.5496 | 8.4527 | 12.4379 | 12.2961 | 12.1379 | 11.9389 | 11.7144 | 11.4471 | 11.1297 | 10.745 | 10.3685 | 9.9695 | 8.0706 | 7.2624 | 7.1399
|  | KINLOSS | CF |  |  |  |  | 11.269 | 11.2058 | 11.1333 | 11.0343 | 10.8925 | 10.7354 | 10.5609 | 10.3282 | 10.1139 | 9.8945 | 8.4578 | 7.1139 | 6.1782 | 12.5772 | 12.5109 | 12.4343 | 12.3466 | 12.2507 | 12.1415 | 12.02 | 11.8517 | 11.6874 | 11.5241 | 10.4374 | 9.4364 | 8.7425 | 12.491 | 12.4134 | 12.3195 | 12.2104 | 12.0848 | 11.9308 | 11.7634 | 11.5399 | 11.3338 | 11.1236 | 9.7399 | 8.4491 | 7.5573
| BRACO | KIPPEN | MINIMUM HEADROOM | NS 66376 95628 | NO | YES | 0.545 | 3.228 | 3.0974 | 2.9361 | 2.7882 | 2.6015 | 2.4025 | 2.2106 | 1.9453 | 1.6943 | 1.4688 | 0.85145 | 0.46064 | 0.23411 | 4.5382 | 4.4933 | 4.4361 | 4.3851 | 4.3178 | 4.2453 | 4.1831 | 4.0178 | 3.8453 | 3.7025 | 3.3096 | 3.0841 | 2.5474 | 4.227 | 4.1106 | 3.9657 | 3.8372 | 3.6668 | 3.4861 | 3.3198 | 3.079 | 2.8474 | 2.6484 | 2.1178 | 1.7974 | 1.6168
|  | KIPPEN | EE |  |  |  |  | 3.228 | 3.0974 | 2.9361 | 2.7882 | 2.6015 | 2.4025 | 2.2106 | 1.9453 | 1.6943 | 1.4688 | 0.85145 | 0.61778 | 0.43513 | 4.5382 | 4.4933 | 4.4361 | 4.3851 | 4.3178 | 4.2453 | 4.1831 | 4.0178 | 3.8453 | 3.7025 | 3.3096 | 3.1055 | 2.8249 | 4.227 | 4.1106 | 3.9657 | 3.8372 | 3.6668 | 3.4861 | 3.3198 | 3.079 | 2.8474 | 2.6484 | 2.1178 | 1.93 | 1.778
|  | KIPPEN | HT |  |  |  |  | 3.2841 | 3.1647 | 3.0402 | 2.8872 | 2.7321 | 2.5566 | 2.4055 | 2.1933 | 1.9892 | 1.8208 | 0.92798 | 0.46064 | 0.23411 | 4.5627 | 4.527 | 4.4851 | 4.4351 | 4.3851 | 4.3249 | 4.2739 | 4.1994 | 4.1127 | 4.0198 | 3.4361 | 3.1627 | 3.028 | 4.28 | 4.1749 | 4.0627 | 3.929 | 3.7953 | 3.6423 | 3.5127 | 3.327 | 3.1433 | 3.0015 | 2.1953 | 1.7974 | 1.6168
|  | KIPPEN | HE |  |  |  |  | 3.2841 | 3.1882 | 3.0882 | 2.9617 | 2.8321 | 2.6882 | 2.5586 | 2.3657 | 2.178 | 2.0321 | 1.0157 | 0.64839 | 0.47084 | 4.5586 | 4.5198 | 4.479 | 4.431 | 4.381 | 4.3198 | 4.2657 | 4.1882 | 4.1086 | 3.9882 | 3.3494 | 3.0841 | 2.8433 | 4.277 | 4.1923 | 4.1045 | 3.9943 | 3.8841 | 3.7566 | 3.6423 | 3.4668 | 3.2953 | 3.1402 | 2.2515 | 1.9198 | 1.8198
|  | KIPPEN | CF |  |  |  |  | 3.2902 | 3.2117 | 3.1208 | 3.0331 | 2.9249 | 2.8086 | 2.6841 | 2.5821 | 2.4515 | 2.3157 | 1.6341 | 0.979 | 0.59125 | 4.5627 | 4.529 | 4.4933 | 4.4566 | 4.4127 | 4.3637 | 4.3147 | 4.2627 | 4.2055 | 4.1453 | 3.7096 | 3.1106 | 2.5474 | 4.2841 | 4.2117 | 4.1351 | 4.0586 | 3.9647 | 3.8627 | 3.7494 | 3.6566 | 3.5372 | 3.4137 | 2.8066 | 2.2055 | 1.8586
| THURSO | KIRKWALL | MINIMUM HEADROOM | HY 44669 10987 | NO | NO | 4.624 | 3.7249 | 2.9494 | 1.6565 | 0.12183 | -1.2098 | -3.5792 | -4.5129 | -5.5731 | -6.522 | -8.1782 | -15.9925 | -21.6506 | -26.8833 | 8.18 | 7.481 | 6.1698 | 4.5504 | 3.2575 | 0.61979 | -0.18429 | -1.0863 | -2.1231 | -3.9486 | -11.8506 | -18.5874 | -25.0098 | 6.2647 | 5.4943 | 4.1218 | 2.4698 | 1.1677 | -1.5129 | -2.4251 | -3.4588 | -4.4996 | -6.4659 | -14.918 | -21.7945 | -28.2516
|  | KIRKWALL | EE |  |  |  |  | 3.8739 | 3.0871 | 2.2575 | 1.3463 | -0.20878 | -1.9476 | -2.9129 | -3.8016 | -5.1486 | -6.3231 | -11.6476 | -16.5996 | -18.7078 | 8.4198 | 7.6912 | 6.9463 | 6.1198 | 4.5504 | 2.7228 | 1.779 | 1.0565 | -0.22511 | -1.2669 | -6.0843 | -12.1435 | -15.2098 | 6.4402 | 5.6361 | 4.8331 | 3.9514 | 2.3402 | 0.45958 | -0.5394 | -1.3874 | -2.7986 | -3.9772 | -9.17 | -15.2812 | -17.7557
|  | KIRKWALL | HT |  |  |  |  | 3.7249 | 2.9494 | 1.6565 | 0.12183 | -1.2098 | -3.5792 | -4.5129 | -5.5731 | -6.522 | -7.8567 | -12.4078 | -18.6027 | -23.4823 | 8.18 | 7.481 | 6.1698 | 4.5504 | 3.2575 | 0.61979 | -0.18429 | -1.0863 | -1.8527 | -2.9037 | -7.2751 | -14.4925 | -20.5925 | 6.2647 | 5.4943 | 4.1218 | 2.4698 | 1.1677 | -1.5129 | -2.4251 | -3.4588 | -4.3496 | -5.5598 | -10.2986 | -17.6925 | -23.8506
|  | KIRKWALL | HE |  |  |  |  | 4.0035 | 3.2555 | 2.1769 | 0.80856 | -0.49552 | -2.8006 | -3.9384 | -5.1945 | -6.3639 | -8.1782 | -15.9925 | -21.6506 | -26.8833 | 8.48 | 7.7871 | 6.6861 | 5.232 | 3.9096 | 1.3198 | 0.18203 | -1.0016 | -2.1231 | -3.9486 | -11.8506 | -18.5874 | -25.0098 | 6.5392 | 5.7943 | 4.6473 | 3.1688 | 1.8382 | -0.77715 | -1.9772 | -3.2812 | -4.4996 | -6.4659 | -14.918 | -21.7945 | -28.2516
|  | KIRKWALL | CF |  |  |  |  | 4.7361 | 4.2402 | 3.7116 | 3.231 | 2.3698 | 1.332 | 0.55448 | -0.16287 | -0.91287 | -1.8129 | -6.7731 | -10.6496 | -12.4067 | 9.2728 | 8.8075 | 8.3249 | 7.8882 | 6.9943 | 5.8637 | 5.0739 | 4.3708 | 3.6606 | 2.8075 | -1.6761 | -5.6506 | -8.6527 | 7.2463 | 6.7708 | 6.2718 | 5.8147 | 4.9198 | 3.7994 | 2.9994 | 2.2535 | 1.4984 | 0.58918 | -4.2986 | -8.3782 | -10.2302
| BROADFORD | KISHORNHILL | MINIMUM HEADROOM | NG 88304 40591 | YES | YES | 0.644 | -0.17596 | -0.18107 | -0.18923 | -0.20147 | -0.21576 | -0.22596 | -0.24535 | -0.25453 | -0.27188 | -0.28515 | -0.31984 | -0.33107 | -0.33209 | -0.30147 | -0.28821 | -0.29127 | -0.29535 | -0.30045 | -0.30249 | -0.30862 | -0.31372 | -0.31882 | -0.32392 | -0.33515 | -0.34331 | -0.34943 | -0.12698 | -0.13311 | -0.13821 | -0.15249 | -0.1678 | -0.17596 | -0.19535 | -0.20249 | -0.21984 | -0.23515 | -0.26576 | -0.27698 | -0.27902
|  | KISHORNHILL | EE |  |  |  |  | -0.1729 | -0.18107 | -0.18923 | -0.20147 | -0.21576 | -0.22596 | -0.24535 | -0.25453 | -0.27188 | -0.28515 | -0.31984 | -0.32494 | -0.328 | -0.28515 | -0.28821 | -0.29127 | -0.29535 | -0.30045 | -0.30249 | -0.30862 | -0.31372 | -0.31882 | -0.32392 | -0.33413 | -0.33719 | -0.34127 | -0.12392 | -0.13311 | -0.13821 | -0.15249 | -0.1678 | -0.17596 | -0.19535 | -0.20249 | -0.21984 | -0.23515 | -0.26576 | -0.27188 | -0.27494
|  | KISHORNHILL | HT |  |  |  |  | -0.17596 | -0.17392 | -0.18311 | -0.19025 | -0.19841 | -0.20964 | -0.22392 | -0.23209 | -0.24739 | -0.26168 | -0.3076 | -0.33107 | -0.33209 | -0.30147 | -0.28515 | -0.28719 | -0.29025 | -0.29433 | -0.29739 | -0.30045 | -0.30453 | -0.30964 | -0.3127 | -0.33107 | -0.33617 | -0.33923 | -0.12698 | -0.12494 | -0.13311 | -0.14025 | -0.14841 | -0.15964 | -0.17188 | -0.18107 | -0.19535 | -0.21168 | -0.25556 | -0.27698 | -0.27902
|  | KISHORNHILL | HE |  |  |  |  | -0.17596 | -0.1729 | -0.18004 | -0.18719 | -0.19535 | -0.20147 | -0.2127 | -0.2229 | -0.23617 | -0.25045 | -0.30351 | -0.31882 | -0.3229 | -0.30147 | -0.28515 | -0.28719 | -0.29127 | -0.29331 | -0.29739 | -0.30045 | -0.30556 | -0.31066 | -0.31474 | -0.33515 | -0.34331 | -0.34943 | -0.12698 | -0.12392 | -0.13107 | -0.13719 | -0.14433 | -0.15147 | -0.16372 | -0.1729 | -0.18617 | -0.20045 | -0.25147 | -0.26678 | -0.2729
|  | KISHORNHILL | CF |  |  |  |  | -0.1678 | -0.17698 | -0.178 | -0.18311 | -0.18923 | -0.19331 | -0.20147 | -0.21066 | -0.21576 | -0.2229 | -0.26168 | -0.30147 | -0.31882 | -0.29433 | -0.28617 | -0.28617 | -0.28821 | -0.28923 | -0.29331 | -0.29535 | -0.29841 | -0.30045 | -0.30249 | -0.31984 | -0.33821 | -0.34841 | -0.11882 | -0.128 | -0.12902 | -0.13515 | -0.13821 | -0.14331 | -0.15249 | -0.16168 | -0.16372 | -0.1729 | -0.21168 | -0.25249 | -0.26882
| BROADFORD | KYLE | MINIMUM HEADROOM | NG 76499 27247 | NO | YES | 0.029 | 4.7071 | 6.3512 | 6.2941 | 6.2257 | 6.1747 | 6.0951 | 6.0114 | 5.8798 | 5.7553 | 5.6829 | 5.4757 | 5.3971 | 5.3696 | 4.899 | 6.5563 | 6.5176 | 6.4676 | 6.4359 | 6.3798 | 6.3227 | 6.2349 | 6.1522 | 6.1104 | 5.9431 | 5.8594 | 5.5727 | 4.5704 | 6.2165 | 6.1645 | 6.0982 | 6.0522 | 5.9798 | 5.9002 | 5.7788 | 5.6665 | 5.6053 | 5.4145 | 5.341 | 5.3145
|  | KYLE | EE |  |  |  |  | 4.7071 | 6.3512 | 6.2941 | 6.2257 | 6.1747 | 6.0951 | 6.0114 | 5.8798 | 5.7553 | 5.6829 | 5.4757 | 5.4369 | 5.4043 | 4.899 | 6.5563 | 6.5176 | 6.4676 | 6.4359 | 6.3798 | 6.3227 | 6.2349 | 6.1522 | 6.1104 | 5.9431 | 5.8594 | 5.7216 | 4.5704 | 6.2165 | 6.1645 | 6.0982 | 6.0522 | 5.9798 | 5.9002 | 5.7788 | 5.6665 | 5.6053 | 5.4145 | 5.3778 | 5.3471
|  | KYLE | HT |  |  |  |  | 4.7378 | 6.388 | 6.3349 | 6.291 | 6.242 | 6.1563 | 6.0614 | 5.9778 | 5.9033 | 5.8318 | 5.538 | 5.3971 | 5.3696 | 4.9214 | 6.5859 | 6.5522 | 6.5298 | 6.4971 | 6.4441 | 6.389 | 6.341 | 6.292 | 6.2431 | 6.04 | 5.9482 | 5.9298 | 4.599 | 6.2492 | 6.2022 | 6.1604 | 6.1176 | 6.041 | 5.9563 | 5.8829 | 5.8155 | 5.7492 | 5.4716 | 5.341 | 5.3145
|  | KYLE | HE |  |  |  |  | 4.7357 | 6.3971 | 6.3502 | 6.3206 | 6.2829 | 6.2329 | 6.1706 | 6.1053 | 6.0247 | 5.9492 | 5.6033 | 5.5186 | 5.489 | 4.9194 | 6.5869 | 6.5563 | 6.5359 | 6.5094 | 6.4737 | 6.4278 | 6.3869 | 6.3339 | 6.2808 | 6.0329 | 5.9186 | 5.7982 | 4.5969 | 6.2573 | 6.2155 | 6.188 | 6.1533 | 6.1063 | 6.0482 | 5.992 | 5.9196 | 5.8512 | 5.5369 | 5.4471 | 5.4124
|  | KYLE | CF |  |  |  |  | 4.7449 | 6.4012 | 6.3727 | 6.3471 | 6.3084 | 6.2778 | 6.2359 | 6.1859 | 6.1522 | 6.0931 | 5.8084 | 5.6257 | 5.5022 | 4.9265 | 6.5941 | 6.5757 | 6.5584 | 6.5298 | 6.5053 | 6.4737 | 6.4339 | 6.4033 | 6.3635 | 6.1206 | 5.8778 | 5.5727 | 4.6051 | 6.2665 | 6.24 | 6.2155 | 6.1798 | 6.1522 | 6.1124 | 6.0665 | 6.0349 | 5.9808 | 5.7145 | 5.5492 | 5.4308
| LAIRG | LAIRG | MINIMUM HEADROOM | NC 58798 07111 | YES | NO | 0.086 | -0.32502 | -0.38625 | -0.45462 | 1.7086 | 1.6484 | 1.5668 | 1.4546 | 1.2923 | 1.1791 | 1.0372 | 0.76375 | 0.66477 | 0.62804 | 0.18824 | 0.15151 | 0.10763 | 2.3015 | 2.2638 | 2.2086 | 2.1372 | 2.0352 | 1.9719 | 1.8903 | 1.7066 | 1.6362 | 1.4576 | -0.029106 | -0.08829 | -0.15258 | 2.0189 | 1.9566 | 1.8791 | 1.775 | 1.6219 | 1.5168 | 1.3831 | 1.1219 | 1.0291 | 0.99947
|  | LAIRG | EE |  |  |  |  | -0.32502 | -0.38625 | -0.45462 | 1.7086 | 1.6484 | 1.5668 | 1.4546 | 1.2923 | 1.1791 | 1.0372 | 0.76375 | 0.70253 | 0.6862 | 0.18824 | 0.15151 | 0.10763 | 2.3015 | 2.2638 | 2.2086 | 2.1372 | 2.0352 | 1.9719 | 1.8903 | 1.7066 | 1.6362 | 1.5505 | -0.029106 | -0.08829 | -0.15258 | 2.0189 | 1.9566 | 1.8791 | 1.775 | 1.6219 | 1.5168 | 1.3831 | 1.1219 | 1.0648 | 1.0454
|  | LAIRG | HT |  |  |  |  | -0.31278 | -0.36176 | -0.42094 | 1.7627 | 1.7025 | 1.5862 | 1.478 | 1.3413 | 1.2576 | 1.1689 | 0.83518 | 0.66477 | 0.62804 | 0.21069 | 0.18008 | 0.14844 | 2.3576 | 2.3229 | 2.2597 | 2.2107 | 2.127 | 2.076 | 2.0148 | 1.7842 | 1.6893 | 1.6678 | -0.01482 | -0.067882 | -0.12094 | 2.0689 | 2.0117 | 1.9076 | 1.8138 | 1.6903 | 1.6086 | 1.5219 | 1.1882 | 1.0291 | 0.99947
|  | LAIRG | HE |  |  |  |  | -0.30564 | -0.34339 | -0.38625 | 1.8117 | 1.7668 | 1.7056 | 1.6525 | 1.5423 | 1.4423 | 1.3311 | 0.86783 | 0.76273 | 0.75049 | 0.21681 | 0.18518 | 0.15967 | 2.3709 | 2.3413 | 2.2954 | 2.2689 | 2.1974 | 2.1372 | 2.0678 | 1.7852 | 1.6893 | 1.6107 | -0.0076776 | -0.048494 | -0.090331 | 2.1097 | 2.0668 | 2.0076 | 1.9556 | 1.8525 | 1.7586 | 1.6576 | 1.2311 | 1.1342 | 1.1219
|  | LAIRG | CF |  |  |  |  | -0.2689 | -0.30462 | -0.35156 | 1.8638 | 1.8138 | 1.774 | 1.7199 | 1.6842 | 1.6066 | 1.526 | 1.2005 | 0.93416 | 0.76375 | 0.23926 | 0.21375 | 0.1811 | 2.4097 | 2.374 | 2.3484 | 2.3097 | 2.2831 | 2.2342 | 2.1791 | 1.9505 | 1.6913 | 1.4576 | 0.020894 | -0.0138 | -0.056657 | 2.1597 | 2.1168 | 2.0791 | 2.0321 | 1.9944 | 1.924 | 1.8495 | 1.5454 | 1.2852 | 1.127
| MYBSTER 1 | LATHERON | MINIMUM HEADROOM | ND 19924 33627 | YES | NO | 0.177 | 1.0665 | 0.9736 | 0.88278 | 0.77972 | 0.67462 | 0.56135 | 0.44707 | 0.27564 | 0.11849 | -0.039669 | -0.356 | -0.46518 | -0.506 | 1.7338 | 1.6818 | 1.6318 | 1.5593 | 1.4889 | 1.4073 | 1.344 | 1.2246 | 1.1175 | 1.0205 | 0.85727 | 0.77462 | 0.46237 | 1.3838 | 1.2971 | 1.2124 | 1.1062 | 0.99911 | 0.8787 | 0.7736 | 0.60013 | 0.43686 | 0.28686 | 0.042984 | -0.046812 | -0.078445
|  | LATHERON | EE |  |  |  |  | 1.0665 | 0.9736 | 0.88278 | 0.77972 | 0.67462 | 0.56135 | 0.44707 | 0.27564 | 0.11849 | -0.039669 | -0.356 | -0.4162 | -0.43457 | 1.7338 | 1.6818 | 1.6318 | 1.5593 | 1.4889 | 1.4073 | 1.344 | 1.2246 | 1.1175 | 1.0205 | 0.85727 | 0.77462 | 0.62972 | 1.3838 | 1.2971 | 1.2124 | 1.1062 | 0.99911 | 0.8787 | 0.7736 | 0.60013 | 0.43686 | 0.28686 | 0.042984 | -0.011098 | -0.035588
|  | LATHERON | HT |  |  |  |  | 1.093 | 1.0093 | 0.91849 | 0.83482 | 0.75217 | 0.63686 | 0.51645 | 0.3787 | 0.28482 | 0.17053 | -0.25089 | -0.46518 | -0.506 | 1.7614 | 1.7205 | 1.6746 | 1.6348 | 1.595 | 1.5287 | 1.4603 | 1.3705 | 1.3256 | 1.2511 | 0.96849 | 0.85523 | 0.83686 | 1.4277 | 1.3542 | 1.2685 | 1.192 | 1.1236 | 1.0144 | 0.90319 | 0.76645 | 0.68788 | 0.57258 | 0.14196 | -0.046812 | -0.078445
|  | LATHERON | HE |  |  |  |  | 1.093 | 1.0348 | 0.96747 | 0.90523 | 0.84911 | 0.77768 | 0.68686 | 0.56441 | 0.44707 | 0.35217 | -0.24783 | -0.356 | -0.37538 | 1.7614 | 1.7287 | 1.6899 | 1.6511 | 1.6195 | 1.5685 | 1.5134 | 1.4318 | 1.3522 | 1.3042 | 0.91645 | 0.83278 | 0.69298 | 1.4277 | 1.3746 | 1.3032 | 1.244 | 1.194 | 1.1185 | 1.0328 | 0.91033 | 0.79298 | 0.71543 | 0.14298 | 0.074616 | 0.05829
|  | LATHERON | CF |  |  |  |  | 1.0971 | 1.043 | 0.994 | 0.94094 | 0.88176 | 0.83278 | 0.76849 | 0.70217 | 0.62053 | 0.53482 | 0.19196 | -0.092731 | -0.31212 | 1.7654 | 1.7338 | 1.7052 | 1.6787 | 1.6369 | 1.6124 | 1.5665 | 1.5154 | 1.4593 | 1.395 | 1.1205 | 0.82156 | 0.46237 | 1.4307 | 1.3767 | 1.3328 | 1.2848 | 1.2205 | 1.1797 | 1.1144 | 1.0481 | 0.96441 | 0.87972 | 0.52462 | 0.25421 | 0.094004
| FIDDES | LAURENCEKIRK | MINIMUM HEADROOM | NO 70915 71028 | NO | NO | 2.822 | 7.4879 | 7.2512 | 6.9338 | 6.5512 | 6.1267 | 5.5042 | 4.7512 | 3.9134 | 2.9542 | 1.8012 | -0.045763 | -0.69576 | -0.83658 | 8.7726 | 8.6338 | 8.4359 | 8.191 | 7.9165 | 7.492 | 6.9624 | 6.3553 | 5.6542 | 4.8053 | 3.6185 | 3.2246 | 2.644 | 8.0854 | 7.8527 | 7.5609 | 7.2007 | 6.7986 | 6.3088 | 5.6354 | 4.8823 | 4.018 | 2.9905 | 1.368 | 0.79454 | 0.67311
|  | LAURENCEKIRK | EE |  |  |  |  | 7.4879 | 7.2512 | 6.9338 | 6.5512 | 6.1267 | 5.6073 | 4.8522 | 4.0736 | 3.2563 | 2.6502 | -0.045763 | -0.60393 | -0.72842 | 8.7726 | 8.6338 | 8.4359 | 8.191 | 7.9165 | 7.5532 | 7.0257 | 6.4695 | 5.8767 | 5.4073 | 3.6185 | 3.2246 | 2.8573 | 8.0854 | 7.8527 | 7.5609 | 7.2007 | 6.7986 | 6.3088 | 5.6435 | 4.9405 | 4.215 | 3.7333 | 1.368 | 0.87618 | 0.76903
|  | LAURENCEKIRK | HT |  |  |  |  | 7.5379 | 7.2869 | 6.9818 | 6.6093 | 6.1981 | 5.5042 | 4.7512 | 3.9134 | 2.9542 | 1.8012 | -0.00086531 | -0.69576 | -0.83658 | 8.7889 | 8.6522 | 8.4553 | 8.2267 | 7.9889 | 7.492 | 6.9624 | 6.3553 | 5.6542 | 4.8053 | 3.8002 | 3.4991 | 3.4134 | 8.1323 | 7.8935 | 7.6047 | 7.2619 | 6.9201 | 6.3109 | 5.6354 | 4.8823 | 4.018 | 2.9905 | 1.415 | 0.79454 | 0.67311
|  | LAURENCEKIRK | HE |  |  |  |  | 7.5471 | 7.3818 | 7.1532 | 6.8604 | 6.5746 | 6.0971 | 5.4675 | 4.8206 | 4.1461 | 3.3746 | 1.1083 | 0.2175 | -0.25903 | 8.7971 | 8.6848 | 8.5461 | 8.3573 | 8.1583 | 7.793 | 7.3155 | 6.8053 | 6.2583 | 5.6175 | 3.99 | 3.5512 | 3.0328 | 8.1425 | 7.9803 | 7.767 | 7.4925 | 7.2282 | 6.7874 | 6.2394 | 5.6823 | 5.067 | 4.3629 | 2.319 | 1.5619 | 1.1639
|  | LAURENCEKIRK | CF |  |  |  |  | 7.592 | 7.4757 | 7.3185 | 7.1053 | 6.8563 | 6.5889 | 6.2695 | 5.8879 | 5.5236 | 5.0991 | 2.9359 | 1.3369 | 0.30424 | 8.84 | 8.7726 | 8.6675 | 8.5359 | 8.3746 | 8.1716 | 7.9216 | 7.6104 | 7.3226 | 6.9716 | 5.1859 | 3.7512 | 2.644 | 8.1884 | 8.0762 | 7.9303 | 7.7343 | 7.5068 | 7.2558 | 6.9547 | 6.5925 | 6.2803 | 5.8996 | 3.9496 | 2.5578 | 1.6701
| STORNOWAY | LAXAY | MINIMUM HEADROOM | NB 33424 21925 | YES | YES | 0.067 | -0.71674 | 6.3947 | 6.3028 | 6.2222 | 6.1284 | 6.0182 | 5.9182 | 5.7702 | 5.6304 | 5.5028 | 5.212 | 5.11 | 5.0743 | -0.0085796 | 7.1355 | 7.0814 | 7.0314 | 6.9692 | 6.8988 | 6.8416 | 6.7447 | 6.6508 | 6.5671 | 6.3722 | 6.2702 | 5.9365 | -0.31368 | 6.7998 | 6.7049 | 6.6294 | 6.5335 | 6.4253 | 6.3324 | 6.1865 | 6.0498 | 5.9294 | 5.6692 | 5.5794 | 5.5467
|  | LAXAY | EE |  |  |  |  | -0.71674 | 6.3947 | 6.3028 | 6.2222 | 6.1284 | 6.0182 | 5.9182 | 5.7702 | 5.6304 | 5.5028 | 5.212 | 5.1518 | 5.1284 | -0.0085796 | 7.1355 | 7.0814 | 7.0314 | 6.9692 | 6.8988 | 6.8416 | 6.7447 | 6.6508 | 6.5671 | 6.3722 | 6.2702 | 6.1253 | -0.31368 | 6.7998 | 6.7049 | 6.6294 | 6.5335 | 6.4253 | 6.3324 | 6.1865 | 6.0498 | 5.9294 | 5.6692 | 5.6141 | 5.5926
|  | LAXAY | HT |  |  |  |  | -0.69021 | 6.4314 | 6.3528 | 6.2804 | 6.1967 | 6.1233 | 6.0294 | 5.9192 | 5.809 | 5.7273 | 5.2702 | 5.11 | 5.0743 | 0.012849 | 7.1671 | 7.1243 | 7.0865 | 7.0386 | 6.9998 | 6.9457 | 6.8682 | 6.8008 | 6.76 | 6.4539 | 6.3743 | 6.3549 | -0.28511 | 6.8437 | 6.7682 | 6.7018 | 6.6182 | 6.5518 | 6.461 | 6.3467 | 6.2396 | 6.1692 | 5.7141 | 5.5794 | 5.5467
|  | LAXAY | HE |  |  |  |  | -0.69123 | 6.4488 | 6.3886 | 6.3355 | 6.2671 | 6.2161 | 6.1345 | 6.0365 | 5.9345 | 5.8682 | 5.3171 | 5.2273 | 5.212 | 0.011829 | 7.1722 | 7.1365 | 7.1018 | 7.0569 | 7.0243 | 6.9743 | 6.9049 | 6.8396 | 6.7977 | 6.4314 | 6.3233 | 6.1855 | -0.28613 | 6.858 | 6.8018 | 6.7477 | 6.6773 | 6.6284 | 6.5488 | 6.4488 | 6.3488 | 6.2896 | 5.7651 | 5.6906 | 5.6773
|  | LAXAY | CF |  |  |  |  | -0.68511 | 6.46 | 6.4171 | 6.3722 | 6.3192 | 6.2631 | 6.2222 | 6.161 | 6.0977 | 6.0324 | 5.708 | 5.4202 | 5.2233 | 0.01591 | 7.1773 | 7.1518 | 7.1253 | 7.0916 | 7.0539 | 7.0273 | 6.9845 | 6.9345 | 6.8855 | 6.6212 | 6.3069 | 5.9365 | -0.27899 | 6.8692 | 6.8294 | 6.7875 | 6.7355 | 6.6784 | 6.6396 | 6.5804 | 6.5151 | 6.4488 | 6.1304 | 5.8569 | 5.6865
| COUPAR ANGUS | LEOCH | MINIMUM HEADROOM | NO 35945 36287 | YES | NO | 0.722 | -2.6089 | -2.7191 | -2.8609 | -2.9803 | -3.1395 | -3.3058 | -3.5038 | -3.767 | -4.0191 | -4.2497 | -4.9935 | -5.3987 | -5.4946 | -1.4078 | -1.4731 | -1.5609 | -1.6293 | -1.7364 | -1.8527 | -1.9609 | -2.1313 | -2.2935 | -2.4344 | -2.8466 | -3.0833 | -3.5476 | -2.0609 | -2.1711 | -2.3089 | -2.4262 | -2.5833 | -2.7476 | -2.9252 | -3.1803 | -3.4221 | -3.6405 | -4.2966 | -4.6354 | -4.7089
|  | LEOCH | EE |  |  |  |  | -2.6089 | -2.7191 | -2.8609 | -2.9803 | -3.1395 | -3.3058 | -3.5038 | -3.767 | -4.0191 | -4.2497 | -4.9935 | -5.3323 | -5.4201 | -1.4078 | -1.4731 | -1.5609 | -1.6293 | -1.7364 | -1.8527 | -1.9609 | -2.1313 | -2.2935 | -2.4344 | -2.8466 | -3.0833 | -3.3507 | -2.0609 | -2.1711 | -2.3089 | -2.4262 | -2.5833 | -2.7476 | -2.9252 | -3.1803 | -3.4221 | -3.6405 | -4.2966 | -4.5731 | -4.6487
|  | LEOCH | HT |  |  |  |  | -2.5527 | -2.6589 | -2.7925 | -2.9038 | -3.0344 | -3.1864 | -3.3497 | -3.5701 | -3.7874 | -3.965 | -4.9487 | -5.3987 | -5.4946 | -1.366 | -1.4242 | -1.4997 | -1.5568 | -1.6282 | -1.7119 | -1.7915 | -1.9221 | -2.0517 | -2.1354 | -2.718 | -2.9354 | -2.9803 | -1.9987 | -2.1048 | -2.2333 | -2.3333 | -2.4568 | -2.6017 | -2.7487 | -2.9599 | -3.165 | -3.317 | -4.2456 | -4.6354 | -4.7089
|  | LEOCH | HE |  |  |  |  | -2.5507 | -2.6211 | -2.6895 | -2.7782 | -2.866 | -2.9721 | -3.0874 | -3.2609 | -3.4272 | -3.5527 | -4.4833 | -4.9374 | -5.0864 | -1.3691 | -1.4129 | -1.4589 | -1.518 | -1.5752 | -1.6456 | -1.7129 | -1.8293 | -1.9425 | -2.0089 | -2.618 | -2.9252 | -3.2007 | -1.9976 | -2.067 | -2.1364 | -2.2293 | -2.316 | -2.4242 | -2.5293 | -2.6997 | -2.8609 | -2.968 | -3.8405 | -4.2374 | -4.3578
|  | LEOCH | CF |  |  |  |  | -2.5415 | -2.5895 | -2.6405 | -2.6844 | -2.7476 | -2.8191 | -2.9027 | -2.9599 | -3.0497 | -3.1395 | -3.6711 | -4.3446 | -4.8201 | -1.364 | -1.3987 | -1.4344 | -1.4691 | -1.5099 | -1.566 | -1.6282 | -1.6752 | -1.7507 | -1.8282 | -2.2701 | -2.8833 | -3.5476 | -1.9915 | -2.0384 | -2.0946 | -2.1374 | -2.1997 | -2.2742 | -2.3609 | -2.418 | -2.5109 | -2.6048 | -3.1262 | -3.7629 | -4.1497
| NAIRN | LETHEN | MINIMUM HEADROOM | NH 92307 50795 | YES | YES | 0.226 | 2.8773 | 2.8181 | 2.7467 | 2.6814 | 2.61 | 2.5334 | 2.4355 | 2.3385 | 2.2355 | 2.1344 | 1.8151 | 1.663 | 1.5926 | 3.1785 | 3.1418 | 3.0938 | 3.0489 | 2.9959 | 2.9367 | 2.8653 | 2.7918 | 2.7193 | 2.654 | 2.4306 | 2.3296 | 2.2296 | 3.131 | 3.0738 | 3.0075 | 2.9463 | 2.8718 | 2.7983 | 2.6983 | 2.6167 | 2.5085 | 2.4106 | 2.1473 | 2.0034 | 1.9361
|  | LETHEN | EE |  |  |  |  | 2.8773 | 2.8181 | 2.7467 | 2.6814 | 2.61 | 2.5334 | 2.4355 | 2.3385 | 2.2355 | 2.1344 | 1.8253 | 1.7661 | 1.7569 | 3.1785 | 3.1418 | 3.0938 | 3.0489 | 2.9959 | 2.9367 | 2.8653 | 2.7918 | 2.7193 | 2.654 | 2.454 | 2.4153 | 2.3408 | 3.131 | 3.0738 | 3.0075 | 2.9463 | 2.8718 | 2.7983 | 2.6983 | 2.6167 | 2.5085 | 2.4106 | 2.1575 | 2.1034 | 2.0953
|  | LETHEN | HT |  |  |  |  | 2.8977 | 2.8416 | 2.7844 | 2.7232 | 2.6589 | 2.5875 | 2.5181 | 2.4375 | 2.3569 | 2.2671 | 1.8916 | 1.712 | 1.6477 | 3.1969 | 3.1673 | 3.1367 | 3.0969 | 3.052 | 3.003 | 2.954 | 2.8887 | 2.8275 | 2.7612 | 2.4928 | 2.3826 | 2.3377 | 3.1544 | 3.1014 | 3.0504 | 2.9932 | 2.93 | 2.8596 | 2.7993 | 2.7177 | 2.6361 | 2.5493 | 2.2187 | 2.0544 | 1.9932
|  | LETHEN | HE |  |  |  |  | 2.8977 | 2.8559 | 2.8151 | 2.7712 | 2.7222 | 2.6671 | 2.6069 | 2.514 | 2.4181 | 2.3171 | 1.8151 | 1.663 | 1.5926 | 3.1969 | 3.1673 | 3.1377 | 3.101 | 3.0561 | 3.0071 | 2.9561 | 2.8877 | 2.8234 | 2.752 | 2.4306 | 2.3296 | 2.2775 | 3.1555 | 3.1136 | 3.0769 | 3.0351 | 2.984 | 2.931 | 2.8698 | 2.7861 | 2.7044 | 2.6147 | 2.1473 | 2.0034 | 1.9361
|  | LETHEN | CF |  |  |  |  | 2.9038 | 2.8712 | 2.8396 | 2.7977 | 2.761 | 2.7202 | 2.6753 | 2.6334 | 2.5855 | 2.5426 | 2.212 | 1.8926 | 1.6722 | 3.202 | 3.1816 | 3.1632 | 3.1357 | 3.1142 | 3.0816 | 3.0459 | 3.0102 | 2.9704 | 2.9285 | 2.6877 | 2.4663 | 2.2296 | 3.1616 | 3.13 | 3.0993 | 3.0596 | 3.0238 | 2.983 | 2.9371 | 2.9014 | 2.8524 | 2.8096 | 2.5187 | 2.2147 | 2.0126
| GRUDIE BRIDGE | LETTEREWE | MINIMUM HEADROOM | NG 93546 70082 | YES | NO | 0 | 0.11494 | 0.11392 | 0.11392 | 0.11392 | 0.11188 | 0.11188 | 0.11086 | 0.11086 | 0.10984 | 0.10984 | 0.10678 | 0.10576 | 0.10576 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.1039 | 0.10288 | 0.10288 | 0.10084 | 0.099816 | 0.099816 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.10738 | 0.10738 | 0.10636 | 0.10636 | 0.1033 | 0.10228 | 0.10228
|  | LETTEREWE | EE |  |  |  |  | 0.11494 | 0.11392 | 0.11392 | 0.11392 | 0.11188 | 0.11188 | 0.11086 | 0.11086 | 0.10984 | 0.10984 | 0.1078 | 0.1078 | 0.1078 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.1039 | 0.10288 | 0.10288 | 0.10186 | 0.10186 | 0.10186 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.10738 | 0.10738 | 0.10636 | 0.10636 | 0.10534 | 0.10534 | 0.10534
|  | LETTEREWE | HT |  |  |  |  | 0.11494 | 0.11494 | 0.11392 | 0.11392 | 0.11392 | 0.11188 | 0.11188 | 0.11188 | 0.11086 | 0.11086 | 0.1078 | 0.10678 | 0.10678 | 0.10696 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10492 | 0.1039 | 0.1039 | 0.10186 | 0.10084 | 0.10084 | 0.11044 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.1084 | 0.10738 | 0.10738 | 0.10534 | 0.1033 | 0.1033
|  | LETTEREWE | HE |  |  |  |  | 0.11494 | 0.11392 | 0.11392 | 0.11392 | 0.11392 | 0.11188 | 0.11188 | 0.11086 | 0.11086 | 0.10984 | 0.10678 | 0.10576 | 0.10576 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.1039 | 0.1039 | 0.10288 | 0.10084 | 0.099816 | 0.099816 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.10738 | 0.10738 | 0.10636 | 0.1033 | 0.10228 | 0.10228
|  | LETTEREWE | CF |  |  |  |  | 0.11494 | 0.11494 | 0.11494 | 0.11392 | 0.11392 | 0.11392 | 0.11392 | 0.11188 | 0.11188 | 0.11188 | 0.10984 | 0.10678 | 0.10576 | 0.10696 | 0.10696 | 0.10696 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.10492 | 0.10288 | 0.10084 | 0.099816 | 0.11044 | 0.11044 | 0.11044 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.1084 | 0.10636 | 0.1033 | 0.10228
| ELGIN | LHANBRYDE | MINIMUM HEADROOM | NJ 27940 61640 | NO | YES | 0.261 | 4.7353 | 4.5598 | 4.372 | 4.2047 | 4.0435 | 3.919 | 3.7394 | 3.5506 | 3.4037 | 3.2343 | 2.5986 | 2.222 | 2.1557 | 4.9965 | 4.923 | 4.8537 | 4.7679 | 4.6761 | 4.6169 | 4.5067 | 4.372 | 4.2986 | 4.2026 | 4.0057 | 3.8424 | 3.5792 | 5.021 | 4.8771 | 4.719 | 4.573 | 4.4312 | 4.319 | 4.1547 | 3.9822 | 3.8486 | 3.6975 | 3.1343 | 2.7955 | 2.7373
|  | LHANBRYDE | EE |  |  |  |  | 4.7353 | 4.5598 | 4.372 | 4.2047 | 4.0435 | 3.919 | 3.7394 | 3.5506 | 3.4037 | 3.2343 | 2.6128 | 2.2618 | 2.1863 | 4.9965 | 4.923 | 4.8537 | 4.7679 | 4.6761 | 4.6169 | 4.5067 | 4.372 | 4.2986 | 4.2026 | 4.0057 | 3.8424 | 3.6455 | 5.021 | 4.8771 | 4.719 | 4.573 | 4.4312 | 4.319 | 4.1547 | 3.9822 | 3.8486 | 3.6975 | 3.1435 | 2.8333 | 2.7659
|  | LHANBRYDE | HT |  |  |  |  | 4.7588 | 4.5812 | 4.3792 | 4.22 | 4.0863 | 3.9547 | 3.7914 | 3.6455 | 3.4812 | 3.3118 | 2.5986 | 2.222 | 2.1557 | 5.0424 | 4.9894 | 4.8996 | 4.8343 | 4.772 | 4.7077 | 4.6292 | 4.572 | 4.4884 | 4.4016 | 4.0557 | 3.92 | 3.8996 | 5.0455 | 4.9006 | 4.7353 | 4.5986 | 4.4802 | 4.3577 | 4.2108 | 4.0802 | 3.9322 | 3.7782 | 3.1343 | 2.7955 | 2.7373
|  | LHANBRYDE | HE |  |  |  |  | 4.7598 | 4.6271 | 4.469 | 4.3384 | 4.2435 | 4.1435 | 4.0343 | 3.9404 | 3.8292 | 3.7128 | 3.0547 | 2.6547 | 2.5057 | 5.0414 | 4.9924 | 4.922 | 4.8486 | 4.8077 | 4.7537 | 4.6884 | 4.6404 | 4.5679 | 4.4833 | 4.121 | 3.9884 | 3.7751 | 5.0455 | 4.9394 | 4.8118 | 4.6986 | 4.6169 | 4.5271 | 4.4261 | 4.3414 | 4.2384 | 4.1312 | 3.5343 | 3.1802 | 3.0486
|  | LHANBRYDE | CF |  |  |  |  | 4.7812 | 4.6802 | 4.5659 | 4.471 | 4.4067 | 4.3322 | 4.2782 | 4.2088 | 4.1496 | 4.1139 | 3.6914 | 3.2537 | 2.8812 | 5.0537 | 5.0149 | 4.9659 | 4.9098 | 4.8802 | 4.8333 | 4.7945 | 4.7363 | 4.6792 | 4.6567 | 4.3251 | 4.0567 | 3.5792 | 5.0659 | 4.9863 | 4.8935 | 4.8128 | 4.7577 | 4.6935 | 4.6414 | 4.5782 | 4.5241 | 4.4924 | 4.1067 | 3.7057 | 3.3792
| FORT WILLIAM | LIDDESDALE | MINIMUM HEADROOM | NM 78116 59480 | YES | NO | 0 | 0.10167 | 0.10167 | 0.099633 | 0.099633 | 0.091469 | 0.090449 | 0.087388 | 0.087388 | 0.086367 | 0.085347 | 0.075143 | 0.071061 | 0.06902 | 0.096755 | 0.096755 | 0.095735 | 0.095735 | 0.087571 | 0.086551 | 0.085531 | 0.085531 | 0.08451 | 0.08349 | 0.074306 | 0.071245 | 0.070224 | 0.10023 | 0.10023 | 0.099214 | 0.099214 | 0.090031 | 0.08901 | 0.08799 | 0.08799 | 0.085949 | 0.084929 | 0.074724 | 0.070643 | 0.069622
|  | LIDDESDALE | EE |  |  |  |  | 0.10167 | 0.10167 | 0.099633 | 0.099633 | 0.091469 | 0.090449 | 0.087388 | 0.087388 | 0.086367 | 0.085347 | 0.075143 | 0.075143 | 0.075143 | 0.096755 | 0.096755 | 0.095735 | 0.095735 | 0.087571 | 0.086551 | 0.085531 | 0.085531 | 0.08451 | 0.08349 | 0.074306 | 0.074306 | 0.074306 | 0.10023 | 0.10023 | 0.099214 | 0.099214 | 0.090031 | 0.08901 | 0.08799 | 0.08799 | 0.085949 | 0.084929 | 0.074724 | 0.074724 | 0.074724
|  | LIDDESDALE | HT |  |  |  |  | 0.10269 | 0.10167 | 0.10167 | 0.099633 | 0.099633 | 0.098612 | 0.098612 | 0.089429 | 0.087388 | 0.086367 | 0.082286 | 0.073102 | 0.072082 | 0.097776 | 0.096755 | 0.096755 | 0.095735 | 0.095735 | 0.094714 | 0.094714 | 0.086551 | 0.085531 | 0.08451 | 0.081449 | 0.073286 | 0.072265 | 0.10126 | 0.10023 | 0.10023 | 0.099214 | 0.099214 | 0.097173 | 0.097173 | 0.08901 | 0.08799 | 0.085949 | 0.081867 | 0.073704 | 0.072684
|  | LIDDESDALE | HE |  |  |  |  | 0.10269 | 0.10167 | 0.10167 | 0.099633 | 0.099633 | 0.098612 | 0.097592 | 0.088408 | 0.087388 | 0.086367 | 0.080245 | 0.071061 | 0.06902 | 0.097776 | 0.096755 | 0.096755 | 0.095735 | 0.095735 | 0.094714 | 0.093694 | 0.085531 | 0.08451 | 0.08451 | 0.080429 | 0.071245 | 0.070224 | 0.10126 | 0.10023 | 0.10023 | 0.099214 | 0.099214 | 0.097173 | 0.096153 | 0.08799 | 0.086969 | 0.085949 | 0.080847 | 0.070643 | 0.069622
|  | LIDDESDALE | CF |  |  |  |  | 0.10269 | 0.10167 | 0.10167 | 0.10167 | 0.099633 | 0.099633 | 0.099633 | 0.098612 | 0.091469 | 0.090449 | 0.085347 | 0.073102 | 0.071061 | 0.097776 | 0.096755 | 0.096755 | 0.096755 | 0.095735 | 0.095735 | 0.095735 | 0.094714 | 0.087571 | 0.086551 | 0.08349 | 0.073286 | 0.071245 | 0.10126 | 0.10023 | 0.10023 | 0.10023 | 0.099214 | 0.099214 | 0.099214 | 0.097173 | 0.090031 | 0.08901 | 0.084929 | 0.073704 | 0.070643
| KEITH 1 | LIMEHILLOCKS | MINIMUM HEADROOM | NJ 52093 50703 | YES | YES | 0.086 | -0.29236 | -0.3393 | -0.38318 | -0.43522 | -0.52705 | -0.61481 | -0.73828 | -0.82909 | -0.94134 | -1.0464 | -1.3097 | -1.3873 | -1.4189 | 0.46478 | 0.42499 | 0.38417 | 0.34336 | 0.28621 | 0.23621 | 0.15662 | 0.10764 | 0.036212 | -0.027053 | -0.18828 | -0.25562 | -0.50767 | 0.060702 | -0.013788 | -0.081135 | -0.14338 | -0.2342 | -0.31889 | -0.44032 | -0.51991 | -0.6342 | -0.7342 | -0.96481 | -1.024 | -1.0485
|  | LIMEHILLOCKS | EE |  |  |  |  | -0.29236 | -0.3393 | -0.38318 | -0.43522 | -0.52705 | -0.61481 | -0.73828 | -0.82909 | -0.94134 | -1.0464 | -1.3097 | -1.3577 | -1.3679 | 0.46478 | 0.42499 | 0.38417 | 0.34336 | 0.28621 | 0.23621 | 0.15662 | 0.10764 | 0.036212 | -0.027053 | -0.18828 | -0.25256 | -0.3546 | 0.060702 | -0.013788 | -0.081135 | -0.14338 | -0.2342 | -0.31889 | -0.44032 | -0.51991 | -0.6342 | -0.7342 | -0.96481 | -1.0036 | -1.0148
|  | LIMEHILLOCKS | HT |  |  |  |  | -0.28011 | -0.31889 | -0.3546 | -0.39746 | -0.47807 | -0.54644 | -0.63828 | -0.72705 | -0.81583 | -0.91379 | -1.2311 | -1.3873 | -1.4189 | 0.47907 | 0.44744 | 0.4158 | 0.37907 | 0.33519 | 0.29642 | 0.24438 | 0.19029 | 0.13927 | 0.082131 | -0.12807 | -0.21787 | -0.25154 | 0.084171 | 0.029069 | -0.022971 | -0.084196 | -0.16379 | -0.22093 | -0.30562 | -0.3893 | -0.47807 | -0.57399 | -0.8893 | -1.024 | -1.0485
|  | LIMEHILLOCKS | HE |  |  |  |  | -0.28011 | -0.31175 | -0.3393 | -0.37603 | -0.41787 | -0.46481 | -0.54848 | -0.63011 | -0.71175 | -0.79236 | -1.2158 | -1.3332 | -1.3954 | 0.47907 | 0.44948 | 0.42091 | 0.38825 | 0.34948 | 0.30968 | 0.25968 | 0.20356 | 0.14744 | 0.091314 | -0.17399 | -0.25562 | -0.33726 | 0.084171 | 0.039273 | 0.0015184 | -0.049502 | -0.11481 | -0.15869 | -0.23726 | -0.31583 | -0.39746 | -0.47807 | -0.86583 | -0.96379 | -0.98113
|  | LIMEHILLOCKS | CF |  |  |  |  | -0.27501 | -0.30154 | -0.32195 | -0.35358 | -0.37909 | -0.41175 | -0.45052 | -0.51481 | -0.56583 | -0.62705 | -0.8944 | -1.1515 | -1.3281 | 0.48417 | 0.46478 | 0.44438 | 0.41887 | 0.39642 | 0.36784 | 0.34029 | 0.3005 | 0.26478 | 0.22601 | 0.017845 | -0.24032 | -0.50767 | 0.092335 | 0.053559 | 0.021927 | -0.026033 | -0.061747 | -0.11481 | -0.14848 | -0.21379 | -0.26481 | -0.32501 | -0.5893 | -0.84644 | -0.96685
| ARDMORE | LOCH CARNAN | MINIMUM HEADROOM | NF 83230 42735 | NO | YES | 0.023 | 9.787 | 9.7707 | 9.7523 | 9.736 | 9.7104 | 9.6982 | 9.6686 | 9.6441 | 9.6125 | 9.587 | 9.5084 | 9.488 | 9.4829 | 9.3466 | 9.3384 | 9.3262 | 9.316 | 9.3007 | 9.2904 | 9.2721 | 9.2517 | 9.2313 | 9.2119 | 9.1323 | 9.1058 | 9.0986 | 9.4066 | 9.3943 | 9.38 | 9.3658 | 9.3474 | 9.3321 | 9.3096 | 9.2841 | 9.2576 | 9.2351 | 9.1382 | 9.1076 | 9.0984
|  | LOCH CARNAN | EE |  |  |  |  | 9.787 | 9.7707 | 9.7523 | 9.736 | 9.7104 | 9.6982 | 9.6686 | 9.6441 | 9.6125 | 9.587 | 9.5084 | 9.488 | 9.4849 | 9.3466 | 9.3384 | 9.3262 | 9.316 | 9.3007 | 9.2904 | 9.2721 | 9.2517 | 9.2313 | 9.2119 | 9.1323 | 9.1058 | 9.1017 | 9.4076 | 9.3943 | 9.38 | 9.3658 | 9.3474 | 9.3321 | 9.3096 | 9.2841 | 9.2576 | 9.2351 | 9.1382 | 9.1076 | 9.1056
|  | LOCH CARNAN | HT |  |  |  |  | 9.787 | 9.7788 | 9.7656 | 9.7533 | 9.7349 | 9.7207 | 9.6982 | 9.6696 | 9.6564 | 9.6309 | 9.5298 | 9.489 | 9.4829 | 9.3466 | 9.3404 | 9.3333 | 9.3241 | 9.3119 | 9.3007 | 9.2843 | 9.266 | 9.2476 | 9.2282 | 9.1435 | 9.1068 | 9.0986 | 9.4066 | 9.3974 | 9.3872 | 9.377 | 9.3607 | 9.3453 | 9.3249 | 9.3015 | 9.28 | 9.2556 | 9.1535 | 9.1107 | 9.0984
|  | LOCH CARNAN | HE |  |  |  |  | 9.787 | 9.7819 | 9.7717 | 9.7604 | 9.7462 | 9.7339 | 9.7156 | 9.687 | 9.6758 | 9.6513 | 9.5431 | 9.5176 | 9.5145 | 9.3466 | 9.3415 | 9.3364 | 9.3272 | 9.317 | 9.3047 | 9.2894 | 9.268 | 9.2527 | 9.2343 | 9.1456 | 9.1262 | 9.1211 | 9.4076 | 9.4004 | 9.3913 | 9.38 | 9.3668 | 9.3525 | 9.3341 | 9.3086 | 9.2892 | 9.2637 | 9.1545 | 9.1311 | 9.126
|  | LOCH CARNAN | CF |  |  |  |  | 9.7911 | 9.788 | 9.7809 | 9.7717 | 9.7625 | 9.7523 | 9.74 | 9.7258 | 9.7115 | 9.6941 | 9.6298 | 9.5513 | 9.5115 | 9.3486 | 9.3466 | 9.3425 | 9.3384 | 9.3323 | 9.3272 | 9.319 | 9.3078 | 9.2976 | 9.2853 | 9.2241 | 9.1568 | 9.1068 | 9.4107 | 9.4076 | 9.4004 | 9.3943 | 9.3872 | 9.379 | 9.3688 | 9.3566 | 9.3443 | 9.329 | 9.2545 | 9.1719 | 9.1147
| GRUDIE BRIDGE | LOCH GLASCARNOCH | MINIMUM HEADROOM | NH 31620 71996 | YES | NO | 0.023 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268
|  | LOCH GLASCARNOCH | EE |  |  |  |  | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268
|  | LOCH GLASCARNOCH | HT |  |  |  |  | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268
|  | LOCH GLASCARNOCH | HE |  |  |  |  | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268
|  | LOCH GLASCARNOCH | CF |  |  |  |  | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.57518 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.5312 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268 | 0.55268
| FORT WILLIAM | LOCHALINE | MINIMUM HEADROOM | NM 67939 45444 | YES | NO | 0.669 | -0.60279 | -0.61911 | -0.64156 | -0.65891 | -0.68646 | -0.69871 | -0.73034 | -0.75585 | -0.78442 | -0.81299 | -0.87422 | -0.89258 | -0.89667 | -0.32728 | -0.3334 | -0.34258 | -0.35279 | -0.36095 | -0.36809 | -0.38034 | -0.38952 | -0.40075 | -0.41197 | -0.4385 | -0.44769 | -0.46095 | -0.2783 | -0.29258 | -0.31095 | -0.32626 | -0.34769 | -0.35993 | -0.38748 | -0.41299 | -0.44156 | -0.46911 | -0.53136 | -0.54667 | -0.55177
|  | LOCHALINE | EE |  |  |  |  | -0.60279 | -0.61911 | -0.64156 | -0.65891 | -0.68646 | -0.69871 | -0.73034 | -0.75585 | -0.78442 | -0.81299 | -0.87422 | -0.88442 | -0.88952 | -0.32728 | -0.3334 | -0.34258 | -0.35279 | -0.36095 | -0.36809 | -0.38034 | -0.38952 | -0.40075 | -0.41197 | -0.4385 | -0.4436 | -0.45585 | -0.2783 | -0.29258 | -0.31095 | -0.32626 | -0.34769 | -0.35993 | -0.38748 | -0.41299 | -0.44156 | -0.46911 | -0.53136 | -0.5385 | -0.54462
|  | LOCHALINE | HT |  |  |  |  | -0.59462 | -0.60993 | -0.62116 | -0.63646 | -0.65075 | -0.67218 | -0.69769 | -0.71095 | -0.73442 | -0.76095 | -0.85381 | -0.89258 | -0.89667 | -0.3232 | -0.33136 | -0.33442 | -0.34156 | -0.34871 | -0.35891 | -0.36707 | -0.3732 | -0.38238 | -0.39462 | -0.43136 | -0.44769 | -0.45177 | -0.27218 | -0.28646 | -0.29564 | -0.31095 | -0.32422 | -0.34156 | -0.36197 | -0.37626 | -0.39564 | -0.41911 | -0.50891 | -0.54667 | -0.55177
|  | LOCHALINE | HE |  |  |  |  | -0.59462 | -0.60891 | -0.61503 | -0.62728 | -0.64054 | -0.65789 | -0.67728 | -0.68952 | -0.71095 | -0.7334 | -0.8385 | -0.86401 | -0.86605 | -0.3232 | -0.33136 | -0.3334 | -0.33748 | -0.34462 | -0.35279 | -0.36197 | -0.36911 | -0.37728 | -0.38748 | -0.43442 | -0.44769 | -0.45177 | -0.27218 | -0.2834 | -0.28748 | -0.29973 | -0.31197 | -0.32524 | -0.34258 | -0.35483 | -0.37013 | -0.39258 | -0.49462 | -0.52013 | -0.52116
|  | LOCHALINE | CF |  |  |  |  | -0.59871 | -0.60075 | -0.61095 | -0.62218 | -0.63136 | -0.64054 | -0.65585 | -0.6732 | -0.68952 | -0.69258 | -0.76503 | -0.8334 | -0.86197 | -0.32524 | -0.32728 | -0.33238 | -0.33544 | -0.33952 | -0.34258 | -0.34871 | -0.35687 | -0.36401 | -0.36707 | -0.39973 | -0.43034 | -0.46095 | -0.2732 | -0.2783 | -0.28646 | -0.29564 | -0.30585 | -0.31401 | -0.32524 | -0.33952 | -0.35279 | -0.35687 | -0.42116 | -0.4885 | -0.51809
| GRUDIE BRIDGE | LOCHCARRON | MINIMUM HEADROOM | NG 91944 41839 | YES | NO | 0.075 | -0.013257 | -0.068359 | -0.1102 | -0.15816 | -0.2153 | -0.25407 | -0.32754 | -0.43775 | -0.55101 | -0.65918 | -0.81632 | -0.86224 | -0.84183 | 0.37654 | 0.34082 | 0.31429 | 0.28674 | 0.24082 | 0.2194 | 0.1694 | 0.10307 | 0.036743 | -0.026522 | -0.13877 | -0.16428 | -0.34897 | 0.18878 | 0.13674 | 0.096947 | 0.052049 | -0.0030531 | -0.037747 | -0.10713 | -0.20611 | -0.3102 | -0.40816 | -0.55203 | -0.59285 | -0.56938
|  | LOCHCARRON | EE |  |  |  |  | -0.013257 | -0.068359 | -0.1102 | -0.15816 | -0.2153 | -0.25407 | -0.32652 | -0.43775 | -0.55101 | -0.65918 | -0.81632 | -0.80611 | -0.8204 | 0.37654 | 0.34082 | 0.31429 | 0.28674 | 0.24082 | 0.2194 | 0.1694 | 0.10307 | 0.036743 | -0.026522 | -0.13877 | -0.15509 | -0.23162 | 0.18878 | 0.13674 | 0.096947 | 0.052049 | -0.0030531 | -0.037747 | -0.10713 | -0.20611 | -0.3102 | -0.40816 | -0.55203 | -0.53571 | -0.54999
|  | LOCHCARRON | HT |  |  |  |  | 8.1633e-06 | -0.037747 | -0.079584 | -0.1102 | -0.15611 | -0.23673 | -0.32754 | -0.4306 | -0.46836 | -0.52346 | -0.7602 | -0.86224 | -0.84183 | 0.39389 | 0.37144 | 0.34491 | 0.32756 | 0.29899 | 0.25715 | 0.20613 | 0.14797 | 0.12858 | 0.089804 | -0.07142 | -0.13367 | -0.10816 | 0.20409 | 0.17042 | 0.13164 | 0.10307 | 0.059192 | -0.0081551 | -0.089788 | -0.18264 | -0.2153 | -0.2704 | -0.49897 | -0.59285 | -0.56938
|  | LOCHCARRON | HE |  |  |  |  | 0.002049 | -0.029584 | -0.058155 | -0.086727 | -0.12142 | -0.15203 | -0.19897 | -0.28469 | -0.34183 | -0.42856 | -0.72448 | -0.78775 | -0.79897 | 0.39287 | 0.37246 | 0.35205 | 0.33572 | 0.30817 | 0.28878 | 0.25511 | 0.20001 | 0.1745 | 0.12348 | -0.073461 | -0.14489 | -0.2153 | 0.20613 | 0.17756 | 0.14797 | 0.12552 | 0.089804 | 0.061233 | 0.015314 | -0.063257 | -0.1102 | -0.18571 | -0.46224 | -0.52346 | -0.53367
|  | LOCHCARRON | CF |  |  |  |  | 0.012253 | -0.012237 | -0.036727 | -0.06938 | -0.086727 | -0.11734 | -0.14285 | -0.17958 | -0.24081 | -0.30611 | -0.53162 | -0.70101 | -0.79387 | 0.40103 | 0.3847 | 0.36736 | 0.34389 | 0.33164 | 0.30817 | 0.29184 | 0.26123 | 0.21736 | 0.1796 | 0.019396 | -0.16428 | -0.34897 | 0.21633 | 0.19389 | 0.16633 | 0.13674 | 0.11736 | 0.087763 | 0.065314 | 0.02858 | -0.028563 | -0.086727 | -0.29081 | -0.45509 | -0.5306
| TAYNUILT | LOCHDONHEAD | MINIMUM HEADROOM | NM 72902 34134 | YES | YES | 0.058 | 0.13206 | 0.11267 | 0.092265 | 0.043286 | 0.001449 | -0.041408 | -0.21284 | -0.32712 | -0.42508 | -0.51896 | -0.66182 | -0.71284 | -0.71794 | 0.38308 | 0.3688 | 0.35451 | 0.32798 | 0.30145 | 0.279 | 0.15145 | 0.073898 | 0.0055306 | -0.053653 | -0.24039 | -0.2761 | -0.28427 | 0.19431 | 0.17594 | 0.15553 | 0.11471 | 0.074918 | 0.037163 | -0.10978 | -0.20467 | -0.29039 | -0.36998 | -0.55263 | -0.60365 | -0.60773
|  | LOCHDONHEAD | EE |  |  |  |  | 0.13206 | 0.11267 | 0.092265 | 0.043286 | 0.001449 | -0.041408 | -0.10671 | -0.22814 | -0.33529 | -0.43631 | -0.65365 | -0.671 | -0.68018 | 0.38308 | 0.3688 | 0.35451 | 0.32798 | 0.30145 | 0.279 | 0.24022 | 0.14227 | 0.059612 | -0.0097755 | -0.16284 | -0.1812 | -0.20773 | 0.19431 | 0.17594 | 0.15553 | 0.11471 | 0.074918 | 0.037163 | -0.01998 | -0.13222 | -0.23222 | -0.32202 | -0.50876 | -0.52508 | -0.53324
|  | LOCHDONHEAD | HT |  |  |  |  | 0.14227 | 0.12696 | 0.11471 | 0.048388 | 0.0024694 | -0.035286 | -0.21284 | -0.32712 | -0.42508 | -0.51896 | -0.62916 | -0.67712 | -0.68324 | 0.38818 | 0.379 | 0.37288 | 0.3392 | 0.31267 | 0.29431 | 0.15145 | 0.073898 | 0.0055306 | -0.053653 | -0.13631 | -0.1659 | -0.16896 | 0.20247 | 0.1892 | 0.17798 | 0.12288 | 0.083082 | 0.047367 | -0.10978 | -0.20467 | -0.29039 | -0.36998 | -0.48733 | -0.53427 | -0.53835
|  | LOCHDONHEAD | HE |  |  |  |  | 0.14227 | 0.1239 | 0.11471 | 0.064714 | 0.029 | -0.013857 | -0.07202 | -0.20161 | -0.31794 | -0.41692 | -0.66182 | -0.71284 | -0.7159 | 0.38818 | 0.37594 | 0.37288 | 0.34635 | 0.32084 | 0.29737 | 0.26778 | 0.16063 | 0.059612 | -0.026102 | -0.24039 | -0.2761 | -0.27814 | 0.20145 | 0.18512 | 0.17186 | 0.13512 | 0.10451 | 0.065735 | 0.014714 | -0.10773 | -0.21998 | -0.31386 | -0.55263 | -0.60365 | -0.60671
|  | LOCHDONHEAD | CF |  |  |  |  | 0.1392 | 0.13614 | 0.12186 | 0.10757 | 0.090224 | 0.068796 | 0.044306 | 0.0034898 | -0.053653 | -0.12916 | -0.43018 | -0.64039 | -0.71794 | 0.38512 | 0.38614 | 0.37594 | 0.36676 | 0.35247 | 0.34022 | 0.32798 | 0.30145 | 0.25655 | 0.21165 | -0.048551 | -0.23427 | -0.28427 | 0.20043 | 0.19737 | 0.18512 | 0.17084 | 0.15451 | 0.13614 | 0.11573 | 0.08002 | 0.024918 | -0.039367 | -0.32712 | -0.53733 | -0.60773
| KILLIN | LOCHEARNHEAD | MINIMUM HEADROOM | NN 58766 24177 | YES | YES | 0.087 | -0.20102 | -0.25306 | -0.29082 | -0.34286 | -0.40306 | -0.4449 | -0.52245 | -0.59898 | -0.67959 | -0.75306 | -0.92857 | -0.97041 | -1 | 0.10306 | 0.065306 | 0.041837 | 0.0071429 | -0.031633 | -0.058163 | -0.10612 | -0.15612 | -0.20612 | -0.25204 | -0.37347 | -0.43878 | -0.58265 | -0.095918 | -0.14694 | -0.18367 | -0.23061 | -0.2898 | -0.32959 | -0.40102 | -0.47551 | -0.55102 | -0.62041 | -0.78061 | -0.81837 | -0.83571
|  | LOCHEARNHEAD | EE |  |  |  |  | -0.20102 | -0.25306 | -0.29082 | -0.34286 | -0.40306 | -0.4449 | -0.52245 | -0.59898 | -0.67959 | -0.75306 | -0.92857 | -0.97041 | -0.9602 | 0.10306 | 0.065306 | 0.041837 | 0.0071429 | -0.031633 | -0.058163 | -0.10612 | -0.15612 | -0.20612 | -0.25204 | -0.37347 | -0.43878 | -0.49184 | -0.095918 | -0.14694 | -0.18367 | -0.23061 | -0.2898 | -0.32959 | -0.40102 | -0.47551 | -0.55102 | -0.62041 | -0.78061 | -0.81837 | -0.8
|  | LOCHEARNHEAD | HT |  |  |  |  | -0.18265 | -0.22143 | -0.26224 | -0.3 | -0.34592 | -0.38673 | -0.4449 | -0.51531 | -0.55204 | -0.61735 | -0.88061 | -0.96429 | -1 | 0.11735 | 0.092857 | 0.068367 | 0.047959 | 0.019388 | -0.0061224 | -0.041837 | -0.089796 | -0.10918 | -0.15102 | -0.31531 | -0.35612 | -0.37857 | -0.076531 | -0.11224 | -0.15102 | -0.18469 | -0.23163 | -0.27041 | -0.32653 | -0.39184 | -0.42653 | -0.48776 | -0.73673 | -0.80816 | -0.83571
|  | LOCHEARNHEAD | HE |  |  |  |  | -0.18265 | -0.21327 | -0.24694 | -0.27347 | -0.31429 | -0.34388 | -0.39796 | -0.45918 | -0.49082 | -0.54796 | -0.85 | -0.89898 | -0.92755 | 0.11735 | 0.092857 | 0.072449 | 0.052041 | 0.02551 | 0.005102 | -0.028571 | -0.070408 | -0.088776 | -0.12857 | -0.32551 | -0.38776 | -0.46939 | -0.076531 | -0.10816 | -0.13878 | -0.16531 | -0.20204 | -0.23265 | -0.28367 | -0.34082 | -0.37041 | -0.42653 | -0.70612 | -0.7449 | -0.76837
|  | LOCHEARNHEAD | CF |  |  |  |  | -0.18163 | -0.20408 | -0.23061 | -0.26633 | -0.28776 | -0.32143 | -0.34796 | -0.3949 | -0.43469 | -0.45102 | -0.65714 | -0.80714 | -0.90408 | 0.11735 | 0.1 | 0.084694 | 0.059184 | 0.044898 | 0.019388 | 0.0040816 | -0.030612 | -0.059184 | -0.070408 | -0.23265 | -0.39286 | -0.58265 | -0.076531 | -0.097959 | -0.12449 | -0.15816 | -0.17755 | -0.21122 | -0.23469 | -0.27755 | -0.31633 | -0.33265 | -0.52857 | -0.66633 | -0.75306
| LYNDHURST | LOCHEE | MINIMUM HEADROOM | NO 38065 31416 | NO | YES | 1.572 | 15.7591 | 15.4347 | 15.1918 | 14.9449 | 14.653 | 14.351 | 14.0132 | 13.5704 | 13.1438 | 12.7622 | 11.5775 | 11.2724 | 11.2908 | 15.8326 | 15.6275 | 15.4459 | 15.2755 | 15.054 | 14.8132 | 14.5857 | 14.2744 | 13.9796 | 13.7193 | 12.8285 | 12.4591 | 9.502 | 16.0056 | 15.7892 | 15.5484 | 15.3229 | 15.0494 | 14.7668 | 14.4556 | 14.0413 | 13.6311 | 13.2637 | 12.176 | 11.8852 | 11.8994
|  | LOCHEE | EE |  |  |  |  | 15.7591 | 15.4347 | 15.1918 | 14.9449 | 14.653 | 14.351 | 14.0132 | 13.5704 | 13.1438 | 12.7622 | 11.5775 | 11.7816 | 11.7469 | 15.8326 | 15.6275 | 15.4459 | 15.2755 | 15.054 | 14.8132 | 14.5857 | 14.2744 | 13.9796 | 13.7193 | 12.8285 | 12.4591 | 11.5347 | 16.0056 | 15.7892 | 15.5484 | 15.3229 | 15.0494 | 14.7668 | 14.4556 | 14.0413 | 13.6311 | 13.2637 | 12.176 | 12.328 | 12.2739
|  | LOCHEE | HT |  |  |  |  | 15.7877 | 15.4959 | 15.2836 | 15.0836 | 14.8408 | 14.5826 | 14.2806 | 13.9306 | 13.5857 | 13.2602 | 11.6571 | 11.2724 | 11.2908 | 15.9071 | 15.7398 | 15.601 | 15.4816 | 15.3255 | 15.1489 | 14.9857 | 14.7561 | 14.5326 | 14.351 | 13.3163 | 12.9928 | 12.9785 | 16.0239 | 15.8515 | 15.6576 | 15.4637 | 15.2382 | 14.9964 | 14.7239 | 14.3994 | 14.0831 | 13.7831 | 12.2872 | 11.8852 | 11.8994
|  | LOCHEE | HE |  |  |  |  | 15.8234 | 15.5949 | 15.4612 | 15.3408 | 15.1959 | 15.0336 | 14.8163 | 14.552 | 14.2949 | 14.0632 | 12.9214 | 12.4632 | 12.5367 | 15.9183 | 15.7632 | 15.6438 | 15.5459 | 15.4163 | 15.2683 | 15.1255 | 14.9255 | 14.7255 | 14.5653 | 13.5622 | 12.9183 | 12.1142 | 16.0413 | 15.9066 | 15.8199 | 15.6974 | 15.5535 | 15.4005 | 15.2035 | 14.9556 | 14.7188 | 14.5046 | 13.4137 | 12.9943 | 13.0535
|  | LOCHEE | CF |  |  |  |  | 15.8755 | 15.7183 | 15.6489 | 15.5744 | 15.4867 | 15.3979 | 15.3142 | 15.2224 | 15.1275 | 15.0234 | 14.2847 | 13.2387 | 12.3551 | 15.9438 | 15.8275 | 15.7479 | 15.6744 | 15.5683 | 15.4591 | 15.3326 | 15.2173 | 15.0836 | 14.9387 | 14.0469 | 12.6102 | 9.502 | 16.079 | 15.9974 | 15.9576 | 15.9178 | 15.828 | 15.7352 | 15.6464 | 15.5627 | 15.4709 | 15.3709 | 14.6413 | 13.6546 | 12.8862
| PORT ANN | LOCHGILPHEAD | MINIMUM HEADROOM | NR 86092 88371 | NO | YES | 1.328 | 16.188 | 16.0339 | 15.8125 | 15.586 | 15.3104 | 15.036 | 14.6553 | 14.1788 | 13.6951 | 13.2666 | 12.6849 | 12.4135 | 12.3135 | 18.0747 | 17.9778 | 17.8288 | 17.69 | 17.5043 | 17.338 | 17.0972 | 16.7482 | 16.3992 | 16.0941 | 15.7023 | 15.4064 | 14.3145 | 17.3237 | 17.1758 | 16.9696 | 16.7584 | 16.4972 | 16.2451 | 15.8941 | 15.4207 | 14.9482 | 14.5349 | 13.986 | 13.7278 | 13.6574
|  | LOCHGILPHEAD | EE |  |  |  |  | 16.188 | 16.0339 | 15.8125 | 15.586 | 15.3104 | 15.036 | 14.6553 | 14.1788 | 13.6951 | 13.2666 | 12.6849 | 12.5472 | 12.4472 | 18.0747 | 17.9778 | 17.8288 | 17.69 | 17.5043 | 17.338 | 17.0972 | 16.7482 | 16.3992 | 16.0941 | 15.7125 | 15.4064 | 14.9258 | 17.3237 | 17.1758 | 16.9696 | 16.7584 | 16.4972 | 16.2451 | 15.8941 | 15.4207 | 14.9482 | 14.5349 | 13.986 | 13.8543 | 13.7584
|  | LOCHGILPHEAD | HT |  |  |  |  | 16.2819 | 16.14 | 15.9768 | 15.7441 | 15.4962 | 15.2696 | 14.8523 | 14.3798 | 14.0053 | 13.6462 | 12.8635 | 12.4135 | 12.337 | 18.1523 | 18.0676 | 17.9707 | 17.8329 | 17.6829 | 17.5564 | 17.2462 | 16.9023 | 16.6543 | 16.4104 | 15.99 | 15.7349 | 15.686 | 17.4176 | 17.2829 | 17.1329 | 16.9207 | 16.6931 | 16.49 | 16.0656 | 15.6043 | 15.2462 | 14.9053 | 14.1564 | 13.7278 | 13.6574
|  | LOCHGILPHEAD | HE |  |  |  |  | 16.2829 | 16.1696 | 16.0462 | 15.8645 | 15.6604 | 15.4553 | 15.1656 | 14.7686 | 14.436 | 14.0972 | 12.687 | 12.4686 | 12.3135 | 18.1513 | 18.0768 | 17.9951 | 17.8819 | 17.7513 | 17.6309 | 17.4523 | 17.1656 | 16.9329 | 16.6809 | 15.7023 | 15.5788 | 15.1349 | 17.4176 | 17.3115 | 17.1941 | 17.0278 | 16.8411 | 16.6564 | 16.3931 | 16.0053 | 15.6788 | 15.3451 | 14.0196 | 13.9625 | 13.8156
|  | LOCHGILPHEAD | CF |  |  |  |  | 16.3104 | 16.2258 | 16.137 | 16.0186 | 15.8931 | 15.7472 | 15.6196 | 15.39 | 15.1686 | 14.9053 | 13.738 | 13.037 | 12.4064 | 18.1604 | 18.1166 | 18.0615 | 17.9798 | 17.8982 | 17.7992 | 17.7217 | 17.5666 | 17.4064 | 17.2186 | 16.2584 | 15.4237 | 14.3145 | 17.436 | 17.3635 | 17.2798 | 17.1676 | 17.0513 | 16.9145 | 16.8013 | 16.589 | 16.3778 | 16.1298 | 14.9941 | 14.4666 | 13.9002
| CLACHAN | LOCHGOILHEAD | MINIMUM HEADROOM | NN 20159 01862 | YES | YES | 0 | -0.18776 | -0.19796 | -0.20816 | -0.21837 | -0.22959 | -0.23673 | -0.2602 | -0.2898 | -0.30408 | -0.32449 | -0.36837 | -0.38265 | -0.38776 | 0.76837 | 0.7602 | 0.74796 | 0.73673 | 0.71939 | 0.71735 | 0.7 | 0.67755 | 0.66429 | 0.65102 | 0.61224 | 0.59796 | 0.54694 | 0.57041 | 0.55612 | 0.54184 | 0.52755 | 0.50612 | 0.50102 | 0.47755 | 0.44592 | 0.43367 | 0.41429 | 0.37959 | 0.36837 | 0.36429
|  | LOCHGOILHEAD | EE |  |  |  |  | -0.18673 | -0.19796 | -0.20816 | -0.21837 | -0.22959 | -0.23673 | -0.2602 | -0.2898 | -0.30408 | -0.32449 | -0.36837 | -0.37551 | -0.38061 | 0.76939 | 0.7602 | 0.74796 | 0.73673 | 0.71939 | 0.71735 | 0.7 | 0.67755 | 0.66429 | 0.65102 | 0.61224 | 0.59796 | 0.57245 | 0.57041 | 0.55612 | 0.54184 | 0.52755 | 0.50612 | 0.50102 | 0.47755 | 0.44592 | 0.43367 | 0.41429 | 0.37959 | 0.37551 | 0.37245
|  | LOCHGOILHEAD | HT |  |  |  |  | -0.18776 | -0.1898 | -0.2 | -0.2102 | -0.21939 | -0.22857 | -0.23878 | -0.24796 | -0.26122 | -0.28163 | -0.35612 | -0.38265 | -0.38776 | 0.76837 | 0.76735 | 0.75816 | 0.75306 | 0.7449 | 0.73673 | 0.72347 | 0.71735 | 0.7051 | 0.6898 | 0.63265 | 0.61531 | 0.6102 | 0.57449 | 0.56735 | 0.55714 | 0.54898 | 0.53776 | 0.52755 | 0.51122 | 0.50204 | 0.48571 | 0.46429 | 0.39082 | 0.36837 | 0.36429
|  | LOCHGOILHEAD | HE |  |  |  |  | -0.18776 | -0.1898 | -0.19592 | -0.20408 | -0.2102 | -0.21735 | -0.22857 | -0.2398 | -0.24388 | -0.26122 | -0.33878 | -0.35816 | -0.3602 | 0.76837 | 0.76735 | 0.76122 | 0.75306 | 0.74592 | 0.74082 | 0.72653 | 0.71327 | 0.70918 | 0.69592 | 0.63469 | 0.61327 | 0.58776 | 0.57449 | 0.56939 | 0.56122 | 0.55306 | 0.54184 | 0.53469 | 0.51633 | 0.49694 | 0.49388 | 0.47449 | 0.40306 | 0.38571 | 0.38265
|  | LOCHGOILHEAD | CF |  |  |  |  | -0.18469 | -0.18878 | -0.19184 | -0.19898 | -0.20408 | -0.20918 | -0.21633 | -0.22653 | -0.23367 | -0.24184 | -0.28367 | -0.33571 | -0.35408 | 0.76939 | 0.77041 | 0.76735 | 0.7602 | 0.75204 | 0.7449 | 0.73878 | 0.72755 | 0.71837 | 0.70714 | 0.66531 | 0.60408 | 0.54694 | 0.57653 | 0.57347 | 0.56939 | 0.56224 | 0.55204 | 0.54286 | 0.5398 | 0.52449 | 0.51122 | 0.49898 | 0.45612 | 0.40102 | 0.38878
| GRUDIE BRIDGE | LOCHINVER | MINIMUM HEADROOM | NC 09516 22243 | YES | NO | 0.265 | -0.73247 | -0.7692 | -0.81716 | -0.86512 | -0.93859 | -0.98451 | -1.0692 | -1.157 | -1.2488 | -1.3263 | -1.4763 | -1.5406 | -1.5539 | -0.40798 | -0.42839 | -0.44778 | -0.47635 | -0.52124 | -0.55696 | -0.6141 | -0.67737 | -0.74267 | -0.79573 | -0.91002 | -0.97124 | -1.1396 | -0.57227 | -0.59676 | -0.65798 | -0.71308 | -0.78247 | -0.82635 | -0.91002 | -0.99573 | -1.0825 | -1.1559 | -1.307 | -1.3723 | -1.3835
|  | LOCHINVER | EE |  |  |  |  | -0.72124 | -0.7641 | -0.81716 | -0.86512 | -0.93859 | -0.98451 | -1.0692 | -1.157 | -1.2488 | -1.3263 | -1.4763 | -1.508 | -1.5314 | -0.38757 | -0.41716 | -0.44778 | -0.47635 | -0.52124 | -0.55696 | -0.6141 | -0.67737 | -0.74267 | -0.79573 | -0.91002 | -0.97124 | -1.0631 | -0.55186 | -0.59676 | -0.65798 | -0.71308 | -0.78247 | -0.82635 | -0.91002 | -0.99573 | -1.0825 | -1.1559 | -1.307 | -1.3386 | -1.3621
|  | LOCHINVER | HT |  |  |  |  | -0.73247 | -0.7692 | -0.80492 | -0.83655 | -0.87941 | -0.91716 | -0.97022 | -1.0182 | -1.0855 | -1.157 | -1.4549 | -1.5406 | -1.5539 | -0.40798 | -0.42839 | -0.44573 | -0.4641 | -0.48757 | -0.51002 | -0.53757 | -0.56614 | -0.61104 | -0.659 | -0.8692 | -0.91818 | -0.92941 | -0.57227 | -0.59369 | -0.62941 | -0.6641 | -0.71308 | -0.75696 | -0.81614 | -0.86512 | -0.93145 | -0.99676 | -1.2845 | -1.3723 | -1.3835
|  | LOCHINVER | HE |  |  |  |  | -0.70492 | -0.74165 | -0.77227 | -0.8039 | -0.83859 | -0.87022 | -0.91716 | -0.98349 | -1.0192 | -1.0794 | -1.3814 | -1.4161 | -1.4243 | -0.37941 | -0.40492 | -0.42533 | -0.44676 | -0.47022 | -0.49369 | -0.52431 | -0.55798 | -0.58349 | -0.62635 | -0.84369 | -0.89982 | -0.98043 | -0.54471 | -0.57124 | -0.5988 | -0.63043 | -0.67329 | -0.709 | -0.76308 | -0.82635 | -0.86206 | -0.91716 | -1.2121 | -1.2478 | -1.2559
|  | LOCHINVER | CF |  |  |  |  | -0.609 | -0.65186 | -0.68757 | -0.72431 | -0.75288 | -0.79267 | -0.82431 | -0.87227 | -0.92124 | -0.94267 | -1.1794 | -1.3478 | -1.4406 | -0.27533 | -0.30594 | -0.33145 | -0.35492 | -0.37431 | -0.40186 | -0.42737 | -0.46818 | -0.50696 | -0.52533 | -0.72839 | -0.92227 | -1.1396 | -0.44471 | -0.48349 | -0.5192 | -0.56206 | -0.59063 | -0.63451 | -0.66716 | -0.71614 | -0.76206 | -0.78349 | -1.0131 | -1.1743 | -1.2692
| LUNANHEAD | LOCHSIDE | MINIMUM HEADROOM | NO 45151 50548 | NO | YES | 3.023 | 5.7617 | 4.6791 | 3.7107 | 2.6168 | 2.0097 | 0.3413 | -0.63931 | -1.5536 | -2.2811 | -3.1852 | -8.3475 | -13.9556 | -18.5199 | 8.2189 | 7.3403 | 6.5648 | 5.6444 | 5.3842 | 3.6189 | 2.8525 | 2.0352 | 1.1076 | -0.26482 | -5.6842 | -11.8332 | -17.8199 | 7.3433 | 6.425 | 5.5535 | 4.428 | 3.9168 | 2.0066 | 1.0801 | 0.22498 | -0.45258 | -1.8873 | -7.7628 | -14.1699 | -19.8026
|  | LOCHSIDE | EE |  |  |  |  | 5.7729 | 4.8454 | 4.1546 | 3.5831 | 2.5556 | 1.3086 | 0.3464 | -0.2689 | -1.4434 | -2.3536 | -5.9301 | -10.4699 | -12.275 | 8.2464 | 7.5127 | 7.0576 | 6.7648 | 6.0372 | 4.9178 | 4.2474 | 3.724 | 2.7301 | 2.0342 | -0.79747 | -6.5189 | -9.3852 | 7.3729 | 6.5882 | 6.0311 | 5.6097 | 4.6291 | 3.2842 | 2.3097 | 1.7689 | 0.54436 | -0.3638 | -4.0118 | -9.5465 | -11.7628
|  | LOCHSIDE | HT |  |  |  |  | 5.7617 | 4.6791 | 3.7107 | 2.6168 | 2.0097 | 0.3413 | -0.63931 | -1.5536 | -2.2811 | -3.0832 | -6.7893 | -12.5016 | -16.7485 | 8.2189 | 7.3403 | 6.5648 | 5.6444 | 5.3842 | 3.6189 | 2.8525 | 2.1944 | 1.7433 | 1.2035 | -1.8465 | -8.3148 | -13.6301 | 7.3433 | 6.425 | 5.5535 | 4.428 | 3.9168 | 2.0066 | 1.0801 | 0.22498 | -0.45258 | -1.2362 | -5.0903 | -11.9148 | -17.1842
|  | LOCHSIDE | HE |  |  |  |  | 5.875 | 5.0862 | 4.227 | 3.3209 | 2.5586 | 0.95457 | 0.21273 | -0.85053 | -1.8454 | -3.1852 | -8.3475 | -13.9556 | -18.5199 | 8.3035 | 7.5964 | 6.7974 | 5.9454 | 5.4291 | 3.7025 | 3.0372 | 2.0352 | 1.1076 | -0.26482 | -5.6842 | -11.8332 | -17.8199 | 7.4352 | 6.7097 | 5.8546 | 4.9148 | 4.278 | 2.4484 | 1.6913 | 0.60049 | -0.42094 | -1.8873 | -7.7628 | -14.1699 | -19.8026
|  | LOCHSIDE | CF |  |  |  |  | 6.1648 | 5.625 | 5.3923 | 5.0301 | 4.5321 | 3.8505 | 3.3219 | 2.8678 | 2.378 | 1.7984 | -0.53217 | -3.3332 | -5.572 | 8.5627 | 8.0076 | 7.8291 | 7.5291 | 7.0944 | 6.4331 | 5.9913 | 5.6178 | 5.1617 | 4.6148 | 2.3209 | -0.3638 | -3.3597 | 7.7025 | 7.1535 | 6.9678 | 6.6576 | 6.1842 | 5.4709 | 4.9678 | 4.5076 | 3.9923 | 3.377 | 0.72804 | -1.9944 | -4.0414
| BRIDGE OF DUN | LOGIE PERT | MINIMUM HEADROOM | NO 67764 64427 | YES | NO | 1.073 | 3.5549 | 3.5355 | 3.5059 | 3.4885 | 3.4661 | 3.4345 | 3.3987 | 3.3763 | 3.3355 | 3.3038 | 3.1865 | 3.1161 | 3.0855 | 3.612 | 3.5977 | 3.5702 | 3.5579 | 3.5406 | 3.513 | 3.4814 | 3.4528 | 3.4181 | 3.3896 | 3.2845 | 3.2355 | 3.2069 | 3.5054 | 3.4788 | 3.4401 | 3.4176 | 3.3911 | 3.3513 | 3.3044 | 3.2758 | 3.2278 | 3.185 | 3.0462 | 2.9778 | 2.9411
|  | LOGIE PERT | EE |  |  |  |  | 3.5549 | 3.5355 | 3.5059 | 3.4885 | 3.4661 | 3.4345 | 3.3987 | 3.3763 | 3.3355 | 3.3038 | 3.1916 | 3.1732 | 3.1712 | 3.612 | 3.5977 | 3.5702 | 3.5579 | 3.5406 | 3.513 | 3.4814 | 3.4528 | 3.4181 | 3.3896 | 3.3069 | 3.2977 | 3.2865 | 3.5054 | 3.4788 | 3.4401 | 3.4176 | 3.3911 | 3.3513 | 3.3044 | 3.2758 | 3.2278 | 3.185 | 3.0666 | 3.0523 | 3.0503
|  | LOGIE PERT | HT |  |  |  |  | 3.564 | 3.5538 | 3.5355 | 3.5192 | 3.4957 | 3.4834 | 3.4579 | 3.4365 | 3.4069 | 3.3753 | 3.2232 | 3.1508 | 3.1243 | 3.6202 | 3.611 | 3.5947 | 3.5814 | 3.56 | 3.5498 | 3.5273 | 3.5028 | 3.4743 | 3.4447 | 3.3253 | 3.2804 | 3.2589 | 3.5156 | 3.4972 | 3.4717 | 3.4493 | 3.4176 | 3.3982 | 3.3635 | 3.3309 | 3.2931 | 3.2544 | 3.0942 | 3.0258 | 2.9993
|  | LOGIE PERT | HE |  |  |  |  | 3.5651 | 3.5569 | 3.5375 | 3.5263 | 3.5028 | 3.4936 | 3.4661 | 3.4477 | 3.4192 | 3.3896 | 3.1865 | 3.1161 | 3.0855 | 3.6202 | 3.613 | 3.5967 | 3.5865 | 3.5661 | 3.5518 | 3.5253 | 3.4967 | 3.4661 | 3.4314 | 3.2845 | 3.2355 | 3.2069 | 3.5146 | 3.5023 | 3.4788 | 3.4615 | 3.4339 | 3.4197 | 3.385 | 3.3462 | 3.3013 | 3.2544 | 3.0462 | 2.9778 | 2.9411
|  | LOGIE PERT | CF |  |  |  |  | 3.5702 | 3.5579 | 3.5487 | 3.5385 | 3.5212 | 3.5028 | 3.4967 | 3.4763 | 3.4651 | 3.4457 | 3.3559 | 3.2222 | 3.1314 | 3.6253 | 3.6151 | 3.6059 | 3.5967 | 3.5814 | 3.5651 | 3.5589 | 3.5396 | 3.5324 | 3.514 | 3.3998 | 3.2998 | 3.2263 | 3.5207 | 3.5054 | 3.4911 | 3.4737 | 3.4533 | 3.4319 | 3.4227 | 3.3952 | 3.3819 | 3.3574 | 3.2125 | 3.0737 | 2.9901
| MILTON OF CRAIGIE | LONGHAUGH | MINIMUM HEADROOM | NO 42768 33789 | NO | NO | 1.65 | 12.5268 | 11.5992 | 10.6217 | 9.4778 | 8.3125 | 7.1258 | 6.186 | 5.3002 | 4.5921 | 3.7615 | 0.69616 | -0.54466 | -0.69058 | 14.8472 | 14.1747 | 13.4635 | 12.5778 | 11.6717 | 10.7462 | 10.1737 | 9.6604 | 9.2339 | 8.7533 | 7.0421 | 6.5482 | 6.1298 | 14.1084 | 13.239 | 12.3268 | 11.2431 | 10.136 | 9.0084 | 8.1615 | 7.3686 | 6.7747 | 6.038 | 3.2951 | 2.2023 | 2.0758
|  | LONGHAUGH | EE |  |  |  |  | 12.5268 | 11.6196 | 10.7431 | 9.6431 | 8.4911 | 7.6309 | 6.5094 | 5.5104 | 4.5921 | 3.7615 | 0.72269 | -0.041596 | -0.21098 | 14.8553 | 14.2125 | 13.5727 | 12.736 | 11.8523 | 11.1696 | 10.4145 | 9.7798 | 9.2339 | 8.7533 | 7.0421 | 6.5482 | 6.1298 | 14.1227 | 13.3023 | 12.49 | 11.4635 | 10.3829 | 9.5145 | 8.4849 | 7.5778 | 6.7747 | 6.038 | 3.3053 | 2.6421 | 2.4921
|  | LONGHAUGH | HT |  |  |  |  | 12.5441 | 11.5992 | 10.6217 | 9.4778 | 8.3125 | 7.1258 | 6.186 | 5.3002 | 4.7911 | 4.04 | 0.69616 | -0.54466 | -0.69058 | 14.8472 | 14.1747 | 13.4635 | 12.5778 | 11.6717 | 10.7462 | 10.1737 | 9.6604 | 9.4594 | 9.0666 | 7.2809 | 6.638 | 6.5615 | 14.1084 | 13.239 | 12.3268 | 11.2431 | 10.136 | 9.0084 | 8.1615 | 7.3686 | 6.9023 | 6.237 | 3.2951 | 2.2023 | 2.0758
|  | LONGHAUGH | HE |  |  |  |  | 12.6778 | 11.9431 | 11.2441 | 10.3564 | 9.4268 | 8.5206 | 7.6002 | 6.8053 | 6.3717 | 5.7227 | 2.6258 | 0.99514 | 0.67269 | 14.9625 | 14.387 | 13.837 | 13.1135 | 12.3482 | 11.5931 | 10.9278 | 10.386 | 10.1523 | 9.739 | 7.8523 | 6.9451 | 6.5002 | 14.239 | 13.5564 | 12.8962 | 12.0543 | 11.1645 | 10.2972 | 9.4421 | 8.7104 | 8.3002 | 7.7155 | 4.9339 | 3.4921 | 3.2033
|  | LONGHAUGH | CF |  |  |  |  | 13.0788 | 12.688 | 12.2758 | 11.838 | 11.3023 | 10.7206 | 10.2278 | 9.6798 | 9.2329 | 8.7717 | 6.4166 | 3.6176 | 1.7247 | 15.2951 | 14.9809 | 14.6411 | 14.2768 | 13.8247 | 13.3247 | 12.9145 | 12.4737 | 12.1155 | 11.7482 | 9.9166 | 7.8349 | 6.3125 | 14.638 | 14.2798 | 13.89 | 13.4717 | 12.9655 | 12.4084 | 11.9441 | 11.4533 | 11.0492 | 10.636 | 8.4319 | 5.8655 | 4.1319
| INVERNESS | LONGMAN DRIVE | MINIMUM HEADROOM | NH 67139 46770 | NO | NO | 4.195 | 9.3035 | 8.4502 | 7.4268 | 6.3709 | 5.1679 | 3.7894 | 2.3868 | 0.6834 | -0.8181 | -2.143 | -9.8356 | -13.2163 | -14.1355 | 9.4658 | 8.8721 | 8.145 | 7.4099 | 6.4938 | 5.4113 | 4.3373 | 3.0577 | 1.9071 | 0.69617 | -5.3626 | -8.2144 | -9.2086 | 7.3839 | 6.63 | 5.7229 | 4.7917 | 3.7125 | 2.4565 | 1.1048 | -0.52856 | -1.9809 | -3.3633 | -10.8977 | -14.3281 | -15.378
|  | LONGMAN DRIVE | EE |  |  |  |  | 9.3035 | 8.4502 | 7.4268 | 6.3709 | 5.1679 | 3.7894 | 2.3868 | 0.6834 | -0.8181 | -2.1427 | -6.314 | -7.4761 | -7.8268 | 9.4658 | 8.8721 | 8.145 | 7.4099 | 6.4938 | 5.4113 | 4.3373 | 3.0577 | 1.9071 | 0.90558 | -2.3264 | -3.4978 | -3.8863 | 7.3839 | 6.63 | 5.7229 | 4.7917 | 3.7125 | 2.4565 | 1.1048 | -0.52856 | -1.9809 | -3.2565 | -7.3126 | -8.5957 | -8.9989
|  | LONGMAN DRIVE | HT |  |  |  |  | 9.7083 | 9.0748 | 8.3823 | 7.6081 | 6.8242 | 5.6548 | 4.5952 | 3.3308 | 2.1945 | 1.0198 | -4.0664 | -6.7874 | -7.6432 | 9.7699 | 9.3219 | 8.8176 | 8.2492 | 7.7193 | 6.8134 | 6.0312 | 5.0868 | 4.2361 | 3.3467 | -0.60395 | -2.9996 | -3.931 | 7.7464 | 7.1895 | 6.5646 | 5.8624 | 5.1807 | 4.0399 | 3.0718 | 1.9411 | 0.91434 | -0.21867 | -5.1768 | -7.986 | -8.9693
|  | LONGMAN DRIVE | HE |  |  |  |  | 9.5969 | 8.8207 | 7.9384 | 6.9495 | 5.8561 | 4.4259 | 3.0282 | 1.2806 | -0.37103 | -2.143 | -9.8356 | -13.2163 | -14.1355 | 9.6752 | 9.1296 | 8.4671 | 7.7328 | 6.9513 | 5.7902 | 4.7108 | 3.3643 | 2.0885 | 0.69617 | -5.3626 | -8.2144 | -9.2086 | 7.6432 | 6.9592 | 6.1582 | 5.2576 | 4.2832 | 2.9473 | 1.6687 | -0.027986 | -1.6312 | -3.3633 | -10.8977 | -14.3281 | -15.378
|  | LONGMAN DRIVE | CF |  |  |  |  | 9.8205 | 9.4019 | 8.9141 | 8.3289 | 7.6867 | 6.9093 | 6.159 | 5.208 | 4.3014 | 3.3223 | -2.1551 | -6.8295 | -9.386 | 9.8416 | 9.5418 | 9.1932 | 8.7602 | 8.2902 | 7.7125 | 7.1758 | 6.4673 | 5.7653 | 5.0026 | 0.78991 | -2.7959 | -4.7455 | 7.8391 | 7.4658 | 7.0311 | 6.5055 | 5.9229 | 5.2024 | 4.5362 | 3.7001 | 2.8914 | 2.0013 | -3.2966 | -7.8233 | -10.2991
| ELGIN | LOSSIEMOUTH | MINIMUM HEADROOM | NJ 23203 69923 | NO | YES | 0.679 | 10.2473 | 9.9861 | 9.7147 | 9.3994 | 9.1065 | 8.7545 | 8.2422 | 7.6708 | 7.4524 | 6.981 | 4.9932 | 3.7779 | 3.5861 | 8.9055 | 8.8279 | 8.7432 | 8.6361 | 8.4636 | 8.2606 | 7.9779 | 7.6616 | 7.582 | 7.333 | 6.2228 | 5.4504 | 4.3126 | 8.3131 | 8.0835 | 7.8458 | 7.5723 | 7.306 | 6.9989 | 6.5397 | 6.0335 | 5.8254 | 5.406 | 3.6101 | 2.5009 | 2.3284
|  | LOSSIEMOUTH | EE |  |  |  |  | 10.2473 | 9.9861 | 9.7147 | 9.3994 | 9.1065 | 8.7545 | 8.2422 | 7.6708 | 7.4524 | 6.981 | 4.9932 | 3.8534 | 3.5953 | 8.9055 | 8.8279 | 8.7432 | 8.6361 | 8.4636 | 8.2606 | 7.9779 | 7.6616 | 7.582 | 7.333 | 6.2228 | 5.4504 | 4.7596 | 8.3131 | 8.0835 | 7.8458 | 7.5723 | 7.306 | 6.9989 | 6.5397 | 6.0335 | 5.8254 | 5.406 | 3.6101 | 2.5662 | 2.3356
|  | LOSSIEMOUTH | HT |  |  |  |  | 10.3218 | 10.082 | 9.8432 | 9.5688 | 9.3014 | 8.9932 | 8.5239 | 8.0626 | 7.5728 | 7.0698 | 5.0228 | 3.7779 | 3.5861 | 8.9524 | 8.8943 | 8.8361 | 8.7616 | 8.6565 | 8.4932 | 8.2647 | 8.0371 | 7.7912 | 7.5361 | 6.5841 | 6.0055 | 5.9147 | 8.3815 | 8.1682 | 7.956 | 7.7131 | 7.4805 | 7.206 | 6.7866 | 6.3693 | 5.9274 | 5.4764 | 3.6346 | 2.5009 | 2.3284
|  | LOSSIEMOUTH | HE |  |  |  |  | 10.3126 | 10.1565 | 9.9953 | 9.8004 | 9.6106 | 9.38 | 9.0351 | 8.6983 | 8.3279 | 7.9494 | 6.1483 | 4.833 | 4.3759 | 8.9412 | 8.88 | 8.8208 | 8.7453 | 8.6657 | 8.5698 | 8.381 | 8.182 | 7.9596 | 7.73 | 6.6534 | 5.7453 | 4.9922 | 8.3733 | 8.2366 | 8.0927 | 7.9244 | 7.758 | 7.554 | 7.2489 | 6.9438 | 6.6131 | 6.2723 | 4.6468 | 3.4407 | 3.0223
|  | LOSSIEMOUTH | CF |  |  |  |  | 10.3769 | 10.2769 | 10.1769 | 10.0524 | 9.9014 | 9.7851 | 9.6198 | 9.4218 | 9.2922 | 9.0994 | 7.7483 | 6.7381 | 5.5453 | 8.9626 | 8.9218 | 8.879 | 8.8279 | 8.7698 | 8.7147 | 8.6432 | 8.5177 | 8.4055 | 8.2626 | 7.2351 | 6.1116 | 4.3126 | 8.405 | 8.3458 | 8.258 | 8.1509 | 8.0325 | 7.9295 | 7.7978 | 7.6376 | 7.5131 | 7.358 | 6.1182 | 5.1733 | 4.0958
| BROADFORD | LOWER OLLACH | MINIMUM HEADROOM | NG 51241 37001 | YES | YES | 0.9 | -0.33599 | -0.36048 | -0.40027 | -0.4268 | -0.4666 | -0.49823 | -0.55129 | -0.60946 | -0.63905 | -0.68293 | -0.78293 | -0.81864 | -0.82782 | -0.18395 | -0.19925 | -0.22476 | -0.24313 | -0.27068 | -0.29007 | -0.32578 | -0.36558 | -0.38293 | -0.4115 | -0.48293 | -0.50946 | -0.6268 | -0.28293 | -0.3064 | -0.34517 | -0.36864 | -0.40844 | -0.43701 | -0.48803 | -0.54517 | -0.5717 | -0.61252 | -0.70538 | -0.74007 | -0.74721
|  | LOWER OLLACH | EE |  |  |  |  | -0.33599 | -0.36048 | -0.40027 | -0.4268 | -0.4666 | -0.49823 | -0.55129 | -0.60946 | -0.63905 | -0.68293 | -0.78293 | -0.79517 | -0.80538 | -0.18395 | -0.19925 | -0.22476 | -0.24313 | -0.27068 | -0.29007 | -0.32578 | -0.36558 | -0.38293 | -0.4115 | -0.48293 | -0.50946 | -0.56048 | -0.28293 | -0.3064 | -0.34517 | -0.36864 | -0.40844 | -0.43701 | -0.48803 | -0.54517 | -0.5717 | -0.61252 | -0.70538 | -0.71762 | -0.7268
|  | LOWER OLLACH | HT |  |  |  |  | -0.3217 | -0.34007 | -0.37068 | -0.39619 | -0.43293 | -0.45333 | -0.49109 | -0.52578 | -0.56558 | -0.60742 | -0.75742 | -0.81864 | -0.82782 | -0.17272 | -0.18191 | -0.20129 | -0.2166 | -0.23905 | -0.25027 | -0.2768 | -0.29721 | -0.32272 | -0.35027 | -0.45027 | -0.48701 | -0.49211 | -0.26864 | -0.28803 | -0.31558 | -0.33905 | -0.37476 | -0.39415 | -0.42987 | -0.45946 | -0.49925 | -0.54007 | -0.68395 | -0.74007 | -0.74721
|  | LOWER OLLACH | HE |  |  |  |  | -0.3217 | -0.33905 | -0.3615 | -0.38089 | -0.41048 | -0.4217 | -0.46048 | -0.48905 | -0.52272 | -0.56252 | -0.73191 | -0.76762 | -0.77272 | -0.17272 | -0.18191 | -0.19925 | -0.21252 | -0.23191 | -0.24007 | -0.26558 | -0.28497 | -0.30946 | -0.33599 | -0.45027 | -0.48905 | -0.53395 | -0.26966 | -0.28701 | -0.30742 | -0.32578 | -0.35538 | -0.36456 | -0.40231 | -0.42782 | -0.4615 | -0.49925 | -0.65946 | -0.69109 | -0.69619
|  | LOWER OLLACH | CF |  |  |  |  | -0.3166 | -0.33395 | -0.35129 | -0.36762 | -0.39211 | -0.4166 | -0.42578 | -0.4564 | -0.48293 | -0.49823 | -0.61456 | -0.71966 | -0.77272 | -0.16762 | -0.17987 | -0.19211 | -0.20333 | -0.21864 | -0.23701 | -0.24415 | -0.2666 | -0.28395 | -0.29517 | -0.38905 | -0.50538 | -0.6268 | -0.26456 | -0.28089 | -0.29721 | -0.31354 | -0.33497 | -0.35946 | -0.36864 | -0.39721 | -0.42374 | -0.43701 | -0.54823 | -0.65129 | -0.69721
| KILLIN | LUBNAIG | MINIMUM HEADROOM | NN 57455 13800 | YES | YES | 0 | 0.20029 | 0.20029 | 0.19212 | 0.1911 | 0.19008 | 0.18192 | 0.17988 | 0.17069 | 0.17069 | 0.16967 | 0.16967 | 0.17069 | 0.17069 | 0.19249 | 0.19249 | 0.18433 | 0.18433 | 0.18331 | 0.17514 | 0.17412 | 0.16494 | 0.16494 | 0.16392 | 0.16392 | 0.168 | 0.16596 | 0.19231 | 0.19231 | 0.18312 | 0.1821 | 0.18108 | 0.17292 | 0.1719 | 0.16169 | 0.16169 | 0.16067 | 0.16067 | 0.16373 | 0.16373
|  | LUBNAIG | EE |  |  |  |  | 0.20029 | 0.20029 | 0.19212 | 0.1911 | 0.19008 | 0.18192 | 0.17988 | 0.17069 | 0.17069 | 0.16967 | 0.17171 | 0.17069 | 0.17069 | 0.19249 | 0.19249 | 0.18433 | 0.18433 | 0.18331 | 0.17514 | 0.17412 | 0.16494 | 0.16494 | 0.16392 | 0.16902 | 0.168 | 0.168 | 0.19231 | 0.19231 | 0.18312 | 0.1821 | 0.18108 | 0.17292 | 0.1719 | 0.16169 | 0.16169 | 0.16067 | 0.16476 | 0.16373 | 0.16373
|  | LUBNAIG | HT |  |  |  |  | 0.20029 | 0.20029 | 0.20029 | 0.1911 | 0.1911 | 0.19008 | 0.19008 | 0.1809 | 0.17886 | 0.17784 | 0.17171 | 0.17069 | 0.17069 | 0.19351 | 0.19249 | 0.19249 | 0.18433 | 0.18433 | 0.18331 | 0.18331 | 0.17412 | 0.1731 | 0.17208 | 0.16902 | 0.168 | 0.168 | 0.19231 | 0.19231 | 0.19231 | 0.1821 | 0.1821 | 0.18108 | 0.18108 | 0.1719 | 0.17088 | 0.16884 | 0.16476 | 0.16373 | 0.16373
|  | LUBNAIG | HE |  |  |  |  | 0.20029 | 0.20029 | 0.20029 | 0.19212 | 0.1911 | 0.19008 | 0.18906 | 0.17988 | 0.17886 | 0.17784 | 0.17273 | 0.17273 | 0.17171 | 0.19249 | 0.19249 | 0.19249 | 0.18433 | 0.18433 | 0.18331 | 0.18229 | 0.17412 | 0.1731 | 0.17208 | 0.17004 | 0.17004 | 0.16902 | 0.19231 | 0.19231 | 0.19231 | 0.18312 | 0.1821 | 0.18108 | 0.18006 | 0.1719 | 0.16986 | 0.16884 | 0.16578 | 0.16578 | 0.16476
|  | LUBNAIG | CF |  |  |  |  | 0.20029 | 0.20029 | 0.20029 | 0.19314 | 0.19212 | 0.19212 | 0.1911 | 0.19008 | 0.19008 | 0.18192 | 0.16967 | 0.17171 | 0.17069 | 0.19351 | 0.19249 | 0.19249 | 0.18535 | 0.18433 | 0.18433 | 0.18433 | 0.18331 | 0.18331 | 0.17514 | 0.16392 | 0.17004 | 0.16596 | 0.19231 | 0.19231 | 0.19231 | 0.18516 | 0.18312 | 0.18312 | 0.1821 | 0.18108 | 0.18108 | 0.17292 | 0.16067 | 0.16476 | 0.16373
| LUNANHEAD | LUNANHEAD | MINIMUM HEADROOM | NO 47042 51733 | NO | YES | 0.909 | 7.1777 | 6.9991 | 6.6695 | 6.1991 | 6.0318 | 5.0869 | 4.6093 | 4.0593 | 3.5542 | 2.9359 | -0.63453 | -4.1917 | -7.21 | 8.7624 | 8.6144 | 8.2787 | 7.7512 | 7.592 | 6.4981 | 6.0879 | 5.5777 | 5.0614 | 4.2522 | 0.85424 | -2.9672 | -6.4968 | 8.1078 | 7.8599 | 7.4445 | 6.8252 | 6.5772 | 5.3935 | 4.9731 | 4.4068 | 3.7792 | 2.8507 | -1.1361 | -5.284 | -8.932
|  | LUNANHEAD | EE |  |  |  |  | 7.1777 | 6.9991 | 6.8308 | 6.6369 | 6.2675 | 5.6216 | 4.991 | 4.4471 | 4.0073 | 3.4216 | 0.91649 | -2.4805 | -3.6896 | 8.7624 | 8.6144 | 8.4604 | 8.2798 | 7.8481 | 7.1655 | 6.7175 | 6.3981 | 5.9522 | 5.5502 | 3.79 | 0.38893 | -1.3325 | 8.1078 | 7.8599 | 7.6007 | 7.3231 | 6.8037 | 6.0252 | 5.4333 | 4.9588 | 4.3935 | 3.8507 | 1.518 | -2.3973 | -3.8412
|  | LUNANHEAD | HT |  |  |  |  | 7.1879 | 7.0471 | 6.6695 | 6.1991 | 6.0318 | 5.0869 | 4.6093 | 4.0593 | 3.5542 | 2.9359 | 0.36138 | -3.5662 | -6.2702 | 8.7859 | 8.6767 | 8.2787 | 7.7512 | 7.592 | 6.4981 | 6.2134 | 5.8675 | 5.592 | 5.2155 | 3.1522 | -0.91209 | -4.207 | 8.1486 | 7.9476 | 7.4445 | 6.8252 | 6.5772 | 5.3935 | 4.9731 | 4.4762 | 4.015 | 3.4394 | 0.82822 | -3.7106 | -7.0116
|  | LUNANHEAD | HE |  |  |  |  | 7.2257 | 7.1144 | 6.8114 | 6.3981 | 6.1665 | 5.3032 | 4.9298 | 4.4849 | 3.8849 | 3.0389 | -0.63453 | -4.1917 | -7.21 | 8.8175 | 8.7042 | 8.3542 | 7.8644 | 7.592 | 6.5246 | 6.0879 | 5.5777 | 5.0614 | 4.2522 | 0.85424 | -2.9672 | -6.4968 | 8.1803 | 8.0078 | 7.5925 | 7.0364 | 6.6996 | 5.565 | 5.0282 | 4.4068 | 3.7792 | 2.8507 | -1.1361 | -5.284 | -8.932
|  | LUNANHEAD | CF |  |  |  |  | 7.3879 | 7.294 | 7.2063 | 7.1155 | 6.9114 | 6.5767 | 6.3471 | 6.1338 | 5.942 | 5.6808 | 4.2246 | 2.5042 | 1.1104 | 8.9818 | 8.8961 | 8.8093 | 8.7216 | 8.4798 | 8.0849 | 7.8216 | 7.5726 | 7.3318 | 7.0134 | 5.7032 | 4.3695 | 2.7022 | 8.366 | 8.2425 | 8.1221 | 7.9915 | 7.7119 | 7.269 | 6.9548 | 6.6476 | 6.3578 | 5.9925 | 4.3364 | 2.6109 | 1.2119
| PORT ANN | LUSSAGIVEN | MINIMUM HEADROOM | NR 63461 86798 | YES | YES | 0 | 0.089429 | 0.089429 | 0.080245 | 0.073102 | 0.070041 | 0.06902 | 0.071061 | 0.06698 | 0.06698 | 0.063918 | 0.064939 | 0.063918 | 0.063918 | 0.089612 | 0.089612 | 0.081449 | 0.074306 | 0.075327 | 0.073286 | 0.073286 | 0.074306 | 0.074306 | 0.072265 | 0.073286 | 0.072265 | 0.072265 | 0.091051 | 0.091051 | 0.082888 | 0.075745 | 0.071663 | 0.070643 | 0.072684 | 0.069622 | 0.070643 | 0.066561 | 0.066561 | 0.065541 | 0.065541
|  | LUSSAGIVEN | EE |  |  |  |  | 0.089429 | 0.089429 | 0.080245 | 0.073102 | 0.070041 | 0.06902 | 0.071061 | 0.070041 | 0.06698 | 0.063918 | 0.064939 | 0.063918 | 0.063918 | 0.089612 | 0.089612 | 0.081449 | 0.074306 | 0.075327 | 0.074306 | 0.077367 | 0.077367 | 0.075327 | 0.072265 | 0.073286 | 0.072265 | 0.072265 | 0.091051 | 0.091051 | 0.082888 | 0.075745 | 0.071663 | 0.070643 | 0.072684 | 0.072684 | 0.070643 | 0.066561 | 0.066561 | 0.065541 | 0.065541
|  | LUSSAGIVEN | HT |  |  |  |  | 0.096571 | 0.089429 | 0.087388 | 0.087388 | 0.080245 | 0.071061 | 0.071061 | 0.06698 | 0.073102 | 0.068 | 0.06698 | 0.063918 | 0.063918 | 0.096755 | 0.089612 | 0.088592 | 0.088592 | 0.081449 | 0.073286 | 0.073286 | 0.074306 | 0.079408 | 0.076347 | 0.075327 | 0.072265 | 0.072265 | 0.098194 | 0.091051 | 0.090031 | 0.090031 | 0.082888 | 0.072684 | 0.072684 | 0.069622 | 0.075745 | 0.070643 | 0.069622 | 0.065541 | 0.065541
|  | LUSSAGIVEN | HE |  |  |  |  | 0.096571 | 0.089429 | 0.089429 | 0.087388 | 0.080245 | 0.080245 | 0.072082 | 0.06902 | 0.075143 | 0.06902 | 0.064939 | 0.063918 | 0.063918 | 0.096755 | 0.089612 | 0.089612 | 0.088592 | 0.081449 | 0.081449 | 0.073286 | 0.074306 | 0.079408 | 0.077367 | 0.074306 | 0.072265 | 0.072265 | 0.098194 | 0.091051 | 0.091051 | 0.090031 | 0.082888 | 0.082888 | 0.074724 | 0.070643 | 0.076765 | 0.071663 | 0.068602 | 0.065541 | 0.065541
|  | LUSSAGIVEN | CF |  |  |  |  | 0.096571 | 0.089429 | 0.089429 | 0.089429 | 0.082286 | 0.080245 | 0.080245 | 0.073102 | 0.073102 | 0.070041 | 0.070041 | 0.06698 | 0.064939 | 0.096755 | 0.089612 | 0.089612 | 0.089612 | 0.082469 | 0.081449 | 0.081449 | 0.074306 | 0.074306 | 0.075327 | 0.077367 | 0.074306 | 0.073286 | 0.098194 | 0.091051 | 0.091051 | 0.091051 | 0.083908 | 0.082888 | 0.082888 | 0.075745 | 0.075745 | 0.071663 | 0.072684 | 0.070643 | 0.068602
| LYNDHURST | LYNDHURST | MINIMUM HEADROOM | NO 37434 32575 | NO | YES | 3.615 | 7.0285 | 6.9132 | 6.8183 | 6.7163 | 6.604 | 6.4928 | 6.2989 | 6.0703 | 5.8846 | 5.6805 | 4.9438 | 4.8132 | 4.8061 | 7.5969 | 7.4724 | 7.3734 | 7.2622 | 7.1408 | 7.0377 | 6.9081 | 6.7663 | 6.6571 | 6.5397 | 6.0265 | 5.7356 | 4.3428 | 7.3484 | 7.2351 | 7.1433 | 7.0464 | 6.9362 | 6.8453 | 6.6606 | 6.4566 | 6.2872 | 6.1106 | 5.4382 | 5.3137 | 5.3066
|  | LYNDHURST | EE |  |  |  |  | 7.0612 | 6.9275 | 6.8214 | 6.7163 | 6.604 | 6.4928 | 6.2989 | 6.0703 | 5.8846 | 5.6805 | 4.9438 | 5.055 | 5.0775 | 7.6346 | 7.4856 | 7.3734 | 7.2622 | 7.1408 | 7.0377 | 6.9081 | 6.7663 | 6.6571 | 6.5397 | 6.0265 | 5.8101 | 5.2642 | 7.379 | 7.2494 | 7.1474 | 7.0464 | 6.9362 | 6.8453 | 6.6606 | 6.4566 | 6.2872 | 6.1106 | 5.4382 | 5.5239 | 5.5249
|  | LYNDHURST | HT |  |  |  |  | 7.0285 | 6.9132 | 6.8183 | 6.7316 | 6.6428 | 6.5612 | 6.3999 | 6.2163 | 6.0244 | 5.8285 | 4.9632 | 4.8132 | 4.8061 | 7.5969 | 7.4724 | 7.3734 | 7.2836 | 7.1989 | 7.1173 | 7.0203 | 6.9316 | 6.8356 | 6.7356 | 6.2724 | 6.1734 | 6.155 | 7.3484 | 7.2351 | 7.1433 | 7.0606 | 6.978 | 6.8994 | 6.7525 | 6.5882 | 6.4178 | 6.2443 | 5.4892 | 5.3137 | 5.3066
|  | LYNDHURST | HE |  |  |  |  | 7.0856 | 6.9734 | 6.8867 | 6.8071 | 6.7254 | 6.6469 | 6.5459 | 6.3999 | 6.254 | 6.105 | 5.3305 | 5.0561 | 5.003 | 7.6571 | 7.5336 | 7.4448 | 7.3632 | 7.2816 | 7.201 | 7.0999 | 7.0061 | 6.9061 | 6.803 | 6.2744 | 5.9081 | 5.3897 | 7.4035 | 7.2933 | 7.2106 | 7.1311 | 7.0545 | 6.977 | 6.8902 | 6.8066 | 6.7168 | 6.5739 | 5.9484 | 5.6862 | 5.6392
|  | LYNDHURST | CF |  |  |  |  | 7.2479 | 7.1734 | 7.104 | 7.0489 | 6.9826 | 6.9295 | 6.8693 | 6.803 | 6.7438 | 6.6805 | 6.1336 | 5.5356 | 5.0459 | 7.8265 | 7.7397 | 7.6632 | 7.602 | 7.5275 | 7.4601 | 7.3877 | 7.302 | 7.2275 | 7.1469 | 6.6214 | 5.7356 | 4.3428 | 7.5637 | 7.4892 | 7.4229 | 7.3658 | 7.3035 | 7.2494 | 7.1902 | 7.126 | 7.0688 | 7.0045 | 6.6331 | 6.1055 | 5.6862
| THURSO | LYNESS | MINIMUM HEADROOM | ND 30350 94625 | YES | NO | 0.005 | 0.21837 | 0.20408 | 0.19082 | 0.17551 | 0.16327 | 0.13878 | 0.11735 | 0.076531 | 0.040816 | 0.038776 | -0.046939 | -0.084694 | -0.09898 | 0.55918 | 0.5449 | 0.52959 | 0.50612 | 0.49796 | 0.47551 | 0.45816 | 0.42653 | 0.39898 | 0.39898 | 0.34286 | 0.31429 | 0.24082 | 0.13265 | 0.11735 | 0.10306 | 0.084694 | 0.070408 | 0.04898 | 0.028571 | -0.0020408 | -0.030612 | -0.047959 | -0.11735 | -0.1398 | -0.14592
|  | LYNESS | EE |  |  |  |  | 0.21837 | 0.20408 | 0.19082 | 0.17551 | 0.16327 | 0.13878 | 0.11735 | 0.076531 | 0.040816 | 0.038776 | -0.046939 | -0.067347 | -0.067347 | 0.55918 | 0.5449 | 0.52959 | 0.50612 | 0.49796 | 0.47551 | 0.45816 | 0.42653 | 0.39898 | 0.39898 | 0.34286 | 0.31429 | 0.27959 | 0.13265 | 0.11735 | 0.10306 | 0.084694 | 0.070408 | 0.04898 | 0.028571 | -0.0020408 | -0.030612 | -0.047959 | -0.11735 | -0.13163 | -0.13469
|  | LYNESS | HT |  |  |  |  | 0.22245 | 0.21224 | 0.20204 | 0.18878 | 0.17755 | 0.16224 | 0.1449 | 0.11735 | 0.10102 | 0.077551 | -0.029592 | -0.078571 | -0.092857 | 0.56633 | 0.56122 | 0.54898 | 0.53673 | 0.52551 | 0.50918 | 0.50102 | 0.48061 | 0.47143 | 0.44796 | 0.37245 | 0.3398 | 0.33571 | 0.13469 | 0.12449 | 0.11122 | 0.09898 | 0.084694 | 0.068367 | 0.053061 | 0.027551 | 0.010204 | -0.014286 | -0.10102 | -0.1398 | -0.14592
|  | LYNESS | HE |  |  |  |  | 0.22245 | 0.21327 | 0.2051 | 0.19388 | 0.18367 | 0.17041 | 0.15918 | 0.13776 | 0.11939 | 0.097959 | -0.044898 | -0.084694 | -0.09898 | 0.56633 | 0.56122 | 0.55 | 0.53673 | 0.52857 | 0.51327 | 0.50816 | 0.48571 | 0.46531 | 0.45714 | 0.36939 | 0.33265 | 0.3 | 0.13469 | 0.12449 | 0.11531 | 0.10714 | 0.094898 | 0.081633 | 0.069388 | 0.05 | 0.02551 | 0.011224 | -0.092857 | -0.12551 | -0.14082
|  | LYNESS | CF |  |  |  |  | 0.22449 | 0.21735 | 0.21122 | 0.20204 | 0.1949 | 0.18776 | 0.17653 | 0.16735 | 0.15714 | 0.1449 | 0.067347 | -0.022449 | -0.085714 | 0.57143 | 0.56224 | 0.55918 | 0.54898 | 0.53776 | 0.52857 | 0.51633 | 0.51327 | 0.5 | 0.48878 | 0.41122 | 0.32959 | 0.24082 | 0.13673 | 0.12959 | 0.12347 | 0.11224 | 0.10306 | 0.094898 | 0.084694 | 0.07449 | 0.063265 | 0.05 | -0.019388 | -0.076531 | -0.12959
| STORNOWAY | MAARUIG | MINIMUM HEADROOM | NB 19162 06332 | YES | YES | 0.012 | 0.16049 | 0.15131 | 0.1411 | 0.14008 | 0.13906 | 0.13702 | 0.13192 | 0.12988 | 0.11967 | 0.11967 | 0.10743 | 0.10335 | 0.10233 | 0.16596 | 0.1578 | 0.14861 | 0.15473 | 0.14657 | 0.14759 | 0.15269 | 0.15371 | 0.14759 | 0.14759 | 0.14045 | 0.13535 | 0.12616 | 0.16884 | 0.15965 | 0.14945 | 0.14843 | 0.14741 | 0.14537 | 0.14027 | 0.13822 | 0.12904 | 0.13108 | 0.11986 | 0.11476 | 0.11271
|  | MAARUIG | EE |  |  |  |  | 0.16049 | 0.15131 | 0.1411 | 0.14008 | 0.1411 | 0.14008 | 0.13192 | 0.12988 | 0.11967 | 0.11967 | 0.10743 | 0.10335 | 0.10437 | 0.16596 | 0.1578 | 0.14861 | 0.15984 | 0.16086 | 0.15984 | 0.15269 | 0.15371 | 0.14759 | 0.14759 | 0.14045 | 0.13535 | 0.12922 | 0.16884 | 0.15965 | 0.14945 | 0.14843 | 0.14945 | 0.14741 | 0.14027 | 0.13822 | 0.12904 | 0.13108 | 0.11986 | 0.11578 | 0.11476
|  | MAARUIG | HT |  |  |  |  | 0.16151 | 0.15845 | 0.15029 | 0.14722 | 0.13906 | 0.13702 | 0.14212 | 0.13804 | 0.12988 | 0.12988 | 0.11049 | 0.10437 | 0.10233 | 0.16596 | 0.16494 | 0.15678 | 0.15576 | 0.14759 | 0.1578 | 0.16188 | 0.15984 | 0.15576 | 0.15269 | 0.14147 | 0.13739 | 0.13637 | 0.16884 | 0.1668 | 0.15965 | 0.15659 | 0.14741 | 0.14537 | 0.14945 | 0.14537 | 0.14129 | 0.14129 | 0.1219 | 0.11476 | 0.11271
|  | MAARUIG | HE |  |  |  |  | 0.16151 | 0.15845 | 0.15029 | 0.14824 | 0.14008 | 0.14008 | 0.14518 | 0.13906 | 0.136 | 0.1309 | 0.11457 | 0.10641 | 0.10641 | 0.16596 | 0.16494 | 0.15678 | 0.15473 | 0.14657 | 0.15984 | 0.16188 | 0.15984 | 0.15576 | 0.15371 | 0.14045 | 0.13637 | 0.13127 | 0.16884 | 0.1668 | 0.15761 | 0.15659 | 0.14741 | 0.14843 | 0.15353 | 0.14741 | 0.14435 | 0.13822 | 0.12496 | 0.11884 | 0.11782
|  | MAARUIG | CF |  |  |  |  | 0.16151 | 0.16049 | 0.15845 | 0.15131 | 0.14212 | 0.1411 | 0.1411 | 0.14518 | 0.14212 | 0.14008 | 0.12682 | 0.11559 | 0.10947 | 0.16596 | 0.16596 | 0.16494 | 0.1578 | 0.14861 | 0.14759 | 0.16086 | 0.1629 | 0.16086 | 0.16086 | 0.14861 | 0.13637 | 0.12616 | 0.16884 | 0.16884 | 0.1668 | 0.15965 | 0.15047 | 0.14945 | 0.14945 | 0.15353 | 0.15047 | 0.14843 | 0.13618 | 0.12496 | 0.1219
| LYNDHURST | MACALPINE ROAD | MINIMUM HEADROOM | NO 38034 33691 | NO | YES | 0.425 | 13.2286 | 12.9551 | 12.648 | 12.3429 | 11.9939 | 11.5735 | 11.3112 | 10.7378 | 10.1724 | 9.6418 | 7.85 | 7.4633 | 7.4337 | 14.9388 | 14.8306 | 14.6949 | 14.5429 | 14.3561 | 14.0929 | 13.9929 | 13.6551 | 13.3061 | 12.9837 | 11.7592 | 11.198 | 8.4378 | 14.1704 | 13.9408 | 13.6265 | 13.3408 | 13 | 12.6122 | 12.399 | 11.8704 | 11.3469 | 10.8653 | 9.2592 | 8.9224 | 8.8969
|  | MACALPINE ROAD | EE |  |  |  |  | 13.2286 | 12.9551 | 12.648 | 12.3429 | 11.9939 | 11.5735 | 11.3204 | 10.7378 | 10.1724 | 9.6418 | 7.85 | 7.949 | 7.9592 | 14.9388 | 14.8306 | 14.6949 | 14.5429 | 14.3561 | 14.0929 | 13.9929 | 13.6551 | 13.3061 | 12.9837 | 11.7592 | 11.198 | 10.1235 | 14.1704 | 13.9408 | 13.6265 | 13.3408 | 13 | 12.6122 | 12.399 | 11.8704 | 11.3469 | 10.8653 | 9.2592 | 9.3459 | 9.349
|  | MACALPINE ROAD | HT |  |  |  |  | 13.2786 | 13.0214 | 12.7367 | 12.4714 | 12.1714 | 11.8306 | 11.3112 | 10.7592 | 10.2133 | 9.9418 | 7.9143 | 7.4633 | 7.4337 | 14.9704 | 14.8765 | 14.7745 | 14.6694 | 14.5204 | 14.3459 | 14.1092 | 13.8541 | 13.5571 | 13.5071 | 12.3786 | 12.0469 | 12.0071 | 14.2031 | 14.0112 | 13.7612 | 13.5092 | 13.2204 | 12.9051 | 12.4286 | 11.9184 | 11.4153 | 11.2265 | 9.351 | 8.9224 | 8.8969
|  | MACALPINE ROAD | HE |  |  |  |  | 13.301 | 13.1653 | 13.0122 | 12.8714 | 12.7041 | 12.5133 | 12.1224 | 11.6847 | 11.2388 | 11.1031 | 9.3806 | 8.5102 | 8.4418 | 14.9786 | 14.8959 | 14.8153 | 14.7367 | 14.6408 | 14.5102 | 14.3337 | 14.0949 | 13.8143 | 13.7847 | 12.499 | 11.5357 | 10.4265 | 14.2122 | 14.1337 | 14 | 13.8561 | 13.6724 | 13.4918 | 13.1245 | 12.7133 | 12.3071 | 12.2224 | 10.65 | 9.8704 | 9.8133
|  | MACALPINE ROAD | CF |  |  |  |  | 13.3898 | 13.3337 | 13.2612 | 13.198 | 13.1235 | 13.0245 | 12.9194 | 12.7449 | 12.5561 | 12.3592 | 11.4408 | 9.8684 | 8.5755 | 15.0235 | 14.9786 | 14.9276 | 14.8816 | 14.8255 | 14.749 | 14.6571 | 14.5173 | 14.3704 | 14.1827 | 13.2173 | 11.2582 | 8.4378 | 14.2582 | 14.2153 | 14.1673 | 14.1245 | 14.0704 | 13.9531 | 13.8449 | 13.6735 | 13.5102 | 13.3265 | 12.502 | 11.0653 | 9.9204
| MACDUFF | MACDUFF | MINIMUM HEADROOM | NJ 70363 63908 | NO | NO | 0.925 | 13.4469 | 12.7694 | 12.098 | 11.401 | 10.6745 | 9.8551 | 8.748 | 7.5388 | 6.5255 | 5.0296 | 1.2418 | -0.53469 | -0.84693 | 15.601 | 15.1633 | 14.7388 | 14.3 | 13.7949 | 13.1898 | 12.5174 | 11.7663 | 11.1571 | 10.2174 | 8.0459 | 7.0265 | 6.1245 | 14.6643 | 14.0163 | 13.3704 | 12.7 | 12.0306 | 11.2674 | 10.2816 | 9.2071 | 8.2929 | 6.9735 | 3.6674 | 2.0867 | 1.8225
|  | MACDUFF | EE |  |  |  |  | 13.4939 | 12.8418 | 12.2276 | 11.5163 | 10.7663 | 9.9622 | 9.2163 | 8.1347 | 7.0337 | 5.8592 | 1.3347 | -0.36122 | -0.75204 | 15.6878 | 15.2694 | 14.902 | 14.3918 | 13.8531 | 13.2582 | 12.7929 | 12.0959 | 11.3949 | 10.6276 | 8.0459 | 7.0265 | 6.1245 | 14.6827 | 14.0602 | 13.4694 | 12.8122 | 12.1174 | 11.3674 | 10.7061 | 9.7225 | 8.7276 | 7.6725 | 3.7347 | 2.2469 | 1.9041
|  | MACDUFF | HT |  |  |  |  | 13.4469 | 12.7694 | 12.098 | 11.401 | 10.6745 | 9.8551 | 8.748 | 7.5388 | 6.5255 | 5.0296 | 1.2418 | -0.53469 | -0.84693 | 15.601 | 15.1633 | 14.7388 | 14.3 | 13.7949 | 13.1898 | 12.5174 | 11.7663 | 11.1571 | 10.2174 | 8.4 | 7.6633 | 7.5296 | 14.6643 | 14.0163 | 13.3704 | 12.7 | 12.0306 | 11.2674 | 10.2816 | 9.2071 | 8.2929 | 6.9735 | 3.6674 | 2.0867 | 1.8225
|  | MACDUFF | HE |  |  |  |  | 13.5531 | 13.0582 | 12.6071 | 12.1071 | 11.5918 | 10.999 | 10.2112 | 9.3694 | 8.7959 | 7.8939 | 4.0408 | 1.8806 | 0.97653 | 15.7163 | 15.3265 | 14.9949 | 14.6255 | 14.249 | 13.7939 | 13.2102 | 12.6163 | 12.2041 | 11.551 | 9.1949 | 7.9388 | 6.8714 | 14.7663 | 14.2857 | 13.8439 | 13.3541 | 12.8643 | 12.3082 | 11.5796 | 10.8143 | 10.2776 | 9.4592 | 6.0612 | 4.2102 | 3.4398
|  | MACDUFF | CF |  |  |  |  | 13.8102 | 13.5184 | 13.2286 | 12.9592 | 12.6367 | 12.2714 | 11.9112 | 11.4755 | 11.0449 | 10.5592 | 7.8684 | 4.7204 | 2.8153 | 15.9418 | 15.7184 | 15.499 | 15.3031 | 15.0663 | 14.7714 | 14.4561 | 14.0735 | 13.702 | 13.2837 | 11.0867 | 8.448 | 6.1786 | 15.0163 | 14.7337 | 14.4408 | 14.1827 | 13.8612 | 13.5051 | 13.1684 | 12.7602 | 12.3622 | 11.9092 | 9.4765 | 6.7 | 5.0571
| CARRADALE 1 | MACHRIE | MINIMUM HEADROOM | NR 90092 33864 | YES | YES | 0 | 1.3459 | 1.301 | 1.5673 | 1.5235 | 1.4663 | 1.4214 | 1.3541 | 1.2827 | 1.2082 | 1.1449 | 1.0316 | 0.99082 | 0.98265 | 1.7026 | 1.673 | 2.1714 | 2.1439 | 2.1041 | 2.0735 | 2.0296 | 1.9786 | 1.9296 | 1.8837 | 1.8041 | 1.7643 | 1.6469 | 1.5681 | 1.5242 | 1.9071 | 1.8633 | 1.8082 | 1.7704 | 1.7061 | 1.6367 | 1.5622 | 1.501 | 1.4041 | 1.3633 | 1.3541
|  | MACHRIE | EE |  |  |  |  | 1.3459 | 1.301 | 1.5673 | 1.5235 | 1.4663 | 1.4214 | 1.3541 | 1.2827 | 1.2082 | 1.1449 | 1.0316 | 1.0143 | 0.99898 | 1.7026 | 1.673 | 2.1714 | 2.1439 | 2.1041 | 2.0735 | 2.0296 | 1.9786 | 1.9296 | 1.8837 | 1.8041 | 1.7643 | 1.702 | 1.5681 | 1.5242 | 1.9071 | 1.8633 | 1.8082 | 1.7704 | 1.7061 | 1.6367 | 1.5622 | 1.501 | 1.4041 | 1.3857 | 1.3714
|  | MACHRIE | HT |  |  |  |  | 1.3643 | 1.3357 | 1.6041 | 1.5724 | 1.5276 | 1.4878 | 1.4347 | 1.3735 | 1.3388 | 1.2776 | 1.0429 | 0.99082 | 0.98265 | 1.7168 | 1.6985 | 2.2041 | 2.1847 | 2.1571 | 2.1306 | 2.0959 | 2.0551 | 2.0367 | 1.9969 | 1.8306 | 1.801 | 1.7959 | 1.5895 | 1.562 | 1.9429 | 1.9184 | 1.8745 | 1.8408 | 1.7867 | 1.7276 | 1.699 | 1.6429 | 1.4102 | 1.3633 | 1.3541
|  | MACHRIE | HE |  |  |  |  | 1.3653 | 1.3398 | 1.6153 | 1.5918 | 1.5531 | 1.5184 | 1.4735 | 1.4194 | 1.3878 | 1.3378 | 1.0908 | 1.0724 | 1.0653 | 1.7158 | 1.7015 | 2.2061 | 2.1918 | 2.1653 | 2.1408 | 2.1102 | 2.0704 | 2.0561 | 2.0184 | 1.8429 | 1.8082 | 1.7531 | 1.5906 | 1.5651 | 1.952 | 1.9316 | 1.8949 | 1.8663 | 1.8194 | 1.7663 | 1.7418 | 1.6939 | 1.4561 | 1.4439 | 1.4367
|  | MACHRIE | CF |  |  |  |  | 1.3704 | 1.352 | 1.6306 | 1.6 | 1.5806 | 1.549 | 1.5235 | 1.4847 | 1.449 | 1.4296 | 1.249 | 1.1327 | 1.0694 | 1.7209 | 1.7097 | 2.2184 | 2.1969 | 2.1837 | 2.1622 | 2.1429 | 2.1143 | 2.0867 | 2.0724 | 1.9245 | 1.7918 | 1.6469 | 1.5957 | 1.5773 | 1.9673 | 1.9347 | 1.9204 | 1.8867 | 1.8643 | 1.8255 | 1.7867 | 1.7745 | 1.5969 | 1.4867 | 1.4357
| FORT WILLIAM | MALLAIG | MINIMUM HEADROOM | NM 67637 94811 | YES | NO | 0.122 | 0.55703 | 0.51111 | 0.47846 | 0.43764 | 0.38254 | 0.32336 | 0.27744 | 0.16927 | 0.06111 | -0.037869 | -0.19501 | -0.31338 | -0.36644 | 0.96111 | 0.93254 | 0.90907 | 0.87948 | 0.84172 | 0.79887 | 0.77131 | 0.70397 | 0.6356 | 0.57846 | 0.45805 | 0.3805 | 0.16315 | 0.66111 | 0.61927 | 0.58254 | 0.54274 | 0.48968 | 0.43662 | 0.3907 | 0.29376 | 0.19376 | 0.10295 | -0.043992 | -0.10624 | -0.12562
|  | MALLAIG | EE |  |  |  |  | 0.55703 | 0.51111 | 0.47846 | 0.43764 | 0.38254 | 0.32336 | 0.27744 | 0.16927 | 0.06111 | -0.037869 | -0.19501 | -0.22562 | -0.24807 | 0.96111 | 0.93254 | 0.90907 | 0.87948 | 0.84172 | 0.79887 | 0.77131 | 0.70397 | 0.6356 | 0.57846 | 0.45805 | 0.40295 | 0.31825 | 0.66111 | 0.61927 | 0.58254 | 0.54274 | 0.48968 | 0.43662 | 0.3907 | 0.29376 | 0.19376 | 0.10295 | -0.043992 | -0.069502 | -0.08991
|  | MALLAIG | HT |  |  |  |  | 0.5754 | 0.54887 | 0.51213 | 0.4856 | 0.44274 | 0.37029 | 0.28254 | 0.18356 | 0.14784 | 0.090702 | -0.15522 | -0.26236 | -0.27869 | 0.97744 | 0.96213 | 0.93662 | 0.92233 | 0.89478 | 0.85703 | 0.80601 | 0.74887 | 0.72846 | 0.69172 | 0.52131 | 0.45193 | 0.43968 | 0.67642 | 0.64989 | 0.61519 | 0.58866 | 0.54989 | 0.48458 | 0.40805 | 0.31927 | 0.28764 | 0.23254 | -0.0052163 | -0.10624 | -0.11848
|  | MALLAIG | HE |  |  |  |  | 0.57336 | 0.55091 | 0.52233 | 0.49682 | 0.45907 | 0.42029 | 0.36723 | 0.28662 | 0.21825 | 0.13968 | -0.19501 | -0.31338 | -0.3195 | 0.9754 | 0.96009 | 0.9407 | 0.92438 | 0.89887 | 0.87642 | 0.84478 | 0.78968 | 0.75499 | 0.70499 | 0.48764 | 0.39478 | 0.31927 | 0.67438 | 0.65295 | 0.6254 | 0.60193 | 0.56927 | 0.5407 | 0.49274 | 0.41621 | 0.36213 | 0.2856 | -0.00011429 | -0.075624 | -0.082767
|  | MALLAIG | CF |  |  |  |  | 0.58152 | 0.56111 | 0.53968 | 0.50907 | 0.49274 | 0.46111 | 0.42744 | 0.39887 | 0.33968 | 0.27438 | 0.047845 | -0.18685 | -0.36644 | 0.98152 | 0.96825 | 0.95397 | 0.92948 | 0.91621 | 0.89682 | 0.86621 | 0.8458 | 0.80499 | 0.76111 | 0.58764 | 0.3805 | 0.16315 | 0.68254 | 0.66519 | 0.64478 | 0.61723 | 0.59887 | 0.57029 | 0.53866 | 0.51009 | 0.45499 | 0.39682 | 0.18458 | 0.00090612 | -0.12562
| KEITH 1 | MARNOCH | MINIMUM HEADROOM | NJ 61955 53001 | NO | YES | 0.401 | 2.4452 | 2.3075 | 2.1452 | 1.9605 | 1.782 | 1.582 | 1.3411 | 1.1207 | 0.88297 | 0.65338 | 0.026849 | -0.13029 | -0.19254 | 3.8524 | 3.7687 | 3.6615 | 3.533 | 3.4207 | 3.282 | 3.1207 | 2.9891 | 2.8268 | 2.6809 | 2.3075 | 2.1728 | 1.7411 | 2.6962 | 2.5922 | 2.4575 | 2.2952 | 2.1646 | 1.982 | 1.7575 | 1.5636 | 1.3401 | 1.133 | 0.60848 | 0.48093 | 0.43297
|  | MARNOCH | EE |  |  |  |  | 2.4452 | 2.3075 | 2.1452 | 1.9605 | 1.782 | 1.582 | 1.3411 | 1.1207 | 0.88297 | 0.65338 | 0.026849 | -0.063967 | -0.10376 | 3.8524 | 3.7687 | 3.6615 | 3.533 | 3.4207 | 3.282 | 3.1207 | 2.9891 | 2.8268 | 2.6809 | 2.3075 | 2.1728 | 1.9656 | 2.6962 | 2.5922 | 2.4575 | 2.2952 | 2.1646 | 1.982 | 1.7575 | 1.5636 | 1.3401 | 1.133 | 0.60848 | 0.53399 | 0.49522
|  | MARNOCH | HT |  |  |  |  | 2.4717 | 2.336 | 2.1881 | 2.0187 | 1.8299 | 1.6554 | 1.486 | 1.2728 | 1.0554 | 0.79522 | 0.17481 | -0.13029 | -0.19254 | 3.8911 | 3.8136 | 3.7228 | 3.6299 | 3.5156 | 3.4044 | 3.3197 | 3.1911 | 3.0615 | 2.9105 | 2.4799 | 2.3126 | 2.286 | 2.7534 | 2.6626 | 2.535 | 2.3881 | 2.2258 | 2.0758 | 1.9279 | 1.7513 | 1.5748 | 1.3483 | 0.74216 | 0.48093 | 0.43297
|  | MARNOCH | HE |  |  |  |  | 2.4789 | 2.3738 | 2.2636 | 2.1422 | 1.9993 | 1.8503 | 1.7034 | 1.5044 | 1.3166 | 1.1238 | 0.23807 | 0.030931 | -0.010906 | 3.8922 | 3.8268 | 3.7503 | 3.6758 | 3.5768 | 3.4728 | 3.3871 | 3.2615 | 3.1422 | 3.0115 | 2.4564 | 2.2493 | 2.0534 | 2.7554 | 2.6768 | 2.586 | 2.4983 | 2.3717 | 2.2442 | 2.1115 | 1.9483 | 1.7758 | 1.5993 | 0.82277 | 0.6442 | 0.56664
|  | MARNOCH | CF |  |  |  |  | 2.4973 | 2.4217 | 2.332 | 2.236 | 2.1452 | 2.0452 | 1.934 | 1.8105 | 1.7095 | 1.5728 | 0.87583 | 0.37787 | 0.072767 | 3.9095 | 3.8605 | 3.8034 | 3.732 | 3.6748 | 3.6075 | 3.5238 | 3.4238 | 3.3666 | 3.2666 | 2.7544 | 2.2217 | 1.7411 | 2.7799 | 2.7258 | 2.6605 | 2.5809 | 2.5003 | 2.4126 | 2.3187 | 2.2064 | 2.1258 | 1.9973 | 1.3728 | 0.90032 | 0.67379
| BEAULY | MARYBANK | MINIMUM HEADROOM | NH 46749 53948 | YES | NO | 0.381 | 3.1455 | 3.1067 | 3.0598 | 2.9996 | 2.9608 | 2.8996 | 2.8292 | 2.7128 | 2.6383 | 2.5179 | 2.3414 | 2.2792 | 2.2455 | 3.4038 | 3.3814 | 3.3538 | 3.3222 | 3.3008 | 3.2651 | 3.2253 | 3.1436 | 3.0967 | 3.0263 | 2.9049 | 2.8487 | 2.6294 | 3.3185 | 3.2777 | 3.2308 | 3.1696 | 3.1298 | 3.0655 | 2.993 | 2.8675 | 2.7879 | 2.6808 | 2.5175 | 2.4583 | 2.4298
|  | MARYBANK | EE |  |  |  |  | 3.1455 | 3.1067 | 3.0598 | 2.9996 | 2.9608 | 2.8996 | 2.8292 | 2.7128 | 2.6383 | 2.5179 | 2.3414 | 2.3026 | 2.2792 | 3.4038 | 3.3814 | 3.3538 | 3.3222 | 3.3008 | 3.2651 | 3.2253 | 3.1436 | 3.0967 | 3.0263 | 2.9049 | 2.8487 | 2.7487 | 3.3185 | 3.2777 | 3.2308 | 3.1696 | 3.1298 | 3.0655 | 2.993 | 2.8675 | 2.7879 | 2.6808 | 2.5175 | 2.4808 | 2.4573
|  | MARYBANK | HT |  |  |  |  | 3.1741 | 3.1383 | 3.1036 | 3.0567 | 3.02 | 2.9353 | 2.869 | 2.7598 | 2.7067 | 2.6434 | 2.3985 | 2.2792 | 2.2455 | 3.4161 | 3.4008 | 3.3804 | 3.3559 | 3.3375 | 3.2885 | 3.2457 | 3.1865 | 3.1579 | 3.1222 | 2.9651 | 2.8926 | 2.8732 | 3.3492 | 3.3134 | 3.2787 | 3.2318 | 3.193 | 3.1063 | 3.0379 | 2.9318 | 2.8787 | 2.8124 | 2.5685 | 2.4583 | 2.4298
|  | MARYBANK | HE |  |  |  |  | 3.172 | 3.1445 | 3.1169 | 3.0802 | 3.0516 | 3.0077 | 2.9547 | 2.9006 | 2.8322 | 2.7567 | 2.4322 | 2.3536 | 2.3394 | 3.4151 | 3.4028 | 3.3845 | 3.3651 | 3.3467 | 3.3222 | 3.2916 | 3.259 | 3.2141 | 3.1671 | 2.962 | 2.8814 | 2.7957 | 3.3471 | 3.3216 | 3.293 | 3.2532 | 3.2247 | 3.1787 | 3.1236 | 3.0665 | 2.9961 | 2.9175 | 2.6002 | 2.5277 | 2.5165
|  | MARYBANK | CF |  |  |  |  | 3.1822 | 3.1587 | 3.1261 | 3.1108 | 3.0781 | 3.0536 | 3.019 | 2.9761 | 2.9434 | 2.8863 | 2.6057 | 2.4394 | 2.3261 | 3.4202 | 3.409 | 3.3875 | 3.3763 | 3.3569 | 3.3406 | 3.3192 | 3.2875 | 3.2651 | 3.2273 | 3.0375 | 2.86 | 2.6294 | 3.3563 | 3.3287 | 3.2961 | 3.2757 | 3.24 | 3.2165 | 3.1777 | 3.1298 | 3.0971 | 3.0349 | 2.7624 | 2.6043 | 2.5073
| LUNANHEAD | MARYTON | MINIMUM HEADROOM | NO 39206 53075 | NO | YES | 0.646 | 7.1556 | 6.8301 | 6.2576 | 5.376 | 4.8291 | 3.3668 | 2.7923 | 2.1617 | 1.6158 | 0.99539 | -3.1056 | -7.9862 | -12.0393 | 9.0709 | 8.9005 | 8.425 | 7.5872 | 7.1617 | 5.6046 | 5.2525 | 4.6985 | 4.0934 | 3.1025 | -0.9444 | -6.2322 | -11.3638 | 8.3337 | 8.0388 | 7.4581 | 6.4857 | 5.9204 | 4.2122 | 3.6653 | 3.053 | 2.5337 | 1.4939 | -3.0857 | -8.6419 | -13.4898
|  | MARYTON | EE |  |  |  |  | 7.1556 | 6.8301 | 6.4597 | 6.0158 | 5.2403 | 4.228 | 3.4036 | 3.1015 | 2.2372 | 1.5811 | -1.326 | -5.8913 | -7.526 | 9.0709 | 8.9005 | 8.677 | 8.3842 | 7.6709 | 6.6821 | 6.0413 | 5.9291 | 5.2005 | 4.7087 | 2.4607 | -2.4546 | -4.8026 | 8.3337 | 8.0388 | 7.6898 | 7.2551 | 6.3939 | 5.252 | 4.4071 | 4.1551 | 3.2367 | 2.5694 | -0.3041 | -5.4908 | -7.4408
|  | MARYTON | HT |  |  |  |  | 7.227 | 6.9025 | 6.2576 | 5.376 | 4.8291 | 3.3668 | 2.7923 | 2.1617 | 1.6158 | 0.99539 | -2.1066 | -7.2985 | -10.9128 | 9.1342 | 8.9811 | 8.425 | 7.5872 | 7.1617 | 5.6046 | 5.2525 | 4.8597 | 4.5587 | 4.1658 | 1.8138 | -3.6087 | -7.9271 | 8.4255 | 8.1439 | 7.4581 | 6.4857 | 5.9204 | 4.2122 | 3.6653 | 3.053 | 2.5337 | 1.9214 | -1.2286 | -7.2092 | -11.6286
|  | MARYTON | HE |  |  |  |  | 7.2291 | 7.0189 | 6.5362 | 5.8464 | 5.3229 | 3.9974 | 3.3709 | 2.6985 | 2.026 | 1.0566 | -3.1056 | -7.9862 | -12.0393 | 9.1291 | 9.0138 | 8.5617 | 7.8556 | 7.3485 | 5.8576 | 5.2974 | 4.6985 | 4.0934 | 3.1025 | -0.9444 | -6.2322 | -11.3638 | 8.4286 | 8.2377 | 7.7061 | 6.9224 | 6.3347 | 4.752 | 4.0745 | 3.3347 | 2.599 | 1.4939 | -3.0857 | -8.6419 | -13.4898
|  | MARYTON | CF |  |  |  |  | 7.2903 | 7.1403 | 6.977 | 6.7658 | 6.4097 | 5.875 | 5.5148 | 5.2138 | 4.8944 | 4.5087 | 3.0587 | 1.1056 | -0.57196 | 9.1597 | 9.0699 | 8.9689 | 8.8189 | 8.4617 | 7.8872 | 7.5148 | 7.2097 | 6.8811 | 6.4872 | 5.0403 | 3.0138 | 0.83315 | 8.4857 | 8.35 | 8.1969 | 7.9867 | 7.5898 | 6.9663 | 6.552 | 6.2153 | 5.8561 | 5.4357 | 3.8806 | 1.8786 | 0.24896
| STRICHEN | MAUD | MINIMUM HEADROOM | NJ 92528 47491 | NO | YES | 0.331 | 4.7361 | 4.6106 | 4.4422 | 4.2606 | 4.0912 | 3.8912 | 3.6575 | 3.4045 | 3.1147 | 2.7708 | 1.9208 | 1.7626 | 1.6973 | 5.8392 | 5.7698 | 5.6718 | 5.5565 | 5.4647 | 5.329 | 5.1718 | 5.0238 | 4.8422 | 4.6596 | 4.1932 | 4.0514 | 3.5351 | 5.3402 | 5.2249 | 5.0708 | 4.9014 | 4.7545 | 4.5636 | 4.3412 | 4.1096 | 3.8494 | 3.5667 | 2.8361 | 2.7004 | 2.6494
|  | MAUD | EE |  |  |  |  | 4.7361 | 4.6106 | 4.4422 | 4.2606 | 4.0912 | 3.8912 | 3.6575 | 3.4045 | 3.1147 | 2.8024 | 1.9208 | 1.8269 | 1.7932 | 5.8392 | 5.7698 | 5.6718 | 5.5565 | 5.4647 | 5.329 | 5.1718 | 5.0238 | 4.8422 | 4.6596 | 4.1932 | 4.0534 | 3.8412 | 5.3402 | 5.2249 | 5.0708 | 4.9014 | 4.7545 | 4.5636 | 4.3412 | 4.1096 | 3.8494 | 3.5667 | 2.8361 | 2.7585 | 2.7259
|  | MAUD | HT |  |  |  |  | 4.7698 | 4.6412 | 4.4841 | 4.3361 | 4.1912 | 4.0065 | 3.7647 | 3.4841 | 3.13 | 2.7708 | 2.0545 | 1.7626 | 1.6973 | 5.8728 | 5.8157 | 5.731 | 5.6626 | 5.5841 | 5.4718 | 5.3514 | 5.1861 | 4.9973 | 4.8004 | 4.3585 | 4.2014 | 4.1738 | 5.3759 | 5.2677 | 5.1249 | 4.9973 | 4.8657 | 4.6963 | 4.4943 | 4.2463 | 3.9453 | 3.6371 | 2.9606 | 2.7004 | 2.6494
|  | MAUD | HE |  |  |  |  | 4.7677 | 4.6902 | 4.5698 | 4.4647 | 4.3361 | 4.1636 | 4.0198 | 3.7779 | 3.5167 | 3.2259 | 2.0994 | 1.88 | 1.832 | 5.8708 | 5.829 | 5.7545 | 5.6973 | 5.6177 | 5.5075 | 5.4198 | 5.2606 | 5.1024 | 4.93 | 4.2953 | 4.0779 | 3.8667 | 5.3749 | 5.3045 | 5.1932 | 5.0983 | 4.9841 | 4.8269 | 4.7004 | 4.4861 | 4.2534 | 3.9973 | 3.0085 | 2.8116 | 2.7596
|  | MAUD | CF |  |  |  |  | 4.781 | 4.7065 | 4.6228 | 4.5341 | 4.4228 | 4.2892 | 4.1432 | 4.0443 | 3.9024 | 3.7371 | 2.7392 | 2.2453 | 1.9208 | 5.88 | 5.8341 | 5.7841 | 5.7392 | 5.6677 | 5.582 | 5.482 | 5.4085 | 5.3055 | 5.1892 | 4.5708 | 4.0514 | 3.5351 | 5.3881 | 5.3187 | 5.2453 | 5.1677 | 5.0657 | 4.9483 | 4.8126 | 4.7259 | 4.5983 | 4.4494 | 3.5769 | 3.0912 | 2.829
| DOUNREAY | MELVICH | MINIMUM HEADROOM | NC 88547 64274 | YES | NO | 0.413 | -0.029433 | -0.063106 | -0.092698 | -0.13964 | -0.17637 | -0.22535 | -0.28351 | -0.32535 | -0.38556 | -0.43045 | -0.55392 | -0.61004 | -0.61617 | 0.26036 | 0.24302 | 0.22873 | 0.20016 | 0.18077 | 0.14914 | 0.10934 | 0.084853 | 0.043016 | 0.018527 | -0.094739 | -0.14984 | -0.23249 | 0.11138 | 0.079751 | 0.050159 | 0.0093429 | -0.026371 | -0.074331 | -0.13045 | -0.16719 | -0.22637 | -0.26719 | -0.38147 | -0.458 | -0.46923
|  | MELVICH | EE |  |  |  |  | -0.029433 | -0.063106 | -0.092698 | -0.13964 | -0.17637 | -0.22535 | -0.28351 | -0.32535 | -0.38556 | -0.43045 | -0.55392 | -0.57127 | -0.58147 | 0.26036 | 0.24302 | 0.22873 | 0.20016 | 0.18077 | 0.14914 | 0.10934 | 0.084853 | 0.043016 | 0.018527 | -0.064127 | -0.09678 | -0.14984 | 0.11138 | 0.079751 | 0.050159 | 0.0093429 | -0.026371 | -0.074331 | -0.13045 | -0.16719 | -0.22637 | -0.26719 | -0.38147 | -0.39984 | -0.40902
|  | MELVICH | HT |  |  |  |  | -0.014127 | -0.038616 | -0.071269 | -0.10494 | -0.12841 | -0.16719 | -0.21311 | -0.25086 | -0.29882 | -0.35086 | -0.51311 | -0.5927 | -0.60188 | 0.27057 | 0.2573 | 0.24302 | 0.22669 | 0.21342 | 0.19098 | 0.16649 | 0.14404 | 0.1124 | 0.080771 | -0.02229 | -0.068208 | -0.075351 | 0.12567 | 0.10322 | 0.071588 | 0.041996 | 0.019547 | -0.017188 | -0.061065 | -0.095759 | -0.14168 | -0.18862 | -0.34372 | -0.41719 | -0.42637
|  | MELVICH | HE |  |  |  |  | -0.015147 | -0.033514 | -0.061065 | -0.085555 | -0.10494 | -0.14066 | -0.17841 | -0.20902 | -0.25596 | -0.29984 | -0.53453 | -0.61004 | -0.61515 | 0.26547 | 0.25118 | 0.23383 | 0.21751 | 0.20016 | 0.17873 | 0.15322 | 0.11955 | 0.087914 | 0.056282 | -0.094739 | -0.14984 | -0.1529 | 0.12465 | 0.10628 | 0.081792 | 0.057302 | 0.039955 | 0.0083224 | -0.028412 | -0.069229 | -0.11719 | -0.16107 | -0.38147 | -0.458 | -0.46311
|  | MELVICH | CF |  |  |  |  | -0.010045 | -0.026371 | -0.0478 | -0.068208 | -0.095759 | -0.11107 | -0.1376 | -0.17127 | -0.18964 | -0.22127 | -0.358 | -0.508 | -0.61617 | 0.27261 | 0.26138 | 0.24914 | 0.23587 | 0.22057 | 0.20832 | 0.19302 | 0.17057 | 0.15628 | 0.13485 | 0.013424 | -0.095759 | -0.23249 | 0.12975 | 0.11547 | 0.094037 | 0.07669 | 0.049139 | 0.035873 | 0.010363 | -0.02331 | -0.039637 | -0.069229 | -0.21923 | -0.36821 | -0.46923
| CHARLESTON | MENZIESHILL | MINIMUM HEADROOM | NO 35918 31022 | NO | YES | 1.957 | 9.9752 | 9.515 | 8.9772 | 8.3528 | 7.7538 | 7.1558 | 6.4599 | 5.6946 | 5.1558 | 4.5262 | 2.4548 | 1.9701 | 1.5885 | 9.4538 | 9.1466 | 8.7823 | 8.3487 | 7.9589 | 7.5599 | 7.0762 | 6.5201 | 6.1599 | 5.7334 | 4.3568 | 3.6293 | 1.1997 | 11.5594 | 11.1226 | 10.6482 | 10.0808 | 9.5614 | 9.0104 | 8.3665 | 7.6471 | 7.3726 | 6.8145 | 5.04 | 4.338 | 3.9267
|  | MENZIESHILL | EE |  |  |  |  | 9.9752 | 9.515 | 8.9772 | 8.3528 | 7.7538 | 7.1558 | 6.4599 | 5.6946 | 5.1558 | 4.5262 | 2.4548 | 2.6466 | 2.7313 | 9.4538 | 9.1466 | 8.7823 | 8.3487 | 7.9589 | 7.5599 | 7.0762 | 6.5201 | 6.1599 | 5.7334 | 4.4068 | 4.0864 | 2.916 | 11.5594 | 11.1226 | 10.6482 | 10.0808 | 9.5614 | 9.0104 | 8.3665 | 7.6471 | 7.3726 | 6.8145 | 5.04 | 5.1329 | 5.142
|  | MENZIESHILL | HT |  |  |  |  | 10.0925 | 9.6568 | 9.1507 | 8.5772 | 8.0568 | 7.5456 | 6.9742 | 6.3334 | 5.7028 | 5.0528 | 2.617 | 1.9701 | 1.7119 | 9.5374 | 9.264 | 8.9109 | 8.5191 | 8.2068 | 7.8946 | 7.567 | 7.1272 | 6.7068 | 6.2609 | 4.5813 | 4.0058 | 3.7323 | 11.6859 | 11.2818 | 10.8206 | 10.3033 | 9.8675 | 9.4196 | 8.9369 | 8.3726 | 7.8084 | 7.2257 | 5.2308 | 4.5359 | 4.2135
|  | MENZIESHILL | HE |  |  |  |  | 10.115 | 9.8079 | 9.3966 | 8.9262 | 8.4895 | 8.0436 | 7.4885 | 6.8579 | 6.2548 | 5.6232 | 3.117 | 2.013 | 1.5885 | 9.5395 | 9.317 | 9.0323 | 8.7048 | 8.3528 | 7.9946 | 7.6211 | 7.1701 | 6.716 | 6.2323 | 4.3568 | 3.6293 | 3.2579 | 11.7022 | 11.4247 | 11.0869 | 10.7012 | 10.3788 | 10.0329 | 9.6247 | 9.1247 | 8.5155 | 7.8706 | 5.3686 | 4.338 | 3.9267
|  | MENZIESHILL | CF |  |  |  |  | 10.1895 | 10.0558 | 9.9017 | 9.6701 | 9.4232 | 9.1568 | 8.8711 | 8.5385 | 8.2395 | 7.9181 | 5.9772 | 3.7334 | 2.1109 | 9.5813 | 9.463 | 9.3038 | 9.1068 | 8.9252 | 8.7079 | 8.4793 | 8.2405 | 8.0038 | 7.7538 | 6.1956 | 4.1905 | 1.1997 | 11.7675 | 11.6318 | 11.4675 | 11.2471 | 11.0502 | 10.8175 | 10.5747 | 10.338 | 10.0951 | 9.8349 | 8.0288 | 5.9226 | 4.4329
| KINTORE | METHLICK | MINIMUM HEADROOM | NJ 85339 36835 | NO | YES | 0.17 | 4.8047 | 4.7455 | 4.6843 | 4.6077 | 4.5169 | 4.423 | 4.3506 | 4.222 | 4.0996 | 4.0139 | 3.6588 | 3.5241 | 3.4373 | 6.319 | 6.269 | 6.22 | 6.1598 | 6.0853 | 6.0077 | 5.9526 | 5.8465 | 5.7465 | 5.7057 | 5.5047 | 5.4353 | 5.1628 | 4.9822 | 4.9047 | 4.8292 | 4.7384 | 4.6302 | 4.52 | 4.4261 | 4.27 | 4.122 | 4.0404 | 3.7384 | 3.6435 | 3.573
|  | METHLICK | EE |  |  |  |  | 4.8047 | 4.7455 | 4.6843 | 4.6077 | 4.5169 | 4.423 | 4.3506 | 4.222 | 4.0996 | 4.0139 | 3.6588 | 3.5863 | 3.5761 | 6.319 | 6.269 | 6.22 | 6.1598 | 6.0853 | 6.0077 | 5.9526 | 5.8465 | 5.7465 | 5.7057 | 5.5047 | 5.4353 | 5.3496 | 4.9822 | 4.9047 | 4.8292 | 4.7384 | 4.6302 | 4.52 | 4.4261 | 4.27 | 4.122 | 4.0404 | 3.7384 | 3.6802 | 3.6598
|  | METHLICK | HT |  |  |  |  | 4.8455 | 4.8016 | 4.7506 | 4.6873 | 4.6424 | 4.572 | 4.4945 | 4.3884 | 4.2761 | 4.1567 | 3.7384 | 3.5333 | 3.4761 | 6.3496 | 6.3118 | 6.27 | 6.2169 | 6.1792 | 6.121 | 6.0567 | 5.972 | 5.9251 | 5.8475 | 5.5853 | 5.4812 | 5.4577 | 5.019 | 4.9567 | 4.8884 | 4.8057 | 4.7424 | 4.6537 | 4.5547 | 4.4312 | 4.3435 | 4.223 | 3.8128 | 3.6435 | 3.6077
|  | METHLICK | HE |  |  |  |  | 4.8445 | 4.8067 | 4.7628 | 4.7057 | 4.6669 | 4.6037 | 4.5302 | 4.4363 | 4.3782 | 4.2537 | 3.6996 | 3.5241 | 3.4373 | 6.3486 | 6.3179 | 6.2782 | 6.2312 | 6.1996 | 6.1486 | 6.0924 | 6.0118 | 5.972 | 5.8894 | 5.572 | 5.4526 | 5.3598 | 5.019 | 4.971 | 4.9159 | 4.8486 | 4.8006 | 4.7282 | 4.6424 | 4.5282 | 4.4506 | 4.3333 | 3.8159 | 3.6526 | 3.573
|  | METHLICK | CF |  |  |  |  | 4.8537 | 4.8241 | 4.7792 | 4.7455 | 4.6965 | 4.669 | 4.619 | 4.5547 | 4.4914 | 4.4659 | 4.123 | 3.7843 | 3.5465 | 6.3567 | 6.3302 | 6.2894 | 6.2577 | 6.2149 | 6.1914 | 6.1516 | 6.0945 | 6.0394 | 6.0179 | 5.7088 | 5.4628 | 5.1628 | 5.0292 | 4.9904 | 4.9322 | 4.8863 | 4.8251 | 4.7914 | 4.7343 | 4.6598 | 4.5873 | 4.5506 | 4.1455 | 3.872 | 3.672
| SHETLAND | MID YELL | MINIMUM HEADROOM | HU4817291442 | YES | YES | 0 | 0.039796 | 0.0061224 | -0.02449 | -0.066327 | -0.1 | -0.14592 | -0.20306 | -0.24184 | -0.29898 | -0.34286 | -0.45816 | -0.49592 | -0.50714 | 0.35408 | 0.33367 | 0.31633 | 0.29388 | 0.27551 | 0.25102 | 0.22041 | 0.1949 | 0.16429 | 0.14082 | 0.067347 | 0.041837 | -0.021429 | 0.20204 | 0.17755 | 0.15612 | 0.12449 | 0.09898 | 0.066327 | 0.022449 | -0.013265 | -0.066327 | -0.10408 | -0.21327 | -0.24694 | -0.25714
|  | MID YELL | EE |  |  |  |  | 0.039796 | 0.0061224 | -0.02449 | -0.066327 | -0.1 | -0.14592 | -0.20306 | -0.24184 | -0.29898 | -0.34286 | -0.45816 | -0.47653 | -0.48571 | 0.35408 | 0.33367 | 0.31633 | 0.29388 | 0.27551 | 0.25102 | 0.22041 | 0.1949 | 0.16429 | 0.14082 | 0.067347 | 0.041837 | 0.0061224 | 0.20204 | 0.17755 | 0.15612 | 0.12449 | 0.09898 | 0.066327 | 0.022449 | -0.013265 | -0.066327 | -0.10408 | -0.21327 | -0.23163 | -0.2398
|  | MID YELL | HT |  |  |  |  | 0.04898 | 0.02551 | 0.0010204 | -0.034694 | -0.056122 | -0.093878 | -0.12755 | -0.17347 | -0.21837 | -0.26633 | -0.42245 | -0.49592 | -0.50714 | 0.36122 | 0.35 | 0.33673 | 0.31735 | 0.30714 | 0.28571 | 0.26939 | 0.24388 | 0.21939 | 0.19184 | 0.10204 | 0.063265 | 0.056122 | 0.20918 | 0.18776 | 0.16837 | 0.14388 | 0.12551 | 0.096939 | 0.070408 | 0.035714 | 0.0020408 | -0.036735 | -0.17755 | -0.24694 | -0.25714
|  | MID YELL | HE |  |  |  |  | 0.05 | 0.033673 | 0.014286 | -0.014286 | -0.033673 | -0.061224 | -0.10102 | -0.12959 | -0.17143 | -0.21327 | -0.39286 | -0.44082 | -0.44796 | 0.36224 | 0.35 | 0.34082 | 0.32449 | 0.31327 | 0.29694 | 0.27551 | 0.25714 | 0.23367 | 0.21224 | 0.1051 | 0.064286 | 0.029592 | 0.2102 | 0.19388 | 0.17857 | 0.15816 | 0.14184 | 0.12245 | 0.095918 | 0.071429 | 0.041837 | 0.011224 | -0.15204 | -0.1949 | -0.20102
|  | MID YELL | CF |  |  |  |  | 0.053061 | 0.037755 | 0.021429 | 0.0030612 | -0.019388 | -0.032653 | -0.058163 | -0.088776 | -0.10714 | -0.13367 | -0.25714 | -0.37449 | -0.43673 | 0.36531 | 0.35408 | 0.34184 | 0.33367 | 0.32143 | 0.3102 | 0.2949 | 0.27653 | 0.26633 | 0.24796 | 0.16735 | 0.068367 | -0.021429 | 0.21122 | 0.19796 | 0.18265 | 0.16837 | 0.15204 | 0.1398 | 0.12041 | 0.097959 | 0.084694 | 0.064286 | -0.027551 | -0.13571 | -0.19286
| KINTORE | MIDMAR | MINIMUM HEADROOM | NJ 68253 06875 | YES | YES | 0.612 | 2.7904 | 2.6455 | 2.4996 | 2.322 | 3.5841 | 3.429 | 3.2188 | 3.0116 | 2.8535 | 2.68 | 2.2096 | 2.0586 | 2.0004 | 3.3363 | 3.269 | 3.1996 | 3.1078 | 4.9116 | 4.8188 | 4.7076 | 4.5851 | 4.4851 | 4.3892 | 4.0667 | 3.9218 | 3.5902 | 3.043 | 2.9175 | 2.7899 | 2.6348 | 4.1382 | 4.0096 | 3.8147 | 3.6157 | 3.482 | 3.3198 | 2.9239 | 2.7861 | 2.7269
|  | MIDMAR | EE |  |  |  |  | 2.7904 | 2.6455 | 2.4996 | 2.322 | 3.5841 | 3.429 | 3.2188 | 3.0116 | 2.8535 | 2.68 | 2.2096 | 2.1249 | 2.0953 | 3.3363 | 3.269 | 3.1996 | 3.1078 | 4.9116 | 4.8188 | 4.7076 | 4.5851 | 4.4851 | 4.3892 | 4.1076 | 3.9912 | 3.8249 | 3.043 | 2.9175 | 2.7899 | 2.6348 | 4.1382 | 4.0096 | 3.8147 | 3.6157 | 3.482 | 3.3198 | 2.9239 | 2.8484 | 2.8208
|  | MIDMAR | HT |  |  |  |  | 2.8251 | 2.6771 | 2.52 | 2.3588 | 3.6525 | 3.4963 | 3.3484 | 3.2106 | 3.0586 | 2.9004 | 2.329 | 2.0586 | 2.0004 | 3.3731 | 3.3108 | 3.2394 | 3.1608 | 4.981 | 4.8984 | 4.8127 | 4.7259 | 4.6361 | 4.5392 | 4.1606 | 4.0076 | 3.9453 | 3.0889 | 2.9654 | 2.8338 | 2.7021 | 4.2433 | 4.1086 | 3.9678 | 3.8555 | 3.7127 | 3.5637 | 3.028 | 2.7861 | 2.7361
|  | MIDMAR | HE |  |  |  |  | 2.8241 | 2.719 | 2.6047 | 2.4812 | 3.7871 | 3.6494 | 3.4994 | 3.3841 | 3.2463 | 3.1045 | 2.3678 | 2.1749 | 2.0831 | 3.371 | 3.32 | 3.2547 | 3.1843 | 5.0055 | 4.9188 | 4.8239 | 4.7331 | 4.6351 | 4.5351 | 4.0667 | 3.9218 | 3.8463 | 3.0868 | 2.995 | 2.894 | 2.794 | 4.3422 | 4.2208 | 4.08 | 3.9851 | 3.8576 | 3.7229 | 3.0341 | 2.8249 | 2.7269
|  | MIDMAR | CF |  |  |  |  | 2.8394 | 2.7537 | 2.6761 | 2.571 | 3.9361 | 3.8096 | 3.7045 | 3.5912 | 3.5147 | 3.4116 | 2.929 | 2.4882 | 2.1994 | 3.3782 | 3.3404 | 3.3006 | 3.2465 | 5.1137 | 5.0525 | 4.9963 | 4.9208 | 4.8688 | 4.7994 | 4.4331 | 4.0076 | 3.5902 | 3.1042 | 3.0287 | 2.9593 | 2.8634 | 4.4708 | 4.3586 | 4.2647 | 4.1545 | 4.0953 | 3.9994 | 3.5412 | 3.1137 | 2.8422
| BRIDGE OF DUN | MILL RD | MINIMUM HEADROOM | NO 71317 57683 | NO | NO | 2.116 | 4.403 | 4.2285 | 3.3489 | 2.0856 | 1.8724 | -0.81131 | -1.6491 | -2.647 | -3.6695 | -5.4695 | -13.5062 | -23.745 | -33.0113 | 6.5581 | 6.4438 | 5.4224 | 3.9489 | 3.6907 | 0.51216 | -0.45927 | -1.5307 | -2.6429 | -4.7185 | -13.648 | -25.6929 | -37.4256 | 5.8012 | 5.5828 | 4.5185 | 2.94 | 2.6859 | -0.64065 | -1.5294 | -2.7192 | -3.9162 | -6.1029 | -15.7468 | -28.0743 | -39.4866
|  | MILL RD | EE |  |  |  |  | 4.403 | 4.2285 | 4.0234 | 3.8081 | 2.9326 | 1.4142 | 0.52032 | -0.038861 | -1.3634 | -2.2715 | -6.8878 | -16.3807 | -20.1103 | 6.5581 | 6.4438 | 6.302 | 6.152 | 5.1907 | 3.3948 | 2.5111 | 2.1326 | 0.79175 | -0.041922 | -4.3164 | -15.3695 | -20.3195 | 5.8012 | 5.5828 | 5.3196 | 5.0614 | 3.9655 | 2.0665 | 1.0236 | 0.4818 | -1.0141 | -1.9988 | -6.9917 | -18.3621 | -22.9213
|  | MILL RD | HT |  |  |  |  | 4.4428 | 4.2846 | 3.3489 | 2.0856 | 1.8724 | -0.81131 | -1.3062 | -2.0062 | -2.5174 | -3.2674 | -8.7368 | -19.6593 | -28.3185 | 6.5897 | 6.4877 | 5.4224 | 3.9489 | 3.804 | 0.57134 | 0.14379 | -0.35723 | -0.65111 | -1.245 | -6.3358 | -18.8929 | -29.5072 | 5.8798 | 5.6818 | 4.5185 | 2.94 | 2.6859 | -0.64065 | -1.2886 | -2.0151 | -2.4988 | -3.2804 | -9.2927 | -22.4366 | -33.158
|  | MILL RD | HE |  |  |  |  | 4.4438 | 4.3132 | 3.552 | 2.4326 | 1.8724 | -0.746 | -1.6491 | -2.647 | -3.6695 | -5.4695 | -13.5062 | -23.745 | -33.0113 | 6.5907 | 6.4999 | 5.6183 | 4.2969 | 3.6907 | 0.51216 | -0.45927 | -1.5307 | -2.6429 | -4.7185 | -13.648 | -25.6929 | -37.4256 | 5.8787 | 5.741 | 4.8114 | 3.44 | 2.7798 | -0.4335 | -1.5294 | -2.7192 | -3.9162 | -6.1029 | -15.7468 | -28.0743 | -39.4866
|  | MILL RD | CF |  |  |  |  | 4.4979 | 4.4356 | 4.3611 | 4.2836 | 3.7856 | 2.9009 | 2.3907 | 1.9632 | 1.5142 | 0.91828 | -1.3858 | -3.9011 | -6.2674 | 6.6275 | 6.5826 | 6.5295 | 6.4703 | 5.8918 | 4.8397 | 4.254 | 3.7938 | 3.304 | 2.6193 | 0.08869 | -2.995 | -6.2195 | 5.9338 | 5.8543 | 5.7543 | 5.6645 | 5.0522 | 3.9553 | 3.3471 | 2.842 | 2.3165 | 1.6185 | -0.99269 | -3.9611 | -6.6162
| ABERNETHY | MILNATHORT | MINIMUM HEADROOM | NO 11900 05074 | NO | YES | 5.971 | -1.7984 | -2.8719 | 19.372 | 17.972 | 16.1944 | 13.9699 | 11.8955 | 9.672 | 7.2006 | 4.9036 | -6.4474 | -13.2484 | -17.3454 | 1.772 | 1.1587 | 23.1097 | 21.9863 | 20.4363 | 18.3434 | 16.7097 | 14.8812 | 13.0526 | 10.7648 | 0.50668 | -6.375 | -11.2831 | 0.15209 | -0.85709 | 21.475 | 20.0383 | 18.1557 | 15.8669 | 13.8189 | 11.6853 | 9.2199 | 6.9648 | -5.2362 | -12.8403 | -17.8372
|  | MILNATHORT | EE |  |  |  |  | -1.7984 | -2.8719 | 19.372 | 17.972 | 16.1944 | 13.9699 | 11.8955 | 9.672 | 7.2006 | 4.9036 | -4.4801 | -12.2178 | -14.729 | 1.772 | 1.1587 | 23.1097 | 21.9863 | 20.4363 | 18.4944 | 16.8383 | 15.1597 | 13.1383 | 11.3342 | 3.8832 | -3.6015 | -6.225 | 0.15209 | -0.85709 | 21.475 | 20.0383 | 18.1557 | 15.8669 | 13.8189 | 11.6853 | 9.2199 | 6.9648 | -2.3188 | -10.7627 | -13.5913
|  | MILNATHORT | HT |  |  |  |  | -1.2596 | -2.1096 | 20.1138 | 18.6679 | 17.6302 | 15.3118 | 13.6322 | 11.7944 | 10.0026 | 8.0557 | -0.84842 | -9.2352 | -14.3392 | 2.0659 | 1.5291 | 23.5046 | 22.2659 | 21.4485 | 19.1189 | 17.7291 | 16.2955 | 14.9557 | 13.4648 | 6.3159 | -1.9056 | -7.4984 | 0.51025 | -0.26118 | 22.0853 | 20.623 | 19.5904 | 16.9883 | 15.2648 | 13.4679 | 11.7455 | 9.8506 | 0.9628 | -8.2535 | -14.1801
|  | MILNATHORT | HE |  |  |  |  | -1.3668 | -2.3066 | 19.9495 | 18.4179 | 17.0485 | 14.5587 | 12.5893 | 10.375 | 8.1689 | 5.5526 | -6.4474 | -13.2484 | -17.3454 | 2.0179 | 1.4873 | 23.4363 | 22.0118 | 20.8159 | 18.3434 | 16.7097 | 14.8812 | 13.0526 | 10.7648 | 0.50668 | -6.375 | -11.2831 | 0.46127 | -0.31424 | 21.9965 | 20.3465 | 18.8893 | 16.1148 | 14.1455 | 11.9393 | 9.7302 | 7.0383 | -5.2362 | -12.8403 | -17.8372
|  | MILNATHORT | CF |  |  |  |  | -1.076 | -1.5413 | 21.3853 | 20.7179 | 19.8097 | 18.6699 | 17.6516 | 16.4689 | 15.3332 | 14.1689 | 7.3434 | 0.88219 | -3.526 | 2.1791 | 1.8689 | 24.4934 | 24.0914 | 23.3781 | 22.2883 | 21.373 | 20.3434 | 19.373 | 18.3873 | 12.9097 | 7.7587 | 4.2597 | 0.67658 | 0.26944 | 23.4128 | 22.8097 | 21.8914 | 20.6332 | 19.5455 | 18.2975 | 17.125 | 15.9577 | 9.2424 | 2.8791 | -1.4821
| MILTON OF CRAIGIE | MILTON OF CRAIGIE | MINIMUM HEADROOM | NO 43137 31857 | NO | NO | 6.757 | -0.68911 | -1.0197 | -1.432 | -1.8279 | -2.3503 | -2.8932 | -3.5391 | -4.1636 | -4.7289 | -5.3258 | -7.0993 | -7.2493 | -7.2575 | 4.7497 | 4.5211 | 4.2384 | 3.9731 | 3.615 | 3.2282 | 2.7701 | 2.3231 | 1.9262 | 1.4874 | 0.2364 | -0.50034 | -2.984 | 0.24405 | -0.046767 | -0.41616 | -0.76718 | -1.2366 | -1.708 | -2.2876 | -2.8641 | -3.3845 | -3.9233 | -5.3947 | -5.4682 | -5.4825
|  | MILTON OF CRAIGIE | EE |  |  |  |  | -0.68911 | -1.0197 | -1.432 | -1.8279 | -2.3503 | -2.8932 | -3.5391 | -4.1636 | -4.7289 | -5.3258 | -6.8779 | -6.7493 | -6.7707 | 4.7497 | 4.5211 | 4.2384 | 3.9731 | 3.615 | 3.2282 | 2.7701 | 2.3231 | 1.9262 | 1.4874 | 0.2364 | -0.25544 | -1.1973 | 0.24405 | -0.046767 | -0.41616 | -0.76718 | -1.2366 | -1.708 | -2.2876 | -2.8641 | -3.3845 | -3.9233 | -5.1335 | -5.0662 | -5.1162
|  | MILTON OF CRAIGIE | HT |  |  |  |  | -0.60442 | -0.91667 | -1.3024 | -1.6912 | -2.1748 | -2.6687 | -3.2085 | -3.7432 | -4.1861 | -4.8473 | -7.0993 | -7.2493 | -7.2575 | 4.8221 | 4.6201 | 4.3731 | 4.1354 | 3.8272 | 3.4782 | 3.1211 | 2.7793 | 2.5078 | 2.0466 | 0.54864 | 0.42415 | 0.39252 | 0.34303 | 0.073641 | -0.25187 | -0.58554 | -1.0008 | -1.4335 | -1.908 | -2.3825 | -2.76 | -3.3478 | -5.3947 | -5.4682 | -5.4825
|  | MILTON OF CRAIGIE | HE |  |  |  |  | -0.58095 | -0.80952 | -1.0748 | -1.3667 | -1.7585 | -2.1381 | -2.6218 | -3.0912 | -3.4779 | -3.9993 | -6.0881 | -6.432 | -6.3942 | 4.8354 | 4.6568 | 4.4619 | 4.2527 | 3.9742 | 3.6813 | 3.3201 | 2.9782 | 2.6976 | 2.3017 | 0.54558 | -0.05238 | -0.93299 | 0.36446 | 0.15731 | -0.073298 | -0.33452 | -0.67738 | -1.0121 | -1.4406 | -1.8662 | -2.1957 | -2.6611 | -4.5611 | -4.7325 | -4.7151
|  | MILTON OF CRAIGIE | CF |  |  |  |  | -0.47177 | -0.59218 | -0.74728 | -0.88707 | -1.085 | -1.3207 | -1.5422 | -1.8156 | -2.0401 | -2.3085 | -3.9085 | -5.6656 | -6.8463 | 4.9078 | 4.7976 | 4.6639 | 4.5446 | 4.3813 | 4.1742 | 3.969 | 3.719 | 3.5017 | 3.2405 | 1.6313 | -0.50034 | -2.984 | 0.45731 | 0.34099 | 0.19507 | 0.067518 | -0.11718 | -0.33452 | -0.53044 | -0.78962 | -1.0019 | -1.257 | -2.7213 | -4.2723 | -5.2151
| STRICHEN | MINTLAW | MINIMUM HEADROOM | NK 00897 48662 | NO | YES | 1.784 | 6.9726 | 6.4838 | 5.9685 | 5.3603 | 4.7144 | 4.1593 | 3.6644 | 3.146 | 2.6675 | 2.1675 | 0.34093 | -0.73764 | -0.86928 | 8.0593 | 7.743 | 7.3889 | 6.9746 | 6.5195 | 6.1787 | 5.9185 | 5.6011 | 5.4287 | 5.1838 | 4.1613 | 3.545 | 2.8073 | 7.5465 | 7.1333 | 6.6874 | 6.1465 | 5.5639 | 5.072 | 4.6414 | 4.1312 | 3.7812 | 3.3455 | 1.8067 | 0.9047 | 0.79042
|  | MINTLAW | EE |  |  |  |  | 6.9726 | 6.4838 | 6.0164 | 5.447 | 4.843 | 4.2654 | 3.7011 | 3.146 | 2.8991 | 2.3909 | 0.34093 | -0.64377 | -0.76418 | 8.0593 | 7.743 | 7.4297 | 7.0419 | 6.6266 | 6.2583 | 5.9195 | 5.6011 | 5.497 | 5.2328 | 4.1613 | 3.545 | 3.1368 | 7.5465 | 7.1333 | 6.7149 | 6.2027 | 5.669 | 5.1516 | 4.6414 | 4.1312 | 3.968 | 3.5282 | 1.8067 | 0.98531 | 0.88327
|  | MINTLAW | HT |  |  |  |  | 6.9879 | 6.4909 | 5.9685 | 5.3603 | 4.7144 | 4.1593 | 3.6644 | 3.2032 | 2.6675 | 2.1675 | 0.35521 | -0.73764 | -0.86928 | 8.0685 | 7.747 | 7.3889 | 6.9746 | 6.5195 | 6.1787 | 5.9185 | 5.6899 | 5.4287 | 5.1838 | 4.3573 | 3.8593 | 3.7879 | 7.5863 | 7.1578 | 6.6874 | 6.1465 | 5.5639 | 5.072 | 4.6425 | 4.2425 | 3.7812 | 3.3455 | 1.8261 | 0.9047 | 0.79042
|  | MINTLAW | HE |  |  |  |  | 7.0236 | 6.6236 | 6.2246 | 5.7409 | 5.2256 | 4.7379 | 4.2919 | 3.8797 | 3.4511 | 2.9981 | 1.0042 | -0.10091 | -0.3305 | 8.097 | 7.8226 | 7.5379 | 7.1909 | 6.8164 | 6.4889 | 6.2052 | 5.9685 | 5.7205 | 5.4685 | 4.4266 | 3.7522 | 3.3144 | 7.619 | 7.2731 | 6.92 | 6.4874 | 6.0323 | 5.5986 | 5.2006 | 4.8404 | 4.4598 | 4.0588 | 2.3976 | 1.469 | 1.271
|  | MINTLAW | CF |  |  |  |  | 7.1062 | 6.8103 | 6.5317 | 6.2164 | 5.8797 | 5.5215 | 5.2134 | 4.8919 | 4.6205 | 4.3052 | 2.4991 | 0.94399 | 0.15113 | 8.1654 | 7.9726 | 7.7807 | 7.5726 | 7.3368 | 7.0919 | 6.8726 | 6.6481 | 6.4675 | 6.2552 | 5.1032 | 3.8858 | 2.8073 | 7.6904 | 7.4404 | 7.2027 | 6.9282 | 6.6282 | 6.3108 | 6.0374 | 5.7465 | 5.5149 | 5.2323 | 3.7241 | 2.3659 | 1.6833
| BRIDGE OF DUN | MONTROSE NORTH | MINIMUM HEADROOM | NO 71226 59070 | NO | NO | 0.78 | 4.9161 | 3.3752 | 2.2997 | 1.515 | 24.465 | 23.9885 | 23.3977 | 22.762 | 22.0895 | 21.2895 | 19.013 | 17.6906 | 17.465 | 5.6365 | 4.0559 | 3.0824 | 2.4406 | 25.0069 | 24.7365 | 24.5508 | 24.3599 | 24.1732 | 23.9548 | 22.9906 | 22.1814 | 21.513 | 5.7798 | 4.2911 | 3.2645 | 2.5237 | 25.5926 | 25.1681 | 24.6804 | 24.1589 | 23.612 | 22.9732 | 21.0518 | 19.8967 | 19.7028
|  | MONTROSE NORTH | EE |  |  |  |  | 5.2518 | 3.8548 | 2.7855 | 1.9314 | 24.811 | 24.2171 | 23.5467 | 23.1416 | 22.5416 | 21.9416 | 19.1252 | 17.7579 | 17.465 | 6.0773 | 4.6926 | 3.6926 | 2.9895 | 25.464 | 25.0548 | 24.713 | 24.5691 | 24.3467 | 24.1426 | 22.9906 | 22.1814 | 21.513 | 6.1002 | 4.8217 | 3.7809 | 2.988 | 25.9967 | 25.463 | 24.8752 | 24.4936 | 23.9875 | 23.4834 | 21.113 | 19.962 | 19.7028
|  | MONTROSE NORTH | HT |  |  |  |  | 4.9161 | 3.3752 | 2.2997 | 1.515 | 24.465 | 23.9885 | 23.3977 | 22.762 | 22.0895 | 21.2895 | 19.013 | 17.6906 | 17.4681 | 5.6365 | 4.0559 | 3.0824 | 2.4406 | 25.0069 | 24.7365 | 24.5508 | 24.3599 | 24.1732 | 23.9548 | 23.2008 | 22.6916 | 22.6028 | 5.7798 | 4.2911 | 3.2645 | 2.5237 | 25.5926 | 25.1681 | 24.6804 | 24.1589 | 23.612 | 22.9732 | 21.0518 | 19.8967 | 19.712
|  | MONTROSE NORTH | HE |  |  |  |  | 5.3079 | 4.0385 | 3.0701 | 2.3671 | 25.3518 | 24.8906 | 24.4548 | 23.9977 | 23.565 | 23.1161 | 21.1895 | 19.6079 | 18.8365 | 6.1048 | 4.7559 | 3.7773 | 3.1181 | 25.612 | 25.2375 | 24.9691 | 24.7446 | 24.5599 | 24.3773 | 23.7742 | 22.9416 | 22.0865 | 6.1666 | 4.9625 | 4.0176 | 3.3411 | 26.4293 | 26.0028 | 25.615 | 25.2283 | 24.863 | 24.4957 | 22.8365 | 21.4773 | 20.813
|  | MONTROSE NORTH | CF |  |  |  |  | 6.3916 | 5.5936 | 4.9375 | 4.3252 | 27.4252 | 26.9783 | 26.6181 | 26.2967 | 25.9946 | 25.6804 | 23.8375 | 21.7579 | 20.2701 | 7.3569 | 6.513 | 5.8497 | 5.2242 | 27.764 | 27.3293 | 26.9732 | 26.6589 | 26.3906 | 26.1222 | 24.7977 | 23.2967 | 21.5569 | 7.1554 | 6.4309 | 5.8349 | 5.2747 | 28.4814 | 28.0569 | 27.711 | 27.414 | 27.1293 | 26.8304 | 25.1946 | 23.3538 | 22.1059
| TARLAND | MOSSAT | MINIMUM HEADROOM | NJ 47470 19897 | NO | NO | 2.155 | 0.14906 | 0.0031429 | -0.1989 | -0.40196 | 3.8876 | 3.6927 | 3.4795 | 3.2958 | 3.1182 | 2.9978 | 2.5999 | 2.4795 | 2.4274 | 0.75824 | 0.66437 | 0.55008 | 0.42151 | 4.3866 | 4.2703 | 4.1448 | 4.0121 | 3.8917 | 3.8376 | 3.5764 | 3.4703 | 3.0805 | 0.47253 | 0.33682 | 0.16743 | -0.010122 | 4.0907 | 3.9254 | 3.7264 | 3.5468 | 3.3764 | 3.2733 | 2.9131 | 2.807 | 2.7652
|  | MOSSAT | EE |  |  |  |  | 0.14906 | 0.0031429 | -0.18971 | -0.39073 | 3.8876 | 3.6927 | 3.4795 | 3.2958 | 3.1182 | 2.9978 | 2.5999 | 2.5325 | 2.508 | 0.75824 | 0.66437 | 0.55008 | 0.42151 | 4.3866 | 4.2703 | 4.1448 | 4.0121 | 3.8917 | 3.8376 | 3.5764 | 3.4703 | 3.3172 | 0.47253 | 0.33682 | 0.16743 | -0.010122 | 4.0907 | 3.9254 | 3.7264 | 3.5468 | 3.3764 | 3.2733 | 2.9131 | 2.855 | 2.8315
|  | MOSSAT | HT |  |  |  |  | 0.18069 | 0.0031429 | -0.1989 | -0.40196 | 3.8968 | 3.706 | 3.5713 | 3.457 | 3.3233 | 3.1907 | 2.7131 | 2.4795 | 2.4274 | 0.77661 | 0.67151 | 0.5511 | 0.42355 | 4.4101 | 4.3019 | 4.2233 | 4.1601 | 4.0846 | 4.0091 | 3.706 | 3.5795 | 3.554 | 0.50314 | 0.35416 | 0.18376 | 0.0041633 | 4.1284 | 3.9591 | 3.8427 | 3.7376 | 3.6152 | 3.4866 | 3.0172 | 2.807 | 2.7652
|  | MOSSAT | HE |  |  |  |  | 0.19294 | 0.084776 | -0.064204 | -0.24584 | 4.0836 | 3.9101 | 3.7366 | 3.5989 | 3.5019 | 3.3764 | 2.7366 | 2.5774 | 2.5448 | 0.78478 | 0.71029 | 0.61743 | 0.50008 | 4.4978 | 4.3917 | 4.2866 | 4.1989 | 4.1376 | 4.0601 | 3.658 | 3.4958 | 3.3417 | 0.51437 | 0.41641 | 0.2858 | 0.12763 | 4.2866 | 4.1325 | 3.9744 | 3.8387 | 3.7591 | 3.6387 | 3.0478 | 2.905 | 2.8774
|  | MOSSAT | CF |  |  |  |  | 0.21845 | 0.14192 | 0.042939 | -0.086653 | 4.2754 | 4.1468 | 4.0203 | 3.8774 | 3.7846 | 3.7193 | 3.2274 | 2.8427 | 2.605 | 0.8062 | 0.75416 | 0.68682 | 0.61233 | 4.6305 | 4.5519 | 4.4703 | 4.3795 | 4.3121 | 4.2652 | 3.8754 | 3.4866 | 3.0805 | 0.54294 | 0.46845 | 0.37661 | 0.26845 | 4.4478 | 4.3407 | 4.2284 | 4.0968 | 4.005 | 3.955 | 3.4764 | 3.1172 | 2.9152
| THURSO | MOUNT PLEASANT | MINIMUM HEADROOM | ND 12706 67832 | YES | NO | 2.034 | 8.0797 | 7.4195 | 6.6174 | 6.0235 | 5.5888 | 5.1429 | 4.6786 | 4.2388 | 3.7858 | 3.495 | 2.2001 | 1.4021 | 1.2654 | 8.8715 | 8.3562 | 7.6899 | 7.2246 | 6.9041 | 6.6297 | 6.3939 | 6.1705 | 5.8746 | 5.8276 | 5.1358 | 4.7531 | 4.4715 | 8.7006 | 8.0863 | 7.3312 | 6.7883 | 6.3985 | 6.0496 | 5.673 | 5.2608 | 4.7781 | 4.6057 | 3.4373 | 2.7526 | 2.6363
|  | MOUNT PLEASANT | EE |  |  |  |  | 8.198 | 7.5541 | 6.8786 | 6.2848 | 5.7725 | 5.3674 | 4.8756 | 4.3133 | 3.7858 | 3.5776 | 2.2001 | 1.4939 | 1.3276 | 8.9776 | 8.4746 | 7.9368 | 7.4684 | 7.0817 | 6.7909 | 6.4919 | 6.1705 | 5.8746 | 5.8358 | 5.1358 | 4.7531 | 4.4715 | 8.8342 | 8.2414 | 7.6169 | 7.0863 | 6.621 | 6.2434 | 5.7791 | 5.2608 | 4.7781 | 4.6496 | 3.4373 | 2.8414 | 2.6904
|  | MOUNT PLEASANT | HT |  |  |  |  | 8.0797 | 7.4195 | 6.6174 | 6.0235 | 5.5888 | 5.1429 | 4.6786 | 4.2388 | 3.848 | 3.495 | 2.2225 | 1.4021 | 1.2654 | 8.8715 | 8.3562 | 7.6899 | 7.2246 | 6.9041 | 6.6297 | 6.3939 | 6.1858 | 6.0001 | 5.8276 | 5.2735 | 4.9072 | 4.846 | 8.7006 | 8.0863 | 7.3312 | 6.7883 | 6.3985 | 6.0496 | 5.673 | 5.2914 | 4.9342 | 4.6057 | 3.4781 | 2.7526 | 2.6363
|  | MOUNT PLEASANT | HE |  |  |  |  | 8.2419 | 7.6827 | 7.0909 | 6.5909 | 6.2052 | 5.8725 | 5.5195 | 5.1613 | 4.8082 | 4.4521 | 3.1144 | 2.3317 | 2.0531 | 9.0154 | 8.5521 | 8.049 | 7.6286 | 7.3041 | 7.0409 | 6.8092 | 6.6021 | 6.4021 | 6.2072 | 5.5409 | 5.1144 | 4.8062 | 8.8608 | 8.3271 | 7.7598 | 7.2904 | 6.9271 | 6.6291 | 6.3291 | 6.0455 | 5.7526 | 5.4251 | 4.2618 | 3.5822 | 3.3424
|  | MOUNT PLEASANT | CF |  |  |  |  | 8.7072 | 8.3582 | 7.9674 | 7.6582 | 7.3429 | 7.0725 | 6.8113 | 6.548 | 6.2644 | 6.0103 | 4.5246 | 3.547 | 2.795 | 9.4195 | 9.1276 | 8.798 | 8.546 | 8.2888 | 8.0644 | 7.8501 | 7.6378 | 7.4327 | 7.249 | 6.1695 | 5.4154 | 4.6888 | 9.321 | 8.9934 | 8.6261 | 8.3414 | 8.0577 | 7.8047 | 7.5761 | 7.3445 | 7.0812 | 6.8547 | 5.4659 | 4.6108 | 3.9608
| BEAULY | MUIR OF ORD | MINIMUM HEADROOM | NH 53420 48534 | NO | NO | 3.192 | 9.1676 | 8.8707 | 8.5268 | 8.1993 | 7.8197 | 7.2391 | 6.387 | 5.5054 | 4.7462 | 4.2554 | 2.4748 | 1.8064 | 1.6319 | 11.0217 | 10.8625 | 10.6574 | 10.4554 | 10.1921 | 9.9105 | 9.5666 | 9.2258 | 8.836 | 8.5105 | 7.3748 | 6.8972 | 5.887 | 10.2993 | 10.0278 | 9.7064 | 9.4034 | 9.0452 | 8.6238 | 7.9044 | 7.1442 | 6.486 | 6.1268 | 4.4503 | 3.8717 | 3.7248
|  | MUIR OF ORD | EE |  |  |  |  | 9.1676 | 8.8707 | 8.5268 | 8.1993 | 7.8197 | 7.4238 | 6.9156 | 6.2666 | 5.3819 | 4.5125 | 2.4748 | 1.985 | 1.8554 | 11.0217 | 10.8625 | 10.6574 | 10.4554 | 10.1921 | 9.9105 | 9.5666 | 9.4278 | 8.9544 | 8.5105 | 7.3748 | 6.8972 | 6.2972 | 10.2993 | 10.0278 | 9.7064 | 9.4034 | 9.0452 | 8.6676 | 8.1891 | 7.6972 | 6.936 | 6.1972 | 4.4503 | 4.0329 | 3.9105
|  | MUIR OF ORD | HT |  |  |  |  | 9.236 | 8.9493 | 8.638 | 8.3421 | 8.0044 | 7.2391 | 6.387 | 5.5054 | 4.7462 | 4.2554 | 2.6462 | 1.8064 | 1.6319 | 11.088 | 10.9523 | 10.7921 | 10.6432 | 10.4615 | 10.0983 | 9.6738 | 9.2258 | 8.836 | 8.686 | 7.7483 | 7.3166 | 7.2278 | 10.3789 | 10.1248 | 9.8391 | 9.5707 | 9.2585 | 8.6238 | 7.9044 | 7.1442 | 6.486 | 6.1268 | 4.6227 | 3.8717 | 3.7248
|  | MUIR OF ORD | HE |  |  |  |  | 9.238 | 9.0421 | 8.8238 | 8.6197 | 8.3738 | 8.137 | 7.8013 | 7.2891 | 6.7942 | 6.2789 | 4.2023 | 3.1666 | 2.734 | 11.086 | 10.9758 | 10.8432 | 10.7207 | 10.5666 | 10.4268 | 10.2115 | 9.8983 | 9.588 | 9.2666 | 8.2044 | 7.4646 | 6.7564 | 10.3799 | 10.2034 | 9.9993 | 9.8074 | 9.5748 | 9.3615 | 9.0472 | 8.587 | 8.1411 | 7.6768 | 5.9064 | 5.0278 | 4.6748
|  | MUIR OF ORD | CF |  |  |  |  | 9.2819 | 9.1329 | 8.9503 | 8.784 | 8.5819 | 8.3717 | 8.185 | 7.9727 | 7.6258 | 7.2768 | 5.8513 | 4.3503 | 3.1962 | 11.1115 | 11.0278 | 10.9146 | 10.8146 | 10.688 | 10.5421 | 10.4227 | 10.237 | 10.0064 | 9.7656 | 8.8534 | 7.4819 | 5.887 | 10.4217 | 10.286 | 10.1197 | 9.9666 | 9.7809 | 9.5829 | 9.4166 | 9.2095 | 8.9034 | 8.5901 | 7.3697 | 6.0278 | 5.0401
| BEAULY | MUIREND | MINIMUM HEADROOM | NH 64508 54337 | YES | NO | 0.098 | 0.22029 | 0.1162 | 0.0039592 | -0.10114 | -0.21951 | -0.30931 | -0.44808 | -0.63073 | -0.80727 | -0.9338 | -1.2522 | -1.3634 | -1.3971 | 1.4529 | 1.3917 | 1.3274 | 1.258 | 1.1815 | 1.1264 | 1.0336 | 0.91722 | 0.8009 | 0.73457 | 0.5111 | 0.4009 | 0.0049796 | 0.92233 | 0.82437 | 0.72437 | 0.62437 | 0.506 | 0.42131 | 0.28049 | 0.099878 | -0.072571 | -0.17053 | -0.46033 | -0.55829 | -0.58584
|  | MUIREND | EE |  |  |  |  | 0.22029 | 0.1162 | 0.0039592 | -0.10114 | -0.21951 | -0.30931 | -0.44808 | -0.63073 | -0.80727 | -0.9338 | -1.2522 | -1.3073 | -1.3338 | 1.4529 | 1.3917 | 1.3274 | 1.258 | 1.1815 | 1.1264 | 1.0336 | 0.91722 | 0.8009 | 0.73457 | 0.5111 | 0.4009 | 0.23661 | 0.92233 | 0.82437 | 0.72437 | 0.62437 | 0.506 | 0.42131 | 0.28049 | 0.099878 | -0.072571 | -0.17053 | -0.46033 | -0.51033 | -0.53584
|  | MUIREND | HT |  |  |  |  | 0.256 | 0.16212 | 0.061102 | -0.033796 | -0.11339 | -0.23584 | -0.36951 | -0.52359 | -0.60318 | -0.71951 | -1.1603 | -1.3634 | -1.3971 | 1.4846 | 1.4366 | 1.3825 | 1.3274 | 1.2846 | 1.2162 | 1.1387 | 1.0458 | 0.99784 | 0.92233 | 0.63763 | 0.52233 | 0.50192 | 0.9662 | 0.88457 | 0.79376 | 0.70396 | 0.63355 | 0.52233 | 0.39886 | 0.24988 | 0.17641 | 0.059061 | -0.37053 | -0.55829 | -0.58584
|  | MUIREND | HE |  |  |  |  | 0.25396 | 0.17947 | 0.098857 | 0.022327 | -0.039918 | -0.11441 | -0.20931 | -0.33788 | -0.42359 | -0.544 | -1.1032 | -1.2358 | -1.2562 | 1.4836 | 1.4407 | 1.3907 | 1.3397 | 1.3019 | 1.2519 | 1.1856 | 1.1029 | 1.0519 | 0.96824 | 0.60396 | 0.44784 | 0.28967 | 0.96416 | 0.89886 | 0.82233 | 0.74682 | 0.68967 | 0.61824 | 0.52233 | 0.3958 | 0.31927 | 0.2009 | -0.31849 | -0.44094 | -0.46135
|  | MUIREND | CF |  |  |  |  | 0.27335 | 0.21314 | 0.12743 | 0.066204 | -0.0011429 | -0.048082 | -0.11033 | -0.18584 | -0.27461 | -0.33278 | -0.75012 | -1.0471 | -1.2307 | 1.4968 | 1.4611 | 1.408 | 1.3672 | 1.3213 | 1.2907 | 1.2468 | 1.1866 | 1.1213 | 1.0866 | 0.74273 | 0.4009 | 0.0049796 | 0.98151 | 0.92641 | 0.84478 | 0.78661 | 0.71824 | 0.67641 | 0.6162 | 0.53457 | 0.4458 | 0.3958 | -0.029714 | -0.30829 | -0.45318
| NAIRN | NAIRN CENTRAL | MINIMUM HEADROOM | NH 88496 56295 | NO | YES | 2.426 | 3.2063 | 2.7584 | 2.2747 | 1.742 | 1.1481 | 0.541 | -0.41308 | -1.407 | -2.0825 | -3.0008 | -6.1784 | -8.0131 | -8.3845 | 5.5032 | 5.3696 | 5.1839 | 4.9135 | 4.6145 | 4.4675 | 4.0359 | 3.5777 | 3.1726 | 2.7369 | 1.1777 | 0.065494 | -0.83757 | 4.1527 | 3.867 | 3.5538 | 3.1201 | 2.615 | 2.118 | 1.315 | 0.48131 | -0.087057 | -0.86359 | -3.6371 | -5.2391 | -5.5615
|  | NAIRN CENTRAL | EE |  |  |  |  | 3.2063 | 2.7584 | 2.2747 | 1.742 | 1.1481 | 0.80121 | 0.039984 | -0.94369 | -1.907 | -2.8121 | -5.959 | -7.8284 | -8.2651 | 5.5032 | 5.3696 | 5.1839 | 4.9135 | 4.6145 | 4.4818 | 4.1175 | 3.6379 | 3.1726 | 2.7369 | 1.1777 | 0.065494 | -0.83757 | 4.1527 | 3.867 | 3.5538 | 3.1201 | 2.615 | 2.316 | 1.6599 | 0.83131 | 0.019065 | -0.74318 | -3.4564 | -5.0881 | -5.4636
|  | NAIRN CENTRAL | HT |  |  |  |  | 3.2879 | 2.8328 | 2.3645 | 1.8502 | 1.3135 | 0.541 | -0.41308 | -1.407 | -2.0825 | -3.0008 | -6.1784 | -8.0131 | -8.3845 | 5.5553 | 5.4379 | 5.2839 | 5.0594 | 4.8216 | 4.4675 | 4.0359 | 3.5777 | 3.3349 | 2.9206 | 1.4839 | 0.69611 | 0.51243 | 4.218 | 3.9395 | 3.6476 | 3.2109 | 2.7568 | 2.118 | 1.315 | 0.48131 | -0.087057 | -0.86359 | -3.6371 | -5.2391 | -5.5615
|  | NAIRN CENTRAL | HE |  |  |  |  | 3.3155 | 3.0135 | 2.7165 | 2.3777 | 2.0165 | 1.5961 | 1.0686 | 0.45019 | 0.14713 | -0.39675 | -3.1947 | -5.3702 | -6.4345 | 5.5584 | 5.4512 | 5.3522 | 5.2226 | 5.042 | 4.8186 | 4.5492 | 4.2226 | 4.1114 | 3.8277 | 2.3073 | 1.0288 | -0.109 | 4.2282 | 4.0282 | 3.8313 | 3.6058 | 3.3619 | 3.016 | 2.567 | 2.0425 | 1.7823 | 1.3201 | -1.1228 | -3.0166 | -3.936
|  | NAIRN CENTRAL | CF |  |  |  |  | 3.5257 | 3.2879 | 3.0186 | 2.8063 | 2.5277 | 2.2655 | 2.0032 | 1.7094 | 1.3777 | 1.0675 | -0.28042 | -2.4774 | -4.6039 | 5.6349 | 5.5461 | 5.4522 | 5.3777 | 5.2441 | 5.091 | 4.9196 | 4.7186 | 4.5022 | 4.291 | 3.3441 | 1.5645 | -0.81614 | 4.3517 | 4.2119 | 4.0517 | 3.9191 | 3.7436 | 3.5752 | 3.3742 | 3.1303 | 2.8599 | 2.6048 | 1.4354 | -0.47889 | -2.3105
| STRICHEN | NEW PITSLIGO | MINIMUM HEADROOM | NJ 88529 54853 | NO | YES | 0.035 | 6.134 | 6.0646 | 5.9809 | 5.9116 | 5.8269 | 5.733 | 5.6146 | 5.5014 | 5.3677 | 5.233 | 4.7503 | 4.6544 | 4.6167 | 6.7769 | 6.735 | 6.6738 | 6.634 | 6.5738 | 6.5034 | 6.4197 | 6.3534 | 6.2605 | 6.1769 | 5.9116 | 5.8411 | 5.5769 | 6.4258 | 6.3595 | 6.2748 | 6.2054 | 6.1228 | 6.0269 | 5.9044 | 5.8003 | 5.6656 | 5.5381 | 5.1269 | 5.0442 | 5.0136
|  | NEW PITSLIGO | EE |  |  |  |  | 6.134 | 6.0646 | 5.9809 | 5.9116 | 5.8269 | 5.733 | 5.6146 | 5.5014 | 5.3677 | 5.233 | 4.7503 | 4.6922 | 4.6718 | 6.7769 | 6.735 | 6.6738 | 6.634 | 6.5738 | 6.5034 | 6.4197 | 6.3534 | 6.2605 | 6.1769 | 5.9116 | 5.8411 | 5.732 | 6.4258 | 6.3595 | 6.2748 | 6.2054 | 6.1228 | 6.0269 | 5.9044 | 5.8003 | 5.6656 | 5.5381 | 5.1269 | 5.0769 | 5.0534
|  | NEW PITSLIGO | HT |  |  |  |  | 6.1503 | 6.0871 | 6.0248 | 5.9565 | 5.8789 | 5.8126 | 5.7014 | 5.5809 | 5.4432 | 5.3065 | 4.833 | 4.6544 | 4.6167 | 6.7993 | 6.7626 | 6.7269 | 6.6891 | 6.6401 | 6.6085 | 6.5401 | 6.4697 | 6.386 | 6.3258 | 6.0044 | 5.9054 | 5.886 | 6.4473 | 6.3881 | 6.3279 | 6.2646 | 6.1901 | 6.1269 | 6.0238 | 5.9095 | 5.783 | 5.6707 | 5.2065 | 5.0442 | 5.0136
|  | NEW PITSLIGO | HE |  |  |  |  | 6.1514 | 6.1034 | 6.0585 | 6.0075 | 5.9483 | 5.9003 | 5.8228 | 5.7085 | 5.582 | 5.4391 | 4.8656 | 4.7432 | 4.7105 | 6.7993 | 6.7667 | 6.7391 | 6.7065 | 6.6616 | 6.633 | 6.5799 | 6.5085 | 6.4299 | 6.3442 | 6.0003 | 5.8891 | 5.7758 | 6.4493 | 6.4003 | 6.3565 | 6.3065 | 6.2473 | 6.2014 | 6.1238 | 6.0197 | 5.9044 | 5.7707 | 5.2554 | 5.1146 | 5.0442
|  | NEW PITSLIGO | CF |  |  |  |  | 6.1626 | 6.1218 | 6.084 | 6.035 | 5.9952 | 5.9452 | 5.9065 | 5.8493 | 5.7881 | 5.7116 | 5.2401 | 4.9585 | 4.7728 | 6.8065 | 6.7809 | 6.7575 | 6.7228 | 6.6962 | 6.6605 | 6.6381 | 6.5901 | 6.5493 | 6.4952 | 6.1809 | 5.8942 | 5.5769 | 6.4585 | 6.4207 | 6.384 | 6.3381 | 6.3003 | 6.2483 | 6.2146 | 6.1544 | 6.0983 | 6.0269 | 5.6024 | 5.3136 | 5.1391
| DUNOON | NEWTON | MINIMUM HEADROOM | NS 04939 98621 | YES | YES | 0.019 | 0.21097 | 0.20791 | 0.20076 | 0.1926 | 0.18546 | 0.17627 | 0.16301 | 0.15178 | 0.1375 | 0.12423 | 0.09362 | 0.082396 | 0.081376 | 0.22784 | 0.22682 | 0.22887 | 0.22376 | 0.21866 | 0.21254 | 0.20233 | 0.19621 | 0.18397 | 0.17682 | 0.15438 | 0.14417 | 0.11662 | 0.21992 | 0.21686 | 0.21175 | 0.20461 | 0.19849 | 0.18828 | 0.174 | 0.16481 | 0.15053 | 0.14032 | 0.11175 | 0.099508 | 0.099508
|  | NEWTON | EE |  |  |  |  | 0.21097 | 0.20791 | 0.20076 | 0.1926 | 0.18546 | 0.17627 | 0.16301 | 0.15178 | 0.1375 | 0.12423 | 0.09362 | 0.09158 | 0.088518 | 0.22784 | 0.23397 | 0.22887 | 0.22376 | 0.21866 | 0.21254 | 0.20233 | 0.19621 | 0.18397 | 0.17682 | 0.15438 | 0.14417 | 0.13193 | 0.21992 | 0.2189 | 0.21175 | 0.20461 | 0.19849 | 0.18828 | 0.174 | 0.16481 | 0.15053 | 0.14032 | 0.11175 | 0.10971 | 0.10563
|  | NEWTON | HT |  |  |  |  | 0.21811 | 0.20791 | 0.20791 | 0.20178 | 0.1926 | 0.18852 | 0.18138 | 0.16811 | 0.15995 | 0.14668 | 0.10382 | 0.082396 | 0.081376 | 0.23499 | 0.22682 | 0.23499 | 0.23091 | 0.22478 | 0.22376 | 0.21764 | 0.20846 | 0.20336 | 0.19519 | 0.1656 | 0.15131 | 0.15131 | 0.22706 | 0.21686 | 0.2189 | 0.21379 | 0.20461 | 0.20053 | 0.19339 | 0.18114 | 0.17298 | 0.16379 | 0.11992 | 0.099508 | 0.099508
|  | NEWTON | HE |  |  |  |  | 0.21811 | 0.20791 | 0.21199 | 0.20382 | 0.1977 | 0.1926 | 0.18852 | 0.17729 | 0.17117 | 0.15689 | 0.11199 | 0.098722 | 0.094641 | 0.23499 | 0.22682 | 0.23601 | 0.23193 | 0.2258 | 0.22376 | 0.22172 | 0.21458 | 0.2054 | 0.19825 | 0.16764 | 0.15029 | 0.13703 | 0.22706 | 0.21686 | 0.22196 | 0.21379 | 0.20869 | 0.20461 | 0.20155 | 0.1893 | 0.18318 | 0.16992 | 0.1291 | 0.11583 | 0.11277
|  | NEWTON | CF |  |  |  |  | 0.22525 | 0.21709 | 0.20689 | 0.20995 | 0.20484 | 0.19668 | 0.1926 | 0.18954 | 0.18138 | 0.17729 | 0.14464 | 0.11301 | 0.096682 | 0.24111 | 0.23499 | 0.23295 | 0.23601 | 0.23295 | 0.2258 | 0.2207 | 0.21968 | 0.21458 | 0.21152 | 0.18499 | 0.15029 | 0.11662 | 0.2342 | 0.22604 | 0.21788 | 0.22094 | 0.21583 | 0.20665 | 0.20461 | 0.20155 | 0.19339 | 0.1893 | 0.15971 | 0.12706 | 0.11379
| REDMOSS | NEWTONHILL | MINIMUM HEADROOM | NO 90190 93653 | NO | NO | 1.199 | 3.1102 | 2.0112 | 0.73366 | 13.8326 | 12.2 | 10.7479 | 9.401 | 7.9704 | 6.8337 | 5.3439 | -1.9255 | -5.9153 | -6.1898 | 5.0704 | 4.2724 | 3.3286 | 16.052 | 14.7347 | 13.6602 | 12.7969 | 11.853 | 11.0173 | 9.9582 | 6.5275 | 4.4898 | 3.701 | 3.8934 | 2.9536 | 1.7495 | 14.5449 | 12.9949 | 11.652 | 10.4306 | 9.1408 | 8.0928 | 6.7357 | 0.81427 | -2.3776 | -2.6112
|  | NEWTONHILL | EE |  |  |  |  | 3.1102 | 2.0592 | 0.87346 | 14.1133 | 12.5633 | 11.1765 | 10.0316 | 8.6592 | 7.3469 | 5.9918 | -1.7582 | -5.7908 | -6.0918 | 5.0704 | 4.2908 | 3.4082 | 16.2337 | 15.0939 | 14.1153 | 13.2265 | 12.3 | 11.4153 | 10.4775 | 6.5275 | 4.4898 | 3.799 | 3.9199 | 3.027 | 1.927 | 14.8643 | 13.4214 | 12.1592 | 11.0582 | 9.8173 | 8.6194 | 7.3816 | 0.95509 | -2.2623 | -2.5184
|  | NEWTONHILL | HT |  |  |  |  | 3.1112 | 2.0112 | 0.73366 | 13.8326 | 12.2 | 10.7479 | 9.401 | 7.9704 | 6.8337 | 5.3439 | -1.9255 | -5.9153 | -6.1898 | 5.0786 | 4.2724 | 3.3286 | 16.052 | 14.7347 | 13.6602 | 12.7969 | 11.853 | 11.0173 | 9.9582 | 6.7714 | 4.9847 | 4.849 | 3.8934 | 2.9536 | 1.7495 | 14.5449 | 12.9949 | 11.652 | 10.4306 | 9.1408 | 8.0928 | 6.7357 | 0.81427 | -2.3776 | -2.6112
|  | NEWTONHILL | HE |  |  |  |  | 3.1939 | 2.2877 | 1.2898 | 14.6582 | 13.3153 | 12.1071 | 10.8582 | 9.6684 | 8.8551 | 7.6908 | 0.0010082 | -4.2235 | -4.9378 | 5.1357 | 4.4245 | 3.6418 | 16.5194 | 15.4092 | 14.4673 | 13.5163 | 12.6357 | 11.9071 | 10.9898 | 7.1826 | 5.0459 | 4.2194 | 3.9709 | 3.1454 | 2.2525 | 15.3388 | 14.0704 | 12.9592 | 11.8112 | 10.7367 | 9.9439 | 8.8735 | 2.4765 | -0.93164 | -1.5694
|  | NEWTONHILL | CF |  |  |  |  | 3.3969 | 2.7367 | 1.9643 | 15.7337 | 14.7582 | 13.9684 | 13.1979 | 12.3714 | 11.6163 | 10.8041 | 3.9316 | -1.6959 | -3.4551 | 5.2888 | 4.7622 | 4.151 | 17.3449 | 16.601 | 16.0439 | 15.4775 | 14.8622 | 14.2969 | 13.6796 | 9.4357 | 5.5816 | 3.701 | 4.1505 | 3.5566 | 2.8729 | 16.3602 | 15.501 | 14.7928 | 14.1071 | 13.3704 | 12.702 | 11.9684 | 6.1347 | 1.3122 | -0.24083
| ALNESS | NIGG | MINIMUM HEADROOM | NH 79490 69773 | YES | NO | 8.5 | -7.4082 | -7.4082 | -7.4102 | -7.4102 | -7.4112 | -7.4112 | -7.4122 | -7.4143 | -7.4143 | -7.4153 | -7.4194 | -7.4214 | -7.4224 | -6.9806 | -6.9806 | -6.9816 | -6.9816 | -6.9816 | -6.9816 | -6.9827 | -6.9837 | -6.9837 | -6.9847 | -6.9867 | -6.9878 | -6.9878 | -7.1561 | -7.1561 | -7.1582 | -7.1582 | -7.1592 | -7.1592 | -7.1602 | -7.1612 | -7.1612 | -7.1633 | -7.1673 | -7.1684 | -7.1694
|  | NIGG | EE |  |  |  |  | -7.4082 | -7.4082 | -7.4102 | -7.4102 | -7.4112 | -7.4112 | -7.4122 | -7.4143 | -7.4143 | -7.4153 | -7.4184 | -7.4184 | -7.4184 | -6.9806 | -6.9806 | -6.9816 | -6.9816 | -6.9816 | -6.9816 | -6.9827 | -6.9837 | -6.9837 | -6.9847 | -6.9857 | -6.9857 | -6.9857 | -7.1561 | -7.1561 | -7.1582 | -7.1582 | -7.1592 | -7.1592 | -7.1602 | -7.1612 | -7.1612 | -7.1633 | -7.1653 | -7.1653 | -7.1653
|  | NIGG | HT |  |  |  |  | -7.4071 | -7.4082 | -7.4082 | -7.4082 | -7.4102 | -7.4102 | -7.4112 | -7.4122 | -7.4122 | -7.4143 | -7.4184 | -7.4194 | -7.4194 | -6.9796 | -6.9806 | -6.9806 | -6.9806 | -6.9816 | -6.9816 | -6.9816 | -6.9827 | -6.9827 | -6.9837 | -6.9857 | -6.9867 | -6.9867 | -7.1551 | -7.1561 | -7.1561 | -7.1561 | -7.1582 | -7.1582 | -7.1592 | -7.1602 | -7.1602 | -7.1612 | -7.1653 | -7.1673 | -7.1673
|  | NIGG | HE |  |  |  |  | -7.4071 | -7.4082 | -7.4082 | -7.4102 | -7.4102 | -7.4112 | -7.4112 | -7.4122 | -7.4143 | -7.4153 | -7.4194 | -7.4214 | -7.4224 | -6.9796 | -6.9806 | -6.9806 | -6.9816 | -6.9816 | -6.9816 | -6.9816 | -6.9827 | -6.9837 | -6.9847 | -6.9867 | -6.9878 | -6.9878 | -7.1551 | -7.1561 | -7.1561 | -7.1582 | -7.1582 | -7.1592 | -7.1592 | -7.1602 | -7.1612 | -7.1633 | -7.1673 | -7.1684 | -7.1694
|  | NIGG | CF |  |  |  |  | -7.4071 | -7.4082 | -7.4082 | -7.4082 | -7.4082 | -7.4102 | -7.4102 | -7.4112 | -7.4112 | -7.4112 | -7.4153 | -7.4194 | -7.4214 | -6.9796 | -6.9806 | -6.9806 | -6.9806 | -6.9806 | -6.9816 | -6.9816 | -6.9816 | -6.9816 | -6.9816 | -6.9847 | -6.9867 | -6.9878 | -7.1551 | -7.1561 | -7.1561 | -7.1561 | -7.1561 | -7.1582 | -7.1582 | -7.1592 | -7.1592 | -7.1592 | -7.1633 | -7.1673 | -7.1684
| CHARLESTON | NINEWELLS | MINIMUM HEADROOM | NO 35148 30641 | NO | YES | 2.667 | 7.76 | 7.5355 | 7.2325 | 6.8865 | 6.6733 | 6.4274 | 6.1835 | 5.91 | 5.6284 | 5.3804 | 4.6488 | 4.3018 | 4.0886 | 7.9478 | 7.8386 | 7.6712 | 7.4988 | 7.3222 | 7.1274 | 6.9233 | 6.6518 | 6.411 | 6.2029 | 5.5722 | 5.1539 | 3.2763 | 7.7391 | 7.5656 | 7.3268 | 7.0748 | 6.8626 | 6.5932 | 6.3187 | 5.9687 | 5.6534 | 5.3738 | 4.5513 | 4.1921 | 3.987
|  | NINEWELLS | EE |  |  |  |  | 7.76 | 7.5355 | 7.2325 | 6.8865 | 6.6733 | 6.4274 | 6.1835 | 5.91 | 5.6284 | 5.3804 | 4.6488 | 4.6692 | 4.6876 | 7.9478 | 7.8386 | 7.6712 | 7.4988 | 7.3222 | 7.1274 | 6.9233 | 6.6518 | 6.411 | 6.2029 | 5.6069 | 5.4518 | 4.66 | 7.7391 | 7.5656 | 7.3268 | 7.0748 | 6.8626 | 6.5932 | 6.3187 | 5.9687 | 5.6534 | 5.3738 | 4.5513 | 4.5615 | 4.5758
|  | NINEWELLS | HT |  |  |  |  | 7.811 | 7.5967 | 7.2978 | 6.9916 | 6.7855 | 6.5682 | 6.3988 | 6.1049 | 5.8549 | 5.6549 | 4.7325 | 4.4314 | 4.2712 | 7.9967 | 7.9049 | 7.7488 | 7.6049 | 7.4906 | 7.3294 | 7.1835 | 6.9212 | 6.7039 | 6.509 | 5.71 | 5.4498 | 5.3222 | 7.8044 | 7.6544 | 7.435 | 7.1717 | 6.984 | 6.784 | 6.6289 | 6.3034 | 6.0187 | 5.7564 | 4.6728 | 4.3381 | 4.185
|  | NINEWELLS | HE |  |  |  |  | 7.8161 | 7.6478 | 7.409 | 7.159 | 6.9988 | 6.8335 | 6.7008 | 6.4774 | 6.2743 | 6.0539 | 4.812 | 4.3018 | 4.0886 | 7.9916 | 7.8967 | 7.7559 | 7.6161 | 7.5039 | 7.3488 | 7.1896 | 6.9345 | 6.7131 | 6.4988 | 5.5722 | 5.2335 | 4.7212 | 7.7993 | 7.6564 | 7.4636 | 7.2636 | 7.1013 | 6.9197 | 6.7207 | 6.4054 | 6.1228 | 5.8534 | 4.6656 | 4.1921 | 3.987
|  | NINEWELLS | CF |  |  |  |  | 7.8467 | 7.7222 | 7.5569 | 7.3722 | 7.2733 | 7.1651 | 7.0916 | 7.011 | 6.9182 | 6.811 | 5.9733 | 5.0233 | 4.36 | 8.012 | 7.9488 | 7.8559 | 7.761 | 7.6896 | 7.612 | 7.5325 | 7.4222 | 7.3039 | 7.1671 | 6.3855 | 5.1539 | 3.2763 | 7.837 | 7.7442 | 7.6177 | 7.485 | 7.384 | 7.2728 | 7.1677 | 7.0238 | 6.8901 | 6.7452 | 5.8095 | 4.8585 | 4.2472
| THURSO | NORTH HOY | MINIMUM HEADROOM | HY 25681 02549 | YES | NO | 0 | 0.16865 | 0.15743 | 0.14824 | 0.1462 | 0.14416 | 0.14824 | 0.14212 | 0.13804 | 0.136 | 0.1309 | 0.11559 | 0.10845 | 0.10335 | 0.17514 | 0.16494 | 0.15678 | 0.15678 | 0.15473 | 0.15678 | 0.16086 | 0.15678 | 0.15473 | 0.15167 | 0.13943 | 0.13433 | 0.12922 | 0.17496 | 0.16373 | 0.15557 | 0.15557 | 0.15251 | 0.15557 | 0.15047 | 0.14639 | 0.14435 | 0.14027 | 0.12598 | 0.11782 | 0.11373
|  | NORTH HOY | EE |  |  |  |  | 0.16865 | 0.15743 | 0.14824 | 0.15641 | 0.15131 | 0.14927 | 0.14212 | 0.13804 | 0.136 | 0.1309 | 0.11763 | 0.11661 | 0.11661 | 0.17514 | 0.16494 | 0.15678 | 0.16902 | 0.16596 | 0.16494 | 0.16086 | 0.15678 | 0.15473 | 0.15167 | 0.14147 | 0.14045 | 0.13739 | 0.17496 | 0.16373 | 0.15557 | 0.16476 | 0.15863 | 0.15761 | 0.15047 | 0.14639 | 0.14435 | 0.14027 | 0.12598 | 0.12496 | 0.12598
|  | NORTH HOY | HT |  |  |  |  | 0.16967 | 0.16661 | 0.15845 | 0.1462 | 0.14416 | 0.14824 | 0.15335 | 0.14824 | 0.14212 | 0.14008 | 0.12069 | 0.11355 | 0.11049 | 0.17616 | 0.17412 | 0.16596 | 0.15678 | 0.15576 | 0.1629 | 0.16698 | 0.16392 | 0.15984 | 0.1578 | 0.14249 | 0.13841 | 0.13637 | 0.17598 | 0.17394 | 0.16476 | 0.15557 | 0.15251 | 0.15557 | 0.16169 | 0.15659 | 0.15047 | 0.14741 | 0.12904 | 0.12292 | 0.12088
|  | NORTH HOY | HE |  |  |  |  | 0.16967 | 0.16661 | 0.15743 | 0.15539 | 0.14416 | 0.15029 | 0.15335 | 0.14824 | 0.14314 | 0.136 | 0.11559 | 0.10845 | 0.10335 | 0.17616 | 0.1731 | 0.16494 | 0.16392 | 0.15473 | 0.16392 | 0.16698 | 0.16188 | 0.15882 | 0.15473 | 0.13943 | 0.13433 | 0.13024 | 0.17598 | 0.1719 | 0.16373 | 0.16271 | 0.15251 | 0.15863 | 0.16271 | 0.15659 | 0.15149 | 0.14537 | 0.12598 | 0.11782 | 0.11373
|  | NORTH HOY | CF |  |  |  |  | 0.16865 | 0.16661 | 0.16559 | 0.15845 | 0.15029 | 0.14824 | 0.15029 | 0.15539 | 0.15029 | 0.15131 | 0.13498 | 0.11865 | 0.10845 | 0.17616 | 0.17514 | 0.17412 | 0.16596 | 0.1578 | 0.15678 | 0.16392 | 0.168 | 0.16596 | 0.16596 | 0.15167 | 0.13943 | 0.12922 | 0.17598 | 0.17394 | 0.17292 | 0.16476 | 0.15659 | 0.15557 | 0.15863 | 0.16373 | 0.15863 | 0.15965 | 0.14333 | 0.127 | 0.11884
| BEAULY | NORTH KESSOCK | MINIMUM HEADROOM | NH 65004 48461 | YES | NO | 1.5 | 2.0292 | 1.9588 | 1.8669 | 1.7935 | 1.7047 | 1.6037 | 1.518 | 1.3822 | 1.2516 | 1.1353 | 0.86898 | 0.78531 | 0.80265 | 2.2498 | 2.208 | 2.1447 | 2.1018 | 2.0437 | 1.9784 | 1.9263 | 1.8345 | 1.7457 | 1.6753 | 1.4978 | 1.4253 | 1.1916 | 2.2206 | 2.1563 | 2.0655 | 2.0022 | 1.9155 | 1.8196 | 1.738 | 1.6053 | 1.4778 | 1.3696 | 1.1227 | 1.0482 | 1.0798
|  | NORTH KESSOCK | EE |  |  |  |  | 2.0292 | 1.9588 | 1.8669 | 1.7935 | 1.7047 | 1.6037 | 1.518 | 1.3822 | 1.2516 | 1.1353 | 0.86898 | 0.8251 | 0.85367 | 2.2498 | 2.208 | 2.1447 | 2.1018 | 2.0437 | 1.9784 | 1.9263 | 1.8345 | 1.7457 | 1.6753 | 1.4978 | 1.4253 | 1.3692 | 2.2206 | 2.1563 | 2.0655 | 2.0022 | 1.9155 | 1.8196 | 1.738 | 1.6053 | 1.4778 | 1.3696 | 1.1227 | 1.0818 | 1.1216
|  | NORTH KESSOCK | HT |  |  |  |  | 2.0578 | 1.9955 | 1.921 | 1.8527 | 1.7751 | 1.7118 | 1.6251 | 1.522 | 1.42 | 1.3567 | 0.95163 | 0.78531 | 0.80265 | 2.2784 | 2.2467 | 2.1998 | 2.162 | 2.111 | 2.0814 | 2.0294 | 1.961 | 1.8978 | 1.8641 | 1.5896 | 1.4988 | 1.5284 | 2.2553 | 2.2002 | 2.1329 | 2.0686 | 1.9941 | 1.938 | 1.8584 | 1.7573 | 1.6584 | 1.6022 | 1.2012 | 1.0482 | 1.0798
|  | NORTH KESSOCK | HE |  |  |  |  | 2.0557 | 2.0118 | 1.9516 | 1.9037 | 1.8373 | 1.7914 | 1.7169 | 1.622 | 1.5312 | 1.4792 | 0.98327 | 0.92102 | 0.90673 | 2.2743 | 2.2498 | 2.2059 | 2.1753 | 2.1273 | 2.1029 | 2.0549 | 1.9865 | 1.9253 | 1.8947 | 1.5671 | 1.5008 | 1.4039 | 2.2533 | 2.2124 | 2.1553 | 2.1084 | 2.0431 | 2.0022 | 1.9329 | 1.84 | 1.7512 | 1.7022 | 1.2298 | 1.1839 | 1.1706
|  | NORTH KESSOCK | CF |  |  |  |  | 2.0629 | 2.0159 | 1.9761 | 1.9353 | 1.8812 | 1.8465 | 1.7894 | 1.7302 | 1.669 | 1.6037 | 1.3027 | 1.0659 | 0.9302 | 2.2784 | 2.2488 | 2.2243 | 2.1967 | 2.158 | 2.1355 | 2.0947 | 2.0498 | 2.0039 | 1.9508 | 1.7222 | 1.4773 | 1.1916 | 2.2594 | 2.2165 | 2.1778 | 2.138 | 2.0849 | 2.0543 | 1.9961 | 1.939 | 1.8778 | 1.8124 | 1.5267 | 1.3022 | 1.1808
| BROADFORD | NOSTIE BRIDGE | MINIMUM HEADROOM | NG 85209 27252 | YES | YES | 0.301 | -1.157 | -1.2305 | -1.3274 | -1.4009 | -1.4948 | -1.6029 | -1.7335 | -1.8448 | -1.9794 | -2.0999 | -2.3988 | -2.5039 | -2.5386 | -0.5121 | -0.55496 | -0.6172 | -0.66618 | -0.73047 | -0.80087 | -0.88863 | -0.95904 | -1.0478 | -1.1274 | -1.3448 | -1.4509 | -1.7886 | -0.81006 | -0.86618 | -0.94373 | -1.0141 | -1.107 | -1.208 | -1.3325 | -1.4376 | -1.5662 | -1.6794 | -1.957 | -2.0539 | -2.0856
|  | NOSTIE BRIDGE | EE |  |  |  |  | -1.157 | -1.2305 | -1.3274 | -1.4009 | -1.4948 | -1.6029 | -1.7335 | -1.8448 | -1.9794 | -2.0999 | -2.3988 | -2.4539 | -2.4927 | -0.5121 | -0.55496 | -0.6172 | -0.66618 | -0.73047 | -0.80087 | -0.88863 | -0.95904 | -1.0478 | -1.1274 | -1.3448 | -1.4509 | -1.6131 | -0.81006 | -0.86618 | -0.94373 | -1.0141 | -1.107 | -1.208 | -1.3325 | -1.4376 | -1.5662 | -1.6794 | -1.957 | -2.005 | -2.0417
|  | NOSTIE BRIDGE | HT |  |  |  |  | -1.1254 | -1.1907 | -1.2529 | -1.3213 | -1.4029 | -1.4703 | -1.5672 | -1.6723 | -1.7794 | -1.8896 | -2.2999 | -2.5039 | -2.5386 | -0.48455 | -0.5223 | -0.56108 | -0.59985 | -0.64883 | -0.68863 | -0.74781 | -0.81414 | -0.88149 | -0.95189 | -1.2223 | -1.3437 | -1.3652 | -0.78965 | -0.83761 | -0.88659 | -0.93863 | -1.0152 | -1.0774 | -1.1682 | -1.2672 | -1.3672 | -1.4733 | -1.8621 | -2.0539 | -2.0856
|  | NOSTIE BRIDGE | HE |  |  |  |  | -1.1264 | -1.1794 | -1.2254 | -1.2754 | -1.3417 | -1.3886 | -1.4713 | -1.5611 | -1.655 | -1.7509 | -2.2121 | -2.3396 | -2.3611 | -0.48965 | -0.51924 | -0.55189 | -0.58455 | -0.62944 | -0.66312 | -0.71822 | -0.77842 | -0.84169 | -0.91006 | -1.2233 | -1.3713 | -1.5162 | -0.79271 | -0.83455 | -0.86924 | -0.90904 | -0.95802 | -1.0029 | -1.0835 | -1.1672 | -1.256 | -1.3468 | -1.7805 | -1.8988 | -1.9172
|  | NOSTIE BRIDGE | CF |  |  |  |  | -1.1162 | -1.1611 | -1.1999 | -1.2539 | -1.2968 | -1.3529 | -1.3876 | -1.457 | -1.5121 | -1.5774 | -1.8866 | -2.1907 | -2.3621 | -0.48047 | -0.50802 | -0.53149 | -0.5672 | -0.59781 | -0.63761 | -0.66312 | -0.71516 | -0.757 | -0.807 | -1.0723 | -1.4172 | -1.7886 | -0.78251 | -0.81006 | -0.83659 | -0.8723 | -0.91006 | -0.9621 | -0.99679 | -1.0611 | -1.1141 | -1.1754 | -1.4733 | -1.7621 | -1.9233
| TAYNUILT | OBAN | MINIMUM HEADROOM | NM 85643 29338 | NO | YES | 1.269 | 9.0049 | 8.6426 | 7.7671 | 6.3885 | 5.8447 | 3.1008 | 1.9579 | 0.8018 | -0.56656 | -2.5278 | -10.1043 | -18.9257 | -26.9921 | 13.0579 | 12.863 | 11.9345 | 10.5212 | 10.2171 | 7.2161 | 6.1947 | 4.7794 | 3.4202 | 1.2804 | -7.1564 | -17.9921 | -28.7166 | 11.4814 | 11.1498 | 10.1416 | 8.5681 | 8.0814 | 4.8426 | 3.6814 | 2.2875 | 0.77323 | -1.5094 | -10.3278 | -21.0645 | -31.0635
|  | OBAN | EE |  |  |  |  | 9.0049 | 8.6426 | 8.2763 | 7.7896 | 6.7028 | 4.9314 | 3.6569 | 2.9987 | 1.4181 | 0.27731 | -4.0921 | -12.288 | -15.6431 | 13.0579 | 12.863 | 12.66 | 12.3947 | 11.3998 | 9.6232 | 8.6038 | 8.0783 | 6.562 | 5.5477 | 1.2049 | -8.9298 | -13.7217 | 11.4814 | 11.1498 | 10.8049 | 10.3528 | 9.1681 | 7.1722 | 5.8712 | 5.2345 | 3.5008 | 2.2885 | -2.4564 | -12.4257 | -16.5257
|  | OBAN | HT |  |  |  |  | 9.1436 | 8.8181 | 7.7671 | 6.3885 | 5.8447 | 3.1008 | 1.9579 | 0.8018 | -0.076767 | -1.0023 | -5.5676 | -15.3625 | -23.0635 | 13.1426 | 12.9794 | 11.9345 | 10.5212 | 10.2385 | 7.2161 | 6.2212 | 5.2824 | 4.6732 | 3.9498 | -0.37779 | -11.8002 | -21.287 | 11.6212 | 11.3314 | 10.1416 | 8.5681 | 8.0814 | 4.8426 | 3.6814 | 2.513 | 1.663 | 0.70487 | -4.3594 | -16.2002 | -25.739
|  | OBAN | HE |  |  |  |  | 9.1447 | 8.9089 | 8.0702 | 6.8936 | 6.112 | 3.4304 | 2.2712 | 0.8018 | -0.56656 | -2.5278 | -10.1043 | -18.9257 | -26.9921 | 13.1375 | 13.0038 | 12.1436 | 10.8896 | 10.2171 | 7.2232 | 6.1947 | 4.7794 | 3.4202 | 1.2804 | -7.1564 | -17.9921 | -28.7166 | 11.6222 | 11.4069 | 10.4518 | 9.0885 | 8.2692 | 5.1018 | 3.8743 | 2.2875 | 0.77323 | -1.5094 | -10.3278 | -21.0645 | -31.0635
|  | OBAN | CF |  |  |  |  | 9.1906 | 9.0579 | 8.912 | 8.7059 | 8.1263 | 7.162 | 6.4692 | 5.8222 | 5.0834 | 4.1681 | 1.0773 | -1.8676 | -4.0972 | 13.1559 | 13.0743 | 12.9824 | 12.8538 | 12.2671 | 11.2202 | 10.56 | 9.9947 | 9.3028 | 8.4222 | 5.2896 | 1.7436 | -1.937 | 11.6671 | 11.5406 | 11.4008 | 11.211 | 10.562 | 9.4436 | 8.6957 | 8.0324 | 7.2579 | 6.2824 | 3.0038 | -0.20228 | -2.5962
| MILTON OF CRAIGIE | OLD CRAIGIE ROAD | MINIMUM HEADROOM | NO 42156 32130 | NO | NO | 0.745 | 6.5142 | 6.0978 | 5.7213 | 5.3478 | 5.0172 | 4.6448 | 4.2101 | 3.6703 | 3.5744 | 3.1774 | 1.8948 | 1.6172 | 1.6101 | 8.256 | 8.0193 | 7.7978 | 7.5672 | 7.3642 | 7.1019 | 6.7887 | 6.4121 | 6.4223 | 6.1601 | 5.1948 | 4.608 | 2.2366 | 7.6672 | 7.2948 | 6.958 | 6.6029 | 6.2927 | 5.9213 | 5.4907 | 4.9887 | 4.9754 | 4.6101 | 3.4346 | 3.1917 | 3.1846
|  | OLD CRAIGIE ROAD | EE |  |  |  |  | 6.5142 | 6.0978 | 5.7213 | 5.3478 | 5.0172 | 4.6448 | 4.2101 | 3.6703 | 3.5744 | 3.1774 | 1.8948 | 2.0172 | 2.0091 | 8.256 | 8.0193 | 7.7978 | 7.5672 | 7.3642 | 7.1019 | 6.7887 | 6.4121 | 6.4223 | 6.1601 | 5.1948 | 4.7489 | 3.8631 | 7.6672 | 7.2948 | 6.958 | 6.6029 | 6.2927 | 5.9213 | 5.4907 | 4.9887 | 4.9754 | 4.6101 | 3.4346 | 3.5427 | 3.5254
|  | OLD CRAIGIE ROAD | HT |  |  |  |  | 6.5754 | 6.2029 | 5.8499 | 5.5519 | 5.2458 | 4.9213 | 4.5948 | 4.204 | 3.8213 | 3.4254 | 2.0744 | 1.6172 | 1.6101 | 8.3285 | 8.1417 | 7.9611 | 7.8101 | 7.6417 | 7.4601 | 7.2836 | 7.0499 | 6.8131 | 6.5499 | 5.7754 | 5.4366 | 5.4111 | 7.7703 | 7.4631 | 7.1611 | 6.9121 | 6.6315 | 6.3295 | 6.0427 | 5.6621 | 5.2887 | 4.8948 | 3.6244 | 3.1917 | 3.1846
|  | OLD CRAIGIE ROAD | HE |  |  |  |  | 6.5978 | 6.3091 | 6.0366 | 5.7978 | 5.5999 | 5.3611 | 5.0999 | 4.7764 | 4.4519 | 4.1091 | 2.9142 | 2.1376 | 2.1213 | 8.3264 | 8.1601 | 7.9917 | 7.8366 | 7.704 | 7.5336 | 7.3621 | 7.1244 | 6.8815 | 6.6131 | 5.6356 | 4.7621 | 3.904 | 7.7836 | 7.5336 | 7.2866 | 7.058 | 6.8723 | 6.6285 | 6.3917 | 6.0621 | 5.7387 | 5.3978 | 4.355 | 3.6489 | 3.6366
|  | OLD CRAIGIE ROAD | CF |  |  |  |  | 6.6713 | 6.4774 | 6.304 | 6.154 | 6.0366 | 5.8907 | 5.7703 | 5.5754 | 5.4591 | 5.2805 | 4.5887 | 3.257 | 2.1213 | 8.3642 | 8.2346 | 8.1182 | 8.005 | 7.9091 | 7.7785 | 7.6468 | 7.4764 | 7.356 | 7.1785 | 6.304 | 4.608 | 2.2366 | 7.8407 | 7.6631 | 7.504 | 7.3509 | 7.2315 | 7.0774 | 6.9274 | 6.7438 | 6.6346 | 6.4652 | 5.7774 | 4.6142 | 3.6152
| KINTORE | OLDMELDRUM | MINIMUM HEADROOM | NJ 81659 27360 | NO | YES | 1.231 | 1.7209 | 1.1964 | 0.55352 | 21.0976 | 20.4588 | 19.5445 | 19.0088 | 18.4445 | 17.8588 | 17.2517 | 15.3598 | 13.2711 | 11.6292 | 2.9964 | 2.6198 | 2.1035 | 21.7313 | 21.3201 | 20.5098 | 20.1731 | 19.8088 | 19.4425 | 18.8884 | 16.7792 | 14.6211 | 12.5721 | 2.2178 | 1.7484 | 1.128 | 21.1568 | 20.5854 | 19.6323 | 19.1456 | 18.6303 | 18.1058 | 17.5394 | 15.3088 | 12.9486 | 10.9915
|  | OLDMELDRUM | EE |  |  |  |  | 1.7362 | 1.2188 | 0.7423 | 21.515 | 20.8068 | 20.0833 | 19.3415 | 18.7874 | 18.116 | 17.8068 | 15.8854 | 13.9854 | 13.3262 | 3.0372 | 2.6556 | 2.3158 | 22.1731 | 21.6486 | 21.0843 | 20.6007 | 20.2598 | 19.767 | 19.4935 | 18.0854 | 16.0945 | 15.1292 | 2.2178 | 1.7729 | 1.3423 | 21.6252 | 20.9578 | 20.2476 | 19.5721 | 19.0762 | 18.4323 | 18.1058 | 16.2466 | 14.0925 | 13.3211
|  | OLDMELDRUM | HT |  |  |  |  | 1.7209 | 1.1964 | 0.55352 | 21.0976 | 20.4588 | 19.5445 | 19.0088 | 18.4445 | 17.8588 | 17.2517 | 15.5874 | 13.415 | 11.968 | 2.9964 | 2.6198 | 2.1035 | 21.7313 | 21.3201 | 20.5098 | 20.1731 | 19.8088 | 19.4425 | 19.018 | 17.8384 | 15.669 | 13.969 | 2.225 | 1.7484 | 1.128 | 21.1568 | 20.5854 | 19.6323 | 19.1456 | 18.6303 | 18.1058 | 17.5394 | 15.8762 | 13.4098 | 11.6558
|  | OLDMELDRUM | HE |  |  |  |  | 1.778 | 1.3433 | 0.8423 | 21.5313 | 20.9486 | 20.0894 | 19.4537 | 18.9303 | 18.3762 | 17.7354 | 15.3598 | 13.2711 | 11.6292 | 3.0586 | 2.7137 | 2.2852 | 21.9843 | 21.5507 | 20.7752 | 20.315 | 19.9098 | 19.4752 | 18.8884 | 16.7792 | 14.6211 | 12.5721 | 2.2729 | 1.8872 | 1.3964 | 21.5537 | 21.0109 | 20.1139 | 19.519 | 19.017 | 18.4833 | 17.815 | 15.3088 | 12.9486 | 10.9915
|  | OLDMELDRUM | CF |  |  |  |  | 1.9178 | 1.5831 | 1.2933 | 22.316 | 21.8976 | 21.5241 | 21.166 | 20.7364 | 20.4364 | 20.0476 | 18.3221 | 17.1292 | 16.1088 | 3.1882 | 2.9331 | 2.6974 | 22.6966 | 22.3568 | 22.0241 | 21.7496 | 21.4476 | 21.2088 | 20.8945 | 19.518 | 18.3496 | 17.1374 | 2.3943 | 2.1086 | 1.8525 | 22.3527 | 21.9517 | 21.5711 | 21.2354 | 20.8547 | 20.5701 | 20.2037 | 18.5731 | 17.3772 | 16.4017
| THURSO | ORMLIE | MINIMUM HEADROOM | ND 10757 67408 | YES | NO | 0.802 | 9.473 | 9.2669 | 9.021 | 8.725 | 8.3465 | 7.9301 | 7.4516 | 6.7801 | 6.173 | 5.6148 | 3.2056 | 2.1016 | 1.9638 | 10.8587 | 10.7301 | 10.5414 | 10.3016 | 10.023 | 9.7189 | 9.374 | 8.9005 | 8.471 | 8.0822 | 6.2659 | 5.472 | 5.3608 | 10.2868 | 10.0888 | 9.8215 | 9.5194 | 9.1776 | 8.8072 | 8.3664 | 7.7337 | 7.1572 | 6.6317 | 4.3164 | 3.2694 | 3.1398
|  | ORMLIE | EE |  |  |  |  | 9.473 | 9.2669 | 9.021 | 8.725 | 8.3465 | 7.9301 | 7.4516 | 6.7801 | 6.173 | 5.6148 | 3.8526 | 3.4495 | 3.3567 | 10.8587 | 10.7301 | 10.5414 | 10.3016 | 10.023 | 9.7189 | 9.374 | 8.9005 | 8.471 | 8.0822 | 6.8301 | 6.5567 | 6.4781 | 10.2868 | 10.0888 | 9.8215 | 9.5194 | 9.1776 | 8.8072 | 8.3664 | 7.7337 | 7.1572 | 6.6317 | 4.9613 | 4.5827 | 4.497
|  | ORMLIE | HT |  |  |  |  | 9.573 | 9.3934 | 9.2097 | 9.0036 | 8.7791 | 8.3812 | 7.9005 | 7.3648 | 6.9056 | 6.4832 | 4.472 | 3.5628 | 3.4128 | 10.9373 | 10.8342 | 10.7301 | 10.6087 | 10.422 | 10.1536 | 9.8475 | 9.4761 | 9.1383 | 8.7934 | 7.3199 | 6.6648 | 6.5587 | 10.396 | 10.2276 | 10.0541 | 9.8582 | 9.597 | 9.2296 | 8.8011 | 8.298 | 7.8439 | 7.3949 | 5.5551 | 4.6949 | 4.5551
|  | ORMLIE | HE |  |  |  |  | 9.5567 | 9.4026 | 9.2495 | 9.0077 | 8.6771 | 8.3087 | 7.8546 | 7.2424 | 6.6526 | 6.0393 | 3.2056 | 2.1016 | 1.9638 | 10.9199 | 10.8189 | 10.7046 | 10.4995 | 10.2546 | 9.9791 | 9.6485 | 9.2016 | 8.774 | 8.3281 | 6.2659 | 5.472 | 5.3608 | 10.3796 | 10.2317 | 10.0409 | 9.7939 | 9.5031 | 9.1745 | 8.749 | 8.1653 | 7.6051 | 7.0194 | 4.3164 | 3.2694 | 3.1398
|  | ORMLIE | CF |  |  |  |  | 9.6005 | 9.5036 | 9.3954 | 9.2863 | 9.1516 | 9.0046 | 8.7965 | 8.5016 | 8.1699 | 7.8118 | 5.7169 | 3.7832 | 2.4965 | 10.9485 | 10.8822 | 10.8077 | 10.7281 | 10.6373 | 10.4985 | 10.325 | 10.1005 | 9.8577 | 9.5965 | 8.0618 | 6.6465 | 5.7005 | 10.4194 | 10.3286 | 10.2225 | 10.1164 | 9.9817 | 9.7898 | 9.5827 | 9.3245 | 9.0296 | 8.7102 | 6.7143 | 4.8694 | 3.6449
| DUNOON | OTTER FERRY | MINIMUM HEADROOM | NR 93352 84713 | YES | YES | 0.494 | -0.59844 | -0.61273 | -0.62396 | -0.63926 | -0.65763 | -0.67804 | -0.69538 | -0.73314 | -0.76885 | -0.78824 | -0.86681 | -0.89028 | -0.8964 | -0.092322 | -0.095384 | -0.10559 | -0.11783 | -0.13212 | -0.15355 | -0.16477 | -0.19232 | -0.21681 | -0.22498 | -0.276 | -0.29742 | -0.32396 | -0.51987 | -0.5311 | -0.54538 | -0.56885 | -0.59334 | -0.62293 | -0.64232 | -0.67906 | -0.71375 | -0.73212 | -0.80457 | -0.82804 | -0.83314
|  | OTTER FERRY | EE |  |  |  |  | -0.59844 | -0.61273 | -0.62396 | -0.63926 | -0.65763 | -0.67804 | -0.69538 | -0.73314 | -0.76885 | -0.78824 | -0.86681 | -0.87804 | -0.88722 | -0.0862 | -0.095384 | -0.10559 | -0.11783 | -0.13212 | -0.15355 | -0.16477 | -0.19232 | -0.21681 | -0.22498 | -0.276 | -0.29742 | -0.31987 | -0.51375 | -0.5311 | -0.54538 | -0.56885 | -0.59334 | -0.62293 | -0.64232 | -0.67906 | -0.71375 | -0.73212 | -0.80457 | -0.81681 | -0.82702
|  | OTTER FERRY | HT |  |  |  |  | -0.59742 | -0.60151 | -0.60865 | -0.61987 | -0.6311 | -0.64947 | -0.66069 | -0.68416 | -0.71477 | -0.7311 | -0.8362 | -0.89028 | -0.8964 | -0.092322 | -0.088241 | -0.095384 | -0.10253 | -0.11375 | -0.12702 | -0.13722 | -0.15355 | -0.17089 | -0.1811 | -0.25253 | -0.28518 | -0.28824 | -0.51987 | -0.51783 | -0.52906 | -0.54436 | -0.56477 | -0.58518 | -0.60457 | -0.63212 | -0.66069 | -0.67498 | -0.776 | -0.82804 | -0.83314
|  | OTTER FERRY | HE |  |  |  |  | -0.59742 | -0.59947 | -0.60457 | -0.61375 | -0.626 | -0.63824 | -0.64742 | -0.66579 | -0.68416 | -0.69334 | -0.80457 | -0.83824 | -0.84334 | -0.092322 | -0.08722 | -0.091302 | -0.099465 | -0.10661 | -0.12089 | -0.12906 | -0.14436 | -0.15763 | -0.16477 | -0.2362 | -0.26681 | -0.28824 | -0.51987 | -0.51477 | -0.52396 | -0.53314 | -0.55049 | -0.56579 | -0.5811 | -0.60661 | -0.63008 | -0.6413 | -0.74334 | -0.77498 | -0.7811
|  | OTTER FERRY | CF |  |  |  |  | -0.5964 | -0.59334 | -0.60151 | -0.60457 | -0.61273 | -0.61987 | -0.6311 | -0.63722 | -0.64844 | -0.66069 | -0.73416 | -0.80049 | -0.84232 | -0.091302 | -0.082118 | -0.089261 | -0.094363 | -0.10151 | -0.11069 | -0.11987 | -0.126 | -0.13824 | -0.1464 | -0.20355 | -0.26579 | -0.32396 | -0.51885 | -0.50763 | -0.51987 | -0.52804 | -0.53824 | -0.54844 | -0.56273 | -0.57498 | -0.58926 | -0.60661 | -0.67804 | -0.7413 | -0.77906
| DUDHOPE | OVERGATE | MINIMUM HEADROOM | NO 40033 30155 | NO | NO | 4.089 | 19.7016 | 19.5404 | 19.2598 | 18.8924 | 18.5782 | 18.221 | 17.8435 | 17.5526 | 17.3016 | 17.0843 | 16.5547 | 16.4271 | 16.3996 | 21.1537 | 21.0077 | 20.8373 | 20.6537 | 20.4924 | 20.3282 | 20.1486 | 19.969 | 19.8139 | 19.672 | 19.1843 | 18.669 | 16.8353 | 21.4098 | 21.2628 | 21.0618 | 20.8088 | 20.57 | 20.3149 | 20.0577 | 19.8516 | 19.6771 | 19.5251 | 19.119 | 18.9761 | 18.8516
|  | OVERGATE | EE |  |  |  |  | 19.7016 | 19.5404 | 19.2598 | 18.8924 | 18.5782 | 18.221 | 17.8435 | 17.5526 | 17.3016 | 17.0843 | 16.5547 | 16.6812 | 16.6496 | 21.1537 | 21.0077 | 20.8373 | 20.6537 | 20.4924 | 20.3282 | 20.1486 | 19.969 | 19.8139 | 19.672 | 19.1843 | 18.87 | 18.0904 | 21.4098 | 21.2628 | 21.0618 | 20.8088 | 20.57 | 20.3149 | 20.0577 | 19.8516 | 19.6771 | 19.5251 | 19.119 | 19.0526 | 19.0241
|  | OVERGATE | HT |  |  |  |  | 19.7149 | 19.571 | 19.268 | 18.9128 | 18.6149 | 18.3302 | 18.1057 | 17.7771 | 17.52 | 17.3241 | 16.6792 | 16.4271 | 16.3996 | 21.1618 | 21.0261 | 20.8577 | 20.6965 | 20.5639 | 20.4384 | 20.3251 | 20.171 | 20.0363 | 19.9128 | 19.4016 | 19.1557 | 19.0924 | 21.422 | 21.2853 | 21.0751 | 20.8343 | 20.6149 | 20.4057 | 20.2496 | 20.0333 | 19.8608 | 19.7282 | 19.2608 | 19.0128 | 18.9496
|  | OVERGATE | HE |  |  |  |  | 19.7384 | 19.6169 | 19.3741 | 19.0475 | 18.7639 | 18.4567 | 18.1669 | 17.8955 | 17.7088 | 17.572 | 17.122 | 16.9067 | 16.9384 | 21.1833 | 21.0465 | 20.8935 | 20.7251 | 20.5761 | 20.4251 | 20.2659 | 20.0914 | 19.9455 | 19.8067 | 19.1955 | 18.9414 | 18.3639 | 21.4424 | 21.3098 | 21.1312 | 20.9118 | 20.6996 | 20.4639 | 20.2465 | 20.0455 | 19.9037 | 19.7924 | 19.1996 | 18.9761 | 18.9557
|  | OVERGATE | CF |  |  |  |  | 19.8537 | 19.7812 | 19.618 | 19.422 | 19.2608 | 19.1016 | 18.9343 | 18.6567 | 18.5231 | 18.3608 | 17.7292 | 17.1924 | 16.7077 | 21.3006 | 21.2169 | 21.1108 | 20.9996 | 20.8996 | 20.8006 | 20.6935 | 20.5404 | 20.4363 | 20.3118 | 19.7128 | 18.669 | 16.8353 | 21.5639 | 21.4853 | 21.3608 | 21.222 | 21.0884 | 20.9608 | 20.8261 | 20.6139 | 20.5016 | 20.369 | 19.8118 | 19.2761 | 18.8516
| CASSLEY | OVERSCAIG | MINIMUM HEADROOM | NC 39711 25382 | YES | NO | 0 | 0.16067 | 0.15353 | 0.15251 | 0.15149 | 0.15149 | 0.14027 | 0.14027 | 0.13312 | 0.1321 | 0.13108 | 0.12802 | 0.127 | 0.12496 | 0.15126 | 0.14309 | 0.14309 | 0.14207 | 0.14207 | 0.13391 | 0.13391 | 0.12574 | 0.12472 | 0.12472 | 0.12472 | 0.12574 | 0.1237 | 0.15392 | 0.14576 | 0.14576 | 0.14474 | 0.14474 | 0.13352 | 0.13352 | 0.12637 | 0.12637 | 0.12535 | 0.12229 | 0.12127 | 0.11923
|  | OVERSCAIG | EE |  |  |  |  | 0.16067 | 0.15353 | 0.15251 | 0.15149 | 0.15149 | 0.14027 | 0.14027 | 0.13312 | 0.1321 | 0.13108 | 0.12802 | 0.127 | 0.127 | 0.15126 | 0.14309 | 0.14309 | 0.14207 | 0.14207 | 0.13391 | 0.13391 | 0.12574 | 0.12472 | 0.12472 | 0.12677 | 0.12574 | 0.12574 | 0.15392 | 0.14576 | 0.14576 | 0.14474 | 0.14474 | 0.13352 | 0.13352 | 0.12637 | 0.12637 | 0.12535 | 0.12229 | 0.12127 | 0.12127
|  | OVERSCAIG | HT |  |  |  |  | 0.16067 | 0.16067 | 0.16067 | 0.15149 | 0.15149 | 0.14843 | 0.14843 | 0.14231 | 0.14027 | 0.14027 | 0.12904 | 0.127 | 0.12496 | 0.15126 | 0.15126 | 0.15023 | 0.14207 | 0.14207 | 0.14207 | 0.14207 | 0.13391 | 0.13289 | 0.13289 | 0.12779 | 0.12574 | 0.12472 | 0.15392 | 0.15392 | 0.1529 | 0.14474 | 0.14474 | 0.14168 | 0.14168 | 0.13454 | 0.13352 | 0.13352 | 0.12331 | 0.12127 | 0.11923
|  | OVERSCAIG | HE |  |  |  |  | 0.16067 | 0.16067 | 0.16067 | 0.15251 | 0.15149 | 0.15149 | 0.15047 | 0.14027 | 0.14027 | 0.14129 | 0.12904 | 0.12802 | 0.12802 | 0.15126 | 0.15126 | 0.15023 | 0.14309 | 0.14207 | 0.14207 | 0.14105 | 0.13391 | 0.13391 | 0.13289 | 0.12677 | 0.12677 | 0.12574 | 0.15392 | 0.15392 | 0.1529 | 0.14576 | 0.14474 | 0.14474 | 0.1427 | 0.13352 | 0.13352 | 0.13454 | 0.12331 | 0.12229 | 0.12229
|  | OVERSCAIG | CF |  |  |  |  | 0.16067 | 0.16067 | 0.16067 | 0.15353 | 0.15353 | 0.15251 | 0.15149 | 0.15149 | 0.14435 | 0.14333 | 0.13312 | 0.13006 | 0.12802 | 0.15126 | 0.15126 | 0.15126 | 0.14309 | 0.14309 | 0.14309 | 0.14207 | 0.14207 | 0.13493 | 0.13391 | 0.12472 | 0.12779 | 0.1237 | 0.15392 | 0.15392 | 0.15392 | 0.14576 | 0.14576 | 0.14576 | 0.14474 | 0.14474 | 0.1376 | 0.13556 | 0.12637 | 0.12433 | 0.12229
| KINTORE | PARK | MINIMUM HEADROOM | NO 79107 99434 | YES | YES | 0.094 | -1.2799 | -1.3635 | -1.4523 | -1.5646 | -1.6788 | -1.8105 | -1.9574 | -2.1207 | -2.2829 | -2.4299 | -2.8778 | -3.1258 | -3.186 | -0.30334 | -0.3564 | -0.40844 | -0.48191 | -0.55538 | -0.64211 | -0.7166 | -0.82579 | -0.92987 | -1.0227 | -1.2748 | -1.4166 | -1.6972 | -0.73803 | -0.81864 | -0.9013 | -1.0105 | -1.1176 | -1.2482 | -1.3717 | -1.535 | -1.6891 | -1.8278 | -2.1972 | -2.4176 | -2.488
|  | PARK | EE |  |  |  |  | -1.2799 | -1.3635 | -1.4523 | -1.5646 | -1.6788 | -1.8105 | -1.9574 | -2.1207 | -2.2829 | -2.4299 | -2.8778 | -3.0809 | -3.1258 | -0.30334 | -0.3564 | -0.40844 | -0.48191 | -0.55538 | -0.64211 | -0.7166 | -0.82579 | -0.92987 | -1.0227 | -1.2748 | -1.3972 | -1.537 | -0.73803 | -0.81864 | -0.9013 | -1.0105 | -1.1176 | -1.2482 | -1.3717 | -1.535 | -1.6891 | -1.8278 | -2.1972 | -2.3615 | -2.3942
|  | PARK | HT |  |  |  |  | -1.2584 | -1.3401 | -1.4329 | -1.5493 | -1.6533 | -1.7686 | -1.9064 | -2.0533 | -2.1697 | -2.3125 | -2.8574 | -3.1258 | -3.186 | -0.27783 | -0.32069 | -0.36967 | -0.43395 | -0.48497 | -0.5513 | -0.62579 | -0.71864 | -0.79109 | -0.87783 | -1.2391 | -1.3891 | -1.4472 | -0.70946 | -0.78191 | -0.86456 | -0.9666 | -1.0574 | -1.1615 | -1.285 | -1.4268 | -1.5248 | -1.6544 | -2.1707 | -2.4176 | -2.488
|  | PARK | HE |  |  |  |  | -1.2564 | -1.3084 | -1.3676 | -1.4482 | -1.5156 | -1.6044 | -1.7237 | -1.8391 | -1.9248 | -2.0503 | -2.6942 | -2.9707 | -3.0942 | -0.27885 | -0.31456 | -0.35844 | -0.41354 | -0.46558 | -0.52987 | -0.61048 | -0.70028 | -0.77171 | -0.86252 | -1.2717 | -1.4166 | -1.4993 | -0.70844 | -0.7564 | -0.81456 | -0.89518 | -0.95436 | -1.0442 | -1.1595 | -1.286 | -1.3891 | -1.5125 | -2.1125 | -2.3442 | -2.4544
|  | PARK | CF |  |  |  |  | -1.2431 | -1.2778 | -1.3207 | -1.3737 | -1.4135 | -1.4758 | -1.5421 | -1.6197 | -1.6829 | -1.7278 | -2.137 | -2.5676 | -2.9084 | -0.27375 | -0.29722 | -0.32681 | -0.36864 | -0.3962 | -0.44416 | -0.4962 | -0.55946 | -0.61456 | -0.64211 | -0.97171 | -1.3227 | -1.6972 | -0.69416 | -0.72885 | -0.77171 | -0.82681 | -0.86558 | -0.92783 | -0.99313 | -1.0727 | -1.1421 | -1.1809 | -1.6084 | -2.0186 | -2.3166
| ALNESS | PEDDIESTON | MINIMUM HEADROOM | NH 74198 63656 | NO | NO | 0.018 | 1.6268 | 1.5829 | 1.5237 | 1.4645 | 1.3941 | 1.34 | 1.2513 | 1.1594 | 1.0635 | 0.98187 | 0.81657 | 0.74412 | 0.72167 | 2.286 | 2.2543 | 2.2094 | 2.1717 | 2.1217 | 2.09 | 2.0288 | 1.9666 | 1.9023 | 1.8451 | 1.7451 | 1.6941 | 1.5482 | 1.9594 | 1.9115 | 1.8482 | 1.7931 | 1.7206 | 1.6747 | 1.5849 | 1.4962 | 1.3992 | 1.3227 | 1.1788 | 1.1125 | 1.0951
|  | PEDDIESTON | EE |  |  |  |  | 1.6268 | 1.5829 | 1.5237 | 1.4645 | 1.3941 | 1.34 | 1.2513 | 1.1594 | 1.0635 | 0.98187 | 0.81657 | 0.78085 | 0.75942 | 2.286 | 2.2543 | 2.2094 | 2.1717 | 2.1217 | 2.09 | 2.0288 | 1.9666 | 1.9023 | 1.8451 | 1.7451 | 1.6941 | 1.6104 | 1.9594 | 1.9115 | 1.8482 | 1.7931 | 1.7206 | 1.6747 | 1.5849 | 1.4962 | 1.3992 | 1.3227 | 1.1788 | 1.1492 | 1.1288
|  | PEDDIESTON | HT |  |  |  |  | 1.639 | 1.5992 | 1.5513 | 1.5145 | 1.4594 | 1.4053 | 1.338 | 1.2778 | 1.2053 | 1.14 | 0.87779 | 0.74412 | 0.72167 | 2.3094 | 2.2829 | 2.2482 | 2.2258 | 2.189 | 2.1584 | 2.1125 | 2.0829 | 2.0349 | 1.9911 | 1.8094 | 1.7329 | 1.7206 | 1.9819 | 1.94 | 1.889 | 1.8502 | 1.7962 | 1.7472 | 1.6798 | 1.6268 | 1.5584 | 1.4951 | 1.237 | 1.1125 | 1.0951
|  | PEDDIESTON | HE |  |  |  |  | 1.638 | 1.6104 | 1.5737 | 1.5482 | 1.5053 | 1.4655 | 1.4074 | 1.3574 | 1.2941 | 1.238 | 0.93289 | 0.85432 | 0.84208 | 2.3064 | 2.2839 | 2.2533 | 2.2329 | 2.1992 | 2.1727 | 2.1309 | 2.1023 | 2.0625 | 2.0237 | 1.8237 | 1.7451 | 1.6727 | 1.9798 | 1.9502 | 1.9064 | 1.8788 | 1.8329 | 1.7951 | 1.737 | 1.6951 | 1.6339 | 1.5778 | 1.2911 | 1.2166 | 1.2064
|  | PEDDIESTON | CF |  |  |  |  | 1.6421 | 1.6176 | 1.589 | 1.5645 | 1.5319 | 1.5002 | 1.4686 | 1.4206 | 1.3747 | 1.3502 | 1.1288 | 0.96453 | 0.85942 | 2.3084 | 2.287 | 2.2676 | 2.2523 | 2.2237 | 2.1951 | 2.1717 | 2.1329 | 2.0982 | 2.088 | 1.9043 | 1.736 | 1.5482 | 1.9829 | 1.9594 | 1.9288 | 1.9064 | 1.8666 | 1.8258 | 1.7972 | 1.7472 | 1.7002 | 1.6819 | 1.4594 | 1.3033 | 1.2135
| PETERHEAD GRANGE | PETERHEAD GRANGE | MINIMUM HEADROOM | NK 11738 46516 | NO | YES | 2.908 | 7.8131 | 7.0886 | 5.9958 | 4.806 | 3.956 | 1.9845 | 0.66311 | -1.0206 | -2.7655 | -4.7604 | -11.8165 | -18.5318 | -22.6369 | 10.9074 | 10.4727 | 9.7451 | 8.8717 | 8.4247 | 6.6676 | 5.89 | 4.8084 | 3.7043 | 2.3625 | -3.3946 | -9.1355 | -14.5477 | 9.2758 | 8.6084 | 7.5747 | 6.3839 | 5.6105 | 3.5278 | 2.3594 | 0.80025 | -0.77934 | -2.613 | -9.1967 | -16.1977 | -20.7181
|  | PETERHEAD GRANGE | EE |  |  |  |  | 7.8131 | 7.0886 | 6.2845 | 5.4407 | 4.6856 | 3.2937 | 1.608 | 0.088616 | -1.7165 | -3.4706 | -10.5216 | -17.1481 | -19.8451 | 10.9074 | 10.4727 | 10.0033 | 9.5145 | 8.9972 | 7.8482 | 6.7309 | 5.788 | 4.4921 | 3.2737 | -1.2753 | -6.7742 | -9.8069 | 9.2758 | 8.6084 | 7.8676 | 7.0829 | 6.3839 | 4.9605 | 3.3819 | 1.9972 | 0.26453 | -1.3712 | -7.8814 | -14.6161 | -17.2906
|  | PETERHEAD GRANGE | HT |  |  |  |  | 7.8427 | 7.0937 | 5.9958 | 4.806 | 3.956 | 1.9845 | 0.66311 | -1.0206 | -2.7655 | -4.7604 | -11.8165 | -18.5318 | -22.6369 | 10.94 | 10.5166 | 9.7451 | 8.8717 | 8.4247 | 6.6676 | 5.89 | 4.8084 | 3.7043 | 2.3625 | -1.7855 | -7.2457 | -11.2946 | 9.3207 | 8.6472 | 7.5747 | 6.3839 | 5.6105 | 3.5278 | 2.3594 | 0.80025 | -0.77934 | -2.613 | -9.1967 | -16.1977 | -20.7181
|  | PETERHEAD GRANGE | HE |  |  |  |  | 7.9202 | 7.4376 | 6.6835 | 5.8233 | 5.1335 | 3.56 | 2.4376 | 1.108 | -0.3124 | -2.1318 | -10.1002 | -16.8389 | -21.7849 | 10.9962 | 10.6645 | 10.0584 | 9.3319 | 8.8196 | 7.2747 | 6.4349 | 5.3941 | 4.2798 | 2.7339 | -3.3946 | -9.1355 | -14.5477 | 9.3921 | 8.9533 | 8.1951 | 7.3064 | 6.6298 | 4.9105 | 3.8707 | 2.5696 | 1.1931 | -0.61914 | -8.4355 | -15.3691 | -20.6926
|  | PETERHEAD GRANGE | CF |  |  |  |  | 8.1498 | 7.8458 | 7.5274 | 7.1815 | 6.757 | 6.1049 | 5.5182 | 5.1437 | 4.5764 | 3.8815 | -0.72771 | -6.1553 | -10.4777 | 11.1584 | 10.9309 | 10.7084 | 10.4696 | 10.0982 | 9.4635 | 8.9176 | 8.5421 | 8.0043 | 7.3288 | 3.6411 | -0.71404 | -4.8691 | 9.6064 | 9.3237 | 9.038 | 8.7217 | 8.2798 | 7.5839 | 6.9849 | 6.6513 | 6.0829 | 5.3819 | 1.0951 | -3.8416 | -7.6926
| PETERHEAD GRANGE | PETERHEAD NORTH STREET | MINIMUM HEADROOM | NK 13470 46450 | NO | YES | 3.65 | 5.4045 | 5.3218 | 5.2218 | 5.1045 | 4.9902 | 4.8535 | 4.6688 | 4.4494 | 4.2576 | 4.0147 | 2.6412 | 1.8718 | 1.6912 | 10.4498 | 10.3529 | 10.2355 | 10.0998 | 9.9661 | 9.809 | 9.6039 | 9.3559 | 9.1396 | 8.9263 | 8.0161 | 7.1763 | 5.2376 | 10.2631 | 10.1457 | 10.0141 | 9.861 | 9.711 | 9.5416 | 9.2682 | 8.959 | 8.6824 | 8.4018 | 7.1029 | 6.2722 | 6.1141
|  | PETERHEAD NORTH STREET | EE |  |  |  |  | 5.4045 | 5.3218 | 5.2218 | 5.1045 | 4.9902 | 4.8535 | 4.6688 | 4.4494 | 4.2576 | 4.0147 | 2.6412 | 1.9157 | 1.73 | 10.4498 | 10.3529 | 10.2355 | 10.0998 | 9.9661 | 9.809 | 9.6039 | 9.3559 | 9.1396 | 8.9263 | 8.0161 | 7.1763 | 6.2039 | 10.2631 | 10.1457 | 10.0141 | 9.861 | 9.711 | 9.5416 | 9.2682 | 8.959 | 8.6824 | 8.4018 | 7.1029 | 6.3192 | 6.1427
|  | PETERHEAD NORTH STREET | HT |  |  |  |  | 5.428 | 5.3555 | 5.2769 | 5.1892 | 5.0882 | 4.9667 | 4.8127 | 4.6188 | 4.429 | 4.2341 | 2.7657 | 1.8718 | 1.6912 | 10.4824 | 10.3988 | 10.31 | 10.208 | 10.0916 | 9.9559 | 9.7835 | 9.5661 | 9.3569 | 9.1416 | 8.1222 | 7.6284 | 7.4937 | 10.2937 | 10.1886 | 10.0773 | 9.9518 | 9.8202 | 9.6692 | 9.4233 | 9.1416 | 8.8641 | 8.5804 | 7.1386 | 6.2722 | 6.1141
|  | PETERHEAD NORTH STREET | HE |  |  |  |  | 5.429 | 5.3647 | 5.3004 | 5.2198 | 5.131 | 5.0208 | 4.8739 | 4.6973 | 4.5198 | 4.331 | 2.8841 | 2.3361 | 2.1698 | 10.4804 | 10.4018 | 10.3212 | 10.2243 | 10.1161 | 9.9824 | 9.8069 | 9.6018 | 9.3927 | 9.1743 | 8.1457 | 7.6406 | 6.6865 | 10.2937 | 10.2171 | 10.1427 | 10.0498 | 9.9549 | 9.8386 | 9.6488 | 9.4386 | 9.2018 | 8.9018 | 7.4396 | 6.809 | 6.5978
|  | PETERHEAD NORTH STREET | CF |  |  |  |  | 5.4524 | 5.4208 | 5.3831 | 5.3412 | 5.2882 | 5.2331 | 5.1657 | 5.0759 | 4.9871 | 4.8953 | 4.2861 | 3.2259 | 2.3004 | 10.512 | 10.4692 | 10.4243 | 10.3702 | 10.31 | 10.2396 | 10.1569 | 10.0478 | 9.9416 | 9.8284 | 8.9641 | 7.509 | 5.2376 | 10.3243 | 10.2876 | 10.2457 | 10.2008 | 10.1447 | 10.0876 | 10.0192 | 9.9294 | 9.8396 | 9.7335 | 8.8539 | 7.8539 | 6.9682
| FORT WILLIAM | PINEGROVE | MINIMUM HEADROOM | NN 10496 73556 | NO | NO | 1.076 | 5.6045 | 5.3678 | 5.1637 | 4.9321 | 4.6668 | 4.426 | 4.1596 | 3.8525 | 3.6137 | 3.4107 | 2.8872 | 2.6821 | 2.6341 | 6.8954 | 6.7586 | 6.6413 | 6.5015 | 6.3372 | 6.1974 | 6.0219 | 5.8158 | 5.6617 | 5.5209 | 5.1025 | 4.9127 | 4.326 | 6.1403 | 5.9311 | 5.7484 | 5.5352 | 5.2923 | 5.0729 | 4.8229 | 4.5372 | 4.3147 | 4.1239 | 3.6301 | 3.4372 | 3.3974
|  | PINEGROVE | EE |  |  |  |  | 5.6045 | 5.3678 | 5.1637 | 4.9321 | 4.6668 | 4.426 | 4.1596 | 3.8525 | 3.6137 | 3.4107 | 2.8872 | 2.8015 | 2.7209 | 6.8954 | 6.7586 | 6.6413 | 6.5015 | 6.3372 | 6.1974 | 6.0219 | 5.8158 | 5.6617 | 5.5209 | 5.1025 | 4.9127 | 4.5862 | 6.1403 | 5.9311 | 5.7484 | 5.5352 | 5.2923 | 5.0729 | 4.8229 | 4.5372 | 4.3147 | 4.1239 | 3.6301 | 3.5545 | 3.475
|  | PINEGROVE | HT |  |  |  |  | 5.6688 | 5.4545 | 5.2739 | 5.0698 | 4.8719 | 4.6362 | 4.4198 | 4.2158 | 3.9923 | 3.8035 | 3.0413 | 2.6821 | 2.6341 | 6.9505 | 6.8362 | 6.7382 | 6.625 | 6.5168 | 6.3852 | 6.2535 | 6.1341 | 5.9943 | 5.8678 | 5.3382 | 5.1005 | 5.0698 | 6.1923 | 6.0168 | 5.8576 | 5.6729 | 5.4954 | 5.2811 | 5.0831 | 4.8974 | 4.6892 | 4.5076 | 3.778 | 3.4372 | 3.3974
|  | PINEGROVE | HE |  |  |  |  | 5.6688 | 5.478 | 5.3219 | 5.1413 | 4.9719 | 4.7688 | 4.577 | 4.3994 | 4.1994 | 4.0403 | 3.2719 | 3.075 | 3.0535 | 6.9484 | 6.8403 | 6.7525 | 6.6474 | 6.5484 | 6.4321 | 6.3086 | 6.1954 | 6.0617 | 5.9484 | 5.3852 | 5.1198 | 4.8413 | 6.1933 | 6.0382 | 5.8994 | 5.7382 | 5.5852 | 5.4035 | 5.226 | 5.0658 | 4.879 | 4.728 | 4.0025 | 3.8147 | 3.7943
|  | PINEGROVE | CF |  |  |  |  | 5.725 | 5.579 | 5.4239 | 5.276 | 5.1341 | 4.9647 | 4.827 | 4.6627 | 4.5066 | 4.426 | 3.8178 | 3.3464 | 3.0668 | 6.978 | 6.8974 | 6.8086 | 6.7188 | 6.6423 | 6.5382 | 6.4443 | 6.3301 | 6.2188 | 6.1576 | 5.6239 | 5.0331 | 4.326 | 6.2311 | 6.1137 | 5.9841 | 5.8566 | 5.7341 | 5.5841 | 5.4596 | 5.3107 | 5.1647 | 5.0933 | 4.5096 | 4.0596 | 3.8015
| TUMMEL BRIDGE | PITLOCHRY | MINIMUM HEADROOM | NN 95756 58991 | NO | YES | 1.109 | 1.6379 | 1.5022 | 1.3338 | 1.1461 | 0.98177 | 0.76952 | 0.50217 | 0.25115 | -0.026398 | -0.25905 | -0.99579 | -1.3784 | -1.4611 | 2.5397 | 2.4805 | 2.4131 | 2.3244 | 2.2366 | 2.1305 | 1.9989 | 1.8703 | 1.7131 | 1.5805 | 1.1131 | 0.81824 | 0.33559 | 2.0908 | 1.9653 | 1.8092 | 1.6357 | 1.4857 | 1.2908 | 1.0418 | 0.80817 | 0.55001 | 0.33368 | -0.34387 | -0.68571 | -0.76224
|  | PITLOCHRY | EE |  |  |  |  | 1.6379 | 1.5022 | 1.3338 | 1.1461 | 0.98177 | 0.76952 | 0.50217 | 0.25115 | -0.026398 | -0.25905 | -0.99579 | -1.3274 | -1.4315 | 2.5397 | 2.4805 | 2.4131 | 2.3244 | 2.2366 | 2.1305 | 1.9989 | 1.8703 | 1.7131 | 1.5805 | 1.1131 | 0.81824 | 0.50906 | 2.0908 | 1.9653 | 1.8092 | 1.6357 | 1.4857 | 1.2908 | 1.0418 | 0.80817 | 0.55001 | 0.33368 | -0.34387 | -0.64183 | -0.73571
|  | PITLOCHRY | HT |  |  |  |  | 1.6869 | 1.5563 | 1.4144 | 1.2746 | 1.1103 | 0.92462 | 0.73585 | 0.49197 | 0.25217 | 0.028704 | -0.90395 | -1.3784 | -1.4611 | 2.5591 | 2.507 | 2.4489 | 2.3897 | 2.3182 | 2.2315 | 2.1407 | 2.0244 | 1.9111 | 1.8019 | 1.305 | 1.054 | 1.007 | 2.1378 | 2.0204 | 1.8898 | 1.7643 | 1.6163 | 1.4439 | 1.2745 | 1.049 | 0.82756 | 0.62143 | -0.25408 | -0.68571 | -0.76224
|  | PITLOCHRY | HE |  |  |  |  | 1.6879 | 1.595 | 1.494 | 1.392 | 1.2705 | 1.1246 | 0.98483 | 0.78789 | 0.60013 | 0.42564 | -0.45497 | -0.86721 | -1.007 | 2.557 | 2.5172 | 2.4754 | 2.4325 | 2.3713 | 2.2978 | 2.2223 | 2.1182 | 2.0223 | 1.9284 | 1.3887 | 1.0529 | 0.73865 | 2.1388 | 2.0551 | 1.9602 | 1.8684 | 1.7571 | 1.6235 | 1.4959 | 1.3122 | 1.1367 | 0.97654 | 0.15409 | -0.21836 | -0.34183
|  | PITLOCHRY | CF |  |  |  |  | 1.7103 | 1.644 | 1.5665 | 1.4685 | 1.393 | 1.295 | 1.1879 | 1.0614 | 0.98074 | 0.88381 | 0.32462 | -0.31926 | -0.7713 | 2.5662 | 2.5366 | 2.5019 | 2.4591 | 2.4223 | 2.3682 | 2.304 | 2.2295 | 2.1723 | 2.1111 | 1.7152 | 1.0907 | 0.33559 | 2.1622 | 2.101 | 2.0286 | 1.9408 | 1.8704 | 1.7816 | 1.6816 | 1.5633 | 1.4908 | 1.4 | 0.86837 | 0.26633 | -0.14285
| ARDMORE | POLLACHAR | MINIMUM HEADROOM | NF 75073 14513 | NO | YES | 0.32 | 1.4239 | 1.3127 | 1.1617 | 1.0341 | 0.927 | 0.78312 | 0.60863 | 0.36067 | 0.14333 | -0.078102 | -0.57606 | -0.67606 | -0.70463 | 2.979 | 2.9107 | 2.8046 | 2.726 | 2.6576 | 2.5607 | 2.4474 | 2.2668 | 2.1107 | 1.9494 | 1.5719 | 1.4576 | 1.1607 | 2.3321 | 2.2209 | 2.0688 | 1.9484 | 1.8494 | 1.7086 | 1.5392 | 1.2954 | 1.0923 | 0.88312 | 0.4219 | 0.3321 | 0.30965
|  | POLLACHAR | EE |  |  |  |  | 1.4239 | 1.3127 | 1.1617 | 1.0341 | 0.927 | 0.78312 | 0.60863 | 0.36067 | 0.14333 | -0.078102 | -0.57606 | -0.63014 | -0.66688 | 2.979 | 2.9168 | 2.8046 | 2.726 | 2.6576 | 2.5607 | 2.4474 | 2.2668 | 2.1107 | 1.9494 | 1.5719 | 1.4576 | 1.275 | 2.3321 | 2.2209 | 2.0688 | 1.9484 | 1.8494 | 1.7086 | 1.5392 | 1.2954 | 1.0923 | 0.88312 | 0.4219 | 0.37394 | 0.33414
|  | POLLACHAR | HT |  |  |  |  | 1.4658 | 1.3403 | 1.2525 | 1.1688 | 1.0586 | 0.94945 | 0.81884 | 0.63414 | 0.37598 | 0.16169 | -0.43116 | -0.67606 | -0.70463 | 3.0056 | 2.9107 | 2.8648 | 2.8229 | 2.7668 | 2.7056 | 2.625 | 2.4933 | 2.2933 | 2.1382 | 1.7392 | 1.5862 | 1.5709 | 2.3821 | 2.2535 | 2.1709 | 2.0984 | 1.9954 | 1.8954 | 1.7709 | 1.6025 | 1.3535 | 1.1474 | 0.56271 | 0.3321 | 0.30965
|  | POLLACHAR | HE |  |  |  |  | 1.4668 | 1.4097 | 1.2984 | 1.2117 | 1.1494 | 1.0658 | 0.95353 | 0.81884 | 0.62292 | 0.44231 | -0.29443 | -0.44443 | -0.45871 | 3.0066 | 2.9719 | 2.879 | 2.8301 | 2.7964 | 2.7464 | 2.675 | 2.576 | 2.427 | 2.2862 | 1.7709 | 1.5994 | 1.4382 | 2.3831 | 2.325 | 2.2066 | 2.1229 | 2.0678 | 1.9882 | 1.8821 | 1.7546 | 1.5678 | 1.3913 | 0.70251 | 0.56271 | 0.54945
|  | POLLACHAR | CF |  |  |  |  | 1.479 | 1.428 | 1.376 | 1.2678 | 1.2178 | 1.1494 | 1.0811 | 0.97394 | 0.86476 | 0.78924 | 0.20557 | -0.223 | -0.41892 | 3.0107 | 2.9862 | 2.9525 | 2.8607 | 2.829 | 2.7882 | 2.7423 | 2.6658 | 2.5801 | 2.5199 | 2.0321 | 1.5739 | 1.1607 | 2.3954 | 2.3464 | 2.2923 | 2.1719 | 2.125 | 2.0556 | 1.9903 | 1.8872 | 1.777 | 1.7066 | 1.1341 | 0.73006 | 0.57904
| FORT WILLIAM | POOR HOUSE | MINIMUM HEADROOM | NM 71766 70148 | YES | NO | 0 | 0.10269 | 0.10065 | 0.09351 | 0.09351 | 0.09249 | 0.09249 | 0.085347 | 0.084327 | 0.084327 | 0.076163 | 0.074122 | 0.074122 | 0.073102 | 0.097776 | 0.096755 | 0.089612 | 0.089612 | 0.088592 | 0.088592 | 0.081449 | 0.081449 | 0.081449 | 0.074306 | 0.072265 | 0.072265 | 0.070224 | 0.10126 | 0.10023 | 0.093092 | 0.092071 | 0.092071 | 0.092071 | 0.083908 | 0.083908 | 0.083908 | 0.075745 | 0.073704 | 0.073704 | 0.072684
|  | POOR HOUSE | EE |  |  |  |  | 0.10269 | 0.10065 | 0.09351 | 0.09351 | 0.09249 | 0.09249 | 0.085347 | 0.084327 | 0.084327 | 0.076163 | 0.074122 | 0.074122 | 0.074122 | 0.097776 | 0.096755 | 0.089612 | 0.089612 | 0.088592 | 0.088592 | 0.081449 | 0.081449 | 0.081449 | 0.074306 | 0.072265 | 0.072265 | 0.072265 | 0.10126 | 0.10023 | 0.093092 | 0.092071 | 0.092071 | 0.092071 | 0.083908 | 0.083908 | 0.083908 | 0.075745 | 0.073704 | 0.073704 | 0.073704
|  | POOR HOUSE | HT |  |  |  |  | 0.10269 | 0.10065 | 0.10065 | 0.10065 | 0.09351 | 0.09351 | 0.09249 | 0.09249 | 0.09249 | 0.084327 | 0.076163 | 0.075143 | 0.074122 | 0.097776 | 0.096755 | 0.096755 | 0.096755 | 0.089612 | 0.089612 | 0.088592 | 0.088592 | 0.088592 | 0.081449 | 0.073286 | 0.072265 | 0.072265 | 0.10126 | 0.10023 | 0.10023 | 0.10023 | 0.092071 | 0.092071 | 0.091051 | 0.091051 | 0.091051 | 0.083908 | 0.075745 | 0.074724 | 0.073704
|  | POOR HOUSE | HE |  |  |  |  | 0.10269 | 0.10065 | 0.10065 | 0.10065 | 0.09351 | 0.09351 | 0.09351 | 0.09249 | 0.091469 | 0.084327 | 0.074122 | 0.074122 | 0.073102 | 0.097776 | 0.096755 | 0.096755 | 0.096755 | 0.089612 | 0.089612 | 0.089612 | 0.088592 | 0.088592 | 0.081449 | 0.072265 | 0.072265 | 0.071245 | 0.10126 | 0.10023 | 0.10023 | 0.099214 | 0.092071 | 0.092071 | 0.092071 | 0.092071 | 0.091051 | 0.083908 | 0.073704 | 0.073704 | 0.072684
|  | POOR HOUSE | CF |  |  |  |  | 0.10269 | 0.10269 | 0.10065 | 0.10065 | 0.10065 | 0.09351 | 0.09351 | 0.09351 | 0.09351 | 0.09351 | 0.083306 | 0.074122 | 0.074122 | 0.097776 | 0.097776 | 0.096755 | 0.096755 | 0.096755 | 0.089612 | 0.089612 | 0.089612 | 0.089612 | 0.089612 | 0.081449 | 0.072265 | 0.070224 | 0.10126 | 0.10126 | 0.10023 | 0.10023 | 0.10023 | 0.092071 | 0.092071 | 0.092071 | 0.092071 | 0.092071 | 0.082888 | 0.073704 | 0.073704
| PORT ANN | PORT ASKAIG | MINIMUM HEADROOM | NR 42082 68818 | NO | YES | 1.944 | -1.1857 | -1.2122 | -1.251 | -1.2785 | -1.3224 | -1.3561 | -1.4081 | -1.4816 | -1.5183 | -1.5734 | -1.6959 | -1.7418 | -1.752 | -0.93361 | -0.94688 | -0.96321 | -0.97749 | -1.002 | -1.0285 | -1.0632 | -1.1173 | -1.1428 | -1.1816 | -1.2755 | -1.302 | -1.4163 | -1.0255 | -1.0499 | -1.0867 | -1.1152 | -1.1571 | -1.1908 | -1.2408 | -1.3132 | -1.354 | -1.4081 | -1.5285 | -1.5724 | -1.5969
|  | PORT ASKAIG | EE |  |  |  |  | -1.1857 | -1.2122 | -1.251 | -1.2785 | -1.3224 | -1.3561 | -1.4081 | -1.4816 | -1.5183 | -1.5734 | -1.6959 | -1.7173 | -1.7316 | -0.93361 | -0.94688 | -0.96321 | -0.97749 | -1.002 | -1.0285 | -1.0632 | -1.1173 | -1.1428 | -1.1816 | -1.2755 | -1.302 | -1.3489 | -1.0255 | -1.0499 | -1.0867 | -1.1152 | -1.1571 | -1.1908 | -1.2408 | -1.3132 | -1.354 | -1.4081 | -1.5285 | -1.5489 | -1.5601
|  | PORT ASKAIG | HT |  |  |  |  | -1.1673 | -1.1877 | -1.2152 | -1.2408 | -1.2744 | -1.2928 | -1.3489 | -1.3928 | -1.4397 | -1.4897 | -1.6571 | -1.7418 | -1.752 | -0.92443 | -0.93566 | -0.94994 | -0.96219 | -0.97545 | -0.9877 | -1.0255 | -1.053 | -1.0867 | -1.1214 | -1.2336 | -1.2857 | -1.2908 | -1.0061 | -1.0285 | -1.055 | -1.0795 | -1.1122 | -1.1346 | -1.1938 | -1.2377 | -1.2826 | -1.3326 | -1.4928 | -1.5724 | -1.5806
|  | PORT ASKAIG | HE |  |  |  |  | -1.1673 | -1.1877 | -1.205 | -1.2255 | -1.254 | -1.2703 | -1.302 | -1.352 | -1.3877 | -1.4326 | -1.6336 | -1.6938 | -1.702 | -0.92749 | -0.93566 | -0.94586 | -0.95606 | -0.96831 | -0.98055 | -0.99688 | -1.0306 | -1.0561 | -1.0928 | -1.2336 | -1.2887 | -1.3265 | -1.0061 | -1.0285 | -1.0448 | -1.0632 | -1.0938 | -1.1091 | -1.1408 | -1.1928 | -1.2306 | -1.2744 | -1.4755 | -1.551 | -1.5601
|  | PORT ASKAIG | CF |  |  |  |  | -1.1663 | -1.1806 | -1.1999 | -1.2152 | -1.2336 | -1.2571 | -1.2693 | -1.303 | -1.3326 | -1.3499 | -1.4938 | -1.6367 | -1.7275 | -0.92443 | -0.93259 | -0.94178 | -0.94994 | -0.95912 | -0.97137 | -0.97851 | -0.99484 | -1.0142 | -1.0285 | -1.1499 | -1.2918 | -1.4163 | -1.005 | -1.0193 | -1.0367 | -1.054 | -1.0703 | -1.0938 | -1.104 | -1.1346 | -1.1642 | -1.1846 | -1.3306 | -1.4775 | -1.5969
| PORT ANN | PORT ELLEN | MINIMUM HEADROOM | NR 36459 45513 | YES | YES | 3.256 | -0.58398 | -0.67786 | -0.79113 | -0.8697 | -0.96664 | -1.0381 | -1.1432 | -1.2952 | -1.4411 | -1.5279 | -1.8115 | -1.8809 | -1.8983 | -0.16133 | -0.21541 | -0.27664 | -0.32051 | -0.37051 | -0.41133 | -0.51337 | -0.60521 | -0.70317 | -0.77358 | -1.0001 | -1.0634 | -1.2695 | -0.36909 | -0.45786 | -0.55888 | -0.62623 | -0.71398 | -0.77521 | -0.87317 | -1.0201 | -1.1548 | -1.2344 | -1.4926 | -1.5599 | -1.5732
|  | PORT ELLEN | EE |  |  |  |  | -0.58398 | -0.67786 | -0.79113 | -0.8697 | -0.96664 | -1.0381 | -1.1207 | -1.2952 | -1.4411 | -1.5279 | -1.8115 | -1.8452 | -1.8677 | -0.16133 | -0.21541 | -0.27664 | -0.32051 | -0.37051 | -0.41133 | -0.46133 | -0.595 | -0.70317 | -0.77358 | -1.0001 | -1.0634 | -1.1634 | -0.36909 | -0.45786 | -0.55888 | -0.62623 | -0.71398 | -0.77521 | -0.85378 | -1.0201 | -1.1548 | -1.2344 | -1.4926 | -1.5242 | -1.5477
|  | PORT ELLEN | HT |  |  |  |  | -0.57378 | -0.64623 | -0.74827 | -0.81153 | -0.89011 | -0.95847 | -1.1432 | -1.2595 | -1.3677 | -1.4554 | -1.7493 | -1.8809 | -1.8983 | -0.14398 | -0.19602 | -0.24807 | -0.28072 | -0.32256 | -0.35725 | -0.51337 | -0.60521 | -0.68072 | -0.74092 | -0.92153 | -1.0021 | -1.0124 | -0.3446 | -0.42419 | -0.51398 | -0.56704 | -0.63745 | -0.6946 | -0.87317 | -0.98949 | -1.0875 | -1.166 | -1.4375 | -1.5599 | -1.5732
|  | PORT ELLEN | HE |  |  |  |  | -0.5748 | -0.63398 | -0.72786 | -0.78194 | -0.85133 | -0.90745 | -0.96766 | -1.0891 | -1.2034 | -1.3024 | -1.683 | -1.7615 | -1.7677 | -0.14398 | -0.18888 | -0.23786 | -0.27153 | -0.30725 | -0.33888 | -0.37664 | -0.47766 | -0.56847 | -0.64909 | -0.92358 | -1.0164 | -1.1011 | -0.3446 | -0.41602 | -0.49664 | -0.5446 | -0.60582 | -0.65378 | -0.7099 | -0.82011 | -0.92725 | -1.0201 | -1.3762 | -1.4477 | -1.4538
|  | PORT ELLEN | CF |  |  |  |  | -0.56868 | -0.61868 | -0.69215 | -0.73704 | -0.79113 | -0.84215 | -0.87276 | -0.92174 | -0.99317 | -1.0411 | -1.3952 | -1.6513 | -1.7666 | -0.14296 | -0.18174 | -0.22256 | -0.24704 | -0.27868 | -0.30929 | -0.32664 | -0.36031 | -0.41745 | -0.45827 | -0.75419 | -1.0287 | -1.2695 | -0.34358 | -0.40276 | -0.46602 | -0.5048 | -0.55378 | -0.59868 | -0.62521 | -0.67317 | -0.74153 | -0.78439 | -1.116 | -1.3497 | -1.4507
| DUNVEGAN | PORTREE | MINIMUM HEADROOM | NG 48102 44602 | NO | NO | 1.301 | 2.2513 | 2.1095 | 1.937 | 1.7391 | 1.5646 | 1.1023 | 0.84316 | 0.49622 | 0.10438 | -0.25889 | -0.99154 | -1.2538 | -1.3222 | 3.3664 | 3.294 | 3.1827 | 3.0613 | 2.9613 | 2.7093 | 2.5521 | 2.3511 | 2.1205 | 1.9134 | 1.4674 | 1.3123 | 0.74805 | 2.945 | 2.8113 | 2.6572 | 2.4919 | 2.3419 | 1.945 | 1.7348 | 1.4205 | 1.0838 | 0.76948 | 0.10928 | -0.13052 | -0.19378
|  | PORTREE | EE |  |  |  |  | 2.2513 | 2.1095 | 1.937 | 1.7391 | 1.5646 | 1.1023 | 0.86254 | 0.49622 | 0.10438 | -0.25889 | -0.99154 | -1.1415 | -1.2242 | 3.3664 | 3.294 | 3.1827 | 3.0613 | 2.9613 | 2.7093 | 2.5521 | 2.3511 | 2.1205 | 1.9134 | 1.4674 | 1.3123 | 1.0399 | 2.945 | 2.8113 | 2.6572 | 2.4919 | 2.3419 | 1.945 | 1.7348 | 1.4205 | 1.0838 | 0.76948 | 0.10928 | -0.031539 | -0.099906
|  | PORTREE | HT |  |  |  |  | 2.2789 | 2.1595 | 2.0115 | 1.8727 | 1.7176 | 1.136 | 0.84316 | 0.51152 | 0.26254 | -0.0078653 | -0.85072 | -1.2538 | -1.3222 | 3.3889 | 3.3501 | 3.2746 | 3.2032 | 3.1113 | 2.8297 | 2.6868 | 2.4919 | 2.3389 | 2.1756 | 1.6327 | 1.397 | 1.3644 | 2.9848 | 2.8613 | 2.7287 | 2.6001 | 2.4583 | 1.9838 | 1.7368 | 1.4419 | 1.2144 | 0.97662 | 0.23683 | -0.13052 | -0.19378
|  | PORTREE | HE |  |  |  |  | 2.2778 | 2.1891 | 2.0809 | 1.9738 | 1.8503 | 1.4523 | 1.3381 | 1.083 | 0.82173 | 0.5554 | -0.58746 | -0.84664 | -0.8997 | 3.3878 | 3.3532 | 3.293 | 3.2338 | 3.1542 | 2.947 | 2.8807 | 2.7195 | 2.5664 | 2.4062 | 1.7307 | 1.5042 | 1.2317 | 2.9838 | 2.8878 | 2.7878 | 2.6889 | 2.5766 | 2.247 | 2.1419 | 1.9215 | 1.697 | 1.4674 | 0.45724 | 0.2154 | 0.16336
|  | PORTREE | CF |  |  |  |  | 2.3391 | 2.2595 | 2.1421 | 2.0411 | 1.9544 | 1.6227 | 1.5289 | 1.4217 | 1.2605 | 1.0727 | 0.14826 | -0.45276 | -0.82419 | 3.4236 | 3.3868 | 3.3368 | 3.2685 | 3.2215 | 3.0511 | 2.9766 | 2.8848 | 2.7991 | 2.6787 | 2.0736 | 1.497 | 0.74805 | 3.0532 | 2.9491 | 2.847 | 2.7552 | 2.6746 | 2.4062 | 2.3185 | 2.2205 | 2.0848 | 1.9236 | 1.1174 | 0.59193 | 0.23989
| MACDUFF | PORTSOY | MINIMUM HEADROOM | NJ 58491 65037 | YES | NO | 0.047 | -0.58655 | -0.63349 | -0.68144 | -0.74165 | -0.82634 | -0.92226 | -1.0488 | -1.2049 | -1.359 | -1.5059 | -2.0314 | -2.3763 | -2.4447 | 0.0073306 | -0.015118 | -0.037567 | -0.065118 | -0.12328 | -0.20083 | -0.26716 | -0.37736 | -0.48553 | -0.5743 | -0.79981 | -0.95696 | -1.1182 | -0.24573 | -0.31206 | -0.37838 | -0.459 | -0.53655 | -0.62532 | -0.73859 | -0.87736 | -1.0151 | -1.1396 | -1.5988 | -1.9019 | -1.961
|  | PORTSOY | EE |  |  |  |  | -0.58655 | -0.63349 | -0.68144 | -0.74165 | -0.82634 | -0.92226 | -1.0488 | -1.2049 | -1.359 | -1.5059 | -2.0192 | -2.3386 | -2.409 | 0.0073306 | -0.015118 | -0.037567 | -0.065118 | -0.12328 | -0.20083 | -0.26716 | -0.37736 | -0.48553 | -0.5743 | -0.79981 | -0.95696 | -1.1019 | -0.24573 | -0.31206 | -0.37838 | -0.459 | -0.53655 | -0.62532 | -0.73859 | -0.87736 | -1.0151 | -1.1396 | -1.5906 | -1.8702 | -1.9304
|  | PORTSOY | HT |  |  |  |  | -0.5692 | -0.61104 | -0.65593 | -0.7141 | -0.78553 | -0.87328 | -0.99981 | -1.1406 | -1.2621 | -1.4008 | -2.0314 | -2.3763 | -2.4447 | 0.021616 | 0.0042694 | -0.014098 | -0.034506 | -0.053894 | -0.085527 | -0.15696 | -0.24267 | -0.29675 | -0.37838 | -0.7243 | -0.87328 | -0.90287 | -0.2243 | -0.28757 | -0.35389 | -0.42736 | -0.49267 | -0.57124 | -0.68655 | -0.8141 | -0.92328 | -1.0488 | -1.5988 | -1.9019 | -1.961
|  | PORTSOY | HE |  |  |  |  | -0.56818 | -0.59369 | -0.62736 | -0.65593 | -0.68451 | -0.72022 | -0.79369 | -0.89165 | -0.97022 | -1.0651 | -1.6223 | -1.9733 | -2.1182 | 0.020596 | 0.0063102 | -0.012057 | -0.030424 | -0.045731 | -0.06818 | -0.095731 | -0.17022 | -0.21104 | -0.28144 | -0.62022 | -0.80798 | -0.97634 | -0.22226 | -0.259 | -0.30593 | -0.34165 | -0.37838 | -0.42736 | -0.50593 | -0.59573 | -0.66614 | -0.75491 | -1.2468 | -1.559 | -1.6896
|  | PORTSOY | CF |  |  |  |  | -0.56104 | -0.58144 | -0.59675 | -0.61614 | -0.64165 | -0.66614 | -0.68655 | -0.71818 | -0.74675 | -0.77736 | -1.0845 | -1.4468 | -1.7733 | 0.022637 | 0.013453 | 0.003249 | -0.0089959 | -0.025322 | -0.040629 | -0.052873 | -0.074302 | -0.10798 | -0.15389 | -0.41614 | -0.72124 | -1.1182 | -0.21104 | -0.23553 | -0.26002 | -0.28451 | -0.31614 | -0.34981 | -0.37634 | -0.4141 | -0.45185 | -0.49165 | -0.76104 | -1.0906 | -1.3804
| WOODHILL | QUEENS LANE NORTH | MINIMUM HEADROOM | NJ 92224 05823 | NO | NO | 0.614 | 1.4027 | 0.89246 | 0.31287 | -0.30244 | 16.0062 | 15.2797 | 14.342 | 13.3511 | 12.3695 | 11.492 | 7.0807 | 4.4175 | 3.893 | 5.0144 | 4.7205 | 4.3848 | 3.9726 | 19.592 | 19.0644 | 18.4164 | 17.7317 | 17.0491 | 16.4511 | 13.144 | 11.344 | 8.3848 | 3.3953 | 2.9289 | 2.4177 | 1.8657 | 17.8215 | 17.1246 | 16.2103 | 15.2991 | 14.3664 | 13.5368 | 9.3001 | 6.792 | 6.3134
|  | QUEENS LANE NORTH | EE |  |  |  |  | 1.4027 | 0.89246 | 0.31287 | -0.30244 | 16.0062 | 15.2797 | 14.342 | 13.3511 | 12.3695 | 11.492 | 7.4899 | 4.892 | 4.2246 | 5.0144 | 4.7205 | 4.3848 | 3.9726 | 19.592 | 19.0644 | 18.4164 | 17.7317 | 17.0491 | 16.4511 | 14.0287 | 12.1909 | 10.2501 | 3.3953 | 2.9289 | 2.4177 | 1.8657 | 17.8215 | 17.1246 | 16.2103 | 15.2991 | 14.3664 | 13.5368 | 9.7705 | 7.4777 | 6.8746
|  | QUEENS LANE NORTH | HT |  |  |  |  | 1.7241 | 1.368 | 0.95879 | 0.55062 | 17.0644 | 16.5562 | 15.7481 | 14.8083 | 13.896 | 12.9501 | 8.1838 | 4.7726 | 4.2715 | 5.2226 | 5.0307 | 4.8124 | 4.5899 | 20.4073 | 20.0471 | 19.5899 | 19.0246 | 18.4879 | 17.9185 | 15.3328 | 13.7389 | 13.5195 | 3.6259 | 3.2769 | 2.8871 | 2.5085 | 18.6083 | 18.1297 | 17.3889 | 16.5185 | 15.6766 | 14.7991 | 10.4511 | 7.3644 | 6.9226
|  | QUEENS LANE NORTH | HE |  |  |  |  | 1.6302 | 1.218 | 0.78022 | 0.30164 | 16.7185 | 16.0736 | 15.244 | 14.2083 | 13.2175 | 12.1644 | 7.0807 | 4.4175 | 3.893 | 5.1644 | 4.9164 | 4.6522 | 4.3624 | 20.0675 | 19.5828 | 18.9909 | 18.2409 | 17.5226 | 16.7583 | 13.144 | 11.344 | 10.4185 | 3.5728 | 3.2749 | 2.9402 | 2.4922 | 18.495 | 17.8726 | 17.0848 | 16.096 | 15.146 | 14.1379 | 9.3001 | 6.792 | 6.3134
|  | QUEENS LANE NORTH | CF |  |  |  |  | 1.7894 | 1.5608 | 1.2955 | 1.0037 | 17.6654 | 17.2991 | 16.8848 | 16.3379 | 15.8287 | 15.2736 | 11.8573 | 8.344 | 5.5593 | 5.2501 | 5.1052 | 4.9379 | 4.7511 | 20.6522 | 20.4011 | 20.0879 | 19.7205 | 19.3277 | 18.9042 | 16.3328 | 13.1491 | 8.3848 | 3.6851 | 3.5085 | 3.2953 | 3.0708 | 19.393 | 19.045 | 18.644 | 18.1175 | 17.6246 | 17.0899 | 13.8134 | 10.4583 | 7.8246
| THURSO | RACKWICK | MINIMUM HEADROOM | ND 20206 99857 | YES | NO | 0 | 0.076163 | 0.076163 | 0.06698 | 0.06698 | 0.059837 | 0.059837 | 0.058816 | 0.055755 | 0.056776 | 0.053714 | 0.048612 | 0.047592 | 0.047592 | 0.080429 | 0.079408 | 0.071245 | 0.071245 | 0.064102 | 0.064102 | 0.063082 | 0.063082 | 0.064102 | 0.064102 | 0.059 | 0.056959 | 0.053898 | 0.076765 | 0.076765 | 0.068602 | 0.067582 | 0.060439 | 0.057378 | 0.060439 | 0.057378 | 0.056357 | 0.053296 | 0.048194 | 0.047173 | 0.047173
|  | RACKWICK | EE |  |  |  |  | 0.076163 | 0.076163 | 0.06698 | 0.06698 | 0.059837 | 0.059837 | 0.062898 | 0.057796 | 0.057796 | 0.053714 | 0.048612 | 0.048612 | 0.047592 | 0.080429 | 0.079408 | 0.071245 | 0.071245 | 0.064102 | 0.064102 | 0.069204 | 0.067163 | 0.066143 | 0.064102 | 0.059 | 0.056959 | 0.055939 | 0.076765 | 0.076765 | 0.068602 | 0.067582 | 0.060439 | 0.057378 | 0.061459 | 0.057378 | 0.058398 | 0.053296 | 0.048194 | 0.048194 | 0.047173
|  | RACKWICK | HT |  |  |  |  | 0.083306 | 0.076163 | 0.074122 | 0.075143 | 0.068 | 0.06698 | 0.059837 | 0.055755 | 0.056776 | 0.061878 | 0.053714 | 0.047592 | 0.047592 | 0.087571 | 0.079408 | 0.078388 | 0.079408 | 0.072265 | 0.071245 | 0.064102 | 0.063082 | 0.064102 | 0.069204 | 0.061041 | 0.05798 | 0.05798 | 0.083908 | 0.076765 | 0.075745 | 0.075745 | 0.068602 | 0.067582 | 0.060439 | 0.058398 | 0.056357 | 0.06248 | 0.052276 | 0.047173 | 0.047173
|  | RACKWICK | HE |  |  |  |  | 0.083306 | 0.077184 | 0.076163 | 0.074122 | 0.06902 | 0.06698 | 0.058816 | 0.058816 | 0.058816 | 0.062898 | 0.053714 | 0.049633 | 0.049633 | 0.087571 | 0.080429 | 0.079408 | 0.078388 | 0.072265 | 0.071245 | 0.063082 | 0.063082 | 0.064102 | 0.069204 | 0.062061 | 0.05798 | 0.05798 | 0.083908 | 0.077786 | 0.076765 | 0.075745 | 0.068602 | 0.067582 | 0.060439 | 0.060439 | 0.057378 | 0.06248 | 0.052276 | 0.050235 | 0.050235
|  | RACKWICK | CF |  |  |  |  | 0.084327 | 0.084327 | 0.076163 | 0.075143 | 0.075143 | 0.068 | 0.068 | 0.065959 | 0.058816 | 0.058816 | 0.059837 | 0.055755 | 0.050653 | 0.087571 | 0.087571 | 0.080429 | 0.079408 | 0.079408 | 0.072265 | 0.072265 | 0.071245 | 0.064102 | 0.064102 | 0.067163 | 0.06002 | 0.053898 | 0.084929 | 0.084929 | 0.076765 | 0.075745 | 0.075745 | 0.068602 | 0.068602 | 0.067582 | 0.060439 | 0.060439 | 0.057378 | 0.053296 | 0.051255
| FORT WILLIAM | RAHOY | MINIMUM HEADROOM | NM 69621 49222 | YES | NO | 0 | 0.97449 | 0.97347 | 0.96531 | 0.96429 | 0.96122 | 0.9602 | 0.95714 | 0.94898 | 0.94592 | 0.9449 | 0.92857 | 0.92551 | 0.92245 | 0.98163 | 0.98061 | 0.97245 | 0.97143 | 0.97041 | 0.96939 | 0.96735 | 0.95918 | 0.95714 | 0.95612 | 0.94184 | 0.9398 | 0.93776 | 0.97959 | 0.97857 | 0.97041 | 0.96837 | 0.96735 | 0.96531 | 0.96327 | 0.95408 | 0.95204 | 0.95 | 0.93469 | 0.93163 | 0.92857
|  | RAHOY | EE |  |  |  |  | 0.97449 | 0.97347 | 0.96531 | 0.96429 | 0.96122 | 0.9602 | 0.95714 | 0.94898 | 0.94592 | 0.9449 | 0.93265 | 0.93061 | 0.93061 | 0.98163 | 0.98061 | 0.97245 | 0.97143 | 0.97041 | 0.96939 | 0.96735 | 0.95918 | 0.95714 | 0.95612 | 0.9449 | 0.94388 | 0.94388 | 0.97959 | 0.97857 | 0.97041 | 0.96837 | 0.96735 | 0.96531 | 0.96327 | 0.95408 | 0.95204 | 0.95 | 0.93878 | 0.93673 | 0.93673
|  | RAHOY | HT |  |  |  |  | 0.97449 | 0.97449 | 0.97347 | 0.97245 | 0.96429 | 0.96327 | 0.9602 | 0.95918 | 0.95714 | 0.94898 | 0.93265 | 0.92959 | 0.92857 | 0.98163 | 0.98163 | 0.98061 | 0.97959 | 0.97143 | 0.97143 | 0.96939 | 0.96837 | 0.96735 | 0.95918 | 0.9449 | 0.94286 | 0.94184 | 0.97959 | 0.97959 | 0.97857 | 0.97755 | 0.96837 | 0.96837 | 0.96531 | 0.96429 | 0.96327 | 0.95408 | 0.93878 | 0.93571 | 0.93469
|  | RAHOY | HE |  |  |  |  | 0.97449 | 0.97347 | 0.97347 | 0.97245 | 0.96429 | 0.96224 | 0.9602 | 0.95714 | 0.95612 | 0.94592 | 0.92857 | 0.92551 | 0.92245 | 0.98163 | 0.98061 | 0.98061 | 0.97959 | 0.97143 | 0.97041 | 0.96939 | 0.96735 | 0.96633 | 0.95714 | 0.94184 | 0.9398 | 0.93776 | 0.97959 | 0.97857 | 0.97857 | 0.97755 | 0.96837 | 0.96735 | 0.96531 | 0.96327 | 0.96122 | 0.95204 | 0.93469 | 0.93163 | 0.92857
|  | RAHOY | CF |  |  |  |  | 0.97449 | 0.97449 | 0.97449 | 0.97347 | 0.97245 | 0.96531 | 0.96429 | 0.96122 | 0.9602 | 0.95918 | 0.9449 | 0.92959 | 0.92653 | 0.98163 | 0.98163 | 0.98163 | 0.98061 | 0.97959 | 0.97245 | 0.97143 | 0.97041 | 0.96939 | 0.96837 | 0.95612 | 0.94286 | 0.94082 | 0.97959 | 0.97959 | 0.97959 | 0.97857 | 0.97755 | 0.97041 | 0.96837 | 0.96735 | 0.96531 | 0.96429 | 0.95 | 0.93571 | 0.93265
| INVERNESS | RAIGMORE | MINIMUM HEADROOM | NH 68427 44693 | NO | NO | 6.857 | 8.297 | 6.8131 | 5.1069 | 3.2681 | 1.1694 | -1.1953 | -3.6011 | -6.3847 | -8.8057 | -11.59 | -24.8726 | -31.0151 | -32.6337 | 8.7569 | 7.6183 | 6.3046 | 4.8909 | 3.2375 | 1.3417 | -0.51729 | -2.6389 | -4.6243 | -7.046 | -17.6137 | -22.9066 | -24.7704 | 5.6054 | 4.1792 | 2.5335 | 0.75782 | -1.2929 | -3.6243 | -5.9606 | -8.6456 | -11.0089 | -13.9044 | -26.9771 | -33.2683 | -35.1863
|  | RAIGMORE | EE |  |  |  |  | 8.297 | 6.8131 | 5.1069 | 3.2681 | 1.1694 | -1.1953 | -3.6011 | -6.3847 | -8.8057 | -10.9023 | -17.5998 | -19.6791 | -20.3592 | 8.7569 | 7.6183 | 6.3046 | 4.8909 | 3.2375 | 1.3417 | -0.51729 | -2.6389 | -4.5312 | -6.1471 | -11.374 | -13.5456 | -14.3188 | 5.6054 | 4.1792 | 2.5335 | 0.75782 | -1.2929 | -3.6243 | -5.9606 | -8.6456 | -11.0089 | -13.0437 | -19.5898 | -21.935 | -22.727
|  | RAIGMORE | HT |  |  |  |  | 9.0535 | 8.0601 | 6.8617 | 5.5293 | 4.2268 | 2.3851 | 0.76509 | -1.1939 | -2.996 | -4.8835 | -13.233 | -18.0111 | -19.5221 | 9.3675 | 8.6075 | 7.6287 | 6.5304 | 5.537 | 3.9628 | 2.7353 | 1.2389 | -0.12548 | -1.5691 | -8.0881 | -12.3966 | -14.1368 | 6.3369 | 5.3852 | 4.2007 | 2.8711 | 1.6151 | -0.2599 | -1.825 | -3.7188 | -5.4576 | -7.286 | -15.4452 | -20.447 | -22.2428
|  | RAIGMORE | HE |  |  |  |  | 8.8319 | 7.464 | 5.9551 | 4.1774 | 2.2413 | -0.29918 | -2.7452 | -5.7359 | -8.5508 | -11.59 | -24.8726 | -31.0151 | -32.6337 | 9.1688 | 8.1122 | 6.8972 | 5.4543 | 3.9371 | 1.8162 | -0.090049 | -2.4221 | -4.6243 | -7.046 | -17.6137 | -22.9066 | -24.7704 | 6.1216 | 4.8065 | 3.3226 | 1.5651 | -0.31756 | -2.8699 | -5.2527 | -8.1683 | -10.9144 | -13.9044 | -26.9771 | -33.2683 | -35.1863
|  | RAIGMORE | CF |  |  |  |  | 9.2167 | 8.4713 | 7.6057 | 6.6478 | 5.5001 | 4.1538 | 2.8276 | 1.1583 | -0.36448 | -2.004 | -11.1704 | -18.8489 | -22.5912 | 9.4939 | 8.9132 | 8.2386 | 7.4946 | 6.5762 | 5.48 | 4.4331 | 3.1257 | 1.9287 | 0.63591 | -6.4847 | -12.4341 | -15.3434 | 6.4932 | 5.7777 | 4.9427 | 4.0173 | 2.8919 | 1.5602 | 0.26598 | -1.3575 | -2.8428 | -4.4454 | -13.3445 | -20.802 | -24.4471
| ARBROATH | REDFORD | MINIMUM HEADROOM | NO 55879 44046 | YES | YES | 0.277 | -1.8742 | -1.964 | -2.0538 | -2.1579 | -2.2752 | -2.3599 | -2.5191 | -2.6997 | -2.8701 | -2.9752 | -3.4232 | -3.6814 | -3.7395 | -0.83339 | -0.89053 | -0.94564 | -1.013 | -1.0926 | -1.1426 | -1.2446 | -1.365 | -1.4773 | -1.5211 | -1.7691 | -1.9007 | -2.1711 | -1.4926 | -1.5762 | -1.662 | -1.7579 | -1.8691 | -1.9487 | -2.0967 | -2.266 | -2.4273 | -2.5211 | -2.9211 | -3.1181 | -3.1834
|  | REDFORD | EE |  |  |  |  | -1.8742 | -1.964 | -2.0538 | -2.1579 | -2.2752 | -2.3599 | -2.5191 | -2.6997 | -2.8701 | -2.9752 | -3.4232 | -3.6385 | -3.6803 | -0.83339 | -0.89053 | -0.94564 | -1.013 | -1.0926 | -1.1426 | -1.2446 | -1.365 | -1.4773 | -1.5211 | -1.7691 | -1.9007 | -2.0405 | -1.4926 | -1.5762 | -1.662 | -1.7579 | -1.8691 | -1.9487 | -2.0967 | -2.266 | -2.4273 | -2.5211 | -2.9211 | -3.0834 | -3.1222
|  | REDFORD | HT |  |  |  |  | -1.8538 | -1.9334 | -2.0181 | -2.114 | -2.1916 | -2.2875 | -2.4211 | -2.5365 | -2.6742 | -2.815 | -3.3814 | -3.6814 | -3.7395 | -0.80482 | -0.8436 | -0.89156 | -0.94972 | -0.98951 | -1.0436 | -1.1222 | -1.1834 | -1.265 | -1.3528 | -1.6793 | -1.813 | -1.8395 | -1.4579 | -1.5293 | -1.6079 | -1.6956 | -1.766 | -1.8558 | -1.9803 | -2.0803 | -2.2099 | -2.3416 | -2.8711 | -3.1181 | -3.1834
|  | REDFORD | HE |  |  |  |  | -1.8487 | -1.9007 | -1.9579 | -2.0222 | -2.0711 | -2.1375 | -2.2467 | -2.3303 | -2.4426 | -2.5569 | -3.1456 | -3.4242 | -3.5314 | -0.80176 | -0.83645 | -0.87727 | -0.92625 | -0.95788 | -1.0038 | -1.0773 | -1.1273 | -1.2018 | -1.2793 | -1.6507 | -1.8314 | -1.9854 | -1.4558 | -1.5058 | -1.562 | -1.6303 | -1.6783 | -1.7487 | -1.8507 | -1.9518 | -2.0589 | -2.1701 | -2.7548 | -3.0191 | -3.1385
|  | REDFORD | CF |  |  |  |  | -1.8273 | -1.865 | -1.9069 | -1.9569 | -1.9967 | -2.0497 | -2.1058 | -2.1803 | -2.2487 | -2.2803 | -2.6875 | -3.0558 | -3.3109 | -0.78849 | -0.81707 | -0.84666 | -0.88849 | -0.914 | -0.9589 | -1.0018 | -1.0579 | -1.114 | -1.1385 | -1.4701 | -1.8109 | -2.1711 | -1.4365 | -1.4722 | -1.515 | -1.5701 | -1.6038 | -1.6589 | -1.713 | -1.7824 | -1.8487 | -1.8793 | -2.2742 | -2.6436 | -2.9242
| BURGHMUIR | REDGORTON | MINIMUM HEADROOM | NO 07650 28860 | NO | YES | 3.659 | 5.4806 | 4.8683 | 4.1959 | 3.4071 | 2.5744 | 1.5846 | 0.68566 | -0.17353 | -0.80618 | -1.7205 | -5.0807 | -6.0296 | -6.1225 | 7.4836 | 7.1112 | 6.7152 | 6.253 | 5.7744 | 5.201 | 4.6561 | 4.1316 | 3.8295 | 3.2663 | 1.1469 | 0.55607 | -0.30006 | 6.7015 | 6.1658 | 5.5974 | 4.9188 | 4.1994 | 3.3372 | 2.5454 | 1.7821 | 1.2637 | 0.45964 | -2.4312 | -3.22 | -3.2995
|  | REDGORTON | EE |  |  |  |  | 5.4918 | 4.8683 | 4.1959 | 3.4071 | 2.5744 | 1.5846 | 0.68566 | -0.17353 | -0.71026 | -1.5348 | -5.0807 | -5.9123 | -5.9868 | 7.4959 | 7.1112 | 6.7152 | 6.253 | 5.7744 | 5.201 | 4.6561 | 4.1316 | 3.8591 | 3.355 | 1.1469 | 0.55607 | 0.103 | 6.7015 | 6.1658 | 5.5974 | 4.9188 | 4.1994 | 3.3372 | 2.5454 | 1.7821 | 1.3443 | 0.62188 | -2.4312 | -3.1108 | -3.1873
|  | REDGORTON | HT |  |  |  |  | 5.4806 | 4.8918 | 4.205 | 3.4336 | 2.6081 | 1.6112 | 0.86219 | 0.070351 | -0.80618 | -1.7205 | -4.9184 | -6.0296 | -6.1225 | 7.4836 | 7.1346 | 6.7326 | 6.2877 | 5.8255 | 5.2581 | 4.8357 | 4.3683 | 3.8295 | 3.2663 | 1.4601 | 0.91117 | 0.86015 | 6.7086 | 6.2107 | 5.6239 | 4.9556 | 4.2454 | 3.38 | 2.7382 | 2.0382 | 1.2637 | 0.45964 | -2.272 | -3.22 | -3.2995
|  | REDGORTON | HE |  |  |  |  | 5.5601 | 5.0357 | 4.4428 | 3.7601 | 3.0255 | 2.1367 | 1.3979 | 0.67749 | -0.087812 | -0.88475 | -4.3143 | -5.4001 | -5.5572 | 7.552 | 7.2193 | 6.8632 | 6.4591 | 6.0367 | 5.5214 | 5.0775 | 4.6367 | 4.1581 | 3.654 | 1.5367 | 0.82953 | 0.36627 | 6.7811 | 6.3392 | 5.8392 | 5.2494 | 4.6229 | 3.8515 | 3.2147 | 2.5831 | 1.9137 | 1.2168 | -1.724 | -2.6312 | -2.7649
|  | REDGORTON | CF |  |  |  |  | 5.802 | 5.3683 | 4.8897 | 4.3601 | 3.7887 | 3.1214 | 2.5785 | 2.0622 | 1.5204 | 0.94484 | -2.1031 | -4.3296 | -5.2205 | 7.7489 | 7.4826 | 7.1938 | 6.8846 | 6.5601 | 6.1765 | 5.8295 | 5.501 | 5.151 | 4.7795 | 2.7469 | 0.91525 | -0.30006 | 6.9974 | 6.6382 | 6.2443 | 5.8056 | 5.327 | 4.7566 | 4.2943 | 3.8515 | 3.3851 | 2.8892 | 0.26882 | -1.7159 | -2.4934
| REDMOSS | REDMOSS | MINIMUM HEADROOM | NJ 94562 01919 | NO | NO | 10.135 | 10.397 | 9.4684 | 7.6144 | 5.2358 | 3.7388 | -0.65606 | -2.1826 | -3.9408 | -5.6999 | -8.3632 | -18.1652 | -28.7999 | -38.5877 | 14.6807 | 13.9735 | 12.1939 | 9.7919 | 8.5939 | 3.9429 | 2.4654 | 0.53884 | -1.2091 | -4.0224 | -14.7193 | -26.9754 | -38.6591 | 13.6286 | 12.8031 | 10.8695 | 8.3133 | 6.9103 | 2.0001 | 0.51231 | -1.554 | -3.4305 | -6.3979 | -17.6122 | -30.3938 | -42.3499
|  | REDMOSS | EE |  |  |  |  | 11.4021 | 10.5144 | 8.3286 | 7.1195 | 5.0531 | 1.9052 | -0.12238 | -1.5765 | -3.6499 | -5.2275 | -10.6581 | -20.153 | -23.7959 | 16.0327 | 15.3939 | 13.1695 | 12.1888 | 10.2521 | 7.1654 | 5.345 | 4.2021 | 2.2174 | 0.79394 | -4.5581 | -15.6448 | -20.0469 | 14.948 | 14.1705 | 11.7695 | 10.647 | 8.5133 | 5.1572 | 3.1123 | 1.7348 | -0.46014 | -2.0724 | -7.9346 | -19.4479 | -23.9275
|  | REDMOSS | HT |  |  |  |  | 11.4868 | 9.4684 | 7.6144 | 5.2358 | 3.7388 | -0.65606 | -2.1826 | -3.6979 | -4.7856 | -6.1918 | -12.4591 | -23.6663 | -32.6877 | 16.048 | 13.9735 | 12.1939 | 9.7919 | 8.5939 | 3.9429 | 2.6848 | 1.4358 | 0.60619 | -0.5734 | -6.7805 | -19.8316 | -30.7938 | 15.0011 | 12.8031 | 10.8695 | 8.3133 | 6.9103 | 2.0001 | 0.51231 | -0.9734 | -1.9989 | -3.3897 | -10.2254 | -23.751 | -34.851
|  | REDMOSS | HE |  |  |  |  | 10.397 | 9.597 | 8.0582 | 5.9654 | 4.3011 | 0.19496 | -1.9489 | -3.9408 | -5.6999 | -8.3632 | -18.1652 | -28.7999 | -38.5877 | 14.6807 | 14.0786 | 12.6103 | 10.4776 | 8.947 | 4.498 | 2.4654 | 0.53884 | -1.2091 | -4.0224 | -14.7193 | -26.9754 | -38.6591 | 13.6286 | 12.9174 | 11.3225 | 9.0644 | 7.3939 | 2.7592 | 0.53986 | -1.554 | -3.4305 | -6.3979 | -17.6122 | -30.3938 | -42.3499
|  | REDMOSS | CF |  |  |  |  | 11.7776 | 11.2807 | 9.5511 | 8.9123 | 7.7297 | 5.9001 | 4.5082 | 3.1888 | 1.9766 | 0.5868 | -4.2744 | -8.7265 | -11.6642 | 16.2909 | 15.9205 | 14.0552 | 13.5929 | 12.4929 | 10.6246 | 9.2776 | 8.045 | 6.8582 | 5.4756 | 0.8766 | -3.255 | -5.9132 | 15.2664 | 14.8205 | 12.8674 | 12.3052 | 11.1103 | 9.1552 | 7.7307 | 6.4113 | 5.1817 | 3.7133 | -1.3254 | -5.9836 | -9.1224
| CASSLEY | RHICONICH | MINIMUM HEADROOM | NC 25554 52924 | YES | NO | 0.237 | -0.57278 | -0.62278 | -0.68094 | -0.75135 | -0.80339 | -0.88196 | -0.96461 | -1.0718 | -1.1748 | -1.2177 | -1.4187 | -1.4901 | -1.5095 | -0.33808 | -0.36971 | -0.40951 | -0.45441 | -0.4891 | -0.5391 | -0.59624 | -0.66461 | -0.73196 | -0.76053 | -0.90849 | -0.96461 | -1.134 | -0.53196 | -0.5789 | -0.634 | -0.70237 | -0.74931 | -0.82584 | -0.90543 | -1.0075 | -1.1064 | -1.1493 | -1.3422 | -1.4075 | -1.4258
|  | RHICONICH | EE |  |  |  |  | -0.57278 | -0.62278 | -0.68094 | -0.75135 | -0.80339 | -0.88196 | -0.96461 | -1.0718 | -1.1748 | -1.2177 | -1.4187 | -1.4513 | -1.4687 | -0.33808 | -0.36971 | -0.40951 | -0.45441 | -0.4891 | -0.5391 | -0.59624 | -0.66461 | -0.73196 | -0.76053 | -0.90849 | -0.96461 | -1.0544 | -0.53196 | -0.5789 | -0.634 | -0.70237 | -0.74931 | -0.82584 | -0.90543 | -1.0075 | -1.1064 | -1.1493 | -1.3422 | -1.3718 | -1.3901
|  | RHICONICH | HT |  |  |  |  | -0.54318 | -0.5891 | -0.6442 | -0.684 | -0.73604 | -0.79522 | -0.86971 | -0.92584 | -0.99931 | -1.0687 | -1.3534 | -1.4901 | -1.5095 | -0.31665 | -0.3442 | -0.37686 | -0.40033 | -0.43094 | -0.46971 | -0.51461 | -0.54829 | -0.59624 | -0.64012 | -0.8289 | -0.91359 | -0.92278 | -0.50339 | -0.54522 | -0.59727 | -0.634 | -0.68298 | -0.74114 | -0.81053 | -0.86665 | -0.93706 | -1.0024 | -1.2789 | -1.4075 | -1.4258
|  | RHICONICH | HE |  |  |  |  | -0.54318 | -0.57788 | -0.62584 | -0.65543 | -0.69216 | -0.74522 | -0.80543 | -0.84931 | -0.91461 | -0.97482 | -1.2993 | -1.385 | -1.4228 | -0.31767 | -0.33706 | -0.36869 | -0.39012 | -0.41563 | -0.44931 | -0.49114 | -0.52073 | -0.56665 | -0.60951 | -0.82584 | -0.91563 | -0.99931 | -0.50339 | -0.53298 | -0.57992 | -0.60951 | -0.64318 | -0.69318 | -0.75237 | -0.79522 | -0.85849 | -0.91767 | -1.2248 | -1.3064 | -1.3167
|  | RHICONICH | CF |  |  |  |  | -0.54012 | -0.57073 | -0.60237 | -0.62992 | -0.66971 | -0.69727 | -0.74012 | -0.79318 | -0.81257 | -0.86053 | -1.1054 | -1.2758 | -1.3881 | -0.31461 | -0.33196 | -0.35339 | -0.36971 | -0.39727 | -0.41665 | -0.44829 | -0.48706 | -0.50135 | -0.53502 | -0.73094 | -0.92278 | -1.134 | -0.49931 | -0.52788 | -0.55849 | -0.58298 | -0.62278 | -0.64727 | -0.69012 | -0.74012 | -0.76257 | -0.80543 | -1.0401 | -1.2054 | -1.3044
| DUDHOPE | ROSEBANK STREET | MINIMUM HEADROOM | NO 39943 31150 | NO | NO | 0.222 | 11.8147 | 11.3331 | 10.6188 | 9.4515 | 8.9576 | 6.9158 | 5.978 | 4.9688 | 3.7392 | 2.5892 | -2.9006 | -9.1618 | -14.1853 | 13.9984 | 13.7076 | 13.0505 | 11.9474 | 11.6627 | 9.478 | 8.7566 | 7.7627 | 6.8076 | 5.2076 | -1.5791 | -10.125 | -19.0179 | 12.4857 | 12.0193 | 11.2387 | 9.9326 | 9.4448 | 7.054 | 6.154 | 5.1775 | 4.1642 | 2.7357 | -4.0358 | -11.6031 | -18.0337
|  | ROSEBANK STREET | EE |  |  |  |  | 11.8147 | 11.3331 | 10.7617 | 10.0974 | 8.9964 | 7.5107 | 6.2903 | 5.2209 | 3.7392 | 2.5892 | -1.2434 | -5.6016 | -7.7516 | 13.9984 | 13.7076 | 13.3158 | 12.8954 | 11.8984 | 10.4341 | 9.4392 | 8.6811 | 7.377 | 6.4443 | 2.6433 | -4.7802 | -9.8557 | 12.4857 | 12.0193 | 11.4479 | 10.8061 | 9.6336 | 7.9897 | 6.7448 | 5.7183 | 4.1642 | 3.0051 | -0.91229 | -6.7174 | -9.447
|  | ROSEBANK STREET | HT |  |  |  |  | 11.9576 | 11.4943 | 10.6188 | 9.4515 | 8.9576 | 6.9158 | 5.978 | 4.9688 | 4.0586 | 2.9882 | -2.3169 | -8.9679 | -13.974 | 14.129 | 13.8515 | 13.0505 | 11.9474 | 11.6627 | 9.478 | 8.8698 | 8.2035 | 7.6433 | 6.8964 | 2.5331 | -5.6097 | -11.9995 | 12.6489 | 12.2112 | 11.2387 | 9.9326 | 9.4448 | 7.054 | 6.154 | 5.1775 | 4.3204 | 3.2714 | -2.2235 | -10.3786 | -16.6796
|  | ROSEBANK STREET | HE |  |  |  |  | 11.9658 | 11.7494 | 11.0811 | 10.1933 | 9.6423 | 7.8198 | 6.8301 | 5.728 | 4.675 | 3.1015 | -2.9006 | -9.1618 | -14.1853 | 14.1137 | 13.9535 | 13.2311 | 12.277 | 11.7443 | 9.6372 | 8.7566 | 7.7627 | 6.8076 | 5.2076 | -1.5791 | -10.125 | -19.0179 | 12.6581 | 12.4377 | 11.6724 | 10.6346 | 9.9959 | 7.8142 | 6.7693 | 5.6061 | 4.4908 | 2.7357 | -4.0358 | -11.6031 | -18.0337
|  | ROSEBANK STREET | CF |  |  |  |  | 12.0668 | 11.9535 | 11.8127 | 11.6045 | 11.1831 | 10.5076 | 10.0545 | 9.5852 | 9.1311 | 8.5852 | 6.0474 | 3.3372 | 0.47699 | 14.1637 | 14.0484 | 13.9076 | 13.6964 | 13.2056 | 12.3943 | 11.8596 | 11.3015 | 10.7464 | 10.075 | 6.8678 | 2.2923 | -4.4812 | 12.7561 | 12.6336 | 12.4846 | 12.2724 | 11.7693 | 10.9377 | 10.4234 | 9.9102 | 9.4091 | 8.7959 | 6.101 | 3.352 | 0.57444
| KEITH 2 | ROTHES | MINIMUM HEADROOM | NJ 27901 49693 | NO | YES | 1.693 | 0.31217 | 0.18666 | 0.056045 | -0.091914 | -0.24702 | -0.38987 | -0.57763 | -0.78273 | -0.97661 | -1.1389 | -1.7195 | -1.9746 | -2.0786 | 1.9081 | 1.804 | 1.704 | 1.5999 | 1.4918 | 1.3948 | 1.2703 | 1.1316 | 1.004 | 0.89686 | 0.52849 | 0.34584 | 0.254 | 1.2816 | 1.1622 | 1.0316 | 0.88768 | 0.74176 | 0.61217 | 0.43258 | 0.24074 | 0.057065 | -0.092935 | -0.63375 | -0.86844 | -0.97253
|  | ROTHES | EE |  |  |  |  | 0.31217 | 0.18666 | 0.056045 | -0.091914 | -0.24702 | -0.38987 | -0.57763 | -0.78273 | -0.97661 | -1.1389 | -1.7195 | -1.9031 | -1.9338 | 1.9081 | 1.804 | 1.704 | 1.5999 | 1.4918 | 1.3948 | 1.2703 | 1.1316 | 1.004 | 0.89686 | 0.52849 | 0.43462 | 0.41727 | 1.2816 | 1.1622 | 1.0316 | 0.88768 | 0.74176 | 0.61217 | 0.43258 | 0.24074 | 0.057065 | -0.092935 | -0.63375 | -0.79804 | -0.82559
|  | ROTHES | HT |  |  |  |  | 0.32747 | 0.21421 | 0.10094 | -0.035792 | -0.14906 | -0.27559 | -0.42967 | -0.60518 | -0.77967 | -0.95008 | -1.6491 | -1.9746 | -2.0786 | 1.9183 | 1.8275 | 1.7356 | 1.6418 | 1.5683 | 1.4846 | 1.3846 | 1.2693 | 1.1601 | 1.0458 | 0.58156 | 0.38564 | 0.31217 | 1.2969 | 1.1918 | 1.0724 | 0.94482 | 0.8387 | 0.71931 | 0.57543 | 0.41013 | 0.25298 | 0.089718 | -0.56742 | -0.86844 | -0.96844
|  | ROTHES | HE |  |  |  |  | 0.34278 | 0.23666 | 0.1387 | 0.025433 | -0.087833 | -0.20518 | -0.36232 | -0.53375 | -0.70008 | -0.86538 | -1.6368 | -1.9368 | -2.0756 | 1.9336 | 1.8448 | 1.7632 | 1.6734 | 1.5928 | 1.5071 | 1.3999 | 1.2765 | 1.1642 | 1.0479 | 0.52849 | 0.34584 | 0.254 | 1.3122 | 1.2142 | 1.1162 | 0.9989 | 0.8938 | 0.78156 | 0.6336 | 0.47033 | 0.31829 | 0.16013 | -0.56742 | -0.84293 | -0.97253
|  | ROTHES | CF |  |  |  |  | 0.39584 | 0.33768 | 0.27339 | 0.21013 | 0.13666 | 0.063188 | -0.026608 | -0.13885 | -0.24191 | -0.34089 | -0.95518 | -1.4991 | -1.8786 | 1.9856 | 1.9326 | 1.8775 | 1.8234 | 1.7652 | 1.7122 | 1.6458 | 1.5642 | 1.4867 | 1.4162 | 0.97339 | 0.59788 | 0.35911 | 1.3642 | 1.3071 | 1.2448 | 1.1816 | 1.1071 | 1.0367 | 0.9489 | 0.84482 | 0.74686 | 0.65502 | 0.072371 | -0.44089 | -0.79498
| DUNOON | ROTHESAY | MINIMUM HEADROOM | NS 08636 64647 | NO | YES | 0.54 | 9.7837 | 9.5653 | 9.2949 | 9.0245 | 8.7072 | 8.3776 | 7.8837 | 7.3174 | 6.7725 | 6.2714 | 4.0908 | 2.3531 | 2.0704 | 10.4592 | 10.3378 | 10.1857 | 10.0296 | 9.8408 | 9.6429 | 9.3776 | 9.0419 | 8.7225 | 8.4378 | 7.2408 | 6.3908 | 5.6908 | 10.2434 | 10.0393 | 9.7934 | 9.5434 | 9.2495 | 8.9322 | 8.4832 | 7.9526 | 7.4475 | 6.9852 | 4.9903 | 3.5169 | 3.2679
|  | ROTHESAY | EE |  |  |  |  | 9.7837 | 9.5653 | 9.2949 | 9.0245 | 8.7072 | 8.3776 | 7.8837 | 7.3174 | 6.7725 | 6.2714 | 4.0908 | 2.5092 | 2.1235 | 10.4592 | 10.3378 | 10.1857 | 10.0296 | 9.8408 | 9.6429 | 9.3776 | 9.0419 | 8.7225 | 8.4378 | 7.2408 | 6.3908 | 5.6908 | 10.2434 | 10.0393 | 9.7934 | 9.5434 | 9.2495 | 8.9322 | 8.4832 | 7.9526 | 7.4475 | 6.9852 | 4.9903 | 3.6709 | 3.3199
|  | ROTHESAY | HT |  |  |  |  | 9.8827 | 9.6908 | 9.4684 | 9.2153 | 8.9735 | 8.7408 | 8.2857 | 7.7847 | 7.2857 | 6.8245 | 4.1204 | 2.3531 | 2.0704 | 10.5245 | 10.4255 | 10.3102 | 10.1776 | 10.0429 | 9.9163 | 9.6878 | 9.4235 | 9.1714 | 8.947 | 7.5776 | 6.7796 | 6.6674 | 10.3332 | 10.1536 | 9.9536 | 9.7189 | 9.4964 | 9.2791 | 8.8556 | 8.3913 | 7.9362 | 7.5138 | 5.0577 | 3.5169 | 3.2679
|  | ROTHESAY | HE |  |  |  |  | 9.8745 | 9.751 | 9.6051 | 9.4266 | 9.2551 | 9.0643 | 8.7561 | 8.3939 | 8.047 | 7.7439 | 5.7806 | 4.3817 | 3.9072 | 10.5184 | 10.4439 | 10.3592 | 10.2521 | 10.1419 | 10.0245 | 9.8551 | 9.6459 | 9.4459 | 9.2755 | 8.0939 | 7.2439 | 6.549 | 10.326 | 10.2107 | 10.0781 | 9.9169 | 9.7597 | 9.5842 | 9.3016 | 8.9638 | 8.6413 | 8.3577 | 6.5281 | 5.3362 | 4.9383
|  | ROTHESAY | CF |  |  |  |  | 9.9123 | 9.8449 | 9.7612 | 9.6755 | 9.5663 | 9.448 | 9.3051 | 9.1725 | 9.0255 | 8.8694 | 7.9 | 6.6949 | 5.6225 | 10.5398 | 10.4888 | 10.4327 | 10.3755 | 10.2959 | 10.2061 | 10.1 | 9.9949 | 9.8817 | 9.7582 | 8.9572 | 7.747 | 6.1837 | 10.3648 | 10.2985 | 10.2209 | 10.1424 | 10.0434 | 9.9362 | 9.8026 | 9.6771 | 9.5362 | 9.3873 | 8.4679 | 7.3485 | 6.3771
| THURSO | ROUSAY | MINIMUM HEADROOM | HY 43876 30573 | YES | NO | 0 | 0.37959 | 0.36531 | 0.34898 | 0.33673 | 0.31633 | 0.30918 | 0.28776 | 0.26735 | 0.24184 | 0.21939 | 0.16122 | 0.14796 | 0.14082 | 0.67143 | 0.66122 | 0.64796 | 0.63878 | 0.62041 | 0.61531 | 0.59694 | 0.57959 | 0.56224 | 0.54796 | 0.50918 | 0.49796 | 0.47551 | 0.45204 | 0.43673 | 0.41837 | 0.40714 | 0.38265 | 0.37143 | 0.34388 | 0.32245 | 0.29694 | 0.27551 | 0.21837 | 0.20204 | 0.19694
|  | ROUSAY | EE |  |  |  |  | 0.37959 | 0.36531 | 0.34898 | 0.33673 | 0.31633 | 0.30918 | 0.28776 | 0.26735 | 0.24184 | 0.21939 | 0.16122 | 0.15306 | 0.14694 | 0.67143 | 0.66122 | 0.64796 | 0.63878 | 0.62041 | 0.61531 | 0.59694 | 0.57959 | 0.56224 | 0.54796 | 0.50918 | 0.49796 | 0.48163 | 0.45204 | 0.43673 | 0.41837 | 0.40714 | 0.38265 | 0.37143 | 0.34388 | 0.32245 | 0.29694 | 0.27551 | 0.21837 | 0.20918 | 0.2051
|  | ROUSAY | HT |  |  |  |  | 0.38469 | 0.37653 | 0.36633 | 0.35816 | 0.34184 | 0.33265 | 0.31633 | 0.30816 | 0.29082 | 0.26735 | 0.18163 | 0.14796 | 0.14082 | 0.67755 | 0.67143 | 0.66122 | 0.65408 | 0.64286 | 0.63367 | 0.61837 | 0.61327 | 0.59796 | 0.58163 | 0.52449 | 0.50306 | 0.50102 | 0.45918 | 0.44694 | 0.43469 | 0.42551 | 0.40918 | 0.39388 | 0.37449 | 0.36122 | 0.34082 | 0.31735 | 0.23571 | 0.20204 | 0.19694
|  | ROUSAY | HE |  |  |  |  | 0.38469 | 0.37857 | 0.36735 | 0.3602 | 0.34592 | 0.33878 | 0.32245 | 0.31633 | 0.29796 | 0.27959 | 0.19388 | 0.17143 | 0.16837 | 0.67755 | 0.67143 | 0.66224 | 0.65714 | 0.64592 | 0.63878 | 0.62653 | 0.62041 | 0.60612 | 0.59082 | 0.53061 | 0.51327 | 0.49796 | 0.45918 | 0.44898 | 0.43878 | 0.42959 | 0.41633 | 0.40408 | 0.38571 | 0.37551 | 0.35714 | 0.33571 | 0.24898 | 0.22653 | 0.22245
|  | ROUSAY | CF |  |  |  |  | 0.38061 | 0.38265 | 0.37755 | 0.36837 | 0.36224 | 0.34898 | 0.34388 | 0.33163 | 0.31939 | 0.31837 | 0.25612 | 0.18776 | 0.16531 | 0.67449 | 0.67347 | 0.66939 | 0.66224 | 0.6551 | 0.6449 | 0.64082 | 0.62959 | 0.61837 | 0.61837 | 0.56837 | 0.50816 | 0.47551 | 0.4551 | 0.45408 | 0.4449 | 0.43571 | 0.42959 | 0.41327 | 0.40816 | 0.39184 | 0.37857 | 0.37653 | 0.31224 | 0.24592 | 0.22041
| CRAIGIEBUCKLER | RUTHRIESTON | MINIMUM HEADROOM | NJ 92574 04060 | NO | NO | 1.675 | 14.0432 | 13.6901 | 13.2677 | 12.8646 | 12.3942 | 11.9003 | 11.4452 | 10.6442 | 9.8667 | 9.1401 | 5.9432 | 3.6983 | 3.3238 | 15.6779 | 15.4779 | 15.2269 | 14.9901 | 14.7024 | 14.3911 | 14.2075 | 13.7442 | 13.2962 | 12.886 | 11.0942 | 9.5973 | 7.5064 | 14.836 | 14.5105 | 14.1177 | 13.7422 | 13.3024 | 12.834 | 12.4422 | 11.7024 | 10.9881 | 10.3258 | 7.484 | 5.4544 | 5.1238
|  | RUTHRIESTON | EE |  |  |  |  | 14.0432 | 13.6901 | 13.2677 | 12.8646 | 12.3942 | 11.9003 | 11.4452 | 10.6442 | 9.8667 | 9.1401 | 6.0156 | 3.8973 | 3.3697 | 15.6779 | 15.4779 | 15.2269 | 14.9901 | 14.7024 | 14.3911 | 14.2075 | 13.7442 | 13.2962 | 12.886 | 11.0942 | 9.5973 | 8.0911 | 14.836 | 14.5105 | 14.1177 | 13.7422 | 13.3024 | 12.834 | 12.4422 | 11.7024 | 10.9881 | 10.3258 | 7.5228 | 5.6381 | 5.1687
|  | RUTHRIESTON | HT |  |  |  |  | 14.1585 | 13.8299 | 13.4575 | 13.1126 | 12.7136 | 12.3238 | 11.5932 | 10.8075 | 10.032 | 9.6095 | 5.9432 | 3.6983 | 3.3238 | 15.7748 | 15.6136 | 15.4207 | 15.2432 | 15.0309 | 14.8299 | 14.4728 | 14.0789 | 13.6911 | 13.5697 | 11.7738 | 10.7432 | 10.582 | 14.8881 | 14.6534 | 14.3136 | 13.9942 | 13.6248 | 13.2677 | 12.6013 | 11.883 | 11.1718 | 10.8156 | 7.484 | 5.4544 | 5.1238
|  | RUTHRIESTON | HE |  |  |  |  | 14.1595 | 13.9707 | 13.7462 | 13.5473 | 13.2952 | 13.0677 | 12.585 | 12.0462 | 11.5279 | 11.3575 | 8.4962 | 6.4064 | 5.6391 | 15.7605 | 15.6422 | 15.4891 | 15.3524 | 15.1809 | 15.0258 | 14.7462 | 14.4269 | 14.1136 | 14.0564 | 12.2289 | 10.6769 | 9.1064 | 14.8871 | 14.7799 | 14.5656 | 14.3799 | 14.1422 | 13.9258 | 13.4809 | 12.982 | 12.5003 | 12.3656 | 9.7595 | 7.9013 | 7.2269
|  | RUTHRIESTON | CF |  |  |  |  | 14.2462 | 14.1401 | 14.0105 | 13.8983 | 13.7483 | 13.585 | 13.4371 | 13.2126 | 13.0054 | 12.783 | 11.5962 | 9.6513 | 7.7952 | 15.8024 | 15.7126 | 15.6044 | 15.5013 | 15.3728 | 15.2258 | 15.084 | 14.8748 | 14.6809 | 14.4707 | 13.2738 | 10.9401 | 7.5064 | 14.9269 | 14.8779 | 14.8054 | 14.7003 | 14.5544 | 14.3973 | 14.2554 | 14.0381 | 13.8381 | 13.6279 | 12.532 | 10.7513 | 9.1003
| TAYNUILT | SALEN | MINIMUM HEADROOM | NM 57252 42849 | NO | YES | 1.069 | 5.5984 | 5.5494 | 5.48 | 5.3841 | 5.2606 | 5.1351 | 5.0126 | 4.9075 | 4.8086 | 4.7565 | 4.5382 | 4.4606 | 4.4453 | 6.1851 | 6.1565 | 6.1106 | 6.0565 | 5.9851 | 5.9167 | 5.8443 | 5.7729 | 5.7096 | 5.678 | 5.5096 | 5.4402 | 5.2188 | 5.8586 | 5.8157 | 5.7504 | 5.6678 | 5.5596 | 5.4545 | 5.3412 | 5.2422 | 5.1473 | 5.0994 | 4.8933 | 4.8188 | 4.8065
|  | SALEN | EE |  |  |  |  | 5.5984 | 5.5494 | 5.48 | 5.3841 | 5.2606 | 5.1351 | 5.0126 | 4.9075 | 4.8086 | 4.7565 | 4.5382 | 4.5024 | 4.478 | 6.1851 | 6.1565 | 6.1106 | 6.0565 | 5.9851 | 5.9167 | 5.8443 | 5.7729 | 5.7096 | 5.678 | 5.5096 | 5.4402 | 5.3382 | 5.8586 | 5.8157 | 5.7504 | 5.6678 | 5.5596 | 5.4545 | 5.3412 | 5.2422 | 5.1473 | 5.0994 | 4.8933 | 4.8616 | 4.8351
|  | SALEN | HT |  |  |  |  | 5.6259 | 5.58 | 5.5208 | 5.4422 | 5.3463 | 5.2126 | 5.1035 | 5.0433 | 4.9606 | 4.8882 | 4.5973 | 4.4606 | 4.4453 | 6.2045 | 6.179 | 6.1443 | 6.1014 | 6.0514 | 5.979 | 5.9167 | 5.88 | 5.829 | 5.7831 | 5.5892 | 5.4984 | 5.4902 | 5.8871 | 5.8494 | 5.7963 | 5.7331 | 5.6514 | 5.531 | 5.432 | 5.3759 | 5.2984 | 5.231 | 4.9484 | 4.8188 | 4.8065
|  | SALEN | HE |  |  |  |  | 5.6269 | 5.5882 | 5.5382 | 5.4688 | 5.3841 | 5.2565 | 5.1514 | 5.0994 | 5.028 | 4.9647 | 4.6596 | 4.5769 | 4.5647 | 6.2055 | 6.182 | 6.1484 | 6.1116 | 6.0637 | 5.9943 | 5.932 | 5.8963 | 5.8545 | 5.8086 | 5.5922 | 5.4953 | 5.4024 | 5.8882 | 5.8555 | 5.8075 | 5.7504 | 5.68 | 5.5708 | 5.478 | 5.429 | 5.3606 | 5.2994 | 5.0137 | 4.931 | 4.9208
|  | SALEN | CF |  |  |  |  | 5.629 | 5.5984 | 5.5688 | 5.5096 | 5.432 | 5.3504 | 5.2769 | 5.2198 | 5.1902 | 5.1371 | 4.8657 | 4.6739 | 4.5494 | 6.2075 | 6.1912 | 6.1678 | 6.1371 | 6.0912 | 6.0463 | 6.0024 | 5.9606 | 5.9392 | 5.8984 | 5.6861 | 5.4718 | 5.2188 | 5.8892 | 5.8626 | 5.83 | 5.781 | 5.7157 | 5.6453 | 5.579 | 5.5259 | 5.5004 | 5.4494 | 5.1984 | 5.0218 | 4.9055
| FORT WILLIAM | SALEN 2 | MINIMUM HEADROOM | NM 69002 65519 | YES | NO | 0.335 | 0.31055 | 0.96565 | 0.90544 | 0.8534 | 0.78708 | 0.7381 | 0.65544 | 0.56769 | 0.47993 | 0.40136 | 0.24524 | 0.16769 | 0.15034 | 0.87636 | 1.7728 | 1.7361 | 1.7014 | 1.6534 | 1.6259 | 1.5697 | 1.5136 | 1.4534 | 1.4024 | 1.2983 | 1.2463 | 1.0891 | 0.63172 | 1.4034 | 1.3493 | 1.3003 | 1.2401 | 1.1942 | 1.1177 | 1.033 | 0.95136 | 0.87789 | 0.73198 | 0.66259 | 0.64728
|  | SALEN 2 | EE |  |  |  |  | 0.31055 | 0.96565 | 0.90544 | 0.8534 | 0.78708 | 0.7381 | 0.65544 | 0.56769 | 0.47993 | 0.40136 | 0.24524 | 0.20749 | 0.18606 | 0.87636 | 1.7728 | 1.7361 | 1.7014 | 1.6534 | 1.6259 | 1.5697 | 1.5136 | 1.4534 | 1.4024 | 1.2983 | 1.2463 | 1.1667 | 0.63172 | 1.4034 | 1.3493 | 1.3003 | 1.2401 | 1.1942 | 1.1177 | 1.033 | 0.95136 | 0.87789 | 0.73198 | 0.6983 | 0.67789
|  | SALEN 2 | HT |  |  |  |  | 0.33402 | 0.99014 | 0.94728 | 0.90749 | 0.85544 | 0.80953 | 0.74626 | 0.69116 | 0.62483 | 0.55442 | 0.25953 | 0.16769 | 0.15034 | 0.89269 | 1.7922 | 1.7687 | 1.7483 | 1.7136 | 1.6871 | 1.6452 | 1.6126 | 1.5708 | 1.5259 | 1.332 | 1.284 | 1.2769 | 0.65417 | 1.4259 | 1.3861 | 1.3493 | 1.3024 | 1.2585 | 1.2024 | 1.1514 | 1.0881 | 1.0238 | 0.74626 | 0.66259 | 0.64728
|  | SALEN 2 | HE |  |  |  |  | 0.32891 | 0.9983 | 0.96361 | 0.93402 | 0.89218 | 0.85851 | 0.79932 | 0.75647 | 0.69728 | 0.63606 | 0.31871 | 0.26871 | 0.25544 | 0.89269 | 1.7932 | 1.7718 | 1.7544 | 1.7228 | 1.7014 | 1.6616 | 1.6361 | 1.5952 | 1.5503 | 1.3381 | 1.284 | 1.2146 | 0.65315 | 1.434 | 1.4034 | 1.3748 | 1.335 | 1.3024 | 1.2524 | 1.2095 | 1.1565 | 1.0983 | 0.80238 | 0.75953 | 0.74626
|  | SALEN 2 | CF |  |  |  |  | 0.33708 | 1.0126 | 0.98606 | 0.94932 | 0.92891 | 0.89116 | 0.86361 | 0.81973 | 0.77687 | 0.75749 | 0.54014 | 0.37891 | 0.26463 | 0.89269 | 1.8024 | 1.7861 | 1.7605 | 1.7493 | 1.7228 | 1.7024 | 1.6697 | 1.6381 | 1.6228 | 1.4473 | 1.2789 | 1.0891 | 0.65621 | 1.4452 | 1.4218 | 1.3881 | 1.3677 | 1.333 | 1.3095 | 1.2687 | 1.2299 | 1.2095 | 1.0095 | 0.85544 | 0.75749
| THURSO | SANDAY | MINIMUM HEADROOM | HY 61184 35797 | YES | NO | 0.03 | 0.28716 | 0.26267 | 0.22593 | 0.20247 | 0.16369 | 0.13614 | 0.086139 | 0.056547 | 0.0085878 | -0.033249 | -0.12202 | -0.15264 | -0.15876 | 0.46879 | 0.45553 | 0.43206 | 0.41879 | 0.39124 | 0.37389 | 0.3392 | 0.32083 | 0.28614 | 0.25655 | 0.19634 | 0.16777 | 0.085118 | 0.39634 | 0.37185 | 0.3341 | 0.31369 | 0.27389 | 0.24736 | 0.20042 | 0.17185 | 0.12491 | 0.084098 | 0.0034857 | -0.023045 | -0.030188
|  | SANDAY | EE |  |  |  |  | 0.28716 | 0.26267 | 0.22593 | 0.20247 | 0.16369 | 0.13614 | 0.086139 | 0.056547 | 0.0085878 | -0.033249 | -0.12202 | -0.13733 | -0.14651 | 0.46879 | 0.45553 | 0.43206 | 0.41879 | 0.39124 | 0.37389 | 0.3392 | 0.32083 | 0.28614 | 0.25655 | 0.19634 | 0.16777 | 0.12389 | 0.39634 | 0.37185 | 0.3341 | 0.31369 | 0.27389 | 0.24736 | 0.20042 | 0.17185 | 0.12491 | 0.084098 | 0.0034857 | -0.0097796 | -0.017943
|  | SANDAY | HT |  |  |  |  | 0.29838 | 0.279 | 0.25247 | 0.23002 | 0.1994 | 0.18002 | 0.14532 | 0.11471 | 0.080016 | 0.03818 | -0.089371 | -0.15264 | -0.15876 | 0.47798 | 0.46675 | 0.45144 | 0.4392 | 0.42185 | 0.41063 | 0.39124 | 0.37491 | 0.3494 | 0.32083 | 0.23512 | 0.19736 | 0.1943 | 0.40859 | 0.39022 | 0.36267 | 0.34226 | 0.31165 | 0.29226 | 0.25859 | 0.23206 | 0.19532 | 0.15655 | 0.034098 | -0.023045 | -0.030188
|  | SANDAY | HE |  |  |  |  | 0.29838 | 0.2841 | 0.26165 | 0.24532 | 0.22083 | 0.20757 | 0.17696 | 0.15144 | 0.11879 | 0.086139 | -0.066922 | -0.099576 | -0.10366 | 0.47798 | 0.46981 | 0.45655 | 0.44736 | 0.42798 | 0.42083 | 0.40247 | 0.3841 | 0.36165 | 0.33512 | 0.2341 | 0.19736 | 0.15757 | 0.40859 | 0.3943 | 0.37287 | 0.35553 | 0.33104 | 0.31879 | 0.28716 | 0.26267 | 0.23206 | 0.19838 | 0.053486 | 0.024914 | 0.018792
|  | SANDAY | CF |  |  |  |  | 0.30349 | 0.28614 | 0.27389 | 0.25757 | 0.23716 | 0.21675 | 0.20859 | 0.1841 | 0.16063 | 0.14838 | 0.048384 | -0.046514 | -0.095494 | 0.48002 | 0.47083 | 0.46267 | 0.45247 | 0.4392 | 0.42696 | 0.41879 | 0.40042 | 0.38308 | 0.37389 | 0.28818 | 0.18614 | 0.085118 | 0.41267 | 0.39838 | 0.38512 | 0.37185 | 0.35042 | 0.329 | 0.32185 | 0.29838 | 0.27389 | 0.26267 | 0.16267 | 0.070833 | 0.025935
| DUNOON | SANDBANK | MINIMUM HEADROOM | NS 15274 81386 | NO | YES | 0.301 | 4.2549 | 4.157 | 4.0559 | 3.9274 | 3.7763 | 3.6457 | 3.4253 | 3.2008 | 3.0284 | 2.8212 | 2.2284 | 1.9457 | 1.8886 | 5.1008 | 5.0325 | 4.9692 | 4.8896 | 4.7906 | 4.7141 | 4.5825 | 4.4376 | 4.3396 | 4.2182 | 3.8712 | 3.6774 | 3.2437 | 4.6927 | 4.5947 | 4.4957 | 4.3794 | 4.2386 | 4.1192 | 3.9151 | 3.7029 | 3.5437 | 3.3508 | 2.811 | 2.5508 | 2.4998
|  | SANDBANK | EE |  |  |  |  | 4.2549 | 4.157 | 4.0559 | 3.9274 | 3.7763 | 3.6457 | 3.4253 | 3.2008 | 3.0284 | 2.8212 | 2.2284 | 2.01 | 1.9365 | 5.1008 | 5.0325 | 4.9692 | 4.8896 | 4.7906 | 4.7141 | 4.5825 | 4.4376 | 4.3396 | 4.2182 | 3.8712 | 3.6774 | 3.4202 | 4.6927 | 4.5947 | 4.4957 | 4.3794 | 4.2386 | 4.1192 | 3.9151 | 3.7029 | 3.5437 | 3.3508 | 2.811 | 2.6141 | 2.5457
|  | SANDBANK | HT |  |  |  |  | 4.307 | 4.2263 | 4.1263 | 4.011 | 3.9039 | 3.7712 | 3.5988 | 3.4447 | 3.2467 | 3.0365 | 2.3131 | 1.9457 | 1.8886 | 5.1345 | 5.0906 | 5.0355 | 4.9661 | 4.909 | 4.8325 | 4.7325 | 4.6498 | 4.5386 | 4.4151 | 3.9978 | 3.8121 | 3.7855 | 4.7355 | 4.6529 | 4.561 | 4.4559 | 4.358 | 4.2386 | 4.0825 | 3.9406 | 3.7631 | 3.5712 | 2.8916 | 2.5508 | 2.4998
|  | SANDBANK | HE |  |  |  |  | 4.307 | 4.2498 | 4.1825 | 4.1008 | 4.0253 | 3.9172 | 3.7621 | 3.6376 | 3.4743 | 3.3172 | 2.6172 | 2.3263 | 2.2416 | 5.1314 | 5.0978 | 5.0559 | 4.9978 | 4.9518 | 4.8855 | 4.7927 | 4.7202 | 4.6212 | 4.5202 | 4.0865 | 3.8427 | 3.5988 | 4.7355 | 4.6784 | 4.6161 | 4.5406 | 4.4712 | 4.3753 | 4.2355 | 4.1192 | 3.9692 | 3.8233 | 3.1712 | 2.907 | 2.8335
|  | SANDBANK | CF |  |  |  |  | 4.3223 | 4.2794 | 4.2294 | 4.1682 | 4.1212 | 4.0518 | 3.9784 | 3.8784 | 3.7886 | 3.7141 | 3.1712 | 2.7314 | 2.41 | 5.1406 | 5.1172 | 5.0896 | 5.0437 | 5.0141 | 4.9651 | 4.9131 | 4.8406 | 4.7763 | 4.7284 | 4.2978 | 3.8314 | 3.2437 | 4.7488 | 4.71 | 4.6621 | 4.607 | 4.5631 | 4.4988 | 4.4314 | 4.3406 | 4.2549 | 4.1876 | 3.6784 | 3.2651 | 2.9733
| SHETLAND | SANDWICK | MINIMUM HEADROOM | HU4308625957 | YES | YES | 0.123 | 0.43265 | 0.36531 | 0.29286 | 4.9631 | 4.8722 | 4.7651 | 4.6784 | 4.5386 | 4.41 | 4.2957 | 4.0651 | 3.9682 | 3.9488 | 1.7184 | 1.6684 | 1.6204 | 5.912 | 5.8427 | 5.761 | 5.7008 | 5.5916 | 5.4906 | 5.4049 | 5.211 | 5.1018 | 4.6855 | 1.0051 | 0.9398 | 0.87245 | 5.3457 | 5.258 | 5.1569 | 5.0743 | 4.9406 | 4.8161 | 4.7069 | 4.4906 | 4.3998 | 4.3814
|  | SANDWICK | EE |  |  |  |  | 0.43265 | 0.36531 | 0.29286 | 4.9631 | 4.8722 | 4.7651 | 4.6784 | 4.5386 | 4.41 | 4.2957 | 4.0651 | 4.0284 | 3.9978 | 1.7184 | 1.6684 | 1.6204 | 5.912 | 5.8427 | 5.761 | 5.7008 | 5.5916 | 5.4906 | 5.4049 | 5.211 | 5.1018 | 4.911 | 1.0051 | 0.9398 | 0.87245 | 5.3457 | 5.258 | 5.1569 | 5.0743 | 4.9406 | 4.8161 | 4.7069 | 4.4906 | 4.4569 | 4.4263
|  | SANDWICK | HT |  |  |  |  | 0.46735 | 0.41224 | 0.35408 | 5.0406 | 4.9824 | 4.8998 | 4.8171 | 4.712 | 4.6437 | 4.5437 | 4.1457 | 3.9682 | 3.9488 | 1.7459 | 1.7133 | 1.6755 | 5.9865 | 5.9508 | 5.8937 | 5.8365 | 5.758 | 5.7171 | 5.6386 | 5.3488 | 5.2304 | 5.2171 | 1.0388 | 0.98776 | 0.93265 | 5.4233 | 5.3682 | 5.2906 | 5.211 | 5.11 | 5.0447 | 4.9498 | 4.5661 | 4.3998 | 4.3814
|  | SANDWICK | HE |  |  |  |  | 0.46633 | 0.42449 | 0.37653 | 5.0784 | 5.0324 | 4.9661 | 4.8927 | 4.7978 | 4.7457 | 4.6569 | 4.2355 | 4.1284 | 4.112 | 1.7449 | 1.7143 | 1.6806 | 5.9947 | 5.9631 | 5.911 | 5.8549 | 5.7804 | 5.7406 | 5.6712 | 5.3376 | 5.1804 | 5.0059 | 1.0378 | 0.99796 | 0.95204 | 5.4569 | 5.4141 | 5.3498 | 5.2784 | 5.1896 | 5.1396 | 5.0559 | 4.6549 | 4.5559 | 4.5416
|  | SANDWICK | CF |  |  |  |  | 0.47347 | 0.43673 | 0.3949 | 5.1161 | 5.0651 | 5.0314 | 4.9784 | 4.9192 | 4.859 | 4.7967 | 4.5008 | 4.2569 | 4.1253 | 1.749 | 1.7224 | 1.6939 | 6.0253 | 5.9845 | 5.9569 | 5.91 | 5.859 | 5.8059 | 5.7498 | 5.4569 | 5.1049 | 4.6855 | 1.0449 | 1.0092 | 0.97245 | 5.4937 | 5.4467 | 5.4131 | 5.3631 | 5.3059 | 5.2488 | 5.1896 | 4.9039 | 4.6702 | 4.5508
| SHETLAND | SCALLOWAY | MINIMUM HEADROOM | HU4139939639 | YES | YES | 0.299 | -2.6699 | -2.7648 | -2.8893 | 3.7217 | 3.5727 | 3.437 | 3.286 | 3.1095 | 2.988 | 2.8391 | 2.4707 | 2.3401 | 2.3156 | -1.0985 | -1.1648 | -1.2393 | 5.0289 | 4.9411 | 4.8472 | 4.7442 | 4.6217 | 4.5421 | 4.4462 | 4.1615 | 4.0207 | 3.485 | -2.0638 | -2.1413 | -2.2281 | 4.2023 | 4.0717 | 3.9421 | 3.7891 | 3.6054 | 3.4758 | 3.3289 | 2.9819 | 2.8564 | 2.8329
|  | SCALLOWAY | EE |  |  |  |  | -2.6699 | -2.7648 | -2.8893 | 3.7217 | 3.5727 | 3.437 | 3.286 | 3.1095 | 2.988 | 2.8391 | 2.4707 | 2.4187 | 2.3758 | -1.0985 | -1.1648 | -1.2393 | 5.0289 | 4.9411 | 4.8472 | 4.7442 | 4.6217 | 4.5421 | 4.4462 | 4.1615 | 4.0207 | 3.7768 | -2.0638 | -2.1413 | -2.2281 | 4.2023 | 4.0717 | 3.9421 | 3.7891 | 3.6054 | 3.4758 | 3.3289 | 2.9819 | 2.934 | 2.8901
|  | SCALLOWAY | HT |  |  |  |  | -2.6413 | -2.7373 | -2.8526 | 3.7891 | 3.684 | 3.5758 | 3.4585 | 3.3554 | 3.234 | 3.1064 | 2.586 | 2.3401 | 2.3156 | -1.0709 | -1.1291 | -1.1913 | 5.1023 | 5.0421 | 4.9758 | 4.9003 | 4.837 | 4.7564 | 4.6727 | 4.3319 | 4.1727 | 4.1564 | -2.0434 | -2.1169 | -2.1995 | 4.2758 | 4.1799 | 4.0768 | 3.9687 | 3.8717 | 3.7513 | 3.6187 | 3.0911 | 2.8564 | 2.8329
|  | SCALLOWAY | HE |  |  |  |  | -2.6403 | -2.6924 | -2.773 | 3.9034 | 3.7952 | 3.6799 | 3.5646 | 3.4768 | 3.3727 | 3.2625 | 2.7146 | 2.5646 | 2.5452 | -1.072 | -1.1118 | -1.1618 | 5.1472 | 5.0758 | 5.0064 | 4.9258 | 4.8687 | 4.7921 | 4.7146 | 4.3187 | 4.1166 | 3.8911 | -2.0444 | -2.0954 | -2.1577 | 4.3391 | 4.2625 | 4.1707 | 4.0636 | 3.9799 | 3.8819 | 3.7687 | 3.2176 | 3.0778 | 3.0595
|  | SCALLOWAY | CF |  |  |  |  | -2.6322 | -2.6771 | -2.726 | 3.9513 | 3.8799 | 3.7829 | 3.6921 | 3.5962 | 3.5462 | 3.4717 | 3.0972 | 2.7411 | 2.5574 | -1.0669 | -1.0985 | -1.1322 | 5.1768 | 5.1268 | 5.0625 | 5.0003 | 4.9299 | 4.888 | 4.8289 | 4.486 | 4.0248 | 3.485 | -2.026 | -2.0556 | -2.0903 | 4.4187 | 4.3534 | 4.2656 | 4.184 | 4.0942 | 4.0472 | 3.9768 | 3.6034 | 3.235 | 3.0666
| TAYNUILT | SCAMMADALE | MINIMUM HEADROOM | NM 84207 19638 | YES | YES | 0 | 0.04249 | 0.032286 | 0.029224 | 0.030245 | 0.028204 | 0.023102 | 0.022082 | 0.020041 | 0.010857 | 0.0088163 | -0.0034286 | -0.0064898 | -0.0085306 | 0.054918 | 0.045735 | 0.049816 | 0.045735 | 0.045735 | 0.047776 | 0.045735 | 0.044714 | 0.038592 | 0.037571 | 0.028388 | 0.023286 | 0.018184 | 0.053296 | 0.044112 | 0.040031 | 0.041051 | 0.03901 | 0.035949 | 0.032888 | 0.030847 | 0.021663 | 0.019622 | 0.010439 | 0.0053367 | 0.0043163
|  | SCAMMADALE | EE |  |  |  |  | 0.04249 | 0.032286 | 0.029224 | 0.031265 | 0.030245 | 0.023102 | 0.022082 | 0.020041 | 0.010857 | 0.0088163 | -0.0034286 | -0.0064898 | -0.0064898 | 0.054918 | 0.045735 | 0.049816 | 0.051857 | 0.051857 | 0.047776 | 0.045735 | 0.044714 | 0.038592 | 0.037571 | 0.028388 | 0.023286 | 0.021245 | 0.053296 | 0.044112 | 0.040031 | 0.043092 | 0.042071 | 0.035949 | 0.032888 | 0.030847 | 0.021663 | 0.019622 | 0.010439 | 0.0063571 | 0.0053367
|  | SCAMMADALE | HT |  |  |  |  | 0.049633 | 0.047592 | 0.037388 | 0.030245 | 0.028204 | 0.032286 | 0.028204 | 0.025143 | 0.023102 | 0.01902 | 0.00065306 | -0.0064898 | -0.0085306 | 0.062061 | 0.061041 | 0.052878 | 0.045735 | 0.048796 | 0.053898 | 0.051857 | 0.048796 | 0.047776 | 0.042673 | 0.031449 | 0.026347 | 0.026347 | 0.060439 | 0.059418 | 0.048194 | 0.041051 | 0.03901 | 0.044112 | 0.040031 | 0.036969 | 0.034929 | 0.029827 | 0.0135 | 0.0053367 | 0.0043163
|  | SCAMMADALE | HE |  |  |  |  | 0.049633 | 0.047592 | 0.038408 | 0.030245 | 0.029224 | 0.035347 | 0.030245 | 0.026163 | 0.026163 | 0.01902 | 0.0016735 | -0.0024082 | -0.0024082 | 0.062061 | 0.061041 | 0.052878 | 0.045735 | 0.049816 | 0.054918 | 0.051857 | 0.049816 | 0.049816 | 0.044714 | 0.03349 | 0.027367 | 0.025327 | 0.060439 | 0.058398 | 0.049214 | 0.041051 | 0.040031 | 0.046153 | 0.042071 | 0.03901 | 0.03799 | 0.030847 | 0.0135 | 0.010439 | 0.010439
|  | SCAMMADALE | CF |  |  |  |  | 0.049633 | 0.047592 | 0.040449 | 0.039429 | 0.031265 | 0.030245 | 0.035347 | 0.031265 | 0.031265 | 0.026163 | 0.01698 | 0.0037143 | 0.00065306 | 0.062061 | 0.061041 | 0.053898 | 0.053898 | 0.045735 | 0.049816 | 0.054918 | 0.051857 | 0.051857 | 0.049816 | 0.039612 | 0.029408 | 0.018184 | 0.060439 | 0.059418 | 0.052276 | 0.050235 | 0.042071 | 0.041051 | 0.046153 | 0.043092 | 0.042071 | 0.03901 | 0.028806 | 0.015541 | 0.01248
| ABERNETHY | SCONE | MINIMUM HEADROOM | NO 14401 25495 | NO | YES | 3.412 | 7.2938 | 6.9826 | 6.6448 | 6.2397 | 5.8499 | 5.3877 | 4.802 | 4.5601 | 4.0132 | 3.454 | 1.2979 | 0.24176 | 0.085641 | 8.6693 | 8.5193 | 8.3418 | 8.1152 | 7.8938 | 7.6275 | 7.2989 | 7.2081 | 6.8989 | 6.6183 | 5.4785 | 4.8326 | 3.9795 | 8.3351 | 8.0576 | 7.7606 | 7.4004 | 7.0494 | 6.6351 | 6.1076 | 5.8729 | 5.38 | 4.9157 | 3.0688 | 2.1576 | 2.0259
|  | SCONE | EE |  |  |  |  | 7.2938 | 6.9826 | 6.6448 | 6.2397 | 5.8499 | 5.3877 | 4.802 | 4.5601 | 4.0132 | 3.504 | 1.3458 | 0.38054 | 0.18972 | 8.6693 | 8.5193 | 8.3418 | 8.1152 | 7.8938 | 7.6275 | 7.2989 | 7.2081 | 6.8989 | 6.6183 | 5.4785 | 4.8326 | 4.2285 | 8.3351 | 8.0576 | 7.7606 | 7.4004 | 7.0494 | 6.6351 | 6.1076 | 5.8729 | 5.38 | 4.9157 | 3.077 | 2.2882 | 2.1127
|  | SCONE | HT |  |  |  |  | 7.3816 | 7.105 | 6.7714 | 6.4428 | 6.056 | 5.6285 | 5.1326 | 4.5744 | 4.0183 | 3.454 | 1.2979 | 0.24176 | 0.085641 | 8.6999 | 8.5948 | 8.4316 | 8.2703 | 8.0754 | 7.8673 | 7.6356 | 7.3479 | 7.0601 | 6.7673 | 5.7805 | 5.2836 | 5.2122 | 8.4127 | 8.1647 | 7.8719 | 7.577 | 7.231 | 6.8545 | 6.4208 | 5.9208 | 5.4259 | 4.9219 | 3.0688 | 2.1576 | 2.0259
|  | SCONE | HE |  |  |  |  | 7.3907 | 7.2071 | 6.9632 | 6.7316 | 6.4387 | 6.1173 | 5.7673 | 5.3438 | 4.9244 | 4.4938 | 2.7469 | 1.5754 | 1.1775 | 8.6979 | 8.6305 | 8.4989 | 8.3703 | 8.2132 | 8.0367 | 7.8418 | 7.5938 | 7.3479 | 7.0948 | 6.0999 | 5.3479 | 4.6989 | 8.4208 | 8.2596 | 8.0504 | 7.8484 | 7.5902 | 7.3055 | 6.9933 | 6.6137 | 6.2382 | 5.8535 | 4.3004 | 3.3168 | 2.9923
|  | SCONE | CF |  |  |  |  | 7.4458 | 7.2989 | 7.1428 | 6.9418 | 6.7601 | 6.5275 | 6.304 | 6.0918 | 5.852 | 5.605 | 4.4458 | 3.1122 | 2.0203 | 8.7193 | 8.6663 | 8.5775 | 8.4642 | 8.3571 | 8.2183 | 8.0734 | 7.9244 | 7.7571 | 7.5856 | 6.752 | 5.5071 | 3.9795 | 8.4708 | 8.3474 | 8.2137 | 8.0413 | 7.8831 | 7.6851 | 7.4902 | 7.3055 | 7.0953 | 6.8688 | 5.8494 | 4.6259 | 3.6576
| THURSO | SHAPINSAY | MINIMUM HEADROOM | HY 48313 17148 | YES | NO | 0 | 0.73163 | 0.71735 | 0.69796 | 0.68673 | 0.66327 | 0.65408 | 0.62755 | 0.59796 | 0.58163 | 0.5602 | 0.50714 | 0.49286 | 0.48571 | 0.85612 | 0.84592 | 0.83163 | 0.82449 | 0.80714 | 0.80204 | 0.78061 | 0.75918 | 0.74898 | 0.73469 | 0.6949 | 0.68367 | 0.65 | 0.79898 | 0.78367 | 0.76735 | 0.7551 | 0.73265 | 0.72449 | 0.69898 | 0.67041 | 0.65714 | 0.63571 | 0.58571 | 0.57245 | 0.56837
|  | SHAPINSAY | EE |  |  |  |  | 0.73163 | 0.71735 | 0.69796 | 0.68673 | 0.66327 | 0.65408 | 0.62755 | 0.59796 | 0.58163 | 0.5602 | 0.50714 | 0.5 | 0.4949 | 0.85612 | 0.84592 | 0.83163 | 0.82449 | 0.80714 | 0.80204 | 0.78061 | 0.75918 | 0.74898 | 0.73469 | 0.6949 | 0.68367 | 0.66633 | 0.79898 | 0.78367 | 0.76735 | 0.7551 | 0.73265 | 0.72449 | 0.69898 | 0.67041 | 0.65714 | 0.63571 | 0.58571 | 0.57959 | 0.57551
|  | SHAPINSAY | HT |  |  |  |  | 0.73163 | 0.72653 | 0.71633 | 0.7051 | 0.68878 | 0.67653 | 0.65612 | 0.64694 | 0.62653 | 0.60408 | 0.52245 | 0.49286 | 0.48571 | 0.85612 | 0.85306 | 0.8449 | 0.83878 | 0.82653 | 0.82041 | 0.80612 | 0.79898 | 0.78673 | 0.76939 | 0.71224 | 0.69388 | 0.69082 | 0.80306 | 0.7949 | 0.78469 | 0.77653 | 0.7602 | 0.75 | 0.72959 | 0.71837 | 0.70102 | 0.67959 | 0.6 | 0.57245 | 0.56837
|  | SHAPINSAY | HE |  |  |  |  | 0.73673 | 0.73061 | 0.71735 | 0.70918 | 0.69796 | 0.68776 | 0.66837 | 0.65816 | 0.63878 | 0.62041 | 0.53367 | 0.51122 | 0.50408 | 0.86122 | 0.85408 | 0.8449 | 0.84082 | 0.83061 | 0.82551 | 0.80816 | 0.80408 | 0.78878 | 0.77551 | 0.71122 | 0.69286 | 0.67551 | 0.80612 | 0.79694 | 0.78571 | 0.77857 | 0.76531 | 0.75612 | 0.73673 | 0.73163 | 0.71122 | 0.69184 | 0.6102 | 0.59082 | 0.58571
|  | SHAPINSAY | CF |  |  |  |  | 0.73367 | 0.73061 | 0.72347 | 0.71633 | 0.70612 | 0.69286 | 0.68878 | 0.66939 | 0.6551 | 0.65306 | 0.59184 | 0.52755 | 0.50918 | 0.85612 | 0.85816 | 0.85102 | 0.84592 | 0.83776 | 0.82653 | 0.82347 | 0.81122 | 0.79898 | 0.79796 | 0.74898 | 0.68776 | 0.65 | 0.80408 | 0.80306 | 0.7949 | 0.78776 | 0.77857 | 0.76531 | 0.76122 | 0.74184 | 0.72755 | 0.72857 | 0.66735 | 0.60612 | 0.58776
| BROADFORD | SHIELDAIG | MINIMUM HEADROOM | NG 81637 52250 | YES | YES | 0 | 0.65918 | 0.6602 | 0.65204 | 0.63673 | 0.62143 | 0.6102 | 0.59286 | 0.58265 | 0.56633 | 0.55 | 0.51429 | 0.50408 | 0.50102 | 0.75816 | 0.7602 | 0.75204 | 0.74286 | 0.73163 | 0.72347 | 0.7102 | 0.70408 | 0.6898 | 0.67959 | 0.65408 | 0.64694 | 0.61837 | 0.68673 | 0.68571 | 0.67959 | 0.66531 | 0.65204 | 0.64082 | 0.62347 | 0.61327 | 0.59898 | 0.58367 | 0.54898 | 0.5398 | 0.53776
|  | SHIELDAIG | EE |  |  |  |  | 0.66531 | 0.6602 | 0.65204 | 0.63673 | 0.62143 | 0.6102 | 0.59286 | 0.58265 | 0.56633 | 0.55 | 0.51429 | 0.5102 | 0.50612 | 0.76327 | 0.7602 | 0.75204 | 0.74286 | 0.73163 | 0.72347 | 0.7102 | 0.70408 | 0.6898 | 0.67959 | 0.65408 | 0.64694 | 0.62959 | 0.69286 | 0.68571 | 0.67959 | 0.66531 | 0.65204 | 0.64082 | 0.62347 | 0.61327 | 0.59898 | 0.58367 | 0.54898 | 0.54592 | 0.54082
|  | SHIELDAIG | HT |  |  |  |  | 0.65918 | 0.66429 | 0.65816 | 0.64796 | 0.6398 | 0.62959 | 0.61429 | 0.60612 | 0.59082 | 0.57449 | 0.52755 | 0.50408 | 0.50102 | 0.75816 | 0.76531 | 0.75918 | 0.75306 | 0.74898 | 0.74082 | 0.73061 | 0.72449 | 0.71429 | 0.70306 | 0.66837 | 0.65204 | 0.65102 | 0.68673 | 0.69184 | 0.68469 | 0.67857 | 0.66735 | 0.6602 | 0.64388 | 0.63776 | 0.62347 | 0.60816 | 0.56224 | 0.5398 | 0.53776
|  | SHIELDAIG | HE |  |  |  |  | 0.65918 | 0.66633 | 0.65918 | 0.65204 | 0.64694 | 0.63776 | 0.62449 | 0.61531 | 0.60204 | 0.58878 | 0.53367 | 0.51735 | 0.51735 | 0.75816 | 0.76633 | 0.75918 | 0.75408 | 0.75102 | 0.7449 | 0.73571 | 0.72857 | 0.71735 | 0.70612 | 0.66837 | 0.65306 | 0.63878 | 0.68673 | 0.69286 | 0.68571 | 0.68163 | 0.67449 | 0.66633 | 0.65306 | 0.64592 | 0.63265 | 0.62041 | 0.56837 | 0.55306 | 0.55204
|  | SHIELDAIG | CF |  |  |  |  | 0.66735 | 0.66531 | 0.66224 | 0.65612 | 0.65102 | 0.64694 | 0.63878 | 0.62755 | 0.62347 | 0.61429 | 0.57755 | 0.53571 | 0.51939 | 0.76735 | 0.76224 | 0.76224 | 0.75714 | 0.75204 | 0.75 | 0.74184 | 0.73469 | 0.73265 | 0.72551 | 0.69184 | 0.65 | 0.61837 | 0.6949 | 0.69286 | 0.6898 | 0.68367 | 0.67857 | 0.67551 | 0.66633 | 0.65816 | 0.65306 | 0.6449 | 0.60816 | 0.56531 | 0.55306
| SHIN | SHIN | MINIMUM HEADROOM | NH 57246 97463 | YES | NO | 0.028 | 2.5261 | 2.5088 | 2.4833 | 2.4639 | 2.4343 | 2.4231 | 2.3873 | 2.3608 | 2.3261 | 2.2965 | 2.2282 | 2.2077 | 2.2006 | 2.4725 | 2.4603 | 2.445 | 2.4287 | 2.4123 | 2.4042 | 2.3817 | 2.3654 | 2.3399 | 2.3215 | 2.2736 | 2.2562 | 2.1868 | 2.4942 | 2.4779 | 2.4565 | 2.4381 | 2.4126 | 2.4014 | 2.3677 | 2.3432 | 2.3095 | 2.2799 | 2.2157 | 2.1973 | 2.1912
|  | SHIN | EE |  |  |  |  | 2.5261 | 2.5088 | 2.4833 | 2.4639 | 2.4343 | 2.4231 | 2.3873 | 2.3608 | 2.3261 | 2.2965 | 2.2282 | 2.218 | 2.2118 | 2.4725 | 2.4603 | 2.445 | 2.4287 | 2.4123 | 2.4042 | 2.3817 | 2.3654 | 2.3399 | 2.3215 | 2.2736 | 2.2562 | 2.2256 | 2.4942 | 2.4779 | 2.4565 | 2.4381 | 2.4126 | 2.4014 | 2.3677 | 2.3432 | 2.3095 | 2.2799 | 2.2157 | 2.2085 | 2.2003
|  | SHIN | HT |  |  |  |  | 2.5373 | 2.519 | 2.5077 | 2.4873 | 2.4731 | 2.4486 | 2.422 | 2.4067 | 2.3792 | 2.3526 | 2.2496 | 2.2077 | 2.2006 | 2.4776 | 2.4685 | 2.4623 | 2.4521 | 2.443 | 2.4266 | 2.4093 | 2.4032 | 2.3838 | 2.3654 | 2.297 | 2.2695 | 2.2664 | 2.5014 | 2.4861 | 2.4738 | 2.4555 | 2.4412 | 2.4208 | 2.3993 | 2.3861 | 2.3606 | 2.3371 | 2.235 | 2.1973 | 2.1912
|  | SHIN | HE |  |  |  |  | 2.5373 | 2.5231 | 2.5159 | 2.4975 | 2.4853 | 2.4649 | 2.4414 | 2.4292 | 2.4067 | 2.3792 | 2.2608 | 2.2312 | 2.2261 | 2.4776 | 2.4695 | 2.4644 | 2.4532 | 2.445 | 2.4317 | 2.4154 | 2.4083 | 2.3919 | 2.3736 | 2.295 | 2.2644 | 2.2358 | 2.5014 | 2.4891 | 2.481 | 2.4677 | 2.4555 | 2.4381 | 2.4177 | 2.4065 | 2.3861 | 2.3606 | 2.2483 | 2.2197 | 2.2157
|  | SHIN | CF |  |  |  |  | 2.5322 | 2.5241 | 2.5149 | 2.5047 | 2.4914 | 2.4812 | 2.4649 | 2.4435 | 2.4414 | 2.4231 | 2.3424 | 2.2639 | 2.2302 | 2.4746 | 2.4705 | 2.4634 | 2.4583 | 2.4501 | 2.444 | 2.4307 | 2.4164 | 2.4123 | 2.4021 | 2.3348 | 2.2583 | 2.1868 | 2.4983 | 2.4922 | 2.483 | 2.4738 | 2.4626 | 2.4534 | 2.4391 | 2.4218 | 2.4167 | 2.4014 | 2.3248 | 2.2514 | 2.2197
| FORT WILLIAM | SHONA BEG | MINIMUM HEADROOM | NM 67173 74363 | YES | NO | 0 | 0.095551 | 0.095551 | 0.095551 | 0.087388 | 0.087388 | 0.087388 | 0.085347 | 0.077184 | 0.077184 | 0.075143 | 0.072082 | 0.062898 | 0.062898 | 0.092673 | 0.092673 | 0.091653 | 0.08451 | 0.08451 | 0.08451 | 0.08349 | 0.075327 | 0.075327 | 0.075327 | 0.073286 | 0.065122 | 0.063082 | 0.096153 | 0.096153 | 0.095133 | 0.08799 | 0.08799 | 0.086969 | 0.084929 | 0.076765 | 0.076765 | 0.074724 | 0.071663 | 0.0635 | 0.0635
|  | SHONA BEG | EE |  |  |  |  | 0.095551 | 0.095551 | 0.095551 | 0.087388 | 0.087388 | 0.087388 | 0.085347 | 0.077184 | 0.077184 | 0.075143 | 0.072082 | 0.064939 | 0.064939 | 0.092673 | 0.092673 | 0.091653 | 0.08451 | 0.08451 | 0.08451 | 0.08349 | 0.075327 | 0.075327 | 0.075327 | 0.073286 | 0.066143 | 0.063082 | 0.096153 | 0.096153 | 0.095133 | 0.08799 | 0.08799 | 0.086969 | 0.084929 | 0.076765 | 0.076765 | 0.074724 | 0.071663 | 0.06452 | 0.06452
|  | SHONA BEG | HT |  |  |  |  | 0.095551 | 0.095551 | 0.096571 | 0.095551 | 0.094531 | 0.087388 | 0.085347 | 0.085347 | 0.085347 | 0.082286 | 0.073102 | 0.062898 | 0.062898 | 0.092673 | 0.092673 | 0.092673 | 0.091653 | 0.091653 | 0.08451 | 0.08349 | 0.08349 | 0.08349 | 0.082469 | 0.074306 | 0.065122 | 0.065122 | 0.096153 | 0.096153 | 0.096153 | 0.095133 | 0.095133 | 0.08799 | 0.084929 | 0.084929 | 0.084929 | 0.082888 | 0.073704 | 0.0635 | 0.0635
|  | SHONA BEG | HE |  |  |  |  | 0.095551 | 0.095551 | 0.095551 | 0.095551 | 0.094531 | 0.087388 | 0.087388 | 0.087388 | 0.084327 | 0.084327 | 0.073102 | 0.065959 | 0.065959 | 0.092673 | 0.092673 | 0.092673 | 0.091653 | 0.091653 | 0.08451 | 0.08451 | 0.08451 | 0.08451 | 0.08349 | 0.074306 | 0.067163 | 0.063082 | 0.096153 | 0.096153 | 0.096153 | 0.095133 | 0.095133 | 0.08799 | 0.08799 | 0.08799 | 0.085949 | 0.084929 | 0.073704 | 0.066561 | 0.066561
|  | SHONA BEG | CF |  |  |  |  | 0.095551 | 0.095551 | 0.095551 | 0.095551 | 0.094531 | 0.09351 | 0.086367 | 0.086367 | 0.086367 | 0.086367 | 0.078204 | 0.076163 | 0.072082 | 0.092673 | 0.092673 | 0.092673 | 0.092673 | 0.091653 | 0.090633 | 0.08349 | 0.08349 | 0.08349 | 0.08349 | 0.076347 | 0.071245 | 0.067163 | 0.096153 | 0.096153 | 0.096153 | 0.096153 | 0.095133 | 0.094112 | 0.086969 | 0.086969 | 0.086969 | 0.086969 | 0.078806 | 0.075745 | 0.072684
| KINTORE | SKENE | MINIMUM HEADROOM | NJ 82203 06495 | NO | YES | 6.481 | 10.4054 | 10.0963 | 9.7054 | 9.2881 | 8.8106 | 8.3891 | 7.6565 | 6.8054 | 6.0197 | 5.2779 | 2.3973 | 0.85239 | 0.35545 | 12.0697 | 11.8463 | 11.5871 | 11.3095 | 11.0054 | 10.784 | 10.4116 | 9.9544 | 9.5463 | 9.1738 | 7.6861 | 6.7646 | 6.3371 | 11.9289 | 11.5993 | 11.2299 | 10.8167 | 10.3044 | 9.9187 | 9.2401 | 8.4452 | 7.7187 | 7.033 | 4.4106 | 3.0493 | 2.4544
|  | SKENE | EE |  |  |  |  | 10.4054 | 10.0963 | 9.7054 | 9.2881 | 8.8106 | 8.3891 | 7.6565 | 6.8054 | 6.0197 | 5.2779 | 2.3973 | 1.1963 | 0.92178 | 12.0697 | 11.8463 | 11.5871 | 11.3095 | 11.0054 | 10.784 | 10.4116 | 9.9544 | 9.5463 | 9.1738 | 7.8616 | 7.5391 | 7.4269 | 11.9289 | 11.5993 | 11.2299 | 10.8167 | 10.3044 | 9.9187 | 9.2401 | 8.4452 | 7.7187 | 7.033 | 4.4106 | 3.4218 | 3.2248
|  | SKENE | HT |  |  |  |  | 10.5412 | 10.2932 | 9.9799 | 9.632 | 9.2248 | 8.7136 | 7.9993 | 7.3463 | 6.5789 | 5.7503 | 2.4003 | 0.85239 | 0.41055 | 12.1922 | 12.0075 | 11.8218 | 11.6085 | 11.3789 | 11.1136 | 10.7769 | 10.4779 | 10.1044 | 9.6983 | 8.0095 | 7.3177 | 7.0575 | 12.0789 | 11.7912 | 11.4993 | 11.1432 | 10.7218 | 10.2422 | 9.5881 | 8.9922 | 8.2861 | 7.5289 | 4.433 | 3.0493 | 2.6218
|  | SKENE | HE |  |  |  |  | 10.5289 | 10.3146 | 10.0585 | 9.7524 | 9.4279 | 9.0483 | 8.5544 | 8.0126 | 7.3616 | 6.6708 | 3.1799 | 1.2218 | 0.35545 | 12.1759 | 11.9952 | 11.8177 | 11.6044 | 11.3718 | 11.1044 | 10.7677 | 10.4534 | 10.0748 | 9.6636 | 7.6861 | 6.7646 | 6.3371 | 12.0636 | 11.8116 | 11.5636 | 11.2718 | 10.9646 | 10.6014 | 10.0595 | 9.5483 | 8.9401 | 8.2891 | 5.035 | 3.2493 | 2.4544
|  | SKENE | CF |  |  |  |  | 10.6024 | 10.4799 | 10.3452 | 10.1799 | 9.984 | 9.7554 | 9.5024 | 9.1677 | 8.982 | 8.6657 | 6.333 | 3.6442 | 1.585 | 12.2381 | 12.134 | 12.0167 | 11.883 | 11.7391 | 11.5718 | 11.384 | 11.134 | 11.0075 | 10.7748 | 9.2544 | 7.7524 | 6.685 | 12.1544 | 12.0126 | 11.8565 | 11.6748 | 11.4881 | 11.2697 | 11.0279 | 10.7044 | 10.531 | 10.232 | 7.9452 | 5.4503 | 3.5626
| BROADFORD | SKULAMUS | MINIMUM HEADROOM | NG 65881 22438 | YES | YES | 2.434 | -2.7914 | 4.3139 | 4.2037 | 4.1068 | 3.9833 | 3.8405 | 3.6782 | 3.4986 | 3.2997 | 3.1323 | 2.7333 | 2.6201 | 2.5905 | -2.1363 | 4.9997 | 4.9323 | 4.8741 | 4.7956 | 4.7068 | 4.6048 | 4.4997 | 4.3803 | 4.2772 | 4.0068 | 3.9088 | 3.5854 | -2.5077 | 4.6027 | 4.5007 | 4.4129 | 4.2956 | 4.167 | 4.016 | 3.8537 | 3.6731 | 3.5211 | 3.1599 | 3.0558 | 3.0303
|  | SKULAMUS | EE |  |  |  |  | -2.7914 | 4.3139 | 4.2037 | 4.1068 | 3.9833 | 3.8405 | 3.6782 | 3.4986 | 3.2997 | 3.1323 | 2.7333 | 2.6792 | 2.6466 | -2.1363 | 4.9997 | 4.9323 | 4.8741 | 4.7956 | 4.7068 | 4.6048 | 4.4997 | 4.3803 | 4.2772 | 4.0068 | 3.9088 | 3.7466 | -2.5077 | 4.6027 | 4.5007 | 4.4129 | 4.2956 | 4.167 | 4.016 | 3.8537 | 3.6731 | 3.5211 | 3.1599 | 3.1139 | 3.0813
|  | SKULAMUS | HT |  |  |  |  | -2.7577 | 4.3517 | 4.2752 | 4.1894 | 4.0782 | 3.9354 | 3.767 | 3.5925 | 3.4221 | 3.2956 | 2.8241 | 2.6201 | 2.5905 | -2.1118 | 5.0343 | 4.9925 | 4.9446 | 4.8782 | 4.8068 | 4.7119 | 4.6129 | 4.516 | 4.4497 | 4.1333 | 4.0068 | 3.9905 | -2.475 | 4.6415 | 4.5721 | 4.4956 | 4.3925 | 4.266 | 4.1139 | 3.9619 | 3.8088 | 3.6976 | 3.2497 | 3.0558 | 3.0303
|  | SKULAMUS | HE |  |  |  |  | -2.7597 | 4.365 | 4.3058 | 4.2364 | 4.1405 | 4.0599 | 3.9476 | 3.7925 | 3.6374 | 3.5364 | 2.9262 | 2.7997 | 2.7762 | -2.1128 | 5.0364 | 5.0007 | 4.9599 | 4.8976 | 4.8507 | 4.7803 | 4.6884 | 4.5946 | 4.5374 | 4.1384 | 3.9915 | 3.8415 | -2.4771 | 4.6558 | 4.5997 | 4.5354 | 4.4466 | 4.3762 | 4.2731 | 4.1333 | 3.9946 | 3.9058 | 3.3456 | 3.2262 | 3.2058
|  | SKULAMUS | CF |  |  |  |  | -2.7454 | 4.3956 | 4.3456 | 4.2813 | 4.2129 | 4.1272 | 4.0701 | 3.9772 | 3.8588 | 3.7537 | 3.2935 | 2.9741 | 2.8007 | -2.1026 | 5.0558 | 5.0252 | 4.9813 | 4.9415 | 4.8854 | 4.8497 | 4.7854 | 4.7119 | 4.6446 | 4.3088 | 3.9537 | 3.5854 | -2.4638 | 4.6823 | 4.6354 | 4.5731 | 4.515 | 4.4333 | 4.3813 | 4.2935 | 4.1925 | 4.0946 | 3.6741 | 3.367 | 3.2241
| WOODHILL | SPRINGHILL | MINIMUM HEADROOM | NJ 89850 06421 | NO | NO | 5.765 | 18.7917 | 18.0693 | 17.2601 | 16.6611 | 15.8274 | 15.0254 | 13.5989 | 12.0295 | 10.4009 | 8.5948 | 0.606 | -4.5195 | -5.5746 | 21.9499 | 21.5713 | 21.1264 | 20.8795 | 20.4274 | 19.8968 | 19.1529 | 18.2876 | 17.4499 | 16.6611 | 13.1193 | 10.3244 | 8.3193 | 20.1152 | 19.4703 | 18.7376 | 18.2346 | 17.4846 | 16.7356 | 15.458 | 14.0489 | 12.6642 | 11.157 | 4.1611 | -0.25012 | -1.142
|  | SPRINGHILL | EE |  |  |  |  | 18.7917 | 18.0693 | 17.2601 | 16.6978 | 15.8825 | 15.0254 | 13.5989 | 12.0295 | 10.4744 | 8.9478 | 1.4744 | -3.9552 | -5.4369 | 21.9499 | 21.5713 | 21.1264 | 20.8795 | 20.4274 | 19.8968 | 19.1529 | 18.2876 | 17.4499 | 16.6611 | 13.1193 | 10.3244 | 8.3193 | 20.1152 | 19.4703 | 18.7376 | 18.2489 | 17.5121 | 16.7356 | 15.458 | 14.0489 | 12.6642 | 11.3111 | 4.8519 | 0.2356 | -1.0154
|  | SPRINGHILL | HT |  |  |  |  | 18.9182 | 18.2029 | 17.4274 | 16.6611 | 15.8274 | 15.2162 | 13.6774 | 12.0672 | 10.4009 | 8.5948 | 0.606 | -4.5195 | -5.5746 | 22.0815 | 21.7489 | 21.3734 | 21.006 | 20.5907 | 20.3631 | 19.6723 | 18.9336 | 18.1693 | 17.3336 | 13.6213 | 11.3978 | 10.9244 | 20.2458 | 19.6111 | 18.9203 | 18.2346 | 17.4846 | 16.9642 | 15.6101 | 14.1887 | 12.7295 | 11.157 | 4.1611 | -0.25012 | -1.142
|  | SPRINGHILL | HE |  |  |  |  | 18.9295 | 18.5285 | 18.0764 | 17.6264 | 17.1142 | 16.8295 | 15.955 | 14.8744 | 13.7631 | 12.5723 | 5.7795 | 0.52743 | -1.7277 | 22.0693 | 21.8356 | 21.5672 | 21.2989 | 20.9836 | 20.856 | 20.407 | 19.8305 | 19.2325 | 18.5764 | 14.9172 | 12.104 | 9.8611 | 20.254 | 19.8978 | 19.4887 | 19.0846 | 18.6152 | 18.3805 | 17.5968 | 16.6458 | 15.6703 | 14.6315 | 8.7019 | 4.1917 | 2.2785
|  | SPRINGHILL | CF |  |  |  |  | 19.104 | 18.8836 | 18.6162 | 18.3519 | 18.0407 | 17.704 | 17.3478 | 17.2703 | 16.8887 | 16.4529 | 12.2846 | 7.1907 | 2.504 | 22.1489 | 21.9938 | 21.8009 | 21.6142 | 21.3927 | 21.1325 | 20.8346 | 20.7754 | 20.454 | 20.0907 | 17.2468 | 13.3846 | 8.7223 | 20.4111 | 20.2131 | 19.9734 | 19.7346 | 19.455 | 19.1438 | 18.8203 | 18.7693 | 18.4305 | 18.0417 | 14.3631 | 9.9417 | 5.9805
| BRIDGE OF DUN | ST CYRUS | MINIMUM HEADROOM | NO 74889 65577 | NO | NO | 0.459 | 4.1141 | 4.0304 | 3.9131 | 3.759 | 3.5906 | 3.4151 | 3.2713 | 3.0855 | 2.9223 | 2.7988 | 2.5315 | 2.4325 | 2.3906 | 6.2131 | 6.1447 | 6.0621 | 5.957 | 5.8427 | 5.7294 | 5.6447 | 5.5233 | 5.4141 | 5.3284 | 5.1478 | 5.0274 | 4.6294 | 4.7866 | 4.6815 | 4.5723 | 4.4325 | 4.2794 | 4.1182 | 3.9927 | 3.8182 | 3.659 | 3.5376 | 3.3223 | 3.2315 | 3.1998
|  | ST CYRUS | EE |  |  |  |  | 4.1141 | 4.0304 | 3.9131 | 3.759 | 3.5906 | 3.4151 | 3.2713 | 3.0855 | 2.9223 | 2.7988 | 2.5315 | 2.4764 | 2.4447 | 6.2131 | 6.1447 | 6.0621 | 5.957 | 5.8427 | 5.7294 | 5.6447 | 5.5233 | 5.4141 | 5.3284 | 5.1478 | 5.0366 | 4.8682 | 4.7866 | 4.6815 | 4.5723 | 4.4325 | 4.2794 | 4.1182 | 3.9927 | 3.8182 | 3.659 | 3.5376 | 3.3223 | 3.2743 | 3.2457
|  | ST CYRUS | HT |  |  |  |  | 4.1488 | 4.0651 | 3.9376 | 3.7886 | 3.6366 | 3.4835 | 3.356 | 3.2121 | 3.1121 | 3.007 | 2.6141 | 2.4325 | 2.3906 | 6.2406 | 6.1723 | 6.0937 | 5.9947 | 5.8947 | 5.8008 | 5.7274 | 5.6396 | 5.5876 | 5.5192 | 5.2672 | 5.1621 | 5.1345 | 4.8192 | 4.7274 | 4.6192 | 4.4876 | 4.3651 | 4.2274 | 4.1151 | 3.9794 | 3.8947 | 3.7896 | 3.3978 | 3.2315 | 3.1998
|  | ST CYRUS | HE |  |  |  |  | 4.1498 | 4.0906 | 3.9896 | 3.8631 | 3.7427 | 3.6039 | 3.4733 | 3.3366 | 3.2447 | 3.1468 | 2.659 | 2.5345 | 2.5141 | 6.2427 | 6.1845 | 6.1131 | 6.0274 | 5.9457 | 5.8539 | 5.7713 | 5.6784 | 5.6264 | 5.5549 | 5.2253 | 5.0723 | 4.9151 | 4.8223 | 4.7447 | 4.656 | 4.5437 | 4.4417 | 4.3172 | 4.2008 | 4.0713 | 3.9947 | 3.8947 | 3.4427 | 3.3304 | 3.3131
|  | ST CYRUS | CF |  |  |  |  | 4.1641 | 4.1162 | 4.0447 | 3.96 | 3.857 | 3.7631 | 3.6651 | 3.56 | 3.4631 | 3.3886 | 3.0253 | 2.71 | 2.5294 | 6.2519 | 6.206 | 6.157 | 6.1008 | 6.0335 | 5.9702 | 5.9029 | 5.8274 | 5.7611 | 5.6978 | 5.3866 | 5.0274 | 4.6294 | 4.8315 | 4.7651 | 4.6968 | 4.6253 | 4.5304 | 4.4539 | 4.36 | 4.2641 | 4.1733 | 4.0917 | 3.7345 | 3.4488 | 3.3162
| ST FERGUS GAS | ST FERGUS GAS TERM | MINIMUM HEADROOM | NK 0916 5377 | NO | NO | 0 | 23.2806 | 23.2184 | 23.148 | 23.0786 | 23.0041 | 22.9204 | 22.8235 | 22.6969 | 22.5755 | 22.4663 | 22.0418 | 21.8378 | 21.7888 | 29.949 | 29.9071 | 29.8531 | 29.8082 | 29.752 | 29.6908 | 29.6316 | 29.5408 | 29.4561 | 29.3806 | 29.1245 | 28.9765 | 28.8214 | 38.898 | 38.8255 | 38.7337 | 38.6612 | 38.5714 | 38.4653 | 38.3684 | 38.2163 | 38.0684 | 37.9429 | 37.552 | 37.3265 | 37.2663
|  | ST FERGUS GAS TERM | EE |  |  |  |  | 23.2806 | 23.2184 | 23.148 | 23.0786 | 23.0041 | 22.9204 | 22.8235 | 22.6969 | 22.5755 | 22.4663 | 22.0602 | 21.8622 | 21.8204 | 29.949 | 29.9071 | 29.8531 | 29.8082 | 29.752 | 29.6908 | 29.6316 | 29.5408 | 29.4561 | 29.3806 | 29.1245 | 28.9765 | 28.848 | 38.898 | 38.8255 | 38.7337 | 38.6612 | 38.5714 | 38.4653 | 38.3684 | 38.2163 | 38.0684 | 37.9429 | 37.552 | 37.3633 | 37.3204
|  | ST FERGUS GAS TERM | HT |  |  |  |  | 23.2918 | 23.2255 | 23.1633 | 23.0908 | 23.0194 | 22.948 | 22.8337 | 22.7092 | 22.5806 | 22.4714 | 22.0418 | 21.8378 | 21.7888 | 29.9663 | 29.9245 | 29.8847 | 29.8418 | 29.7898 | 29.75 | 29.6827 | 29.6041 | 29.5224 | 29.4633 | 29.1827 | 29.0663 | 29.0429 | 38.9214 | 38.849 | 38.7837 | 38.7071 | 38.6194 | 38.5541 | 38.4337 | 38.2959 | 38.152 | 38.048 | 37.5551 | 37.3265 | 37.2663
|  | ST FERGUS GAS TERM | HE |  |  |  |  | 23.2918 | 23.25 | 23.2112 | 23.1653 | 23.1102 | 23.0622 | 22.9867 | 22.8929 | 22.8031 | 22.7316 | 22.2806 | 22.0245 | 21.9 | 29.9643 | 29.9316 | 29.9041 | 29.8694 | 29.8265 | 29.798 | 29.7429 | 29.6796 | 29.6143 | 29.5704 | 29.2541 | 29.0714 | 28.9163 | 38.9214 | 38.8724 | 38.8265 | 38.7735 | 38.7061 | 38.6429 | 38.551 | 38.4378 | 38.3296 | 38.2347 | 37.7204 | 37.4776 | 37.352
|  | ST FERGUS GAS TERM | CF |  |  |  |  | 23.3071 | 23.2796 | 23.251 | 23.2163 | 23.1857 | 23.148 | 23.1184 | 23.0755 | 23.0337 | 22.9959 | 22.7041 | 22.4031 | 22.1663 | 29.9735 | 29.951 | 29.9255 | 29.8969 | 29.8724 | 29.8408 | 29.8173 | 29.7776 | 29.7388 | 29.7051 | 29.4602 | 29.152 | 28.8214 | 38.9398 | 38.9031 | 38.8694 | 38.8224 | 38.7867 | 38.7367 | 38.7092 | 38.649 | 38.601 | 38.548 | 38.1745 | 37.8133 | 37.5612
| PERSLEY | ST MACHAR | MINIMUM HEADROOM | NJ 93584 08102 | NO | NO | 0.355 | 14.4867 | 14.0337 | 13.5102 | 12.9367 | 12.302 | 11.6571 | 10.6286 | 9.4663 | 8.3643 | 7.3888 | 2.9673 | -0.14082 | -0.65918 | 15.4218 | 15.1708 | 14.8759 | 14.5576 | 14.1433 | 13.7035 | 13.0973 | 12.3831 | 11.7188 | 11.1606 | 8.7076 | 7.1963 | 5.978 | 14.6718 | 14.2524 | 13.7596 | 13.2218 | 12.6178 | 12.0035 | 11.0473 | 9.9596 | 8.9341 | 8.0382 | 4.0361 | 1.382 | 0.95347
|  | ST MACHAR | EE |  |  |  |  | 14.4867 | 14.0337 | 13.5102 | 12.9367 | 12.302 | 11.6571 | 10.6286 | 9.4663 | 8.3643 | 7.3888 | 2.9673 | 0.11327 | -0.65918 | 15.4218 | 15.1708 | 14.8759 | 14.5576 | 14.1433 | 13.7035 | 13.0973 | 12.3831 | 11.7188 | 11.1606 | 8.7076 | 7.1963 | 5.978 | 14.6718 | 14.2524 | 13.7596 | 13.2218 | 12.6178 | 12.0035 | 11.0473 | 9.9596 | 8.9341 | 8.0382 | 4.0361 | 1.6576 | 0.95347
|  | ST MACHAR | HT |  |  |  |  | 14.6847 | 14.2969 | 13.8888 | 13.4408 | 12.9694 | 12.4367 | 11.4888 | 10.449 | 9.448 | 8.3694 | 3.1755 | -0.14082 | -0.60204 | 15.5463 | 15.4096 | 15.2157 | 15.0004 | 14.7494 | 14.4167 | 13.9188 | 13.3535 | 12.832 | 12.2453 | 9.4861 | 7.8412 | 7.6586 | 14.8106 | 14.5269 | 14.1453 | 13.7208 | 13.2769 | 12.7749 | 11.9086 | 10.9524 | 10.0494 | 9.0637 | 4.3371 | 1.382 | 1.0055
|  | ST MACHAR | HE |  |  |  |  | 14.648 | 14.3663 | 14.0673 | 13.7173 | 13.3469 | 12.9184 | 12.2133 | 11.3806 | 10.6122 | 9.7786 | 5.402 | 2.5408 | 1.8286 | 15.5137 | 15.3382 | 15.1178 | 14.8596 | 14.5688 | 14.2269 | 13.8004 | 13.2688 | 12.7688 | 12.232 | 9.6382 | 8.0943 | 7.032 | 14.7729 | 14.58 | 14.2912 | 13.9555 | 13.6045 | 13.1943 | 12.5351 | 11.7616 | 11.0524 | 10.279 | 6.2524 | 3.7647 | 3.1841
|  | ST MACHAR | CF |  |  |  |  | 14.7714 | 14.6255 | 14.4429 | 14.251 | 14.0235 | 13.7929 | 13.5204 | 13.1776 | 12.8541 | 12.5041 | 10.0673 | 7.55 | 5.0041 | 15.5657 | 15.4861 | 15.379 | 15.23 | 15.0535 | 14.8616 | 14.6473 | 14.3637 | 14.1004 | 13.8137 | 11.9392 | 9.5769 | 6.5912 | 14.8545 | 14.7555 | 14.6331 | 14.4586 | 14.2371 | 14.0106 | 13.7473 | 13.4188 | 13.1055 | 12.7708 | 10.4902 | 8.1382 | 5.8249
| THURSO | ST MARYS | MINIMUM HEADROOM | HY 46965 01396 | YES | NO | 0.264 | -2.2849 | -2.3767 | -2.4584 | -2.5594 | -2.6747 | -2.7614 | -2.9043 | -3.1033 | -3.3022 | -3.5808 | -4.1308 | -4.2543 | -4.3022 | -1.2308 | -1.289 | -1.3359 | -1.4033 | -1.5022 | -1.5594 | -1.6757 | -1.8186 | -1.9073 | -2.0247 | -2.2359 | -2.3604 | -2.8094 | -1.9982 | -2.0869 | -2.1665 | -2.2676 | -2.392 | -2.4686 | -2.6145 | -2.7971 | -2.9114 | -3.0624 | -3.4216 | -3.4931 | -3.5186
|  | ST MARYS | EE |  |  |  |  | -2.2849 | -2.3767 | -2.4584 | -2.5594 | -2.6747 | -2.7614 | -2.9043 | -3.1033 | -3.2767 | -3.5186 | -4.1308 | -4.1982 | -4.2318 | -1.2308 | -1.289 | -1.3359 | -1.4033 | -1.5022 | -1.5594 | -1.6757 | -1.8186 | -1.9073 | -2.0247 | -2.2359 | -2.3553 | -2.5441 | -1.9982 | -2.0869 | -2.1665 | -2.2676 | -2.392 | -2.4686 | -2.6145 | -2.7971 | -2.9114 | -3.0624 | -3.4216 | -3.4624 | -3.4869
|  | ST MARYS | HT |  |  |  |  | -2.2573 | -2.3267 | -2.3982 | -2.4727 | -2.5604 | -2.6502 | -2.8329 | -3.0278 | -3.3022 | -3.5808 | -4.0339 | -4.2543 | -4.3022 | -1.1971 | -1.2318 | -1.2706 | -1.3063 | -1.3594 | -1.4124 | -1.5002 | -1.5767 | -1.6961 | -1.8359 | -2.1696 | -2.2624 | -2.2788 | -1.9492 | -2.0033 | -2.0665 | -2.1227 | -2.2063 | -2.288 | -2.4114 | -2.5278 | -2.7124 | -2.9012 | -3.3441 | -3.4931 | -3.5186
|  | ST MARYS | HE |  |  |  |  | -2.2573 | -2.3114 | -2.3686 | -2.4216 | -2.492 | -2.5665 | -2.6655 | -2.8155 | -3.0094 | -3.2369 | -3.99 | -4.1461 | -4.1829 | -1.1992 | -1.2298 | -1.2665 | -1.2982 | -1.3431 | -1.3941 | -1.4706 | -1.539 | -1.639 | -1.7492 | -2.1584 | -2.3267 | -2.5104 | -1.9502 | -1.9982 | -2.0584 | -2.1053 | -2.1808 | -2.2553 | -2.3584 | -2.4451 | -2.5737 | -2.7186 | -3.2982 | -3.4145 | -3.4349
|  | ST MARYS | CF |  |  |  |  | -2.2482 | -2.291 | -2.339 | -2.3931 | -2.4359 | -2.4992 | -2.5624 | -2.639 | -2.7063 | -2.8206 | -3.5757 | -3.9369 | -4.1584 | -1.188 | -1.2135 | -1.24 | -1.2798 | -1.2992 | -1.342 | -1.3818 | -1.4482 | -1.4808 | -1.5492 | -1.9818 | -2.3604 | -2.8094 | -1.9339 | -1.9716 | -2.0145 | -2.0737 | -2.1084 | -2.1706 | -2.2308 | -2.3165 | -2.3553 | -2.442 | -2.9257 | -3.29 | -3.4206
| WILLOWDALE | ST NICHOLAS | MINIMUM HEADROOM | NJ 93737 06782 | NO | NO | 2.316 | 8.2618 | 7.9648 | 7.5699 | 7.0689 | 6.4995 | 5.8791 | 5.2557 | 4.824 | 4.4026 | 4.0261 | 2.3495 | 0.92096 | 0.70464 | 10.824 | 10.7006 | 10.5036 | 10.2169 | 9.8567 | 9.4801 | 9.0904 | 8.7689 | 8.4526 | 8.1628 | 6.6842 | 5.2475 | 1.2924 | 9.8087 | 9.5373 | 9.1679 | 8.7189 | 8.2026 | 7.6557 | 7.1046 | 6.6975 | 6.3006 | 5.9485 | 4.4067 | 3.1322 | 2.9424
|  | ST NICHOLAS | EE |  |  |  |  | 8.2618 | 8.0842 | 7.6179 | 7.0985 | 6.4995 | 5.8791 | 5.2557 | 4.824 | 4.4026 | 4.0261 | 2.3495 | 1.1546 | 0.7577 | 10.824 | 10.7169 | 10.5036 | 10.2169 | 9.8567 | 9.4801 | 9.0904 | 8.7689 | 8.4526 | 8.1628 | 6.6842 | 5.2475 | 3.2587 | 9.8087 | 9.5801 | 9.1679 | 8.7189 | 8.2026 | 7.6557 | 7.1046 | 6.6975 | 6.3006 | 5.9485 | 4.4067 | 3.3485 | 2.9842
|  | ST NICHOLAS | HT |  |  |  |  | 8.2924 | 7.9648 | 7.5699 | 7.0689 | 6.5567 | 5.9781 | 5.6404 | 5.2659 | 4.8904 | 4.5077 | 2.4495 | 0.92096 | 0.70464 | 10.8557 | 10.7006 | 10.5271 | 10.3067 | 10.0679 | 9.7873 | 9.5914 | 9.3628 | 9.1383 | 8.9057 | 7.7128 | 6.9036 | 6.7934 | 9.8689 | 9.5373 | 9.171 | 8.7475 | 8.3067 | 7.8057 | 7.4904 | 7.1444 | 6.7965 | 6.4363 | 4.5301 | 3.1322 | 2.9424
|  | ST NICHOLAS | HE |  |  |  |  | 8.2852 | 8.1699 | 8.0036 | 7.8057 | 7.5373 | 7.2832 | 6.9791 | 6.6546 | 6.3393 | 6.0169 | 4.3444 | 3.1465 | 2.7138 | 10.8414 | 10.7679 | 10.6669 | 10.5638 | 10.4036 | 10.2434 | 10.0291 | 9.7904 | 9.5506 | 9.2985 | 7.8067 | 6.3067 | 4.3618 | 9.8648 | 9.7261 | 9.5363 | 9.3332 | 9.0944 | 8.8659 | 8.5914 | 8.2893 | 8.0006 | 7.7046 | 6.1924 | 5.1434 | 4.7863
|  | ST NICHOLAS | CF |  |  |  |  | 8.321 | 8.2414 | 8.1771 | 8.0567 | 7.9199 | 7.7128 | 7.573 | 7.4046 | 7.2628 | 7.1046 | 6.1271 | 5.0332 | 3.9179 | 10.8577 | 10.7955 | 10.7393 | 10.6526 | 10.5383 | 10.3771 | 10.2271 | 10.0332 | 9.8434 | 9.6383 | 8.2016 | 5.6271 | 1.2924 | 9.9128 | 9.8179 | 9.7342 | 9.5975 | 9.4352 | 9.2506 | 9.125 | 8.9699 | 8.8404 | 8.6944 | 7.7975 | 6.8026 | 5.8179
| ARDMORE / HARRIS GRID | STOCKINISH | MINIMUM HEADROOM | NG 13447 94222 | YES | YES | 0.288 | 0.20221 | 0.18078 | 0.15731 | 0.11956 | 0.089963 | 0.045065 | 0.013433 | -0.046771 | -0.09269 | -0.13861 | -0.24167 | -0.2682 | -0.27738 | 0.41241 | 0.39609 | 0.37874 | 0.35017 | 0.3318 | 0.29813 | 0.28078 | 0.23996 | 0.21241 | 0.17976 | 0.11445 | 0.099147 | 0.047106 | 0.26139 | 0.23486 | 0.20935 | 0.17058 | 0.142 | 0.10017 | 0.071596 | 0.013433 | -0.032486 | -0.077384 | -0.17432 | -0.19677 | -0.20596
|  | STOCKINISH | EE |  |  |  |  | 0.20221 | 0.18078 | 0.15731 | 0.11956 | 0.089963 | 0.045065 | 0.013433 | -0.046771 | -0.09269 | -0.13861 | -0.24167 | -0.25596 | -0.26514 | 0.41241 | 0.39609 | 0.37874 | 0.35017 | 0.3318 | 0.29813 | 0.28078 | 0.23996 | 0.21241 | 0.17976 | 0.11445 | 0.099147 | 0.067514 | 0.26139 | 0.23486 | 0.20935 | 0.17058 | 0.142 | 0.10017 | 0.071596 | 0.013433 | -0.032486 | -0.077384 | -0.17432 | -0.18759 | -0.19677
|  | STOCKINISH | HT |  |  |  |  | 0.22262 | 0.20527 | 0.18996 | 0.15425 | 0.13588 | 0.10017 | 0.069555 | 0.024657 | -0.0182 | -0.038608 | -0.20391 | -0.2682 | -0.27738 | 0.43078 | 0.41547 | 0.40119 | 0.37772 | 0.36956 | 0.34404 | 0.3267 | 0.29711 | 0.26956 | 0.25833 | 0.14711 | 0.10935 | 0.10425 | 0.28486 | 0.26343 | 0.24098 | 0.20833 | 0.19098 | 0.15629 | 0.12772 | 0.084861 | 0.042004 | 0.025678 | -0.13555 | -0.19677 | -0.20596
|  | STOCKINISH | HE |  |  |  |  | 0.22262 | 0.20731 | 0.192 | 0.17058 | 0.15731 | 0.12772 | 0.10425 | 0.063433 | 0.023637 | 0.009351 | -0.18044 | -0.22636 | -0.23453 | 0.42976 | 0.41649 | 0.40527 | 0.38588 | 0.37568 | 0.35731 | 0.33996 | 0.31343 | 0.28486 | 0.27874 | 0.15731 | 0.12262 | 0.095065 | 0.28486 | 0.26751 | 0.24915 | 0.22262 | 0.21037 | 0.18078 | 0.15731 | 0.11853 | 0.079759 | 0.069555 | -0.1131 | -0.15698 | -0.16412
|  | STOCKINISH | CF |  |  |  |  | 0.2216 | 0.21445 | 0.19915 | 0.18792 | 0.16853 | 0.15731 | 0.13282 | 0.11343 | 0.087922 | 0.060371 | -0.060037 | -0.17126 | -0.22534 | 0.42874 | 0.4216 | 0.40731 | 0.39813 | 0.38282 | 0.37466 | 0.35833 | 0.34711 | 0.32772 | 0.30731 | 0.22058 | 0.12568 | 0.047106 | 0.28384 | 0.27568 | 0.25527 | 0.23996 | 0.21547 | 0.20731 | 0.1818 | 0.16343 | 0.13792 | 0.11139 | -0.0049347 | -0.11208 | -0.15698
| PORT ANN | STONEFIELD | MINIMUM HEADROOM | NR 86244 73400 | YES | YES | 0 | 0.33905 | 0.32986 | 0.32986 | 0.3217 | 0.3217 | 0.31354 | 0.17884 | 0.0217 | -0.070137 | -0.12014 | -0.1334 | -0.13646 | -0.13646 | 0.32498 | 0.3158 | 0.3158 | 0.30866 | 0.30866 | 0.30049 | 0.15049 | -0.016854 | -0.11481 | -0.16787 | -0.18216 | -0.18318 | -0.1842 | 0.33406 | 0.32589 | 0.32589 | 0.31671 | 0.31671 | 0.30752 | 0.17385 | 0.018749 | -0.072067 | -0.12309 | -0.13635 | -0.13839 | -0.13839
|  | STONEFIELD | EE |  |  |  |  | 0.33905 | 0.32986 | 0.32986 | 0.3217 | 0.3217 | 0.31354 | 0.31354 | 0.23292 | 0.12578 | 0.038027 | -0.1334 | -0.1334 | -0.1334 | 0.32498 | 0.3158 | 0.3158 | 0.30866 | 0.30866 | 0.30049 | 0.30049 | 0.21274 | 0.095391 | 0.00049286 | -0.18216 | -0.18216 | -0.18216 | 0.33406 | 0.32589 | 0.32589 | 0.31671 | 0.31671 | 0.30752 | 0.30855 | 0.22997 | 0.12181 | 0.036096 | -0.13635 | -0.13635 | -0.13635
|  | STONEFIELD | HT |  |  |  |  | 0.34007 | 0.33803 | 0.33088 | 0.32986 | 0.32884 | 0.32782 | 0.17884 | 0.0217 | -0.070137 | -0.12014 | -0.13238 | -0.1334 | -0.13442 | 0.32498 | 0.32396 | 0.31682 | 0.3158 | 0.3158 | 0.3158 | 0.15049 | -0.016854 | -0.11481 | -0.16787 | -0.18216 | -0.18216 | -0.18318 | 0.33508 | 0.33304 | 0.32589 | 0.32589 | 0.32385 | 0.32283 | 0.17385 | 0.018749 | -0.072067 | -0.12309 | -0.13635 | -0.13635 | -0.13737
|  | STONEFIELD | HE |  |  |  |  | 0.34007 | 0.33803 | 0.33088 | 0.32986 | 0.32884 | 0.32884 | 0.32068 | 0.22578 | 0.11048 | 0.02272 | -0.1334 | -0.13646 | -0.13646 | 0.32498 | 0.32396 | 0.31682 | 0.3158 | 0.3158 | 0.3158 | 0.30764 | 0.20559 | 0.080085 | -0.014813 | -0.18216 | -0.18318 | -0.18318 | 0.33508 | 0.33304 | 0.32589 | 0.32589 | 0.32385 | 0.32385 | 0.31569 | 0.22385 | 0.10548 | 0.01977 | -0.13635 | -0.13839 | -0.13839
|  | STONEFIELD | CF |  |  |  |  | 0.34007 | 0.34007 | 0.33088 | 0.33088 | 0.32986 | 0.32986 | 0.32884 | 0.3217 | 0.29211 | 0.24211 | 0.024761 | -0.12932 | -0.13136 | 0.32498 | 0.32498 | 0.31682 | 0.31682 | 0.3158 | 0.3158 | 0.3158 | 0.30866 | 0.276 | 0.22498 | -0.014813 | -0.18114 | -0.1842 | 0.33508 | 0.33508 | 0.32589 | 0.32589 | 0.32589 | 0.32589 | 0.32385 | 0.31671 | 0.28712 | 0.23916 | 0.02079 | -0.13329 | -0.13533
| FIDDES | STONEHAVEN | MINIMUM HEADROOM | NO 85903 85641 | NO | NO | 5.7 | 9.6472 | 8.786 | 7.6442 | 6.3207 | 5.0023 | 3.7074 | 2.7717 | 1.8523 | 1.3442 | 0.51356 | -3.3048 | -6.4966 | -7.966 | 11.1197 | 10.5503 | 9.6748 | 8.5156 | 7.4023 | 6.284 | 5.7574 | 5.2707 | 5.0085 | 4.586 | 2.186 | -0.37216 | -2.8211 | 10.3697 | 9.5983 | 8.5115 | 7.2615 | 6.0146 | 4.738 | 3.8942 | 3.0483 | 2.5758 | 1.8125 | -1.7609 | -5.0487 | -6.7303
|  | STONEHAVEN | EE |  |  |  |  | 9.6523 | 8.8493 | 7.9278 | 6.8085 | 5.4574 | 4.2483 | 3.438 | 2.4666 | 1.4748 | 0.59009 | -2.8997 | -5.9038 | -6.7905 | 11.1197 | 10.5503 | 9.8962 | 9.1095 | 8.0217 | 7.035 | 6.4227 | 5.8605 | 5.2411 | 4.7227 | 2.6778 | 0.18703 | -1.2956 | 10.3697 | 9.5983 | 8.7023 | 7.6952 | 6.4534 | 5.2901 | 4.5911 | 3.6972 | 2.7523 | 1.9319 | -1.3232 | -4.3681 | -5.3089
|  | STONEHAVEN | HT |  |  |  |  | 9.6472 | 8.786 | 7.6442 | 6.3207 | 5.0023 | 3.7074 | 2.7717 | 1.8523 | 1.3442 | 0.51356 | -3.3048 | -6.4966 | -7.966 | 11.187 | 10.6074 | 9.6748 | 8.5156 | 7.4023 | 6.284 | 5.7574 | 5.2707 | 5.0085 | 4.586 | 2.6095 | 0.26356 | -1.2671 | 10.4238 | 9.6115 | 8.5115 | 7.2615 | 6.0146 | 4.738 | 3.8942 | 3.0483 | 2.5758 | 1.8125 | -1.7609 | -5.0487 | -6.7303
|  | STONEHAVEN | HE |  |  |  |  | 9.7319 | 9.087 | 8.2707 | 7.3023 | 6.2819 | 5.0921 | 4.1799 | 3.3666 | 2.9595 | 2.1727 | -1.7364 | -4.8732 | -6.8283 | 11.2615 | 10.7554 | 10.0636 | 9.1493 | 8.2074 | 7.1187 | 6.438 | 5.8625 | 5.4778 | 4.8738 | 2.186 | -0.37216 | -2.8211 | 10.5146 | 9.885 | 9.0789 | 8.1207 | 7.1748 | 5.9972 | 5.1411 | 4.3585 | 3.9748 | 3.2064 | -0.62318 | -3.8609 | -5.9936
|  | STONEHAVEN | CF |  |  |  |  | 9.9278 | 9.586 | 9.1227 | 8.685 | 8.0452 | 7.3758 | 6.8432 | 6.3207 | 5.8789 | 5.7197 | 3.1697 | 0.36866 | -1.6895 | 11.3911 | 11.088 | 10.6891 | 10.3483 | 9.8329 | 9.2738 | 8.8085 | 8.3503 | 7.9503 | 7.7136 | 5.6207 | 3.0646 | 0.5207 | 10.6942 | 10.3238 | 9.837 | 9.4146 | 8.8044 | 8.1707 | 7.6605 | 7.1534 | 6.7166 | 6.584 | 4.1513 | 1.5585 | -0.25379
| STRICHEN | STONEYHILL | MINIMUM HEADROOM | NK 6773 4109 | YES | YES | 0 | -2.449 | -2.45 | -2.45 | -2.451 | -2.451 | -2.451 | -2.451 | -2.452 | -2.452 | -2.4531 | -2.4551 | -2.4551 | -2.4561 | -2.3878 | -2.3888 | -2.3888 | -2.3898 | -2.3898 | -2.3898 | -2.3908 | -2.3918 | -2.3918 | -2.3929 | -2.3949 | -2.3949 | -2.3959 | -2.3214 | -2.3224 | -2.3224 | -2.3235 | -2.3235 | -2.3235 | -2.3255 | -2.3265 | -2.3265 | -2.3276 | -2.3306 | -2.3316 | -2.3327
|  | STONEYHILL | EE |  |  |  |  | -2.449 | -2.45 | -2.45 | -2.451 | -2.451 | -2.451 | -2.451 | -2.452 | -2.452 | -2.4531 | -2.4541 | -2.4541 | -2.4541 | -2.3878 | -2.3888 | -2.3888 | -2.3898 | -2.3898 | -2.3898 | -2.3908 | -2.3918 | -2.3918 | -2.3929 | -2.3939 | -2.3939 | -2.3939 | -2.3214 | -2.3224 | -2.3224 | -2.3235 | -2.3235 | -2.3235 | -2.3255 | -2.3265 | -2.3265 | -2.3276 | -2.3286 | -2.3286 | -2.3286
|  | STONEYHILL | HT |  |  |  |  | -2.449 | -2.45 | -2.45 | -2.45 | -2.45 | -2.451 | -2.451 | -2.451 | -2.451 | -2.452 | -2.4541 | -2.4551 | -2.4551 | -2.3878 | -2.3888 | -2.3888 | -2.3888 | -2.3888 | -2.3898 | -2.3898 | -2.3908 | -2.3908 | -2.3918 | -2.3939 | -2.3949 | -2.3949 | -2.3214 | -2.3224 | -2.3224 | -2.3224 | -2.3224 | -2.3235 | -2.3235 | -2.3255 | -2.3255 | -2.3265 | -2.3286 | -2.3306 | -2.3306
|  | STONEYHILL | HE |  |  |  |  | -2.449 | -2.45 | -2.45 | -2.45 | -2.451 | -2.451 | -2.451 | -2.451 | -2.452 | -2.452 | -2.4551 | -2.4551 | -2.4561 | -2.3878 | -2.3888 | -2.3888 | -2.3888 | -2.3898 | -2.3898 | -2.3898 | -2.3908 | -2.3918 | -2.3918 | -2.3949 | -2.3949 | -2.3959 | -2.3214 | -2.3224 | -2.3224 | -2.3224 | -2.3235 | -2.3235 | -2.3235 | -2.3255 | -2.3265 | -2.3265 | -2.3306 | -2.3316 | -2.3327
|  | STONEYHILL | CF |  |  |  |  | -2.449 | -2.449 | -2.45 | -2.45 | -2.45 | -2.45 | -2.451 | -2.451 | -2.451 | -2.451 | -2.4531 | -2.4551 | -2.4551 | -2.3878 | -2.3878 | -2.3888 | -2.3888 | -2.3888 | -2.3888 | -2.3898 | -2.3898 | -2.3898 | -2.3908 | -2.3929 | -2.3949 | -2.3949 | -2.3214 | -2.3214 | -2.3224 | -2.3224 | -2.3224 | -2.3224 | -2.3235 | -2.3235 | -2.3235 | -2.3255 | -2.3276 | -2.3306 | -2.3316
| PERSLEY | STONEYWOOD T1&T2 | MINIMUM HEADROOM | NJ 89285 11082 | NO | NO | 2.242 | 13.1191 | 12.5528 | 11.8752 | 11.113 | 10.3446 | 9.5385 | 8.7834 | 7.9109 | 7.2681 | 6.4599 | 3.3966 | 1.2875 | 0.84766 | 14.4205 | 14.0868 | 13.7144 | 13.3042 | 12.893 | 12.4828 | 12.0338 | 11.4532 | 11.0093 | 10.6134 | 8.6603 | 7.5562 | 7.046 | 14.1134 | 13.6787 | 13.1828 | 12.6338 | 12.0124 | 11.3256 | 10.6287 | 9.8103 | 9.1879 | 8.6144 | 6.0103 | 4.2338 | 3.544
|  | STONEYWOOD T1&T2 | EE |  |  |  |  | 13.1191 | 12.5528 | 11.8752 | 11.113 | 10.3446 | 9.5385 | 8.7834 | 7.9109 | 7.3109 | 6.7395 | 3.7721 | 1.6732 | 0.93847 | 14.4205 | 14.0868 | 13.7144 | 13.3042 | 12.893 | 12.4828 | 12.0338 | 11.4532 | 11.0093 | 10.6134 | 9.0715 | 8.395 | 8.1583 | 14.1134 | 13.6787 | 13.1828 | 12.6338 | 12.0124 | 11.3256 | 10.6287 | 9.8103 | 9.1879 | 8.6195 | 6.2603 | 4.544 | 3.945
|  | STONEYWOOD T1&T2 | HT |  |  |  |  | 13.1844 | 12.6242 | 11.9834 | 11.2109 | 10.466 | 9.6895 | 8.8395 | 7.9405 | 7.2681 | 6.4599 | 3.3966 | 1.2875 | 0.84766 | 14.5215 | 14.2215 | 13.9144 | 13.5348 | 13.1807 | 12.8124 | 12.3572 | 11.8685 | 11.4817 | 11.0083 | 9.1481 | 8.1215 | 7.8348 | 14.2368 | 13.844 | 13.4287 | 12.8777 | 12.2021 | 11.5093 | 10.743 | 9.9287 | 9.3246 | 8.6144 | 6.0103 | 4.2338 | 3.8675
|  | STONEYWOOD T1&T2 | HE |  |  |  |  | 13.1793 | 12.6824 | 12.0997 | 11.4109 | 10.7272 | 9.9997 | 9.367 | 8.5772 | 8.0507 | 7.4966 | 4.4558 | 2.3466 | 1.2956 | 14.5021 | 14.196 | 13.8828 | 13.5083 | 13.1399 | 12.7572 | 12.3501 | 11.8389 | 11.4042 | 10.9389 | 8.6603 | 7.5562 | 7.046 | 14.2134 | 13.8195 | 13.4052 | 12.9072 | 12.4134 | 11.7899 | 11.1787 | 10.4134 | 9.8205 | 9.1858 | 6.0175 | 4.3164 | 3.544
|  | STONEYWOOD T1&T2 | CF |  |  |  |  | 13.2497 | 12.866 | 12.4058 | 11.8854 | 11.3721 | 10.8038 | 10.3926 | 9.9334 | 9.6732 | 9.4436 | 7.3568 | 4.7793 | 2.3456 | 14.5583 | 14.3419 | 14.1042 | 13.8419 | 13.5838 | 13.3062 | 13.045 | 12.7205 | 12.4807 | 12.243 | 10.5338 | 8.8093 | 7.4266 | 14.2868 | 14.0083 | 13.693 | 13.3389 | 12.9919 | 12.5124 | 12.1491 | 11.7328 | 11.4858 | 11.1644 | 8.7756 | 6.3236 | 4.2644
| DYCE | STONEYWOOD T3 | MINIMUM HEADROOM | NJ 89285 11082 | NO | YES | 0.095 | 19.3614 | 19.3165 | 19.2695 | 19.2154 | 19.1644 | 19.1022 | 19.0267 | 18.9389 | 18.8563 | 18.7879 | 18.5206 | 18.3491 | 18.2818 | 18.8057 | 18.7863 | 18.7608 | 18.7352 | 18.7067 | 18.6761 | 18.6332 | 18.5689 | 18.5108 | 18.4638 | 18.2832 | 18.1832 | 18.1281 | 19.375 | 19.3526 | 19.3199 | 19.2852 | 19.2383 | 19.1781 | 19.1046 | 19.0189 | 18.9393 | 18.874 | 18.574 | 18.3975 | 18.3352
|  | STONEYWOOD T3 | EE |  |  |  |  | 19.3614 | 19.3165 | 19.2695 | 19.2154 | 19.1644 | 19.1022 | 19.0267 | 18.9389 | 18.8563 | 18.7879 | 18.5206 | 18.3869 | 18.3593 | 18.8057 | 18.7863 | 18.7608 | 18.7352 | 18.7067 | 18.6761 | 18.6332 | 18.5689 | 18.5108 | 18.4638 | 18.2893 | 18.2414 | 18.2342 | 19.375 | 19.3526 | 19.3199 | 19.2852 | 19.2383 | 19.1781 | 19.1046 | 19.0189 | 18.9393 | 18.874 | 18.574 | 18.4342 | 18.4097
|  | STONEYWOOD T3 | HT |  |  |  |  | 19.3757 | 19.342 | 19.3022 | 19.2603 | 19.2165 | 19.1634 | 19.1001 | 19.0226 | 18.9512 | 18.8746 | 18.5389 | 18.3491 | 18.2818 | 18.8159 | 18.8016 | 18.7812 | 18.7608 | 18.7393 | 18.7128 | 18.6863 | 18.6465 | 18.5965 | 18.5444 | 18.3169 | 18.2189 | 18.1801 | 19.3832 | 19.3648 | 19.3444 | 19.3169 | 19.2873 | 19.2393 | 19.1812 | 19.1036 | 19.0352 | 18.9608 | 18.5832 | 18.3975 | 18.3352
|  | STONEYWOOD T3 | HE |  |  |  |  | 19.3746 | 19.342 | 19.3083 | 19.2716 | 19.2297 | 19.1808 | 19.1206 | 19.0471 | 18.9767 | 18.9032 | 18.5552 | 18.4032 | 18.3083 | 18.8148 | 18.7985 | 18.7822 | 18.7638 | 18.7403 | 18.7148 | 18.6852 | 18.6383 | 18.5873 | 18.5332 | 18.2832 | 18.1832 | 18.1281 | 19.3832 | 19.3659 | 19.3495 | 19.325 | 19.2965 | 19.2546 | 19.1965 | 19.121 | 19.0546 | 18.9822 | 18.6352 | 18.4454 | 18.3506
|  | STONEYWOOD T3 | CF |  |  |  |  | 19.3879 | 19.3695 | 19.3501 | 19.3297 | 19.3042 | 19.2757 | 19.243 | 19.2052 | 19.1654 | 19.1257 | 18.8726 | 18.6318 | 18.4532 | 18.822 | 18.8118 | 18.8016 | 18.7903 | 18.7781 | 18.7608 | 18.7444 | 18.725 | 18.7026 | 18.6812 | 18.4995 | 18.3281 | 18.2108 | 19.3893 | 19.3801 | 19.3679 | 19.3597 | 19.3454 | 19.3271 | 19.3026 | 19.2781 | 19.2383 | 19.1995 | 18.9485 | 18.7118 | 18.524
| CLACHAN | STRACHUR | MINIMUM HEADROOM | NN 08672 01180 | YES | YES | 0.137 | 0.22056 | 0.20015 | 0.16749 | 0.14504 | 0.10729 | 0.066473 | 0.0032082 | -0.048833 | -0.073322 | -0.1121 | -0.21822 | -0.24781 | -0.257 | 0.59504 | 0.5828 | 0.55831 | 0.54504 | 0.51545 | 0.493 | 0.45321 | 0.41545 | 0.40321 | 0.3777 | 0.31035 | 0.28484 | 0.1777 | 0.39913 | 0.3828 | 0.35117 | 0.33076 | 0.29607 | 0.25831 | 0.20015 | 0.15321 | 0.12872 | 0.091984 | -0.0069959 | -0.033527 | -0.039649
|  | STRACHUR | EE |  |  |  |  | 0.22056 | 0.20015 | 0.16749 | 0.14504 | 0.10729 | 0.066473 | 0.0032082 | -0.048833 | -0.073322 | -0.1121 | -0.21822 | -0.23455 | -0.24475 | 0.59504 | 0.5828 | 0.55831 | 0.54504 | 0.51545 | 0.493 | 0.45321 | 0.41545 | 0.40321 | 0.3777 | 0.31035 | 0.28484 | 0.2328 | 0.39913 | 0.3828 | 0.35117 | 0.33076 | 0.29607 | 0.25831 | 0.20015 | 0.15321 | 0.12872 | 0.091984 | -0.0069959 | -0.020261 | -0.029445
|  | STRACHUR | HT |  |  |  |  | 0.23484 | 0.21545 | 0.18994 | 0.16443 | 0.12974 | 0.10015 | 0.055249 | 0.023616 | -0.020261 | -0.073322 | -0.20189 | -0.24781 | -0.257 | 0.60627 | 0.59607 | 0.58178 | 0.56443 | 0.54096 | 0.52668 | 0.49913 | 0.4828 | 0.45219 | 0.41851 | 0.3328 | 0.30729 | 0.30015 | 0.41035 | 0.40015 | 0.37464 | 0.35117 | 0.32158 | 0.29198 | 0.25219 | 0.22362 | 0.1828 | 0.13382 | 0.012392 | -0.033527 | -0.039649
|  | STRACHUR | HE |  |  |  |  | 0.23484 | 0.21953 | 0.19811 | 0.1828 | 0.15525 | 0.12158 | 0.069535 | 0.045045 | 0.0093306 | -0.027404 | -0.17026 | -0.20189 | -0.20598 | 0.60627 | 0.59709 | 0.58382 | 0.57362 | 0.54913 | 0.53484 | 0.50525 | 0.48688 | 0.46341 | 0.4379 | 0.33994 | 0.30933 | 0.26341 | 0.41035 | 0.40117 | 0.38382 | 0.36647 | 0.343 | 0.31239 | 0.26749 | 0.24402 | 0.21137 | 0.17566 | 0.041984 | 0.011371 | 0.0083102
|  | STRACHUR | CF |  |  |  |  | 0.2379 | 0.22566 | 0.21239 | 0.193 | 0.18076 | 0.15933 | 0.14402 | 0.11749 | 0.095045 | 0.079739 | -0.062098 | -0.15598 | -0.20189 | 0.60831 | 0.60015 | 0.59198 | 0.57566 | 0.56749 | 0.55117 | 0.54402 | 0.52464 | 0.50525 | 0.49607 | 0.39811 | 0.28994 | 0.1777 | 0.41443 | 0.40525 | 0.39607 | 0.3777 | 0.36545 | 0.34504 | 0.3328 | 0.30729 | 0.28484 | 0.27158 | 0.14402 | 0.053208 | 0.0093306
| TARLAND | STRATHDON | MINIMUM HEADROOM | NJ 37343 11904 | YES | NO | 0.213 | 0.072608 | 0.038935 | 0.0083224 | -0.037596 | -0.07331 | -0.11821 | -0.17841 | -0.21617 | -0.27739 | -0.31821 | -0.4376 | -0.46923 | -0.48351 | 0.43383 | 0.41444 | 0.39404 | 0.36853 | 0.3471 | 0.31649 | 0.28077 | 0.25934 | 0.22261 | 0.19506 | 0.11955 | 0.099139 | 0.02771 | 0.36853 | 0.33689 | 0.30832 | 0.26649 | 0.23179 | 0.18791 | 0.12975 | 0.095057 | 0.035873 | -0.00086122 | -0.11107 | -0.13862 | -0.15188
|  | STRATHDON | EE |  |  |  |  | 0.072608 | 0.038935 | 0.0083224 | -0.037596 | -0.07331 | -0.11821 | -0.17841 | -0.21617 | -0.27739 | -0.31821 | -0.4376 | -0.45596 | -0.46311 | 0.43383 | 0.41444 | 0.39404 | 0.36853 | 0.3471 | 0.31649 | 0.28077 | 0.25934 | 0.22261 | 0.19506 | 0.11955 | 0.099139 | 0.065465 | 0.36853 | 0.33689 | 0.30832 | 0.26649 | 0.23179 | 0.18791 | 0.12975 | 0.095057 | 0.035873 | -0.00086122 | -0.11107 | -0.12739 | -0.13453
|  | STRATHDON | HT |  |  |  |  | 0.086894 | 0.059343 | 0.028731 | -0.00086122 | -0.025351 | -0.062086 | -0.10698 | -0.1427 | -0.19066 | -0.23862 | -0.39168 | -0.46923 | -0.48351 | 0.44302 | 0.42771 | 0.41036 | 0.39506 | 0.38179 | 0.35934 | 0.33281 | 0.31138 | 0.28383 | 0.25526 | 0.16036 | 0.12261 | 0.11342 | 0.38179 | 0.3573 | 0.32975 | 0.30118 | 0.27873 | 0.24302 | 0.2022 | 0.16649 | 0.12261 | 0.07771 | -0.068208 | -0.13862 | -0.15188
|  | STRATHDON | HE |  |  |  |  | 0.086894 | 0.066486 | 0.039955 | 0.019547 | 0.00015918 | -0.031473 | -0.068208 | -0.099841 | -0.14066 | -0.18658 | -0.37739 | -0.43351 | -0.44678 | 0.44302 | 0.43179 | 0.41649 | 0.40322 | 0.392 | 0.37057 | 0.3471 | 0.32669 | 0.30118 | 0.27261 | 0.15628 | 0.11036 | 0.074649 | 0.38179 | 0.36342 | 0.33996 | 0.31751 | 0.30118 | 0.27261 | 0.23791 | 0.20526 | 0.16547 | 0.12363 | -0.054943 | -0.11719 | -0.14576
|  | STRATHDON | CF |  |  |  |  | 0.091996 | 0.07669 | 0.0522 | 0.034853 | 0.007302 | -0.0018816 | -0.028412 | -0.061065 | -0.080453 | -0.11004 | -0.23964 | -0.36413 | -0.43045 | 0.4471 | 0.43791 | 0.42465 | 0.41342 | 0.39608 | 0.38996 | 0.37363 | 0.35118 | 0.33996 | 0.31955 | 0.22873 | 0.12057 | 0.02771 | 0.38689 | 0.37363 | 0.35016 | 0.33689 | 0.30934 | 0.29914 | 0.27363 | 0.242 | 0.22363 | 0.19812 | 0.074649 | -0.043718 | -0.108
| STRICHEN | STRICHEN | MINIMUM HEADROOM | NJ 95900 55137 | NO | YES | 0.216 | 4.5795 | 4.153 | 3.7142 | 3.2765 | 2.8408 | 2.754 | 2.653 | 2.5316 | 2.4091 | 2.2775 | 1.9163 | 1.7826 | 1.7122 | 6.8724 | 6.4367 | 5.9846 | 5.5275 | 5.0775 | 4.9938 | 4.8969 | 4.7938 | 4.6795 | 4.5591 | 4.2163 | 4.0949 | 3.7642 | 4.2051 | 3.754 | 3.2826 | 2.8112 | 2.3469 | 2.2346 | 2.0908 | 1.9398 | 1.7714 | 1.5918 | 1.1153 | 0.98159 | 0.92444
|  | STRICHEN | EE |  |  |  |  | 4.5795 | 4.153 | 3.7142 | 3.2765 | 2.8408 | 2.754 | 2.653 | 2.5316 | 2.4091 | 2.2775 | 1.9163 | 1.8408 | 1.8183 | 6.8724 | 6.4367 | 5.9846 | 5.5275 | 5.0775 | 4.9938 | 4.8969 | 4.7938 | 4.6795 | 4.5591 | 4.2163 | 4.0949 | 3.954 | 4.2051 | 3.754 | 3.2826 | 2.8112 | 2.3469 | 2.2346 | 2.0908 | 1.9398 | 1.7714 | 1.5918 | 1.1153 | 1.0316 | 1.0112
|  | STRICHEN | HT |  |  |  |  | 4.604 | 4.1867 | 3.7612 | 3.3418 | 2.9102 | 2.8377 | 2.7469 | 2.6316 | 2.4898 | 2.3653 | 1.9908 | 1.7826 | 1.7122 | 6.8928 | 6.4673 | 6.0234 | 5.5867 | 5.1418 | 5.0744 | 4.9949 | 4.8918 | 4.7683 | 4.6591 | 4.3377 | 4.1918 | 4.153 | 4.2285 | 3.7846 | 3.3295 | 2.8806 | 2.4163 | 2.3173 | 2.1928 | 2.0367 | 1.8459 | 1.6806 | 1.2091 | 0.98159 | 0.92444
|  | STRICHEN | HE |  |  |  |  | 4.602 | 4.1928 | 3.7765 | 3.3632 | 2.9408 | 2.8755 | 2.804 | 2.6928 | 2.5755 | 2.4418 | 1.954 | 1.8183 | 1.753 | 6.8918 | 6.4642 | 6.0275 | 5.5928 | 5.152 | 5.1071 | 5.0591 | 4.9622 | 4.8642 | 4.7489 | 4.2836 | 4.0969 | 3.9285 | 4.2265 | 3.804 | 3.3683 | 2.9408 | 2.5 | 2.4204 | 2.3295 | 2.1928 | 2.0479 | 1.8795 | 1.2244 | 1.0357 | 0.9724
|  | STRICHEN | CF |  |  |  |  | 4.6163 | 4.2244 | 3.8255 | 3.4275 | 3.0295 | 2.9857 | 2.9398 | 2.8836 | 2.8306 | 2.7622 | 2.3346 | 2.0377 | 1.8398 | 6.9 | 6.4826 | 6.0551 | 5.6275 | 5.203 | 5.1714 | 5.1346 | 5.0795 | 5.0275 | 4.9602 | 4.5673 | 4.1836 | 3.7642 | 4.2408 | 3.8265 | 3.4061 | 2.9826 | 2.5642 | 2.5061 | 2.4408 | 2.3663 | 2.303 | 2.2142 | 1.7183 | 1.3612 | 1.1112
| THURSO | STROMNESS | MINIMUM HEADROOM | HY 25978 10409 | NO | NO | 0.132 | 2.3114 | 1.9308 | 1.3247 | 0.65939 | 0.35327 | -0.53653 | -0.88959 | -1.2814 | -1.7059 | -2.3722 | -5.0335 | -7.4743 | -9.8784 | 4.4278 | 4.0859 | 3.4757 | 2.7859 | 2.5329 | 1.5318 | 1.2053 | 0.76551 | 0.35837 | -0.32735 | -3.0631 | -6.0314 | -8.9814 | 3.2737 | 2.9349 | 2.3033 | 1.59 | 1.3104 | 0.28286 | -0.049796 | -0.51102 | -0.95796 | -1.6845 | -4.6824 | -7.6865 | -10.6569
|  | STROMNESS | EE |  |  |  |  | 2.3196 | 1.941 | 1.541 | 1.1808 | 0.68694 | 0.068571 | -0.43551 | -0.80592 | -1.3549 | -1.7835 | -2.8059 | -5.0712 | -6.0202 | 4.4451 | 4.1114 | 3.7665 | 3.4563 | 2.9798 | 2.3349 | 1.8951 | 1.6461 | 1.1829 | 0.85224 | -0.29776 | -3.0671 | -4.4631 | 3.2859 | 2.9624 | 2.5818 | 2.2451 | 1.742 | 1.0604 | 0.58898 | 0.23796 | -0.35184 | -0.78755 | -1.9018 | -4.6957 | -5.8192
|  | STROMNESS | HT |  |  |  |  | 2.3114 | 1.9308 | 1.3247 | 0.65939 | 0.35327 | -0.53653 | -0.88959 | -1.2273 | -1.4835 | -1.8294 | -3.4763 | -5.9855 | -8.2273 | 4.4278 | 4.0859 | 3.4757 | 2.7859 | 2.5329 | 1.5318 | 1.2339 | 0.95633 | 0.78082 | 0.51347 | -0.96204 | -4.1488 | -6.9365 | 3.2737 | 2.9349 | 2.3033 | 1.59 | 1.3104 | 0.28286 | -0.049796 | -0.37735 | -0.6049 | -0.9202 | -2.6763 | -5.8059 | -8.6192
|  | STROMNESS | HE |  |  |  |  | 2.3696 | 2.0135 | 1.5114 | 0.93184 | 0.54102 | -0.34265 | -0.8202 | -1.2814 | -1.7059 | -2.3722 | -5.0335 | -7.4743 | -9.8784 | 4.4869 | 4.1665 | 3.6543 | 3.0441 | 2.6716 | 1.6727 | 1.2053 | 0.76551 | 0.35837 | -0.32735 | -3.0631 | -6.0314 | -8.9814 | 3.3329 | 3.0206 | 2.492 | 1.8686 | 1.4727 | 0.45429 | -0.038571 | -0.51102 | -0.95796 | -1.6845 | -4.6824 | -7.6865 | -10.6569
|  | STROMNESS | CF |  |  |  |  | 2.5502 | 2.2941 | 2.038 | 1.8502 | 1.54 | 1.139 | 0.85735 | 0.57878 | 0.31143 | -0.004898 | -1.4212 | -2.4447 | -3.1712 | 4.6635 | 4.438 | 4.2063 | 4.0492 | 3.7502 | 3.3308 | 3.042 | 2.7737 | 2.5257 | 2.2278 | 0.95735 | -0.054898 | -1.2998 | 3.5022 | 3.2778 | 3.0543 | 2.9002 | 2.59 | 2.1451 | 1.8543 | 1.5645 | 1.2839 | 0.94714 | -0.45796 | -1.5376 | -2.3131
| THURSO | STRONSAY | MINIMUM HEADROOM | HY 64548 27016 | YES | NO | 0.012 | 0.67449 | 0.66224 | 0.65 | 0.62755 | 0.61837 | 0.59694 | 0.57959 | 0.5449 | 0.51122 | 0.48367 | 0.4449 | 0.43571 | 0.43163 | 0.81327 | 0.80408 | 0.79184 | 0.77245 | 0.76633 | 0.74592 | 0.73163 | 0.70612 | 0.68367 | 0.66327 | 0.64592 | 0.63673 | 0.59082 | 0.75816 | 0.74388 | 0.72857 | 0.70612 | 0.69592 | 0.67347 | 0.65408 | 0.62449 | 0.5949 | 0.57041 | 0.5398 | 0.53163 | 0.52857
|  | STRONSAY | EE |  |  |  |  | 0.67449 | 0.66224 | 0.65 | 0.62755 | 0.61837 | 0.59694 | 0.57959 | 0.5449 | 0.51122 | 0.48367 | 0.45102 | 0.44082 | 0.43776 | 0.81327 | 0.80408 | 0.79184 | 0.77245 | 0.76633 | 0.74592 | 0.73163 | 0.70612 | 0.68367 | 0.66327 | 0.65102 | 0.63673 | 0.61531 | 0.75816 | 0.74388 | 0.72857 | 0.70612 | 0.69592 | 0.67347 | 0.65408 | 0.62449 | 0.5949 | 0.57041 | 0.54592 | 0.53673 | 0.53469
|  | STRONSAY | HT |  |  |  |  | 0.68571 | 0.67551 | 0.66531 | 0.65306 | 0.64388 | 0.62449 | 0.60204 | 0.59184 | 0.56735 | 0.55306 | 0.4449 | 0.43571 | 0.43163 | 0.82347 | 0.81735 | 0.80714 | 0.79694 | 0.7898 | 0.77551 | 0.75714 | 0.74898 | 0.73265 | 0.72551 | 0.64592 | 0.65102 | 0.64898 | 0.76735 | 0.75714 | 0.74286 | 0.72755 | 0.71735 | 0.69796 | 0.67653 | 0.66837 | 0.64694 | 0.63367 | 0.5398 | 0.53163 | 0.52857
|  | STRONSAY | HE |  |  |  |  | 0.68571 | 0.67653 | 0.66837 | 0.65612 | 0.64796 | 0.63163 | 0.61327 | 0.60408 | 0.58571 | 0.57551 | 0.45306 | 0.45408 | 0.45102 | 0.82347 | 0.81735 | 0.8102 | 0.79796 | 0.79082 | 0.77857 | 0.76122 | 0.7551 | 0.73673 | 0.72959 | 0.64898 | 0.64592 | 0.62551 | 0.76735 | 0.75918 | 0.74796 | 0.73571 | 0.72551 | 0.71122 | 0.68776 | 0.68061 | 0.65918 | 0.65102 | 0.54796 | 0.55 | 0.54694
|  | STRONSAY | CF |  |  |  |  | 0.68061 | 0.67959 | 0.66939 | 0.66531 | 0.6551 | 0.65102 | 0.63673 | 0.62245 | 0.62041 | 0.60612 | 0.53061 | 0.48367 | 0.4551 | 0.82143 | 0.81735 | 0.81122 | 0.8051 | 0.79796 | 0.79082 | 0.78061 | 0.76531 | 0.76633 | 0.75408 | 0.69592 | 0.64592 | 0.59082 | 0.76224 | 0.76122 | 0.75306 | 0.7449 | 0.73469 | 0.72755 | 0.71224 | 0.69694 | 0.6949 | 0.68367 | 0.61735 | 0.57143 | 0.55306
| FORT WILLIAM | STRONTIAN | MINIMUM HEADROOM | NM 81521 61955 | YES | NO | 0 | 0.15 | 0.13571 | 0.11429 | 0.083673 | 0.066327 | 0.035714 | 0.011224 | -0.028571 | -0.066327 | -0.080612 | -0.14898 | -0.17143 | -0.17449 | 0.51633 | 0.49898 | 0.48469 | 0.46327 | 0.45408 | 0.43265 | 0.41429 | 0.38878 | 0.36122 | 0.3551 | 0.3051 | 0.28367 | 0.20408 | 0.36837 | 0.34796 | 0.32857 | 0.29796 | 0.28367 | 0.25408 | 0.23163 | 0.19286 | 0.15612 | 0.14694 | 0.082653 | 0.065306 | 0.061224
|  | STRONTIAN | EE |  |  |  |  | 0.15 | 0.13571 | 0.11429 | 0.083673 | 0.066327 | 0.035714 | 0.011224 | -0.028571 | -0.066327 | -0.080612 | -0.14898 | -0.15918 | -0.16633 | 0.51633 | 0.49898 | 0.48469 | 0.46327 | 0.45408 | 0.43265 | 0.41429 | 0.38878 | 0.36122 | 0.3551 | 0.3051 | 0.28367 | 0.2449 | 0.36837 | 0.34796 | 0.32857 | 0.29796 | 0.28367 | 0.25408 | 0.23163 | 0.19286 | 0.15612 | 0.14694 | 0.082653 | 0.073469 | 0.067347
|  | STRONTIAN | HT |  |  |  |  | 0.15612 | 0.14286 | 0.12857 | 0.11224 | 0.094898 | 0.068367 | 0.053061 | 0.02449 | -0.0061224 | -0.02449 | -0.12653 | -0.17143 | -0.17449 | 0.52347 | 0.51531 | 0.50204 | 0.4898 | 0.48061 | 0.46327 | 0.4551 | 0.43265 | 0.41224 | 0.40102 | 0.33367 | 0.3051 | 0.30306 | 0.37857 | 0.36327 | 0.34592 | 0.32857 | 0.31327 | 0.28878 | 0.27449 | 0.2449 | 0.21633 | 0.2 | 0.10714 | 0.065306 | 0.061224
|  | STRONTIAN | HE |  |  |  |  | 0.15612 | 0.14388 | 0.13265 | 0.12143 | 0.1102 | 0.088776 | 0.07551 | 0.046939 | 0.022449 | 0.0071429 | -0.10816 | -0.13878 | -0.14184 | 0.52347 | 0.51122 | 0.50204 | 0.49082 | 0.48367 | 0.46939 | 0.45918 | 0.4398 | 0.42347 | 0.40918 | 0.33367 | 0.3 | 0.26531 | 0.37857 | 0.36531 | 0.35204 | 0.33571 | 0.32347 | 0.30408 | 0.29184 | 0.26735 | 0.24082 | 0.22653 | 0.12347 | 0.094898 | 0.091837
|  | STRONTIAN | CF |  |  |  |  | 0.15714 | 0.14898 | 0.14082 | 0.12959 | 0.12347 | 0.10714 | 0.087755 | 0.079592 | 0.061224 | 0.042857 | -0.044898 | -0.1051 | -0.14286 | 0.52653 | 0.51735 | 0.50918 | 0.49796 | 0.49184 | 0.47959 | 0.46735 | 0.45816 | 0.4449 | 0.42959 | 0.35612 | 0.28469 | 0.20408 | 0.38163 | 0.37143 | 0.35918 | 0.34592 | 0.33878 | 0.32143 | 0.30306 | 0.29592 | 0.27857 | 0.2602 | 0.17653 | 0.12041 | 0.090816
| SHETLAND | SUMBURGH | MINIMUM HEADROOM | HU3900512755 | YES | YES | 0.023 | -0.64237 | -0.68319 | -0.71584 | -0.75462 | -0.80564 | -0.83625 | -0.90053 | -0.96584 | -1.0342 | -1.0924 | -1.1862 | -1.2352 | -1.2424 | 0.03518 | 0.014771 | -0.0015551 | -0.025024 | -0.048494 | -0.066861 | -0.099514 | -0.13319 | -0.16992 | -0.20564 | -0.28013 | -0.32298 | -0.45564 | -0.25156 | -0.28727 | -0.31686 | -0.34951 | -0.39033 | -0.41788 | -0.46992 | -0.52604 | -0.58217 | -0.63727 | -0.72911 | -0.77604 | -0.78217
|  | SUMBURGH | EE |  |  |  |  | -0.64237 | -0.68319 | -0.71584 | -0.75462 | -0.80564 | -0.83625 | -0.90053 | -0.96584 | -1.0342 | -1.0924 | -1.1862 | -1.2056 | -1.223 | 0.03518 | 0.014771 | -0.0015551 | -0.025024 | -0.048494 | -0.066861 | -0.099514 | -0.13319 | -0.16992 | -0.20564 | -0.28013 | -0.32298 | -0.39543 | -0.25156 | -0.28727 | -0.31686 | -0.34951 | -0.39033 | -0.41788 | -0.46992 | -0.52604 | -0.58217 | -0.63727 | -0.72911 | -0.74747 | -0.7638
|  | SUMBURGH | HT |  |  |  |  | -0.62604 | -0.6536 | -0.68013 | -0.70564 | -0.74645 | -0.77809 | -0.82604 | -0.88115 | -0.9087 | -0.96074 | -1.1842 | -1.2352 | -1.2424 | 0.046404 | 0.033139 | 0.019873 | 0.0035469 | -0.015841 | -0.033188 | -0.057678 | -0.085229 | -0.098494 | -0.124 | -0.25768 | -0.28319 | -0.29135 | -0.24135 | -0.26584 | -0.29033 | -0.3138 | -0.34645 | -0.37502 | -0.41482 | -0.46074 | -0.48625 | -0.53217 | -0.72502 | -0.77604 | -0.78217
|  | SUMBURGH | HE |  |  |  |  | -0.62604 | -0.64849 | -0.67196 | -0.69033 | -0.72298 | -0.74951 | -0.78931 | -0.83931 | -0.86074 | -0.9036 | -1.1301 | -1.1465 | -1.1526 | 0.043343 | 0.032118 | 0.019873 | 0.0076286 | -0.008698 | -0.020943 | -0.044412 | -0.069922 | -0.082167 | -0.10666 | -0.24237 | -0.27911 | -0.34237 | -0.24135 | -0.26074 | -0.28013 | -0.29849 | -0.32502 | -0.34543 | -0.37809 | -0.41788 | -0.43931 | -0.47502 | -0.674 | -0.69135 | -0.69747
|  | SUMBURGH | CF |  |  |  |  | -0.61992 | -0.63931 | -0.6587 | -0.68523 | -0.70156 | -0.72809 | -0.74849 | -0.78319 | -0.81482 | -0.84849 | -0.98829 | -1.0944 | -1.1465 | 0.047424 | 0.03722 | 0.027016 | 0.01069 | 0.0015061 | -0.01482 | -0.027065 | -0.046453 | -0.065841 | -0.085229 | -0.18523 | -0.30258 | -0.45564 | -0.23727 | -0.25156 | -0.26992 | -0.29135 | -0.30666 | -0.32911 | -0.34645 | -0.37196 | -0.39951 | -0.42809 | -0.54339 | -0.63523 | -0.69033
| ALNESS | TAIN | MINIMUM HEADROOM | NH 77578 81489 | NO | NO | 1.422 | 7.8634 | 7.7206 | 7.5512 | 7.3961 | 15.8995 | 15.6332 | 15.1383 | 14.6097 | 14.1608 | 13.6138 | 12.3781 | 12.022 | 11.9638 | 9.5185 | 9.4236 | 9.3032 | 9.192 | 17.3057 | 17.122 | 16.9567 | 16.5965 | 16.2516 | 15.9342 | 15.1291 | 14.6975 | 13.7036 | 8.9047 | 8.7558 | 8.5639 | 8.3935 | 16.6383 | 16.3648 | 16.0546 | 15.5506 | 15.0189 | 14.5189 | 13.4138 | 12.9965 | 12.9332
|  | TAIN | EE |  |  |  |  | 7.8634 | 7.7206 | 7.5512 | 7.3961 | 15.8995 | 15.6332 | 15.375 | 14.7648 | 14.175 | 13.6138 | 12.3781 | 12.2332 | 12.1659 | 9.5185 | 9.4236 | 9.3032 | 9.192 | 17.3057 | 17.122 | 16.9567 | 16.5965 | 16.2516 | 15.9342 | 15.1291 | 14.8689 | 14.4791 | 8.9047 | 8.7558 | 8.5639 | 8.3935 | 16.6383 | 16.3648 | 16.1067 | 15.5506 | 15.0189 | 14.5189 | 13.4138 | 13.2822 | 13.2006
|  | TAIN | HT |  |  |  |  | 7.9236 | 7.8001 | 7.6726 | 7.5318 | 16.073 | 15.6332 | 15.1383 | 14.6097 | 14.1608 | 13.722 | 12.6608 | 12.1332 | 12.0659 | 9.5818 | 9.5042 | 9.4257 | 9.3369 | 17.4934 | 17.2455 | 16.9852 | 16.6975 | 16.4628 | 16.2159 | 15.4801 | 15.1434 | 15.1046 | 9.0068 | 8.8772 | 8.7496 | 8.5966 | 16.8975 | 16.4822 | 16.0546 | 15.5904 | 15.2026 | 14.8046 | 13.6904 | 13.1781 | 13.123
|  | TAIN | HE |  |  |  |  | 7.9144 | 7.8114 | 7.7052 | 7.5869 | 16.1444 | 15.974 | 15.7822 | 15.4077 | 15.0138 | 14.6373 | 12.7036 | 12.022 | 11.9638 | 9.5716 | 9.4991 | 9.4226 | 9.3369 | 17.4873 | 17.3699 | 17.2332 | 16.9893 | 16.7424 | 16.522 | 15.2791 | 14.6975 | 14.3352 | 8.9996 | 8.8772 | 8.7496 | 8.6047 | 16.924 | 16.7291 | 16.4934 | 16.1373 | 15.7873 | 15.4291 | 13.6934 | 12.9965 | 12.9332
|  | TAIN | CF |  |  |  |  | 7.9257 | 7.8461 | 7.7532 | 7.6614 | 16.2506 | 16.1026 | 15.9842 | 15.8628 | 15.6067 | 15.3159 | 13.873 | 12.7322 | 12.024 | 9.5808 | 9.5308 | 9.4624 | 9.4022 | 17.5822 | 17.4781 | 17.3761 | 17.2791 | 17.0985 | 16.9087 | 15.8965 | 14.8138 | 13.7036 | 9.0078 | 8.9343 | 8.8292 | 8.7394 | 17.1006 | 16.9455 | 16.8087 | 16.6893 | 16.4352 | 16.171 | 14.8404 | 13.7414 | 12.9597
| ARDMORE / HARRIS GRID | TARBERT | MINIMUM HEADROOM | NB 15289 00157 | NO | YES | 0.14 | 0.050669 | -0.0054531 | -0.11158 | -0.19321 | -0.25443 | -0.35851 | -0.46158 | -0.54423 | -0.65341 | -0.74831 | -0.97382 | -1.0432 | -1.0616 | 0.33638 | 0.30577 | 0.2323 | 0.17822 | 0.14455 | 0.065976 | -0.0054531 | -0.060555 | -0.133 | -0.19627 | -0.37076 | -0.44933 | -0.72076 | 0.21291 | 0.15781 | 0.054751 | -0.024841 | -0.079943 | -0.17994 | -0.28096 | -0.35851 | -0.46464 | -0.55443 | -0.76362 | -0.82586 | -0.84525
|  | TARBERT | EE |  |  |  |  | 0.050669 | -0.0054531 | -0.11158 | -0.19321 | -0.25443 | -0.35851 | -0.46158 | -0.54423 | -0.65341 | -0.74831 | -0.97382 | -1.0065 | -1.031 | 0.33638 | 0.30577 | 0.2323 | 0.17822 | 0.14455 | 0.065976 | -0.0054531 | -0.060555 | -0.133 | -0.19627 | -0.37076 | -0.44933 | -0.57994 | 0.21291 | 0.16087 | 0.054751 | -0.024841 | -0.079943 | -0.17994 | -0.28096 | -0.35851 | -0.46464 | -0.55443 | -0.76362 | -0.79321 | -0.81668
|  | TARBERT | HT |  |  |  |  | 0.086384 | -0.0054531 | -0.054433 | -0.1177 | -0.19525 | -0.26668 | -0.3228 | -0.40443 | -0.48607 | -0.57586 | -0.89627 | -1.0432 | -1.0616 | 0.37108 | 0.31189 | 0.2874 | 0.24761 | 0.19149 | 0.14659 | 0.11496 | 0.060873 | 0.0067918 | -0.050351 | -0.26362 | -0.35749 | -0.36872 | 0.24965 | 0.15781 | 0.11189 | 0.050669 | -0.020759 | -0.088106 | -0.13913 | -0.21668 | -0.29627 | -0.37994 | -0.68709 | -0.82586 | -0.84525
|  | TARBERT | HE |  |  |  |  | 0.086384 | 0.046588 | -0.033004 | -0.081984 | -0.12586 | -0.20341 | -0.25239 | -0.32994 | -0.39831 | -0.4728 | -0.83198 | -0.92688 | -0.94117 | 0.37108 | 0.34761 | 0.29047 | 0.25679 | 0.23128 | 0.16598 | 0.13434 | 0.081282 | 0.034343 | -0.017698 | -0.26974 | -0.38811 | -0.50851 | 0.24965 | 0.21291 | 0.1323 | 0.083322 | 0.042506 | -0.036065 | -0.077902 | -0.15239 | -0.21464 | -0.28811 | -0.62484 | -0.71464 | -0.72688
|  | TARBERT | CF |  |  |  |  | 0.093527 | 0.063935 | 0.020057 | -0.049331 | -0.084024 | -0.12892 | -0.19525 | -0.22994 | -0.2779 | -0.32382 | -0.56974 | -0.80647 | -0.92994 | 0.37618 | 0.35985 | 0.33026 | 0.28026 | 0.25679 | 0.22414 | 0.16598 | 0.13944 | 0.10067 | 0.065976 | -0.14933 | -0.4228 | -0.72076 | 0.25781 | 0.2323 | 0.18944 | 0.117 | 0.083322 | 0.038424 | -0.031984 | -0.063616 | -0.11362 | -0.15545 | -0.39219 | -0.6177 | -0.7177
| PORT ANN | TARBERT JURA | MINIMUM HEADROOM | NR 60552 82166 | YES | YES | 0.092 | 0.16447 | 0.15631 | 0.15529 | 0.15529 | 0.15427 | 0.14611 | 0.14509 | 0.1359 | 0.13488 | 0.13692 | 0.13386 | 0.13386 | 0.13386 | 0.15362 | 0.14647 | 0.14545 | 0.14545 | 0.14443 | 0.13627 | 0.13525 | 0.12709 | 0.12607 | 0.13117 | 0.12504 | 0.13015 | 0.12811 | 0.16058 | 0.15241 | 0.15037 | 0.15037 | 0.14935 | 0.14119 | 0.14017 | 0.132 | 0.12996 | 0.13302 | 0.12894 | 0.13098 | 0.13098
|  | TARBERT JURA | EE |  |  |  |  | 0.16447 | 0.15631 | 0.15529 | 0.15529 | 0.15427 | 0.14611 | 0.14509 | 0.1359 | 0.13488 | 0.13692 | 0.13488 | 0.13488 | 0.13386 | 0.15362 | 0.14647 | 0.14545 | 0.14545 | 0.14443 | 0.13627 | 0.13525 | 0.12709 | 0.12607 | 0.13117 | 0.13117 | 0.13117 | 0.13015 | 0.16058 | 0.15241 | 0.15037 | 0.15037 | 0.14935 | 0.14119 | 0.14017 | 0.132 | 0.12996 | 0.13302 | 0.132 | 0.132 | 0.13098
|  | TARBERT JURA | HT |  |  |  |  | 0.16549 | 0.16345 | 0.16345 | 0.15529 | 0.15529 | 0.15427 | 0.15325 | 0.14509 | 0.14304 | 0.14304 | 0.13488 | 0.13386 | 0.13386 | 0.15464 | 0.15362 | 0.15362 | 0.14545 | 0.14545 | 0.14443 | 0.14341 | 0.13525 | 0.13423 | 0.13423 | 0.13117 | 0.13015 | 0.13015 | 0.16058 | 0.15956 | 0.15956 | 0.15037 | 0.15037 | 0.14935 | 0.14833 | 0.14017 | 0.13915 | 0.13915 | 0.132 | 0.13098 | 0.13098
|  | TARBERT JURA | HE |  |  |  |  | 0.16549 | 0.16345 | 0.16345 | 0.15529 | 0.15529 | 0.15427 | 0.15325 | 0.14611 | 0.14407 | 0.14202 | 0.13488 | 0.13488 | 0.13488 | 0.15464 | 0.15362 | 0.15362 | 0.14545 | 0.14545 | 0.14443 | 0.14341 | 0.13627 | 0.13525 | 0.13321 | 0.13117 | 0.13117 | 0.13117 | 0.16058 | 0.15956 | 0.15956 | 0.15037 | 0.15037 | 0.14935 | 0.14833 | 0.14119 | 0.14017 | 0.13711 | 0.132 | 0.132 | 0.132
|  | TARBERT JURA | CF |  |  |  |  | 0.16549 | 0.16345 | 0.16345 | 0.16345 | 0.15631 | 0.15529 | 0.15529 | 0.15427 | 0.15427 | 0.14611 | 0.13386 | 0.13488 | 0.13386 | 0.15464 | 0.15362 | 0.15362 | 0.15362 | 0.14647 | 0.14545 | 0.14545 | 0.14443 | 0.14443 | 0.13627 | 0.12504 | 0.13117 | 0.12811 | 0.16058 | 0.15956 | 0.15956 | 0.15956 | 0.15241 | 0.15037 | 0.15037 | 0.14935 | 0.14935 | 0.14119 | 0.12894 | 0.132 | 0.13098
| PORT ANN | TARBERT LOCH FYNE | MINIMUM HEADROOM | NR 86003 68479 | NO | YES | 1.516 | 0.92675 | 0.8492 | 0.76654 | 0.67164 | 0.57471 | 0.46246 | 0.32267 | 0.18695 | 0.099196 | -0.0079469 | -0.27631 | -0.37529 | -0.39264 | 1.6441 | 1.5961 | 1.5431 | 1.4798 | 1.4237 | 1.3492 | 1.2563 | 1.1614 | 1.1023 | 1.0318 | 0.81756 | 0.72369 | 0.45838 | 1.2921 | 1.2237 | 1.1431 | 1.0543 | 0.96654 | 0.86144 | 0.73083 | 0.60124 | 0.51858 | 0.41654 | 0.16144 | 0.066543 | 0.050216
|  | TARBERT LOCH FYNE | EE |  |  |  |  | 0.92675 | 0.8492 | 0.76654 | 0.67164 | 0.57471 | 0.46246 | 0.32267 | 0.18695 | 0.099196 | -0.0079469 | -0.27631 | -0.32121 | -0.35795 | 1.6441 | 1.5961 | 1.5431 | 1.4798 | 1.4237 | 1.3492 | 1.2563 | 1.1614 | 1.1023 | 1.0318 | 0.81756 | 0.72369 | 0.57675 | 1.2921 | 1.2237 | 1.1431 | 1.0543 | 0.96654 | 0.86144 | 0.73083 | 0.60124 | 0.51858 | 0.41654 | 0.16144 | 0.12062 | 0.081849
|  | TARBERT LOCH FYNE | HT |  |  |  |  | 0.96144 | 0.88389 | 0.80124 | 0.73083 | 0.64001 | 0.55532 | 0.47777 | 0.37675 | 0.28593 | 0.18287 | -0.19264 | -0.37529 | -0.39264 | 1.6737 | 1.6278 | 1.5808 | 1.5359 | 1.4859 | 1.4298 | 1.39 | 1.3227 | 1.2655 | 1.1931 | 0.93083 | 0.81144 | 0.79716 | 1.3267 | 1.2584 | 1.1829 | 1.1165 | 1.0359 | 0.95532 | 0.88389 | 0.78899 | 0.70226 | 0.60532 | 0.24001 | 0.066543 | 0.050216
|  | TARBERT LOCH FYNE | HE |  |  |  |  | 0.96144 | 0.90226 | 0.84205 | 0.78287 | 0.70124 | 0.62777 | 0.53899 | 0.45532 | 0.38287 | 0.29818 | -0.088559 | -0.18856 | -0.19672 | 1.6727 | 1.6359 | 1.6002 | 1.5584 | 1.5125 | 1.4604 | 1.4084 | 1.3502 | 1.2972 | 1.238 | 0.95532 | 0.82573 | 0.7043 | 1.3267 | 1.2757 | 1.2196 | 1.1625 | 1.091 | 1.0206 | 0.94205 | 0.86246 | 0.79001 | 0.71144 | 0.34409 | 0.2492 | 0.24307
|  | TARBERT LOCH FYNE | CF |  |  |  |  | 0.97164 | 0.94001 | 0.89511 | 0.85634 | 0.7992 | 0.75532 | 0.67981 | 0.60022 | 0.55838 | 0.49307 | 0.16858 | -0.059988 | -0.20591 | 1.6808 | 1.6604 | 1.6278 | 1.6063 | 1.5645 | 1.5359 | 1.4839 | 1.4267 | 1.3972 | 1.3472 | 1.0716 | 0.79307 | 0.45838 | 1.337 | 1.3063 | 1.2645 | 1.2288 | 1.1767 | 1.1349 | 1.0676 | 0.99307 | 0.95634 | 0.89511 | 0.58389 | 0.36552 | 0.23083
| TAYNUILT | TAYNUILT | MINIMUM HEADROOM | NN 01856 31079 | NO | YES | 0.203 | 2.3911 | 2.3513 | 2.3247 | 2.2911 | 2.2431 | 2.1962 | 2.1605 | 2.1013 | 2.039 | 1.9849 | 1.8605 | 1.8145 | 1.7982 | 2.788 | 2.7615 | 2.7411 | 2.7186 | 2.6809 | 2.6451 | 2.6217 | 2.5758 | 2.5288 | 2.4921 | 2.387 | 2.3309 | 2.1217 | 2.6513 | 2.6125 | 2.586 | 2.5543 | 2.5054 | 2.4564 | 2.4278 | 2.3707 | 2.3094 | 2.2584 | 2.1411 | 2.0962 | 2.0788
|  | TAYNUILT | EE |  |  |  |  | 2.3911 | 2.3513 | 2.3247 | 2.2911 | 2.2431 | 2.1962 | 2.1605 | 2.1013 | 2.039 | 1.9849 | 1.8605 | 1.8349 | 1.8176 | 2.788 | 2.7615 | 2.7411 | 2.7186 | 2.6809 | 2.6451 | 2.6217 | 2.5758 | 2.5288 | 2.4921 | 2.387 | 2.3339 | 2.2462 | 2.6513 | 2.6125 | 2.586 | 2.5543 | 2.5054 | 2.4564 | 2.4278 | 2.3707 | 2.3094 | 2.2584 | 2.1411 | 2.1176 | 2.0992
|  | TAYNUILT | HT |  |  |  |  | 2.4033 | 2.3778 | 2.3502 | 2.3268 | 2.2941 | 2.2656 | 2.2258 | 2.1758 | 2.1482 | 2.0992 | 1.8962 | 1.8145 | 1.7982 | 2.8002 | 2.786 | 2.7676 | 2.7523 | 2.7278 | 2.7105 | 2.6809 | 2.6441 | 2.6298 | 2.5972 | 2.4451 | 2.3921 | 2.3819 | 2.6707 | 2.6492 | 2.6247 | 2.5992 | 2.5656 | 2.539 | 2.4951 | 2.4482 | 2.4217 | 2.3747 | 2.1788 | 2.0962 | 2.0788
|  | TAYNUILT | HE |  |  |  |  | 2.4013 | 2.3809 | 2.3625 | 2.3441 | 2.3166 | 2.2951 | 2.2574 | 2.2125 | 2.19 | 2.1482 | 1.9329 | 1.8768 | 1.8737 | 2.7982 | 2.786 | 2.7707 | 2.7584 | 2.7339 | 2.7196 | 2.69 | 2.6533 | 2.64 | 2.6094 | 2.44 | 2.3645 | 2.288 | 2.6686 | 2.6502 | 2.6298 | 2.6125 | 2.5819 | 2.5615 | 2.5227 | 2.4758 | 2.4584 | 2.4135 | 2.2115 | 2.1574 | 2.1533
|  | TAYNUILT | CF |  |  |  |  | 2.4043 | 2.39 | 2.3727 | 2.3523 | 2.338 | 2.3145 | 2.289 | 2.2676 | 2.24 | 2.2074 | 2.0758 | 1.9339 | 1.8635 | 2.8043 | 2.7911 | 2.7798 | 2.7625 | 2.7523 | 2.7319 | 2.7074 | 2.688 | 2.6635 | 2.636 | 2.5125 | 2.3309 | 2.1217 | 2.6758 | 2.6625 | 2.6451 | 2.6227 | 2.6105 | 2.586 | 2.5605 | 2.5411 | 2.5115 | 2.4788 | 2.3472 | 2.2064 | 2.1411
| BURGHMUIR | THIMBLEROW | MINIMUM HEADROOM | NO 11356 23764 | NO | YES | 1.037 | 10.4659 | 10.3077 | 10.1291 | 9.9057 | 9.524 | 9.1251 | 8.6271 | 8.0087 | 7.422 | 6.8832 | 5.3149 | 5.0791 | 5.0944 | 15.8526 | 15.7547 | 15.6404 | 15.5261 | 15.2985 | 15.0159 | 14.6751 | 14.2567 | 13.8506 | 13.4393 | 12.1016 | 11.1128 | 7.1526 | 13.92 | 13.773 | 13.4414 | 13.0944 | 12.7016 | 12.2802 | 11.7883 | 11.0985 | 10.4506 | 9.873 | 8.4251 | 8.0914 | 8.1016
|  | THIMBLEROW | EE |  |  |  |  | 10.4659 | 10.3077 | 10.1291 | 9.9057 | 9.524 | 9.1251 | 8.6271 | 8.0087 | 7.422 | 6.8832 | 5.4383 | 5.8536 | 5.7516 | 15.8526 | 15.7547 | 15.6404 | 15.5261 | 15.2985 | 15.0159 | 14.6751 | 14.2567 | 13.8506 | 13.4393 | 12.1016 | 11.3261 | 9.6526 | 13.92 | 13.773 | 13.4414 | 13.0944 | 12.7016 | 12.2802 | 11.7883 | 11.0985 | 10.4506 | 9.873 | 8.5322 | 8.7659 | 8.6332
|  | THIMBLEROW | HT |  |  |  |  | 10.5077 | 10.3567 | 10.2026 | 10.0659 | 9.8434 | 9.5455 | 9.0965 | 8.6016 | 8.1261 | 7.5904 | 5.3149 | 5.0791 | 5.0944 | 15.8965 | 15.8169 | 15.7342 | 15.6547 | 15.5628 | 15.4659 | 15.2251 | 14.9424 | 14.67 | 14.3618 | 12.8506 | 12.524 | 12.4934 | 13.9608 | 13.824 | 13.6342 | 13.3649 | 13.0598 | 12.7608 | 12.3149 | 11.8189 | 11.3659 | 10.871 | 8.4251 | 8.0914 | 8.1016
|  | THIMBLEROW | HE |  |  |  |  | 10.5179 | 10.4118 | 10.3047 | 10.1883 | 10.072 | 9.9628 | 9.7893 | 9.423 | 9.0996 | 8.7455 | 7.2363 | 6.6577 | 7.0781 | 15.8965 | 15.8271 | 15.7536 | 15.674 | 15.5853 | 15.5047 | 15.3628 | 15.1118 | 14.8863 | 14.6087 | 13.1567 | 11.9669 | 10.6751 | 13.97 | 13.872 | 13.7751 | 13.6689 | 13.4781 | 13.2924 | 12.9628 | 12.5934 | 12.2659 | 11.9057 | 10.2291 | 9.6485 | 10.1353
|  | THIMBLEROW | CF |  |  |  |  | 10.5679 | 10.5271 | 10.47 | 10.4118 | 10.3434 | 10.271 | 10.2036 | 10.1077 | 10.0281 | 9.9404 | 9.0526 | 7.6904 | 6.371 | 15.921 | 15.8812 | 15.8281 | 15.7751 | 15.7098 | 15.6373 | 15.5659 | 15.4057 | 15.2281 | 15.0342 | 13.6863 | 11.1128 | 7.1526 | 14.0128 | 13.9761 | 13.92 | 13.8679 | 13.8047 | 13.7016 | 13.5791 | 13.4006 | 13.2465 | 13.0863 | 11.9506 | 10.4955 | 9.3363
| TAYNUILT | TIRORAN BRIDGE | MINIMUM HEADROOM | NM 48666 28729 | YES | YES | 0 | 0.19416 | 0.18498 | 0.18294 | 0.17376 | 0.17273 | 0.17069 | 0.16049 | 0.15743 | 0.15947 | 0.15845 | 0.15131 | 0.14722 | 0.14722 | 0.19045 | 0.18229 | 0.18229 | 0.17412 | 0.1731 | 0.1731 | 0.1629 | 0.16596 | 0.1629 | 0.16188 | 0.1629 | 0.16188 | 0.15984 | 0.19537 | 0.1872 | 0.18414 | 0.17598 | 0.17496 | 0.17292 | 0.16271 | 0.16067 | 0.16169 | 0.16067 | 0.15455 | 0.15149 | 0.15149
|  | TIRORAN BRIDGE | EE |  |  |  |  | 0.19416 | 0.18498 | 0.18294 | 0.17376 | 0.17273 | 0.17069 | 0.16049 | 0.15743 | 0.16355 | 0.16151 | 0.15131 | 0.15029 | 0.15029 | 0.19045 | 0.18229 | 0.18229 | 0.17412 | 0.1731 | 0.1731 | 0.1629 | 0.16596 | 0.17004 | 0.16902 | 0.1629 | 0.1629 | 0.15984 | 0.19537 | 0.1872 | 0.18414 | 0.17598 | 0.17496 | 0.17292 | 0.16271 | 0.16067 | 0.16578 | 0.16373 | 0.15455 | 0.15455 | 0.15353
|  | TIRORAN BRIDGE | HT |  |  |  |  | 0.19518 | 0.19212 | 0.18294 | 0.18294 | 0.1809 | 0.17886 | 0.16865 | 0.16865 | 0.15947 | 0.15845 | 0.15335 | 0.14722 | 0.14722 | 0.19147 | 0.18943 | 0.18229 | 0.18229 | 0.18127 | 0.18024 | 0.17106 | 0.17106 | 0.1629 | 0.16188 | 0.16494 | 0.16188 | 0.16188 | 0.19639 | 0.19435 | 0.18414 | 0.18414 | 0.18312 | 0.18108 | 0.1719 | 0.17088 | 0.16169 | 0.16067 | 0.15761 | 0.15149 | 0.15149
|  | TIRORAN BRIDGE | HE |  |  |  |  | 0.19518 | 0.19212 | 0.18498 | 0.18294 | 0.18294 | 0.18294 | 0.17273 | 0.17171 | 0.16253 | 0.15947 | 0.15641 | 0.15335 | 0.15233 | 0.19147 | 0.18943 | 0.18229 | 0.18229 | 0.18229 | 0.18229 | 0.1731 | 0.1731 | 0.16494 | 0.1629 | 0.16698 | 0.16494 | 0.16188 | 0.19639 | 0.19435 | 0.1872 | 0.18414 | 0.18414 | 0.18414 | 0.17496 | 0.17394 | 0.16476 | 0.16271 | 0.15965 | 0.15659 | 0.15557
|  | TIRORAN BRIDGE | CF |  |  |  |  | 0.19518 | 0.19314 | 0.19212 | 0.18396 | 0.18396 | 0.18396 | 0.18192 | 0.17478 | 0.17273 | 0.17273 | 0.15845 | 0.15641 | 0.15233 | 0.19147 | 0.19045 | 0.18943 | 0.18229 | 0.18229 | 0.18229 | 0.18127 | 0.17412 | 0.1731 | 0.1731 | 0.16698 | 0.16392 | 0.15984 | 0.19639 | 0.19537 | 0.19435 | 0.18516 | 0.18516 | 0.18516 | 0.18414 | 0.177 | 0.17496 | 0.17496 | 0.16169 | 0.15965 | 0.15557
| BOAT OF GARTEN | TOMATIN | MINIMUM HEADROOM | NH 79106 29734 | YES | YES | 1.304 | -0.62589 | -0.64528 | -0.67181 | -0.69426 | -0.72283 | -0.82793 | -0.97079 | -1.1238 | -1.2106 | -1.2422 | -1.382 | -1.4065 | -1.4116 | -0.25854 | -0.26977 | -0.28916 | -0.30344 | -0.32793 | -0.35956 | -0.43507 | -0.51364 | -0.55854 | -0.59834 | -0.67487 | -0.69834 | -0.78916 | -0.36977 | -0.38916 | -0.42283 | -0.4412 | -0.47691 | -0.55242 | -0.67895 | -0.80956 | -0.88201 | -0.93609 | -1.0555 | -1.0759 | -1.0749
|  | TOMATIN | EE |  |  |  |  | -0.62589 | -0.64528 | -0.67181 | -0.69426 | -0.72283 | -0.74426 | -0.77895 | -0.92895 | -1.0708 | -1.2422 | -1.382 | -1.3963 | -1.3963 | -0.25854 | -0.26977 | -0.28916 | -0.30344 | -0.32793 | -0.34222 | -0.36875 | -0.45446 | -0.51569 | -0.59834 | -0.67487 | -0.69834 | -0.73507 | -0.36977 | -0.38916 | -0.42283 | -0.4412 | -0.47691 | -0.4963 | -0.54018 | -0.68507 | -0.7963 | -0.93609 | -1.0555 | -1.0667 | -1.0636
|  | TOMATIN | HT |  |  |  |  | -0.61875 | -0.63609 | -0.65446 | -0.67487 | -0.69936 | -0.82793 | -0.97079 | -1.1238 | -1.2106 | -1.2412 | -1.3494 | -1.4065 | -1.4116 | -0.24936 | -0.25752 | -0.27079 | -0.28201 | -0.30038 | -0.35956 | -0.43507 | -0.51364 | -0.55854 | -0.57691 | -0.65038 | -0.67895 | -0.67691 | -0.35752 | -0.37283 | -0.39528 | -0.41467 | -0.44222 | -0.55242 | -0.67895 | -0.80956 | -0.88201 | -0.91262 | -1.0259 | -1.0759 | -1.0749
|  | TOMATIN | HE |  |  |  |  | -0.61875 | -0.63201 | -0.64834 | -0.66364 | -0.68099 | -0.69936 | -0.72283 | -0.81875 | -0.93099 | -1.0494 | -1.3432 | -1.383 | -1.3881 | -0.24936 | -0.2565 | -0.26977 | -0.27793 | -0.29732 | -0.30242 | -0.32181 | -0.37385 | -0.43405 | -0.49528 | -0.65344 | -0.69324 | -0.73201 | -0.35752 | -0.36875 | -0.39018 | -0.40344 | -0.42691 | -0.43813 | -0.46467 | -0.56058 | -0.66262 | -0.76875 | -1.0157 | -1.0514 | -1.0514
|  | TOMATIN | CF |  |  |  |  | -0.61467 | -0.62793 | -0.64018 | -0.65446 | -0.66773 | -0.68201 | -0.69426 | -0.71262 | -0.79732 | -0.88916 | -1.2116 | -1.3096 | -1.3718 | -0.24528 | -0.25548 | -0.26262 | -0.27691 | -0.28507 | -0.29732 | -0.30446 | -0.31977 | -0.37385 | -0.41977 | -0.59834 | -0.69018 | -0.78916 | -0.35446 | -0.36773 | -0.38201 | -0.39936 | -0.4116 | -0.43201 | -0.43916 | -0.46058 | -0.54936 | -0.62691 | -0.90038 | -1.0014 | -1.0432
| LAIRG | TORBOLL | MINIMUM HEADROOM | NC 75779 00296 | YES | NO | 0 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10269 | 0.10269 | 0.10269 | 0.10269 | 0.10269 | 0.096571 | 0.094531 | 0.094531 | 0.094531 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.097776 | 0.097776 | 0.097776 | 0.097776 | 0.097776 | 0.090633 | 0.089612 | 0.089612 | 0.089612 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10126 | 0.10126 | 0.10126 | 0.10126 | 0.10126 | 0.094112 | 0.092071 | 0.092071 | 0.092071
|  | TORBOLL | EE |  |  |  |  | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10269 | 0.10269 | 0.10269 | 0.10371 | 0.10371 | 0.096571 | 0.094531 | 0.094531 | 0.094531 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.097776 | 0.097776 | 0.097776 | 0.098796 | 0.097776 | 0.090633 | 0.089612 | 0.089612 | 0.089612 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10126 | 0.10126 | 0.10126 | 0.10228 | 0.10126 | 0.094112 | 0.092071 | 0.092071 | 0.092071
|  | TORBOLL | HT |  |  |  |  | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10984 | 0.10984 | 0.10269 | 0.10371 | 0.10371 | 0.10371 | 0.094531 | 0.094531 | 0.094531 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.10492 | 0.097776 | 0.098796 | 0.098796 | 0.098796 | 0.089612 | 0.089612 | 0.089612 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.1084 | 0.10126 | 0.10228 | 0.10228 | 0.10228 | 0.092071 | 0.092071 | 0.092071
|  | TORBOLL | HE |  |  |  |  | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10984 | 0.10269 | 0.10269 | 0.10269 | 0.10371 | 0.094531 | 0.094531 | 0.094531 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10492 | 0.097776 | 0.097776 | 0.097776 | 0.098796 | 0.089612 | 0.089612 | 0.089612 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.1084 | 0.10126 | 0.10126 | 0.10126 | 0.10228 | 0.092071 | 0.092071 | 0.092071
|  | TORBOLL | CF |  |  |  |  | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.11188 | 0.10473 | 0.10473 | 0.10473 | 0.10269 | 0.094531 | 0.094531 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.10594 | 0.098796 | 0.098796 | 0.098796 | 0.097776 | 0.089612 | 0.089612 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10942 | 0.10228 | 0.10228 | 0.10228 | 0.10126 | 0.093092 | 0.092071
| KINTORE | TORRYBURN | MINIMUM HEADROOM | NJ 79129 15653 | NO | YES | 2.005 | 11.6211 | 11.0598 | 10.1772 | 9.0109 | 7.97 | 6.0568 | 5.0068 | 3.87 | 2.7639 | 1.8119 | -3.4585 | -8.0493 | -11.8749 | 13.1221 | 12.6476 | 11.7476 | 10.668 | 9.97 | 8.2017 | 7.5394 | 6.7251 | 5.7935 | 4.5823 | -0.43608 | -5.1055 | -9.4483 | 12.4507 | 11.9588 | 11.0721 | 9.8996 | 9.0721 | 7.1445 | 6.3017 | 5.316 | 4.3323 | 3.1884 | -2.6147 | -7.684 | -12.2453
|  | TORRYBURN | EE |  |  |  |  | 11.6221 | 11.0721 | 10.4792 | 9.8211 | 8.5762 | 7.1007 | 5.8323 | 5.069 | 3.7547 | 2.5598 | -1.8626 | -6.082 | -7.5779 | 13.1456 | 12.6639 | 12.1292 | 11.5476 | 10.5639 | 9.3547 | 8.468 | 7.9333 | 6.9425 | 6.1017 | 3.1078 | -1.1289 | -2.7789 | 12.466 | 11.9884 | 11.4394 | 10.7639 | 9.6486 | 8.2731 | 7.1966 | 6.4956 | 5.3149 | 4.2966 | 0.13943 | -4.7157 | -6.4902
|  | TORRYBURN | HT |  |  |  |  | 11.6211 | 11.0598 | 10.1772 | 9.0109 | 7.97 | 6.0568 | 5.0068 | 3.87 | 2.7639 | 1.8119 | -2.6453 | -7.3565 | -10.7024 | 13.1221 | 12.6476 | 11.7476 | 10.668 | 9.97 | 8.2017 | 7.5394 | 6.7915 | 6.0966 | 5.366 | 2.3068 | -2.6728 | -6.733 | 12.4507 | 11.9588 | 11.0721 | 9.8996 | 9.0721 | 7.1445 | 6.3017 | 5.316 | 4.3323 | 3.4394 | -0.79527 | -6.2606 | -10.3473
|  | TORRYBURN | HE |  |  |  |  | 11.6864 | 11.1935 | 10.4445 | 9.5119 | 8.6527 | 6.9496 | 5.8568 | 4.7466 | 3.6027 | 2.4292 | -3.4585 | -8.0493 | -11.8749 | 13.1874 | 12.7598 | 11.9915 | 11.0211 | 10.2119 | 8.5292 | 7.6404 | 6.7251 | 5.7935 | 4.5823 | -0.43608 | -5.1055 | -9.4483 | 12.5149 | 12.0762 | 11.3292 | 10.368 | 9.4711 | 7.6629 | 6.6445 | 5.5874 | 4.5098 | 3.1884 | -2.6147 | -7.684 | -12.2453
|  | TORRYBURN | CF |  |  |  |  | 11.8598 | 11.5343 | 11.1649 | 10.7711 | 10.0996 | 9.2466 | 8.5741 | 7.8843 | 7.1996 | 6.419 | 3.1649 | 0.49657 | -1.3881 | 13.3404 | 13.0476 | 12.7251 | 12.367 | 11.72 | 10.9721 | 10.4251 | 9.8741 | 9.3404 | 8.7027 | 6.0639 | 3.8792 | 2.62 | 12.669 | 12.3751 | 12.0364 | 11.6874 | 11.0384 | 10.2517 | 9.6374 | 9.0088 | 8.3996 | 7.6833 | 4.5802 | 1.9282 | 0.19351
| LAIRG | TRESSADY | MINIMUM HEADROOM | NC 70537 03678 | YES | NO | 0.013 | 0.26233 | 0.246 | 0.22356 | 0.196 | 0.18172 | 0.15315 | 0.11539 | 0.089882 | 0.052127 | 0.020494 | -0.048894 | -0.069302 | -0.072363 | 0.36427 | 0.35509 | 0.34284 | 0.32243 | 0.31529 | 0.2959 | 0.27345 | 0.25713 | 0.23162 | 0.21223 | 0.17039 | 0.16019 | 0.15917 | 0.3235 | 0.30616 | 0.28779 | 0.26024 | 0.24697 | 0.21942 | 0.18677 | 0.15922 | 0.1235 | 0.094933 | 0.029627 | 0.010239 | 0.0071776
|  | TRESSADY | EE |  |  |  |  | 0.26233 | 0.246 | 0.22356 | 0.196 | 0.18172 | 0.15315 | 0.11539 | 0.089882 | 0.052127 | 0.020494 | -0.048894 | -0.033588 | -0.03869 | 0.36427 | 0.35509 | 0.34284 | 0.32243 | 0.31529 | 0.2959 | 0.27345 | 0.25713 | 0.23162 | 0.21223 | 0.17039 | 0.18162 | 0.17345 | 0.3235 | 0.30616 | 0.28779 | 0.26024 | 0.24697 | 0.21942 | 0.18677 | 0.15922 | 0.1235 | 0.094933 | 0.029627 | 0.043912 | 0.03881
|  | TRESSADY | HT |  |  |  |  | 0.27356 | 0.25825 | 0.24294 | 0.22151 | 0.20723 | 0.18172 | 0.15417 | 0.13988 | 0.11131 | 0.082739 | -0.022363 | -0.069302 | -0.072363 | 0.37345 | 0.36529 | 0.35509 | 0.34386 | 0.33468 | 0.31937 | 0.29998 | 0.29386 | 0.27447 | 0.25611 | 0.18774 | 0.16019 | 0.15917 | 0.33473 | 0.3184 | 0.30616 | 0.28575 | 0.27248 | 0.24901 | 0.22248 | 0.20718 | 0.18065 | 0.1531 | 0.053096 | 0.010239 | 0.0071776
|  | TRESSADY | HE |  |  |  |  | 0.27458 | 0.26029 | 0.25009 | 0.23274 | 0.22049 | 0.19907 | 0.17662 | 0.16233 | 0.13784 | 0.11335 | -0.009098 | -0.03869 | -0.044812 | 0.37447 | 0.36733 | 0.35917 | 0.34794 | 0.3408 | 0.32651 | 0.31019 | 0.30407 | 0.28774 | 0.27039 | 0.19488 | 0.17651 | 0.16937 | 0.33575 | 0.32248 | 0.31126 | 0.29493 | 0.28575 | 0.26534 | 0.24085 | 0.22963 | 0.20718 | 0.18065 | 0.065341 | 0.03881 | 0.034729
|  | TRESSADY | CF |  |  |  |  | 0.27458 | 0.26335 | 0.25009 | 0.23886 | 0.22458 | 0.21539 | 0.19804 | 0.1756 | 0.17253 | 0.15621 | 0.071514 | 0.015392 | -0.017261 | 0.37447 | 0.36733 | 0.35815 | 0.35304 | 0.34488 | 0.33774 | 0.32549 | 0.31121 | 0.31019 | 0.29998 | 0.24182 | 0.20407 | 0.1806 | 0.33575 | 0.32554 | 0.3133 | 0.30208 | 0.28779 | 0.27861 | 0.2633 | 0.24085 | 0.23779 | 0.22248 | 0.14187 | 0.089831 | 0.060239
| SHETLAND | TUMBLIN | MINIMUM HEADROOM | HU3334053363 | YES | YES | 0.183 | 5.0936 | 5.0324 | 4.9661 | 4.9038 | 4.8304 | 4.7498 | 4.6345 | 4.5385 | 4.4191 | 4.3151 | 4.0702 | 3.9947 | 3.9753 | 5.4036 | 5.3547 | 5.3067 | 5.2669 | 5.2016 | 5.1445 | 5.0638 | 5.0077 | 4.924 | 4.8587 | 4.7424 | 4.6802 | 4.4547 | 5.1767 | 5.1196 | 5.0594 | 5.0012 | 4.9318 | 4.8634 | 4.7798 | 4.7002 | 4.6042 | 4.5042 | 4.2696 | 4.194 | 4.1767
|  | TUMBLIN | EE |  |  |  |  | 5.0936 | 5.0324 | 4.9661 | 4.9038 | 4.8304 | 4.7498 | 4.6345 | 4.5385 | 4.4191 | 4.3151 | 4.0702 | 4.0375 | 4.0079 | 5.4036 | 5.3547 | 5.3067 | 5.2669 | 5.2016 | 5.1445 | 5.0638 | 5.0077 | 4.924 | 4.8587 | 4.7424 | 4.6802 | 4.5649 | 5.1767 | 5.1196 | 5.0594 | 5.0012 | 4.9318 | 4.8634 | 4.7798 | 4.7002 | 4.6042 | 4.5042 | 4.2696 | 4.2369 | 4.2083
|  | TUMBLIN | HT |  |  |  |  | 5.114 | 5.062 | 5.012 | 4.9559 | 4.8936 | 4.8365 | 4.7681 | 4.6926 | 4.6161 | 4.5263 | 4.16 | 3.9947 | 3.9753 | 5.4271 | 5.3985 | 5.371 | 5.3394 | 5.2924 | 5.2659 | 5.2108 | 5.1536 | 5.0934 | 5.0271 | 4.7934 | 4.7312 | 4.723 | 5.1971 | 5.1491 | 5.1032 | 5.0512 | 4.994 | 4.941 | 4.8767 | 4.8053 | 4.7349 | 4.6624 | 4.3532 | 4.194 | 4.1767
|  | TUMBLIN | HE |  |  |  |  | 5.113 | 5.0691 | 5.0253 | 4.9773 | 4.9242 | 4.8742 | 4.8059 | 4.7273 | 4.6508 | 4.5691 | 4.1947 | 4.0824 | 4.0355 | 5.4271 | 5.4026 | 5.374 | 5.3455 | 5.3036 | 5.2791 | 5.2271 | 5.1751 | 5.1159 | 5.0536 | 4.8128 | 4.7434 | 4.6353 | 5.1961 | 5.1553 | 5.1145 | 5.0696 | 5.0196 | 4.9736 | 4.9083 | 4.8349 | 4.7634 | 4.6869 | 4.3379 | 4.2318 | 4.1879
|  | TUMBLIN | CF |  |  |  |  | 5.1273 | 5.0967 | 5.0661 | 5.0222 | 4.9896 | 4.9467 | 4.9008 | 4.8651 | 4.8171 | 4.7722 | 4.5089 | 4.2508 | 4.1038 | 5.4322 | 5.4087 | 5.3914 | 5.3628 | 5.3394 | 5.3138 | 5.2771 | 5.2547 | 5.2138 | 5.1812 | 4.9842 | 4.7271 | 4.4547 | 5.2094 | 5.1838 | 5.1583 | 5.1267 | 5.0961 | 5.0604 | 5.0206 | 4.9828 | 4.94 | 4.8951 | 4.6389 | 4.4042 | 4.2542
| TUMMEL BRIDGE | TUMMEL BRIDGE | MINIMUM HEADROOM | NN 75906 59080 | YES | YES | 0.13 | 0.24539 | 0.2209 | 0.19845 | 0.1658 | 0.13927 | 0.10458 | 0.0658 | 0.018861 | -0.025016 | -0.064812 | -0.18318 | -0.21073 | -0.23318 | 0.36682 | 0.35866 | 0.34743 | 0.33519 | 0.32396 | 0.30764 | 0.28111 | 0.24641 | 0.21784 | 0.19029 | 0.10866 | 0.085188 | 0.053555 | 0.19437 | 0.16988 | 0.14539 | 0.1158 | 0.087229 | 0.055596 | 0.017841 | -0.027057 | -0.067873 | -0.10563 | -0.21583 | -0.24236 | -0.26481
|  | TUMMEL BRIDGE | EE |  |  |  |  | 0.24539 | 0.2209 | 0.19845 | 0.1658 | 0.13927 | 0.10458 | 0.0658 | 0.018861 | -0.025016 | -0.064812 | -0.18318 | -0.20971 | -0.21073 | 0.36682 | 0.35866 | 0.34743 | 0.33519 | 0.32396 | 0.30764 | 0.28111 | 0.24641 | 0.21784 | 0.19029 | 0.10866 | 0.09131 | 0.086208 | 0.19437 | 0.16988 | 0.14539 | 0.1158 | 0.087229 | 0.055596 | 0.017841 | -0.027057 | -0.067873 | -0.10563 | -0.21583 | -0.24236 | -0.2444
|  | TUMMEL BRIDGE | HT |  |  |  |  | 0.25151 | 0.23621 | 0.21784 | 0.19641 | 0.17498 | 0.14437 | 0.11886 | 0.080086 | 0.046412 | 0.012739 | -0.13318 | -0.1944 | -0.21583 | 0.3709 | 0.36376 | 0.3556 | 0.34845 | 0.33927 | 0.32804 | 0.31886 | 0.29539 | 0.26988 | 0.24743 | 0.14539 | 0.10253 | 0.087229 | 0.20049 | 0.18315 | 0.16376 | 0.14335 | 0.12192 | 0.093351 | 0.068861 | 0.034167 | 0.00049388 | -0.031139 | -0.16991 | -0.22808 | -0.24747
|  | TUMMEL BRIDGE | HE |  |  |  |  | 0.25151 | 0.23927 | 0.2209 | 0.20151 | 0.17804 | 0.15253 | 0.12498 | 0.086208 | 0.052535 | 0.0158 | -0.15665 | -0.21073 | -0.23318 | 0.3709 | 0.36376 | 0.35764 | 0.34845 | 0.34029 | 0.32804 | 0.31886 | 0.29233 | 0.26682 | 0.24335 | 0.12192 | 0.085188 | 0.068861 | 0.20049 | 0.18315 | 0.16682 | 0.14845 | 0.12498 | 0.10151 | 0.073963 | 0.037229 | 0.0045755 | -0.030118 | -0.19338 | -0.24236 | -0.26481
|  | TUMMEL BRIDGE | CF |  |  |  |  | 0.25049 | 0.24539 | 0.23315 | 0.21886 | 0.2056 | 0.18927 | 0.1709 | 0.15866 | 0.13723 | 0.11172 | -0.018894 | -0.13216 | -0.21583 | 0.37192 | 0.36988 | 0.36478 | 0.35866 | 0.35458 | 0.34743 | 0.33927 | 0.33213 | 0.32192 | 0.30458 | 0.21682 | 0.13825 | 0.053555 | 0.2056 | 0.19539 | 0.18417 | 0.1709 | 0.15968 | 0.14233 | 0.12498 | 0.1056 | 0.086208 | 0.061718 | -0.061751 | -0.16991 | -0.24747
| MACDUFF | TURRIFF | MINIMUM HEADROOM | NJ 72407 50271 | NO | NO | 0.683 | 2.316 | 2.0425 | 1.6323 | 1.1527 | 0.55475 | -0.3126 | -1.2565 | -2.3432 | -3.5116 | -4.5616 | -7.0259 | -8.3248 | -8.8085 | 6.119 | 5.8558 | 5.5333 | 5.1986 | 4.7731 | 4.1792 | 3.4262 | 2.566 | 1.5803 | 0.62924 | -1.1422 | -1.8106 | -2.3657 | 0.89403 | 0.63791 | 0.30526 | -0.031478 | -0.45597 | -1.0315 | -1.7784 | -2.8345 | -3.9713 | -5.006 | -7.5203 | -8.6203 | -9.0325
|  | TURRIFF | EE |  |  |  |  | 2.316 | 2.0425 | 1.6323 | 1.1701 | 0.60169 | -0.17893 | -1.1963 | -2.0004 | -3.0136 | -4.0534 | -7.0259 | -8.1993 | -8.6218 | 6.119 | 5.8558 | 5.5333 | 5.1986 | 4.7731 | 4.1792 | 3.4262 | 2.8935 | 2.0609 | 1.1629 | -1.1422 | -1.8106 | -2.332 | 0.89403 | 0.63791 | 0.30526 | -0.031478 | -0.45597 | -1.0315 | -1.7784 | -2.5805 | -3.5845 | -4.6131 | -7.5203 | -8.4774 | -8.7825
|  | TURRIFF | HT |  |  |  |  | 2.3956 | 2.0823 | 1.6384 | 1.1527 | 0.55475 | -0.3126 | -1.2565 | -2.3432 | -3.5116 | -4.5616 | -6.9708 | -8.3248 | -8.8085 | 6.1486 | 5.9384 | 5.6354 | 5.318 | 4.9129 | 4.2272 | 3.4701 | 2.566 | 1.5803 | 0.62924 | -0.9228 | -1.5361 | -1.7687 | 1.0063 | 0.77975 | 0.48791 | 0.19403 | -0.17944 | -0.83658 | -1.7652 | -2.8345 | -3.9713 | -5.006 | -7.4549 | -8.6203 | -9.0325
|  | TURRIFF | HE |  |  |  |  | 2.4139 | 2.1884 | 1.8792 | 1.5058 | 1.0354 | 0.36903 | -0.49933 | -1.3708 | -2.2748 | -3.0463 | -6.1687 | -7.3412 | -8.0167 | 6.1701 | 5.9813 | 5.7445 | 5.4813 | 5.1384 | 4.6568 | 3.9588 | 3.2231 | 2.4456 | 1.6813 | -0.73913 | -1.4993 | -2.1228 | 1.0165 | 0.8226 | 0.58077 | 0.33485 | 0.010359 | -0.41515 | -1.0254 | -1.8937 | -2.7866 | -3.556 | -6.7733 | -7.9203 | -8.4876
|  | TURRIFF | CF |  |  |  |  | 2.4813 | 2.3323 | 2.1435 | 1.9078 | 1.6047 | 1.2007 | 0.77413 | 0.22618 | -0.29423 | -0.83709 | -3.3953 | -5.7432 | -6.9993 | 6.2343 | 6.1088 | 5.9374 | 5.767 | 5.5333 | 5.2201 | 4.8966 | 4.4527 | 4.0323 | 3.5782 | 1.2282 | -1.0004 | -2.3657 | 1.0777 | 0.93791 | 0.76342 | 0.60526 | 0.38485 | 0.10016 | -0.18658 | -0.5978 | -0.9876 | -1.41 | -3.8794 | -6.3366 | -7.6774
| RANNOCH | TYNDRUM | MINIMUM HEADROOM | NN 32894 30860 | YES | YES | 0.497 | 0.068482 | 0.055216 | 0.033788 | 0.019502 | -0.0039673 | -0.029478 | -0.045804 | -0.076416 | -0.094784 | -0.12131 | -0.21723 | -0.32642 | -0.36825 | 0.35624 | 0.34501 | 0.33073 | 0.32154 | 0.29909 | 0.27869 | 0.2593 | 0.22664 | 0.19807 | 0.1644 | 0.0031755 | -0.072335 | -0.10703 | 0.33073 | 0.30828 | 0.28277 | 0.25113 | 0.21848 | 0.18073 | 0.13481 | 0.075624 | 0.025624 | -0.033559 | -0.30805 | -0.41417 | -0.45295
|  | TYNDRUM | EE |  |  |  |  | 0.068482 | 0.055216 | 0.033788 | 0.019502 | -0.0039673 | -0.029478 | -0.045804 | -0.076416 | -0.094784 | -0.12131 | -0.1754 | -0.19376 | -0.20703 | 0.35624 | 0.34501 | 0.33073 | 0.32154 | 0.29909 | 0.27869 | 0.26746 | 0.24195 | 0.2246 | 0.20624 | 0.16542 | 0.13889 | 0.10624 | 0.33073 | 0.30828 | 0.28277 | 0.2542 | 0.22562 | 0.18991 | 0.1593 | 0.11746 | 0.083788 | 0.053176 | -0.021314 | -0.03662 | -0.045804
|  | TYNDRUM | HT |  |  |  |  | 0.070522 | 0.069502 | 0.053176 | 0.037869 | 0.021543 | 0.0062367 | -0.012131 | -0.038661 | -0.047845 | -0.073355 | -0.15499 | -0.19478 | -0.21009 | 0.3593 | 0.35624 | 0.34909 | 0.33991 | 0.32767 | 0.31848 | 0.30522 | 0.28481 | 0.27664 | 0.26032 | 0.19297 | 0.16236 | 0.15113 | 0.34807 | 0.33991 | 0.3246 | 0.31542 | 0.29807 | 0.27869 | 0.2593 | 0.23073 | 0.20828 | 0.18685 | 0.090931 | 0.054196 | 0.03991
|  | TYNDRUM | HE |  |  |  |  | 0.069502 | 0.067461 | 0.052155 | 0.040931 | 0.025624 | 0.0144 | -0.008049 | -0.033559 | -0.045804 | -0.071314 | -0.21723 | -0.32642 | -0.33152 | 0.35828 | 0.35522 | 0.33787 | 0.32358 | 0.3042 | 0.28379 | 0.2593 | 0.22664 | 0.19807 | 0.1644 | 0.0031755 | -0.072335 | -0.078457 | 0.33583 | 0.31134 | 0.28277 | 0.25113 | 0.21848 | 0.18073 | 0.13481 | 0.075624 | 0.025624 | -0.033559 | -0.30805 | -0.41417 | -0.42131
|  | TYNDRUM | CF |  |  |  |  | 0.075624 | 0.071543 | 0.061339 | 0.051135 | 0.042971 | 0.033788 | 0.020522 | 0.009298 | -0.0060082 | -0.023355 | -0.10193 | -0.21723 | -0.36825 | 0.35624 | 0.35522 | 0.34909 | 0.33991 | 0.32869 | 0.31542 | 0.29909 | 0.27971 | 0.2593 | 0.23889 | 0.11338 | -0.0090694 | -0.10703 | 0.33379 | 0.33379 | 0.31746 | 0.29399 | 0.27052 | 0.24603 | 0.2195 | 0.18277 | 0.15011 | 0.11338 | -0.10907 | -0.31111 | -0.45295
| DUNVEGAN | UIG | MINIMUM HEADROOM | NG 39131 64412 | YES | NO | 1.494 | 0.93187 | 0.88085 | 0.81963 | 0.74412 | 0.69106 | 0.61044 | 0.52167 | 0.40942 | 0.30534 | 0.25534 | 0.041057 | -0.036494 | -0.058943 | 0.98034 | 0.94769 | 0.91198 | 0.85993 | 0.82932 | 0.77422 | 0.7181 | 0.64361 | 0.57218 | 0.54769 | 0.39259 | 0.31708 | 0.059935 | 0.89794 | 0.85509 | 0.79692 | 0.72652 | 0.67448 | 0.59692 | 0.51223 | 0.40713 | 0.30815 | 0.26223 | 0.06019 | -0.010218 | -0.029606
|  | UIG | EE |  |  |  |  | 0.93187 | 0.88085 | 0.81963 | 0.74412 | 0.69106 | 0.61044 | 0.52167 | 0.40942 | 0.30534 | 0.25534 | 0.041057 | 0.0022816 | -0.024249 | 0.98034 | 0.94769 | 0.91198 | 0.85993 | 0.82932 | 0.77422 | 0.7181 | 0.64361 | 0.57218 | 0.54769 | 0.39259 | 0.31708 | 0.20075 | 0.89794 | 0.85509 | 0.79692 | 0.72652 | 0.67448 | 0.59692 | 0.51223 | 0.40713 | 0.30815 | 0.26223 | 0.06019 | 0.027537 | 0.0030469
|  | UIG | HT |  |  |  |  | 0.96351 | 0.91555 | 0.85534 | 0.81147 | 0.7584 | 0.69208 | 0.61555 | 0.55534 | 0.47473 | 0.39922 | 0.10636 | -0.036494 | -0.058943 | 1.0018 | 0.97524 | 0.93953 | 0.91504 | 0.88647 | 0.84259 | 0.79463 | 0.75993 | 0.71096 | 0.66402 | 0.47626 | 0.39361 | 0.37932 | 0.92652 | 0.88672 | 0.83162 | 0.78774 | 0.73774 | 0.67346 | 0.60407 | 0.54794 | 0.47243 | 0.39897 | 0.12141 | -0.010218 | -0.029606
|  | UIG | HE |  |  |  |  | 0.96044 | 0.92269 | 0.87575 | 0.84106 | 0.80024 | 0.7482 | 0.67779 | 0.63085 | 0.56147 | 0.49412 | 0.15228 | 0.060445 | 0.050241 | 0.99973 | 0.97524 | 0.94667 | 0.92218 | 0.89973 | 0.86096 | 0.81504 | 0.7834 | 0.73647 | 0.69259 | 0.463 | 0.35483 | 0.25177 | 0.92448 | 0.89488 | 0.84999 | 0.81631 | 0.77652 | 0.72652 | 0.66223 | 0.61427 | 0.54692 | 0.48672 | 0.16631 | 0.079578 | 0.069373
|  | UIG | CF |  |  |  |  | 0.96963 | 0.92881 | 0.89616 | 0.86759 | 0.82575 | 0.78902 | 0.74412 | 0.68902 | 0.66249 | 0.61351 | 0.35432 | 0.16861 | 0.057384 | 1.0028 | 0.98034 | 0.95891 | 0.94259 | 0.91402 | 0.89259 | 0.85789 | 0.81708 | 0.80075 | 0.763 | 0.54769 | 0.32728 | 0.059935 | 0.93366 | 0.90101 | 0.87141 | 0.84386 | 0.80611 | 0.77243 | 0.72754 | 0.67448 | 0.65101 | 0.60305 | 0.35611 | 0.17856 | 0.075496
| GRUDIE BRIDGE | ULLAPOOL | MINIMUM HEADROOM | NH 13018 94588 | NO | NO | 0.283 | -0.32716 | -0.37308 | -0.42002 | -0.47308 | 3.6759 | 3.6198 | 3.5453 | 3.479 | 3.4014 | 3.33 | 3.1381 | 3.0637 | 3.0381 | 0.27896 | 0.24529 | 0.21059 | 0.16773 | 4.3361 | 4.2912 | 4.2341 | 4.1861 | 4.1279 | 4.0749 | 3.9473 | 3.9004 | 3.8851 | -0.54043 | -0.59043 | -0.65063 | -0.7241 | 3.4218 | 3.3494 | 3.2514 | 3.1739 | 3.0739 | 2.9851 | 2.779 | 2.7034 | 2.681
|  | ULLAPOOL | EE |  |  |  |  | -0.32716 | -0.37308 | -0.42002 | -0.47308 | 3.6759 | 3.6198 | 3.5453 | 3.479 | 3.4014 | 3.33 | 3.1381 | 3.0973 | 3.0739 | 0.27896 | 0.24529 | 0.21059 | 0.16773 | 4.3361 | 4.2912 | 4.2341 | 4.1861 | 4.1279 | 4.0749 | 3.9473 | 3.9208 | 3.8973 | -0.54043 | -0.59043 | -0.65063 | -0.7241 | 3.4218 | 3.3494 | 3.2514 | 3.1739 | 3.0739 | 2.9851 | 2.779 | 2.7402 | 2.7137
|  | ULLAPOOL | HT |  |  |  |  | -0.3088 | -0.35267 | -0.39145 | -0.43839 | 3.7177 | 3.6647 | 3.6157 | 3.5555 | 3.4953 | 3.432 | 3.1943 | 3.0637 | 3.0381 | 0.30141 | 0.27386 | 0.25141 | 0.21467 | 4.3881 | 4.3463 | 4.3188 | 4.2728 | 4.2259 | 4.1779 | 3.9881 | 3.9004 | 3.8851 | -0.50369 | -0.54961 | -0.58941 | -0.64961 | 3.5034 | 3.4361 | 3.3871 | 3.3116 | 3.2351 | 3.1514 | 2.8443 | 2.7034 | 2.681
|  | ULLAPOOL | HE |  |  |  |  | -0.31084 | -0.34145 | -0.37512 | -0.40982 | 3.7575 | 3.7157 | 3.6728 | 3.6157 | 3.5616 | 3.5045 | 3.1881 | 3.0841 | 3.0728 | 0.29937 | 0.27488 | 0.25549 | 0.22488 | 4.4024 | 4.3698 | 4.3432 | 4.2973 | 4.2606 | 4.2157 | 4.0126 | 3.9514 | 3.9432 | -0.50471 | -0.54145 | -0.57614 | -0.62308 | 3.5381 | 3.4851 | 3.4432 | 3.3698 | 3.3086 | 3.2341 | 2.9045 | 2.8137 | 2.8034
|  | ULLAPOOL | CF |  |  |  |  | -0.30676 | -0.33329 | -0.36492 | -0.39043 | 3.782 | 3.7463 | 3.7116 | 3.68 | 3.6422 | 3.6075 | 3.4198 | 3.2412 | 3.0759 | 0.30549 | 0.28304 | 0.26263 | 0.24529 | 4.4279 | 4.4024 | 4.3749 | 4.3565 | 4.3279 | 4.3004 | 4.1534 | 4.0065 | 3.9249 | -0.49859 | -0.52716 | -0.56594 | -0.59145 | 3.5769 | 3.5361 | 3.4902 | 3.4586 | 3.4137 | 3.3688 | 3.1381 | 2.9116 | 2.8055
| SHETLAND | UNST | MINIMUM HEADROOM | HP6398113411 | YES | YES | 0.383 | -0.62207 | -0.64452 | -0.67309 | -0.70371 | -0.74044 | -0.77616 | -0.80983 | -0.85269 | -0.90473 | -0.95371 | -1.0772 | -1.119 | -1.1262 | 0.029967 | 0.0054776 | -0.019012 | -0.042482 | -0.079216 | -0.12003 | -0.1435 | -0.1935 | -0.23228 | -0.27105 | -0.37003 | -0.40881 | -0.51697 | -0.3986 | -0.42513 | -0.45167 | -0.48126 | -0.51493 | -0.54962 | -0.58432 | -0.65064 | -0.70371 | -0.75371 | -0.84146 | -0.87003 | -0.87718
|  | UNST | EE |  |  |  |  | -0.62207 | -0.64452 | -0.67309 | -0.70371 | -0.74044 | -0.77616 | -0.80983 | -0.85269 | -0.90473 | -0.95371 | -1.0772 | -1.0945 | -1.1088 | 0.029967 | 0.0054776 | -0.019012 | -0.042482 | -0.079216 | -0.12003 | -0.1435 | -0.1935 | -0.23228 | -0.27105 | -0.37003 | -0.40881 | -0.47513 | -0.3986 | -0.42513 | -0.45167 | -0.48126 | -0.51493 | -0.54962 | -0.58432 | -0.65064 | -0.70371 | -0.75371 | -0.84146 | -0.85167 | -0.86289
|  | UNST | HT |  |  |  |  | -0.61085 | -0.63024 | -0.65473 | -0.6833 | -0.70881 | -0.74248 | -0.77105 | -0.80983 | -0.8435 | -0.86901 | -1.0313 | -1.119 | -1.1262 | 0.048335 | 0.034049 | 0.013641 | -0.011869 | -0.027176 | -0.055747 | -0.079216 | -0.11289 | -0.1486 | -0.16799 | -0.31493 | -0.37616 | -0.37922 | -0.3884 | -0.41187 | -0.43432 | -0.46187 | -0.48432 | -0.51493 | -0.54044 | -0.57513 | -0.60983 | -0.6333 | -0.80473 | -0.87003 | -0.87718
|  | UNST | HE |  |  |  |  | -0.61085 | -0.62718 | -0.64452 | -0.67003 | -0.69044 | -0.71799 | -0.74758 | -0.78432 | -0.81901 | -0.8486 | -1.019 | -1.0639 | -1.0833 | 0.048335 | 0.034049 | 0.018743 | -0.0067673 | -0.016971 | -0.043502 | -0.06391 | -0.097584 | -0.1333 | -0.1435 | -0.29452 | -0.35575 | -0.41187 | -0.3884 | -0.40677 | -0.42513 | -0.45064 | -0.46799 | -0.49452 | -0.52207 | -0.55575 | -0.58942 | -0.61595 | -0.78126 | -0.82105 | -0.83534
|  | UNST | CF |  |  |  |  | -0.61187 | -0.62309 | -0.6384 | -0.65473 | -0.67513 | -0.68534 | -0.70575 | -0.72207 | -0.74452 | -0.76391 | -0.86289 | -0.98228 | -1.0547 | 0.051396 | 0.041192 | 0.023845 | 0.01058 | -0.0077878 | -0.019012 | -0.041461 | -0.059829 | -0.083298 | -0.10677 | -0.22309 | -0.37309 | -0.51697 | -0.38432 | -0.3986 | -0.41085 | -0.42411 | -0.44146 | -0.44962 | -0.46799 | -0.4833 | -0.50167 | -0.52105 | -0.63738 | -0.7833 | -0.81901
| SHETLAND | VOE | MINIMUM HEADROOM | HU4117663079 | YES | YES | 0.192 | 6.2266 | 6.147 | 6.0654 | 5.9735 | 5.8531 | 5.7541 | 5.6052 | 5.4409 | 5.2878 | 5.1868 | 4.8378 | 4.7358 | 4.7092 | 6.7331 | 6.679 | 6.628 | 6.5627 | 6.4811 | 6.4158 | 6.3199 | 6.2107 | 6.1066 | 6.0443 | 5.7852 | 5.6617 | 5.2178 | 6.2666 | 6.1952 | 6.1207 | 6.038 | 5.9441 | 5.8666 | 5.7543 | 5.6299 | 5.5176 | 5.4288 | 5.1278 | 5.0278 | 4.9962
|  | VOE | EE |  |  |  |  | 6.2266 | 6.147 | 6.0654 | 5.9735 | 5.8531 | 5.7541 | 5.6052 | 5.4409 | 5.2878 | 5.1868 | 4.8378 | 4.7939 | 4.7623 | 6.7331 | 6.679 | 6.628 | 6.5627 | 6.4811 | 6.4158 | 6.3199 | 6.2107 | 6.1066 | 6.0443 | 5.7852 | 5.6617 | 5.4597 | 6.2666 | 6.1952 | 6.1207 | 6.038 | 5.9441 | 5.8666 | 5.7543 | 5.6299 | 5.5176 | 5.4288 | 5.1278 | 5.085 | 5.0492
|  | VOE | HT |  |  |  |  | 6.2562 | 6.1899 | 6.1205 | 6.0419 | 5.9654 | 5.8766 | 5.7623 | 5.6368 | 5.5409 | 5.4052 | 4.948 | 4.7358 | 4.7092 | 6.7678 | 6.728 | 6.6852 | 6.6352 | 6.5882 | 6.5301 | 6.4617 | 6.3801 | 6.325 | 6.2413 | 5.9321 | 5.7974 | 5.7841 | 6.2911 | 6.2309 | 6.1666 | 6.0962 | 6.0207 | 5.9421 | 5.8543 | 5.7533 | 5.6748 | 5.5707 | 5.2237 | 5.0278 | 5.0023
|  | VOE | HE |  |  |  |  | 6.2541 | 6.198 | 6.1388 | 6.0746 | 6.0082 | 5.9286 | 5.8307 | 5.7215 | 5.6307 | 5.5225 | 5.0225 | 4.8807 | 4.8194 | 6.7648 | 6.7301 | 6.6974 | 6.6494 | 6.6097 | 6.5546 | 6.4882 | 6.4148 | 6.3597 | 6.2831 | 5.926 | 5.7474 | 5.5556 | 6.2911 | 6.2421 | 6.189 | 6.1309 | 6.0686 | 5.9982 | 5.9105 | 5.8135 | 5.7309 | 5.636 | 5.1717 | 5.0431 | 4.9962
|  | VOE | CF |  |  |  |  | 6.2746 | 6.2307 | 6.1776 | 6.1337 | 6.0715 | 6.0286 | 5.9654 | 5.8939 | 5.8194 | 5.7399 | 5.3684 | 5.0858 | 4.9092 | 6.7739 | 6.7443 | 6.7066 | 6.677 | 6.6341 | 6.5984 | 6.5515 | 6.4943 | 6.4392 | 6.376 | 6.0566 | 5.6852 | 5.2178 | 6.3023 | 6.2656 | 6.2248 | 6.189 | 6.139 | 6.0992 | 6.0472 | 5.9911 | 5.9339 | 5.8707 | 5.5441 | 5.2666 | 5.0748
| DUDHOPE | WALTON | MINIMUM HEADROOM | NO 38995 30333 | NO | NO | 2.26 | 16.3022 | 15.9124 | 15.0257 | 13.8808 | 13.5563 | 11.3706 | 10.8012 | 10.0522 | 9.1328 | 7.6144 | 1.4573 | -5.8692 | -12.4886 | 17.1512 | 16.9196 | 15.9655 | 14.7471 | 14.5573 | 12.0277 | 11.1869 | 10.2604 | 9.3063 | 7.6083 | 0.18384 | -9.6631 | -19.8998 | 16.7144 | 16.3859 | 15.3716 | 14.0522 | 13.7542 | 11.1165 | 10.5328 | 9.5308 | 8.5053 | 6.7379 | -0.49678 | -9.5009 | -17.8141
|  | WALTON | EE |  |  |  |  | 16.34 | 15.9124 | 15.5002 | 15.0961 | 14.1849 | 12.8022 | 11.9236 | 11.3757 | 10.2349 | 9.4236 | 6.042 | -0.14882 | -2.8427 | 17.2532 | 16.9542 | 16.6716 | 16.3675 | 15.443 | 13.9298 | 13.0961 | 12.6869 | 11.5328 | 10.7716 | 6.9389 | -2.0447 | -7.2458 | 16.7838 | 16.3859 | 16.0002 | 15.6196 | 14.6093 | 13.0073 | 12.0655 | 11.5502 | 10.293 | 9.4389 | 5.7185 | -2.109 | -5.4631
|  | WALTON | HT |  |  |  |  | 16.3022 | 15.9593 | 15.0257 | 13.8808 | 13.5563 | 11.3706 | 10.8012 | 10.1573 | 9.6216 | 8.94 | 4.7216 | -3.2233 | -9.6162 | 17.1512 | 16.9196 | 15.9655 | 14.7471 | 14.5747 | 12.0471 | 11.6318 | 11.1512 | 10.8063 | 10.2655 | 6.1961 | -3.5141 | -11.5549 | 16.7144 | 16.4257 | 15.3716 | 14.0522 | 13.7542 | 11.1165 | 10.544 | 9.8971 | 9.394 | 8.6991 | 4.0583 | -5.7131 | -13.708
|  | WALTON | HE |  |  |  |  | 16.4236 | 16.14 | 15.3971 | 14.4104 | 13.8624 | 11.7583 | 10.9522 | 10.0522 | 9.1328 | 7.6144 | 1.4573 | -5.8692 | -12.4886 | 17.2757 | 17.0298 | 16.2236 | 15.1083 | 14.5573 | 12.0277 | 11.1869 | 10.2604 | 9.3063 | 7.6083 | 0.18384 | -9.6631 | -19.8998 | 16.8369 | 16.5869 | 15.7502 | 14.5981 | 13.993 | 11.4369 | 10.5328 | 9.5308 | 8.5053 | 6.7379 | -0.49678 | -9.5009 | -17.8141
|  | WALTON | CF |  |  |  |  | 16.7777 | 16.5991 | 16.4063 | 16.2369 | 15.7512 | 14.9624 | 14.4726 | 14.0614 | 13.64 | 13.1042 | 10.9022 | 8.543 | 6.4747 | 17.6267 | 17.444 | 17.2604 | 17.1073 | 16.5573 | 15.5971 | 14.9889 | 14.4808 | 13.9604 | 13.2971 | 10.4012 | 6.2359 | 0.49914 | 17.1961 | 17.0298 | 16.8461 | 16.6879 | 16.1349 | 15.2032 | 14.6451 | 14.191 | 13.7206 | 13.1144 | 10.7502 | 8.2196 | 6.0165
| INVERNESS | WATERLOO PLACE | MINIMUM HEADROOM | NH 66301 45800 | NO | NO | 5.779 | 11.3977 | 28.1973 | 27.9982 | 27.8256 | 27.6304 | 27.39 | 27.1453 | 26.7904 | 26.464 | 26.1596 | 25.1412 | 24.695 | 24.5522 | 11.8921 | 27.4663 | 27.3797 | 27.3153 | 27.1898 | 27.0172 | 26.8369 | 26.583 | 26.3484 | 26.131 | 25.3362 | 25.0064 | 24.8992 | 11.0643 | 27.623 | 27.5076 | 27.4196 | 27.3148 | 27.1696 | 26.9412 | 26.6075 | 26.3008 | 26.0142 | 25.0266 | 24.5982 | 24.464
|  | WATERLOO PLACE | EE |  |  |  |  | 11.3977 | 28.1973 | 27.9982 | 27.8256 | 27.6304 | 27.39 | 27.1453 | 26.7904 | 26.464 | 26.1596 | 25.2408 | 25.0739 | 25.0455 | 11.8921 | 27.4788 | 27.3797 | 27.3153 | 27.1898 | 27.0172 | 26.8369 | 26.583 | 26.3484 | 26.131 | 25.4348 | 25.2983 | 25.2752 | 11.0643 | 27.6283 | 27.5076 | 27.4196 | 27.3148 | 27.1696 | 26.9412 | 26.6075 | 26.3008 | 26.0142 | 25.1348 | 24.9713 | 24.9429
|  | WATERLOO PLACE | HT |  |  |  |  | 11.4424 | 28.2329 | 28.1165 | 27.9833 | 27.829 | 27.5564 | 27.289 | 26.9808 | 26.7212 | 26.463 | 25.4191 | 24.9907 | 24.8595 | 11.908 | 27.4663 | 27.4259 | 27.3783 | 27.3211 | 27.1715 | 26.9874 | 26.771 | 26.583 | 26.3936 | 25.5968 | 25.2622 | 25.1593 | 11.0816 | 27.623 | 27.561 | 27.4908 | 27.4081 | 27.1749 | 26.9662 | 26.7498 | 26.5614 | 26.3157 | 25.3064 | 24.8929 | 24.767
|  | WATERLOO PLACE | HE |  |  |  |  | 11.4357 | 28.2555 | 28.0997 | 27.9612 | 27.7958 | 27.5828 | 27.3592 | 27.0515 | 26.7558 | 26.4466 | 25.1412 | 24.695 | 24.5522 | 11.9066 | 27.5018 | 27.4191 | 27.3677 | 27.3052 | 27.1566 | 26.9912 | 26.7657 | 26.5489 | 26.32 | 25.3362 | 25.0064 | 24.8992 | 11.0797 | 27.6596 | 27.5658 | 27.4975 | 27.4158 | 27.2917 | 27.148 | 26.8542 | 26.5729 | 26.2786 | 25.0266 | 24.5982 | 24.464
|  | WATERLOO PLACE | CF |  |  |  |  | 11.4741 | 28.3526 | 28.2795 | 28.1583 | 28.0655 | 27.9352 | 27.8208 | 27.6708 | 27.4991 | 27.3116 | 26.2606 | 25.3033 | 24.5888 | 11.9191 | 27.5345 | 27.5057 | 27.4307 | 27.3956 | 27.3388 | 27.298 | 27.2129 | 27.0874 | 26.9479 | 26.169 | 25.4593 | 24.9376 | 11.0989 | 27.7052 | 27.6668 | 27.585 | 27.536 | 27.4504 | 27.3975 | 27.3307 | 27.2307 | 27.1071 | 26.1041 | 25.1862 | 24.503
| LYNDHURST | WEST KIRKTON | MINIMUM HEADROOM | NO 39194 33796 | NO | YES | 2.703 | 10.9494 | 10.5586 | 10.0872 | 9.6157 | 9.1218 | 8.6106 | 8.3851 | 7.8841 | 7.4025 | 6.9576 | 5.4025 | 5.079 | 5.0616 | 12.4025 | 12.2004 | 11.9463 | 11.7045 | 11.4341 | 11.1576 | 11.0933 | 10.8239 | 10.5627 | 10.3167 | 9.3382 | 8.8943 | 6.5841 | 12.1285 | 11.7877 | 11.3642 | 10.9407 | 10.4836 | 10.0081 | 9.8428 | 9.3632 | 8.904 | 8.4887 | 7.1244 | 6.8397 | 6.8244
|  | WEST KIRKTON | EE |  |  |  |  | 10.9494 | 10.5586 | 10.0872 | 9.6157 | 9.1218 | 8.6106 | 8.3851 | 7.8841 | 7.4025 | 6.9576 | 5.4025 | 5.5402 | 5.5831 | 12.4025 | 12.2004 | 11.9463 | 11.7045 | 11.4341 | 11.1576 | 11.0933 | 10.8239 | 10.5627 | 10.3167 | 9.3382 | 8.8943 | 8.0055 | 12.1285 | 11.7877 | 11.3642 | 10.9407 | 10.4836 | 10.0081 | 9.8428 | 9.3632 | 8.904 | 8.4887 | 7.1244 | 7.2264 | 7.2458
|  | WEST KIRKTON | HT |  |  |  |  | 11.027 | 10.6382 | 10.2035 | 9.7453 | 9.2923 | 8.9065 | 8.4474 | 7.9627 | 7.4902 | 7.3657 | 5.4902 | 5.079 | 5.0616 | 12.4678 | 12.28 | 12.077 | 11.8555 | 11.6392 | 11.4535 | 11.2361 | 10.9902 | 10.7535 | 10.7698 | 9.8494 | 9.6116 | 9.5882 | 12.1928 | 11.8775 | 11.5193 | 11.1315 | 10.7275 | 10.3785 | 9.9581 | 9.5009 | 9.0571 | 8.9897 | 7.2417 | 6.8397 | 6.8244
|  | WEST KIRKTON | HE |  |  |  |  | 11.0402 | 10.7821 | 10.4494 | 10.1178 | 9.7821 | 9.4851 | 9.1229 | 8.7494 | 8.38 | 8.3474 | 6.8484 | 6.0014 | 5.9218 | 12.4637 | 12.3208 | 12.1361 | 11.9637 | 11.777 | 11.6106 | 11.4106 | 11.1953 | 10.979 | 10.9994 | 9.98 | 9.1341 | 8.2086 | 12.204 | 12.004 | 11.7193 | 11.4366 | 11.1356 | 10.8611 | 10.5234 | 10.1642 | 9.8132 | 9.8183 | 8.403 | 7.6744 | 7.6122
|  | WEST KIRKTON | CF |  |  |  |  | 11.1218 | 10.978 | 10.7882 | 10.5851 | 10.3678 | 10.1759 | 10.0249 | 9.8188 | 9.6545 | 9.479 | 8.8055 | 7.3708 | 6.0963 | 12.4994 | 12.4065 | 12.2831 | 12.1637 | 12.027 | 11.8933 | 11.7688 | 11.6035 | 11.4606 | 11.3055 | 10.5994 | 8.9708 | 6.5841 | 12.2764 | 12.1662 | 12.006 | 11.8336 | 11.6377 | 11.452 | 11.3081 | 11.103 | 10.9346 | 10.755 | 10.1071 | 8.7948 | 7.7315
| KILLIN | WESTER DRUMMOND | MINIMUM HEADROOM | NN 72155 44784 | YES | YES | 0 | 0.087388 | 0.087388 | 0.086367 | 0.078204 | 0.078204 | 0.070041 | 0.068 | 0.068 | 0.06698 | 0.065959 | 0.065959 | 0.061878 | 0.061878 | 0.090633 | 0.090633 | 0.089612 | 0.081449 | 0.081449 | 0.074306 | 0.076347 | 0.073286 | 0.073286 | 0.074306 | 0.077367 | 0.072265 | 0.071245 | 0.090031 | 0.090031 | 0.08901 | 0.080847 | 0.080847 | 0.072684 | 0.070643 | 0.071663 | 0.070643 | 0.068602 | 0.068602 | 0.06452 | 0.06452
|  | WESTER DRUMMOND | EE |  |  |  |  | 0.087388 | 0.087388 | 0.086367 | 0.078204 | 0.078204 | 0.070041 | 0.068 | 0.073102 | 0.068 | 0.06698 | 0.065959 | 0.065959 | 0.062898 | 0.090633 | 0.090633 | 0.089612 | 0.081449 | 0.081449 | 0.074306 | 0.076347 | 0.080429 | 0.077367 | 0.077367 | 0.077367 | 0.077367 | 0.073286 | 0.090031 | 0.090031 | 0.08901 | 0.080847 | 0.080847 | 0.072684 | 0.070643 | 0.075745 | 0.070643 | 0.069622 | 0.068602 | 0.068602 | 0.066561
|  | WESTER DRUMMOND | HT |  |  |  |  | 0.094531 | 0.094531 | 0.087388 | 0.085347 | 0.085347 | 0.077184 | 0.077184 | 0.068 | 0.06698 | 0.065959 | 0.068 | 0.061878 | 0.061878 | 0.097776 | 0.097776 | 0.090633 | 0.088592 | 0.088592 | 0.081449 | 0.081449 | 0.073286 | 0.073286 | 0.075327 | 0.077367 | 0.073286 | 0.073286 | 0.097173 | 0.097173 | 0.090031 | 0.08799 | 0.08799 | 0.079827 | 0.079827 | 0.071663 | 0.070643 | 0.068602 | 0.069622 | 0.06452 | 0.06452
|  | WESTER DRUMMOND | HE |  |  |  |  | 0.094531 | 0.094531 | 0.087388 | 0.087388 | 0.085347 | 0.079224 | 0.078204 | 0.06902 | 0.06902 | 0.06698 | 0.06902 | 0.063918 | 0.063918 | 0.097776 | 0.097776 | 0.090633 | 0.089612 | 0.088592 | 0.081449 | 0.081449 | 0.074306 | 0.074306 | 0.075327 | 0.077367 | 0.075327 | 0.073286 | 0.097173 | 0.097173 | 0.090031 | 0.090031 | 0.08799 | 0.081867 | 0.080847 | 0.071663 | 0.071663 | 0.069622 | 0.070643 | 0.067582 | 0.067582
|  | WESTER DRUMMOND | CF |  |  |  |  | 0.096571 | 0.094531 | 0.087388 | 0.087388 | 0.087388 | 0.086367 | 0.078204 | 0.078204 | 0.071061 | 0.071061 | 0.06902 | 0.064939 | 0.064939 | 0.097776 | 0.097776 | 0.090633 | 0.090633 | 0.090633 | 0.089612 | 0.081449 | 0.081449 | 0.074306 | 0.074306 | 0.078388 | 0.072265 | 0.071245 | 0.098194 | 0.097173 | 0.090031 | 0.090031 | 0.090031 | 0.08901 | 0.080847 | 0.080847 | 0.073704 | 0.073704 | 0.071663 | 0.068602 | 0.068602
| THURSO | WESTRAY | MINIMUM HEADROOM | HY 50213 39413 | YES | NO | 0 | -0.89388 | -0.92143 | -0.94388 | -0.98061 | -1.0071 | -1.0449 | -1.0694 | -1.1184 | -1.1612 | -1.2 | -1.2837 | -1.3112 | -1.3235 | -0.44184 | -0.46122 | -0.47551 | -0.5051 | -0.52347 | -0.55408 | -0.56531 | -0.6051 | -0.63469 | -0.66429 | -0.72959 | -0.75102 | -0.82347 | -0.61633 | -0.64388 | -0.66429 | -0.70408 | -0.72959 | -0.77041 | -0.79286 | -0.84592 | -0.88878 | -0.92857 | -1.0122 | -1.0378 | -1.048
|  | WESTRAY | EE |  |  |  |  | -0.89388 | -0.92143 | -0.94388 | -0.98061 | -1.0071 | -1.0449 | -1.0694 | -1.1184 | -1.1612 | -1.2 | -1.2837 | -1.299 | -1.3112 | -0.44184 | -0.46122 | -0.47551 | -0.5051 | -0.52347 | -0.55408 | -0.56531 | -0.6051 | -0.63469 | -0.66429 | -0.72959 | -0.75102 | -0.78469 | -0.61633 | -0.64388 | -0.66429 | -0.70408 | -0.72959 | -0.77041 | -0.79286 | -0.84592 | -0.88878 | -0.92857 | -1.0122 | -1.0265 | -1.0367
|  | WESTRAY | HT |  |  |  |  | -0.87755 | -0.89796 | -0.91837 | -0.95 | -0.96531 | -0.9949 | -1.0194 | -1.0561 | -1.0949 | -1.1092 | -1.2571 | -1.3112 | -1.3235 | -0.42755 | -0.4398 | -0.4551 | -0.47755 | -0.48469 | -0.50714 | -0.52245 | -0.55102 | -0.58163 | -0.58469 | -0.6949 | -0.72959 | -0.74082 | -0.59796 | -0.61837 | -0.63776 | -0.67143 | -0.68367 | -0.71531 | -0.7398 | -0.78061 | -0.81837 | -0.83163 | -0.98469 | -1.0378 | -1.048
|  | WESTRAY | HE |  |  |  |  | -0.87755 | -0.8949 | -0.91122 | -0.93571 | -0.94796 | -0.97347 | -0.99592 | -1.0296 | -1.0622 | -1.0745 | -1.2337 | -1.2724 | -1.2816 | -0.42653 | -0.43776 | -0.45 | -0.47245 | -0.47857 | -0.49898 | -0.51327 | -0.54184 | -0.56633 | -0.57245 | -0.69286 | -0.73163 | -0.76327 | -0.59694 | -0.61429 | -0.63163 | -0.65714 | -0.66939 | -0.69592 | -0.71837 | -0.7551 | -0.78878 | -0.8 | -0.96122 | -1.002 | -1.0092
|  | WESTRAY | CF |  |  |  |  | -0.87857 | -0.89082 | -0.90612 | -0.92143 | -0.94388 | -0.95306 | -0.97551 | -0.98878 | -1.0122 | -1.0367 | -1.1306 | -1.2316 | -1.2724 | -0.42653 | -0.43673 | -0.44898 | -0.4602 | -0.47755 | -0.48163 | -0.49898 | -0.51122 | -0.53163 | -0.55102 | -0.62959 | -0.73571 | -0.82347 | -0.59694 | -0.60918 | -0.62755 | -0.64184 | -0.66735 | -0.67347 | -0.69694 | -0.71327 | -0.73776 | -0.76224 | -0.85918 | -0.96327 | -1
| TARLAND | WHITEHOUSE | MINIMUM HEADROOM | NJ 61658 15058 | NO | NO | 1.067 | 3.0675 | 2.8093 | 2.5328 | 2.2277 | 1.8889 | 1.6042 | 1.2471 | 0.86443 | 0.50525 | 0.51239 | -0.28557 | -0.557 | -0.65189 | 4.5869 | 4.4165 | 4.244 | 4.0369 | 3.8012 | 3.6195 | 3.3797 | 3.1236 | 2.8818 | 2.9848 | 2.4491 | 2.194 | 1.3369 | 3.8961 | 3.6563 | 3.4134 | 3.1287 | 2.8124 | 2.5665 | 2.2297 | 1.8552 | 1.5052 | 1.5665 | 0.83382 | 0.58382 | 0.50525
|  | WHITEHOUSE | EE |  |  |  |  | 3.0675 | 2.8093 | 2.5328 | 2.2277 | 1.8889 | 1.6042 | 1.2471 | 0.86443 | 0.50525 | 0.51239 | -0.28557 | -0.45087 | -0.51108 | 4.5869 | 4.4165 | 4.244 | 4.0369 | 3.8012 | 3.6195 | 3.3797 | 3.1236 | 2.8818 | 2.9848 | 2.4491 | 2.194 | 1.8236 | 3.8961 | 3.6563 | 3.4134 | 3.1287 | 2.8124 | 2.5665 | 2.2297 | 1.8552 | 1.5052 | 1.5665 | 0.83382 | 0.68586 | 0.63076
|  | WHITEHOUSE | HT |  |  |  |  | 3.1236 | 2.8726 | 2.6012 | 2.3185 | 2.0348 | 1.7573 | 1.4869 | 1.2399 | 0.96239 | 0.6828 | -0.079445 | -0.557 | -0.65189 | 4.6287 | 4.4797 | 4.3114 | 4.1287 | 3.943 | 3.7767 | 3.6165 | 3.4675 | 3.2991 | 3.1216 | 2.7175 | 2.4604 | 2.4083 | 3.9542 | 3.741 | 3.4991 | 3.2359 | 2.9746 | 2.7206 | 2.4726 | 2.241 | 1.9838 | 1.7185 | 1.0226 | 0.58382 | 0.50525
|  | WHITEHOUSE | HE |  |  |  |  | 3.1287 | 2.9297 | 2.7236 | 2.5022 | 2.2848 | 2.0501 | 1.792 | 1.5634 | 1.3134 | 1.0583 | 0.038922 | -0.26414 | -0.32128 | 4.6328 | 4.5012 | 4.3665 | 4.2093 | 4.0593 | 3.895 | 3.7165 | 3.5685 | 3.3981 | 3.2226 | 2.6399 | 2.3104 | 1.9532 | 3.9604 | 3.7818 | 3.6042 | 3.4001 | 3.2032 | 2.9828 | 2.744 | 2.5338 | 2.2971 | 2.0573 | 1.1369 | 0.85933 | 0.81035
|  | WHITEHOUSE | CF |  |  |  |  | 3.1655 | 3.0175 | 2.8563 | 2.6991 | 2.5165 | 2.3675 | 2.194 | 2.0022 | 1.8206 | 1.6787 | 0.70933 | 0.25015 | -0.23353 | 4.6604 | 4.5644 | 4.4614 | 4.3563 | 4.2287 | 4.1257 | 3.995 | 3.8461 | 3.7083 | 3.6052 | 2.7981 | 2.2563 | 1.3369 | 3.993 | 3.8573 | 3.7155 | 3.5675 | 3.395 | 3.2634 | 3.095 | 2.9042 | 2.7267 | 2.6104 | 1.6644 | 1.3144 | 0.8777
| PERSLEY | WHITESTRIPES | MINIMUM HEADROOM | NJ 92850 11054 | NO | NO | 0.578 | 7.1042 | 6.5838 | 5.9685 | 5.3389 | 4.6103 | 3.8277 | 3.1124 | 2.2195 | 1.5767 | 0.7634 | -3.0223 | -5.6999 | -7.2519 | 8.7991 | 8.5318 | 8.2022 | 7.8818 | 7.5012 | 7.0899 | 6.9144 | 6.4705 | 6.041 | 5.6308 | 3.844 | 2.3185 | 0.60932 | 7.9833 | 7.5466 | 7.0109 | 6.468 | 5.8333 | 5.1435 | 4.6476 | 3.8731 | 3.2394 | 2.5394 | -0.60139 | -2.8463 | -4.0728
|  | WHITESTRIPES | EE |  |  |  |  | 7.1042 | 6.5838 | 5.9685 | 5.3389 | 4.6103 | 3.8277 | 3.2869 | 2.4246 | 1.5767 | 0.7634 | -2.7978 | -5.5815 | -7.2029 | 8.7991 | 8.5318 | 8.2022 | 7.8818 | 7.5012 | 7.0899 | 6.9144 | 6.4705 | 6.041 | 5.6308 | 3.844 | 2.3185 | 0.88483 | 7.9833 | 7.5466 | 7.0109 | 6.468 | 5.8333 | 5.1435 | 4.7384 | 3.9792 | 3.2394 | 2.5394 | -0.40343 | -2.7412 | -4.0289
|  | WHITESTRIPES | HT |  |  |  |  | 7.1705 | 6.645 | 6.0614 | 5.4063 | 4.7318 | 3.9705 | 3.1124 | 2.2195 | 1.6654 | 0.82871 | -3.0223 | -5.6999 | -7.2519 | 8.8705 | 8.6216 | 8.3471 | 8.0318 | 7.7236 | 7.3603 | 6.9573 | 6.5195 | 6.3532 | 5.9675 | 4.1603 | 2.9736 | 2.243 | 8.07 | 7.6302 | 7.1496 | 6.5945 | 6.0282 | 5.3792 | 4.6476 | 3.8731 | 3.4445 | 2.718 | -0.60139 | -2.8463 | -4.0728
|  | WHITESTRIPES | HE |  |  |  |  | 7.1899 | 6.8205 | 6.3981 | 5.9022 | 5.3869 | 4.7869 | 4.1542 | 3.4869 | 3.1552 | 2.544 | -0.86925 | -3.7937 | -5.8315 | 8.8654 | 8.6685 | 8.443 | 8.1767 | 7.9165 | 7.6042 | 7.2675 | 6.9052 | 6.8063 | 6.4777 | 4.6297 | 3.0032 | 1.4195 | 8.0813 | 7.7741 | 7.4221 | 6.9986 | 6.566 | 6.0506 | 5.5037 | 4.9139 | 4.6925 | 4.1639 | 1.2506 | -1.1483 | -2.8187
|  | WHITESTRIPES | CF |  |  |  |  | 7.2736 | 6.9961 | 6.6501 | 6.295 | 5.8736 | 5.4481 | 5.0644 | 4.6461 | 4.2369 | 3.8154 | 1.6124 | -1.4305 | -4.3264 | 8.9012 | 8.742 | 8.5399 | 8.345 | 8.1063 | 7.8756 | 7.6308 | 7.3624 | 7.0971 | 6.8236 | 5.4991 | 3.3124 | 0.60932 | 8.1558 | 7.9272 | 7.6323 | 7.3435 | 6.9853 | 6.6282 | 6.2976 | 5.9302 | 5.569 | 5.1986 | 3.3792 | 0.82106 | -1.5034
| CARRADALE 1 | WHITING BAY | MINIMUM HEADROOM | NS 04169 26277 | YES | YES | 0.331 | 7.343 | 7.2644 | 7.1859 | 7.1134 | 7.0185 | 6.9246 | 6.8042 | 6.7022 | 6.5787 | 6.4675 | 6.1981 | 6.1063 | 6.0848 | 7.3393 | 7.2852 | 7.2393 | 7.1955 | 7.1312 | 7.0669 | 6.9893 | 6.925 | 6.8414 | 6.7669 | 6.5791 | 6.5118 | 6.3322 | 7.2973 | 7.2218 | 7.1483 | 7.081 | 6.9912 | 6.9024 | 6.784 | 6.6912 | 6.5697 | 6.4646 | 6.2146 | 6.1259 | 6.1075
|  | WHITING BAY | EE |  |  |  |  | 7.343 | 7.2644 | 7.1859 | 7.1134 | 7.0185 | 6.9246 | 6.8042 | 6.7022 | 6.5787 | 6.4675 | 6.1981 | 6.1614 | 6.1318 | 7.3393 | 7.2852 | 7.2393 | 7.1955 | 7.1312 | 7.0669 | 6.9893 | 6.925 | 6.8414 | 6.7669 | 6.5791 | 6.5118 | 6.4026 | 7.2973 | 7.2218 | 7.1483 | 7.081 | 6.9912 | 6.9024 | 6.784 | 6.6912 | 6.5697 | 6.4646 | 6.2146 | 6.1789 | 6.1493
|  | WHITING BAY | HT |  |  |  |  | 7.3685 | 7.3073 | 7.2491 | 7.1859 | 7.1093 | 7.0471 | 6.9604 | 6.8634 | 6.7665 | 6.6614 | 6.2838 | 6.1063 | 6.0848 | 7.3608 | 7.325 | 7.2924 | 7.2546 | 7.2087 | 7.173 | 7.1169 | 7.0567 | 6.9934 | 6.924 | 6.672 | 6.5638 | 6.5536 | 7.3248 | 7.2657 | 7.2116 | 7.1514 | 7.0789 | 7.0228 | 6.9391 | 6.8483 | 6.7544 | 6.6575 | 6.2942 | 6.1259 | 6.1075
|  | WHITING BAY | HE |  |  |  |  | 7.3685 | 7.3185 | 7.2777 | 7.2287 | 7.1675 | 7.1236 | 7.0461 | 6.9624 | 6.8777 | 6.7899 | 6.3716 | 6.2644 | 6.2491 | 7.3608 | 7.3271 | 7.2995 | 7.2689 | 7.2281 | 7.1995 | 7.1495 | 7.0934 | 7.0332 | 6.9761 | 6.7006 | 6.5873 | 6.4934 | 7.3248 | 7.2748 | 7.2361 | 7.1912 | 7.131 | 7.0901 | 7.0167 | 6.9391 | 6.8575 | 6.7728 | 6.383 | 6.2799 | 6.2667
|  | WHITING BAY | CF |  |  |  |  | 7.3777 | 7.3389 | 7.3032 | 7.2573 | 7.2185 | 7.1685 | 7.1328 | 7.0716 | 7.0226 | 6.9634 | 6.6808 | 6.4063 | 6.2685 | 7.3669 | 7.3414 | 7.3199 | 7.2863 | 7.2608 | 7.225 | 7.2026 | 7.1546 | 7.1199 | 7.0771 | 6.8546 | 6.5822 | 6.3322 | 7.332 | 7.2963 | 7.2616 | 7.2177 | 7.1799 | 7.132 | 7.1004 | 7.0391 | 6.9912 | 6.933 | 6.6626 | 6.3993 | 6.281
| MYBSTER 1 | WICK | MINIMUM HEADROOM | ND 35583 50947 | NO | NO | 1.226 | 6.1471 | 5.7756 | 5.3399 | 4.8624 | 4.3838 | 3.9205 | 3.3032 | 2.8858 | 2.3736 | 1.8226 | -0.08558 | -1.2642 | -1.4795 | 8.6226 | 8.3797 | 8.0716 | 7.7134 | 7.391 | 7.0899 | 6.7471 | 6.6124 | 6.3124 | 6.0328 | 5.0389 | 4.3542 | 3.5175 | 7.3134 | 6.9614 | 6.5379 | 6.094 | 5.6338 | 5.192 | 4.6134 | 4.3328 | 3.8185 | 3.3103 | 1.6297 | 0.61952 | 0.44197
|  | WICK | EE |  |  |  |  | 6.1471 | 5.7756 | 5.3399 | 4.8665 | 4.3838 | 3.9205 | 3.3032 | 2.9654 | 2.3818 | 1.8226 | -0.08558 | -1.0866 | -1.3233 | 8.6226 | 8.3797 | 8.0716 | 7.7226 | 7.391 | 7.0899 | 6.7471 | 6.6124 | 6.3124 | 6.0328 | 5.0389 | 4.3542 | 3.692 | 7.3134 | 6.9614 | 6.5379 | 6.094 | 5.6338 | 5.192 | 4.6134 | 4.3552 | 3.8185 | 3.3103 | 1.6297 | 0.78585 | 0.57462
|  | WICK | HT |  |  |  |  | 6.1654 | 5.7971 | 5.3522 | 4.8624 | 4.4205 | 3.9991 | 3.4563 | 2.8858 | 2.3736 | 2.144 | -0.010069 | -1.2642 | -1.4795 | 8.6379 | 8.4022 | 8.0838 | 7.7134 | 7.4042 | 7.1654 | 6.9042 | 6.6307 | 6.393 | 6.345 | 5.3705 | 4.8369 | 4.745 | 7.3552 | 7.0185 | 6.6001 | 6.1481 | 5.7287 | 5.3512 | 4.8583 | 4.3328 | 3.8583 | 3.6971 | 1.7236 | 0.61952 | 0.44197
|  | WICK | HE |  |  |  |  | 6.2042 | 5.945 | 5.6471 | 5.3114 | 4.9858 | 4.7124 | 4.3134 | 3.8777 | 3.4583 | 3.3012 | 1.1961 | 0.11034 | -0.24068 | 8.6695 | 8.4787 | 8.2389 | 7.9512 | 7.6899 | 7.4848 | 7.2471 | 7.0022 | 6.7705 | 6.7175 | 5.5971 | 4.8654 | 4.1777 | 7.393 | 7.1471 | 6.8593 | 6.541 | 6.2236 | 5.9644 | 5.593 | 5.1848 | 4.7961 | 4.6981 | 2.7869 | 1.8461 | 1.5512
|  | WICK | CF |  |  |  |  | 6.3828 | 6.195 | 5.9797 | 5.7542 | 5.544 | 5.3124 | 5.094 | 4.8899 | 4.6389 | 4.3838 | 3.2971 | 1.9379 | 0.83483 | 8.8216 | 8.6818 | 8.5103 | 8.3307 | 8.1593 | 7.9685 | 7.7879 | 7.6246 | 7.443 | 7.2542 | 6.4032 | 5.1063 | 3.5175 | 7.5654 | 7.3899 | 7.1787 | 6.9593 | 6.7614 | 6.5328 | 6.3134 | 6.1165 | 5.8787 | 5.6358 | 4.6491 | 3.392 | 2.4461
| WOODHILL | WOODHILL | MINIMUM HEADROOM | NJ 91259 07053 | NO | NO | 4.834 | 3.9133 | 3.4214 | 2.8592 | 2.2235 | 1.4949 | 1.0949 | -0.10101 | -1.3877 | -2.6275 | -3.8 | -9.2622 | -12.8602 | -13.4867 | 5.5143 | 5.3255 | 5.0725 | 4.6949 | 4.2296 | 3.952 | 3.3469 | 2.5918 | 1.9061 | 1.2602 | -1.4663 | -3.5061 | -5.3602 | 5.4214 | 4.9806 | 4.4061 | 3.7653 | 3.0725 | 2.5061 | 1.4878 | 0.33878 | -0.71734 | -1.698 | -6.5102 | -9.7959 | -10.3755
|  | WOODHILL | EE |  |  |  |  | 3.9133 | 3.4214 | 2.8592 | 2.2235 | 1.4949 | 1.0949 | -0.10101 | -1.3877 | -2.6275 | -3.8 | -8.9724 | -12.4816 | -13.298 | 5.5143 | 5.3255 | 5.0725 | 4.6949 | 4.2296 | 3.952 | 3.3469 | 2.5918 | 1.9061 | 1.2602 | -1.4663 | -3.5061 | -5.3602 | 5.4214 | 4.9806 | 4.4061 | 3.7653 | 3.0725 | 2.5061 | 1.4878 | 0.33878 | -0.71734 | -1.698 | -6.2306 | -9.452 | -10.1867
|  | WOODHILL | HT |  |  |  |  | 4.0776 | 3.5602 | 3.0357 | 2.4796 | 1.9337 | 1.3296 | 0.11838 | -0.8755 | -2.049 | -3.2775 | -9.2622 | -12.8602 | -13.4867 | 5.6072 | 5.4623 | 5.2929 | 5.0092 | 4.7347 | 4.4153 | 3.8572 | 3.3704 | 2.7551 | 2.1153 | -0.83162 | -2.2847 | -2.7031 | 5.602 | 5.2112 | 4.7276 | 4.2041 | 3.6908 | 3.0929 | 2.0316 | 1.1306 | 0.052049 | -1.0531 | -6.5102 | -9.7959 | -10.3755
|  | WOODHILL | HE |  |  |  |  | 4.0582 | 3.7623 | 3.4541 | 3.1143 | 2.7857 | 2.35 | 1.6327 | 1.0214 | 0.1296 | -0.8255 | -5.8082 | -8.8153 | -10.1418 | 5.5969 | 5.4592 | 5.3235 | 5.1112 | 4.8031 | 4.448 | 4.002 | 3.5327 | 2.9449 | 2.3337 | -0.68877 | -2.1673 | -3.899 | 5.5786 | 5.2541 | 4.9357 | 4.5153 | 4.0398 | 3.4959 | 2.6959 | 1.9153 | 1.0592 | 0.16736 | -4.448 | -7.052 | -8.2653
|  | WOODHILL | CF |  |  |  |  | 4.1582 | 4.0102 | 3.8439 | 3.649 | 3.4296 | 3.2082 | 2.9439 | 2.5939 | 2.2214 | 1.9582 | -0.76734 | -4.0592 | -6.8092 | 5.6398 | 5.5633 | 5.4755 | 5.3694 | 5.252 | 5.0969 | 4.8582 | 4.5449 | 4.2612 | 4.0643 | 2.0663 | -1.0163 | -5.3235 | 5.699 | 5.5296 | 5.3418 | 5.1214 | 4.8765 | 4.6143 | 4.2888 | 3.8337 | 3.4204 | 3.1347 | 0.16021 | -2.8928 | -5.3918

## Primary Headroom Gen
#VALUE! | Grid Supply Point | Primary Substation | Scenario | Grid Reference | Single Transformer Site (YES/NO) | Upstream Constraint (YES / NO) | Outstanding Contracted Generation (MVA) | Generation Headroom Winter (MVA) | [12 empty] | Generation Headroom Summer (MVA) | [12 empty] | Generation Headroom Spring/Autumn (MVA)
[8 empty] | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
| FORT AUGUSTUS | ABERCHALDER | MINIMUM HEADROOM | NH 33843 03575 | YES | YES | 0 | 0.19895 | 0.19684 | 0.19684 | 0.19579 | 0.19474 | 0.19368 | 0.19053 | 0.18947 | 0.18842 | 0.18421 | 0.15474 | 0.11579 | 0.088421 | 0.20105 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19474 | 0.19263 | 0.19053 | 0.18842 | 0.18316 | 0.14947 | 0.10526 | 0.071579 | 0.20211 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19263 | 0.19158 | 0.18947 | 0.18316 | 0.14947 | 0.10526 | 0.071579
|  | ABERCHALDER | EE |  |  |  |  | 0.19895 | 0.19789 | 0.19684 | 0.19684 | 0.19579 | 0.19474 | 0.19263 | 0.19158 | 0.18947 | 0.18737 | 0.16211 | 0.12842 | 0.095789 | 0.20105 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19368 | 0.19263 | 0.19158 | 0.18947 | 0.15789 | 0.12316 | 0.085263 | 0.20211 | 0.20105 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.19474 | 0.19368 | 0.19158 | 0.18947 | 0.15789 | 0.12105 | 0.082105
|  | ABERCHALDER | HT |  |  |  |  | 0.19895 | 0.19684 | 0.19684 | 0.19579 | 0.19474 | 0.19368 | 0.19053 | 0.18947 | 0.18842 | 0.18421 | 0.15474 | 0.11579 | 0.088421 | 0.20105 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19474 | 0.19263 | 0.19053 | 0.18842 | 0.18316 | 0.14947 | 0.10526 | 0.071579 | 0.20211 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19263 | 0.19158 | 0.18947 | 0.18316 | 0.14947 | 0.10526 | 0.071579
|  | ABERCHALDER | HE |  |  |  |  | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19368 | 0.19263 | 0.19053 | 0.18526 | 0.16632 | 0.13895 | 0.10842 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.19895 | 0.19789 | 0.19579 | 0.19263 | 0.18947 | 0.18421 | 0.16211 | 0.13158 | 0.097895 | 0.20211 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19263 | 0.19158 | 0.18947 | 0.18316 | 0.14947 | 0.10526 | 0.071579
|  | ABERCHALDER | CF |  |  |  |  | 0.2 | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19579 | 0.19368 | 0.19263 | 0.18316 | 0.16526 | 0.14316 | 0.20316 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.19684 | 0.19579 | 0.19263 | 0.17895 | 0.15895 | 0.13474 | 0.20421 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.19789 | 0.19579 | 0.19263 | 0.18 | 0.16 | 0.13474
| TUMMEL BRIDGE | ABERFELDY | MINIMUM HEADROOM | NN 84889 48876 | NO | YES | 0 | 6.7295 | 6.6674 | 6.5884 | 6.4558 | 6.2295 | 5.7347 | 5.1926 | 4.6295 | 4.1084 | 3.4811 | 0.87368 | -3.1632 | -6.1074 | 7.0021 | 6.8463 | 6.6484 | 6.4326 | 6.1737 | 5.7074 | 5.2737 | 4.8032 | 4.2621 | 3.6084 | 1.4095 | -2.4558 | -5.5695 | 6.2326 | 6.1684 | 6.0589 | 5.8568 | 5.6126 | 5.0811 | 4.4979 | 3.8979 | 3.3389 | 2.6547 | -0.12947 | -4.5147 | -7.8021
|  | ABERFELDY | EE |  |  |  |  | 6.7526 | 6.6979 | 6.6221 | 6.5432 | 6.4074 | 5.8537 | 5.1926 | 4.6295 | 4.1084 | 3.4811 | 0.87368 | -3.1632 | -6.1074 | 7.0568 | 6.9368 | 6.7989 | 6.6337 | 6.4179 | 5.9116 | 5.2937 | 4.8032 | 4.3358 | 3.7347 | 1.4095 | -2.4558 | -5.5695 | 6.2558 | 6.1958 | 6.1158 | 6.0137 | 5.8032 | 5.2147 | 4.4979 | 3.8979 | 3.3389 | 2.6547 | -0.12947 | -4.5147 | -7.8021
|  | ABERFELDY | HT |  |  |  |  | 6.7295 | 6.6674 | 6.5884 | 6.4558 | 6.2295 | 5.7347 | 5.2716 | 4.7937 | 4.2116 | 3.5516 | 1.3137 | -2.2379 | -4.6305 | 7.0021 | 6.8463 | 6.6484 | 6.4326 | 6.1737 | 5.7074 | 5.2737 | 4.82 | 4.2621 | 3.6084 | 1.4653 | -2.3611 | -5.0211 | 6.2326 | 6.1684 | 6.0589 | 5.8568 | 5.6126 | 5.0811 | 4.5821 | 4.0674 | 3.4358 | 2.7147 | 0.25789 | -3.6989 | -6.4347
|  | ABERFELDY | HE |  |  |  |  | 6.7842 | 6.7505 | 6.7116 | 6.6695 | 6.6242 | 6.0695 | 5.5232 | 5.0463 | 4.5274 | 3.9158 | 2.1411 | -0.86737 | -4.1705 | 7.12 | 7.0358 | 6.9368 | 6.8063 | 6.6179 | 6.1021 | 5.5663 | 5.1189 | 4.6147 | 3.9937 | 2.4484 | -0.59263 | -3.8979 | 6.2326 | 6.1684 | 6.0589 | 5.8568 | 5.6126 | 5.0811 | 4.5821 | 4.0674 | 3.4358 | 2.7147 | 0.25789 | -3.6989 | -6.4347
|  | ABERFELDY | CF |  |  |  |  | 6.8011 | 6.7821 | 6.76 | 6.74 | 6.7168 | 6.5789 | 6.4589 | 6.3379 | 6.1947 | 6.0021 | 4.7516 | 2.9274 | 0.89368 | 7.1558 | 7.1221 | 7.0811 | 7.0379 | 6.98 | 6.8263 | 6.6537 | 6.4589 | 6.2874 | 6.0842 | 4.7863 | 2.8579 | 0.67158 | 6.3042 | 6.2853 | 6.2632 | 6.2421 | 6.2179 | 6.0863 | 5.9695 | 5.7642 | 5.5768 | 5.3716 | 3.9937 | 1.9232 | -0.35789
| STRATHLEVEN | ABERFOYLE | MINIMUM HEADROOM | NS 53215 99705 | YES | YES | 0.05 | 4.2679 | 4.2332 | 4.1953 | 4.1521 | 4.0921 | 3.9689 | 3.8458 | 3.7121 | 3.5826 | 3.4553 | 2.8121 | 2.2311 | 1.7795 | 4.3858 | 4.3153 | 4.2353 | 4.1374 | 4.0321 | 3.9058 | 3.7816 | 3.6458 | 3.5174 | 3.3816 | 2.7553 | 2.2058 | 1.7079 | 4.4342 | 4.3616 | 4.2774 | 4.1774 | 4.07 | 3.9363 | 3.7995 | 3.6542 | 3.5132 | 3.3732 | 2.6668 | 2.0205 | 1.5068
|  | ABERFOYLE | EE |  |  |  |  | 4.2784 | 4.2384 | 4.1953 | 4.1521 | 4.1026 | 3.9753 | 3.8458 | 3.7121 | 3.5826 | 3.4553 | 2.8121 | 2.2311 | 1.7795 | 4.4111 | 4.3426 | 4.2647 | 4.1753 | 4.0742 | 3.9521 | 3.83 | 3.7037 | 3.5805 | 3.4605 | 2.8447 | 2.2847 | 1.8353 | 4.4605 | 4.3826 | 4.2953 | 4.1953 | 4.0816 | 3.9416 | 3.7995 | 3.6542 | 3.5132 | 3.3732 | 2.6668 | 2.0205 | 1.5068
|  | ABERFOYLE | HT |  |  |  |  | 4.2679 | 4.2332 | 4.1984 | 4.1616 | 4.0921 | 3.9689 | 3.8489 | 3.7195 | 3.5932 | 3.4626 | 2.8668 | 2.3542 | 1.8995 | 4.3858 | 4.3153 | 4.2353 | 4.1374 | 4.0321 | 3.9058 | 3.7816 | 3.6458 | 3.5174 | 3.3816 | 2.7553 | 2.2058 | 1.7079 | 4.4342 | 4.3616 | 4.2774 | 4.1774 | 4.07 | 3.9363 | 3.8058 | 3.6637 | 3.5247 | 3.3826 | 2.7174 | 2.1353 | 1.6132
|  | ABERFOYLE | HE |  |  |  |  | 4.2942 | 4.2732 | 4.2511 | 4.2268 | 4.2026 | 4.1532 | 4.07 | 3.9711 | 3.8742 | 3.7795 | 3.3153 | 2.8974 | 2.5026 | 4.4447 | 4.4037 | 4.3563 | 4.2921 | 4.2216 | 4.1205 | 4.0268 | 3.9279 | 3.8289 | 3.7311 | 3.2563 | 2.8258 | 2.4247 | 4.4342 | 4.3616 | 4.2774 | 4.1774 | 4.07 | 3.9363 | 3.8058 | 3.6637 | 3.5247 | 3.3826 | 2.7174 | 2.1353 | 1.6132
|  | ABERFOYLE | CF |  |  |  |  | 4.3037 | 4.2932 | 4.2826 | 4.27 | 4.2595 | 4.2405 | 4.2216 | 4.2037 | 4.1858 | 4.1689 | 3.9195 | 3.6795 | 3.4753 | 4.4668 | 4.4437 | 4.4184 | 4.3868 | 4.3542 | 4.3142 | 4.2721 | 4.2247 | 4.1753 | 4.1258 | 3.8489 | 3.5974 | 3.3763 | 4.5163 | 4.4932 | 4.4658 | 4.4353 | 4.4016 | 4.3563 | 4.3111 | 4.2616 | 4.21 | 4.1584 | 3.8732 | 3.6068 | 3.3784
| KEITH 2 | ABERLOUR | MINIMUM HEADROOM | NJ 24809 40878 | NO | YES | 0 | 5.9211 | 5.8842 | 5.8358 | 5.7758 | 5.5758 | 5.2989 | 5.2326 | 4.9126 | 4.5947 | 4.2674 | 2.14 | -0.52211 | -2.2042 | 5.6368 | 5.4926 | 5.4126 | 5.3347 | 5.1126 | 4.8779 | 4.8074 | 4.5716 | 4.3021 | 4.0305 | 2.1684 | -0.30842 | -2.0726 | 6.1516 | 6.0674 | 5.9958 | 5.9242 | 5.7547 | 5.4768 | 5.4158 | 5.0768 | 4.7547 | 4.4263 | 2.2526 | -0.58842 | -2.4695
|  | ABERLOUR | EE |  |  |  |  | 5.9368 | 5.9074 | 5.86 | 5.8116 | 5.64 | 5.3274 | 5.2779 | 4.9126 | 4.5947 | 4.2674 | 2.14 | -0.52211 | -2.2042 | 5.6705 | 5.5421 | 5.4716 | 5.4021 | 5.1874 | 4.9295 | 4.8779 | 4.5779 | 4.3168 | 4.0516 | 2.1684 | -0.30842 | -2.0726 | 6.1674 | 6.1084 | 6.0421 | 5.9747 | 5.8095 | 5.4937 | 5.4484 | 5.0768 | 4.7547 | 4.4263 | 2.2526 | -0.58842 | -2.4695
|  | ABERLOUR | HT |  |  |  |  | 5.9211 | 5.8842 | 5.8358 | 5.7758 | 5.5758 | 5.2989 | 5.2326 | 4.9568 | 4.6347 | 4.3105 | 2.4958 | 0.43789 | -0.88 | 5.6368 | 5.4926 | 5.4126 | 5.3347 | 5.1126 | 4.8779 | 4.8074 | 4.5716 | 4.3021 | 4.0305 | 2.3179 | 0.16421 | -1.2726 | 6.1516 | 6.0674 | 5.9958 | 5.9242 | 5.7547 | 5.4768 | 5.4158 | 5.1368 | 4.8095 | 4.4789 | 2.5621 | 0.26632 | -1.2347
|  | ABERLOUR | HE |  |  |  |  | 5.9568 | 5.9379 | 5.9147 | 5.8884 | 5.8 | 5.4853 | 5.4516 | 5.1905 | 4.9263 | 4.6442 | 2.9432 | 1.0147 | -1.0653 | 5.7137 | 5.6074 | 5.5705 | 5.5316 | 5.3474 | 5.0916 | 5.0568 | 4.8432 | 4.6305 | 4.3937 | 2.8274 | 0.96316 | -1.0526 | 6.1516 | 6.0674 | 5.9958 | 5.9242 | 5.7547 | 5.4768 | 5.4158 | 5.1368 | 4.8095 | 4.4789 | 2.5621 | 0.26632 | -1.2347
|  | ABERLOUR | CF |  |  |  |  | 5.9684 | 5.9579 | 5.9453 | 5.9305 | 5.9168 | 5.8137 | 5.8021 | 5.7105 | 5.6326 | 5.5305 | 4.7 | 3.4947 | 2.28 | 5.7547 | 5.7 | 5.6779 | 5.6547 | 5.5705 | 5.4674 | 5.4463 | 5.3547 | 5.2737 | 5.16 | 4.3589 | 3.1863 | 1.9337 | 6.1989 | 6.1884 | 6.1758 | 6.1621 | 6.1295 | 6.0042 | 5.9863 | 5.8747 | 5.78 | 5.6705 | 4.8695 | 3.5726 | 2.2211
| ABERNETHY | ABERNETHY | MINIMUM HEADROOM | NO 20094 17132 | YES | YES | 0 | 2.3458 | 2.3026 | 2.2532 | 2.2037 | 2.1353 | 1.9679 | 1.8184 | 1.6584 | 1.45 | 1.1184 | 0.57211 | -2.5868 | -3.5647 | 2.1721 | 2.1247 | 2.07 | 2.0184 | 1.9416 | 1.77 | 1.6163 | 1.4532 | 1.2342 | 0.87211 | 0.42053 | -2.2289 | -3.2247 | 2.1247 | 2.0847 | 2.0374 | 1.9858 | 1.9079 | 1.7216 | 1.5542 | 1.3753 | 1.1395 | 0.75737 | 0.21947 | -1.0332 | -1.9521
|  | ABERNETHY | EE |  |  |  |  | 2.3584 | 2.3342 | 2.2942 | 2.2563 | 2.2058 | 2.0384 | 1.8342 | 1.6816 | 1.5353 | 1.3279 | 0.57211 | -0.43 | -1.3437 | 2.1953 | 2.1595 | 2.1163 | 2.0763 | 2.0216 | 1.8532 | 1.6437 | 1.5016 | 1.3605 | 1.1447 | 0.45211 | -0.56474 | -1.5837 | 2.1447 | 2.1142 | 2.0763 | 2.0395 | 1.9879 | 1.8016 | 1.5711 | 1.4068 | 1.2479 | 1.0121 | 0.21947 | -0.89105 | -1.9521
|  | ABERNETHY | HT |  |  |  |  | 2.3458 | 2.3026 | 2.2532 | 2.2037 | 2.1353 | 1.9679 | 1.8184 | 1.6584 | 1.45 | 1.1184 | 0.61737 | -0.47842 | -1.2721 | 2.1721 | 2.1247 | 2.07 | 2.0184 | 1.9416 | 1.77 | 1.6163 | 1.4532 | 1.2342 | 0.87211 | 0.42053 | -0.80684 | -1.6932 | 2.1247 | 2.0847 | 2.0374 | 1.9858 | 1.9079 | 1.7216 | 1.5542 | 1.3753 | 1.1395 | 0.75737 | 0.23842 | -1.0332 | -1.9447
|  | ABERNETHY | HE |  |  |  |  | 2.3721 | 2.3595 | 2.3447 | 2.3279 | 2.2889 | 2.1132 | 1.9289 | 1.7805 | 1.61 | 1.4089 | 0.96684 | -2.5868 | -3.5647 | 2.2247 | 2.2026 | 2.1784 | 2.1553 | 2.1089 | 1.9332 | 1.7353 | 1.5858 | 1.4068 | 1.1921 | 0.81 | -2.2289 | -3.2247 | 2.1247 | 2.0847 | 2.0374 | 1.9858 | 1.9079 | 1.7216 | 1.5542 | 1.3753 | 1.1395 | 0.75737 | 0.23842 | -1.0332 | -1.9447
|  | ABERNETHY | CF |  |  |  |  | 2.3795 | 2.3732 | 2.3647 | 2.3553 | 2.3479 | 2.2995 | 2.2458 | 2.1816 | 2.1258 | 2.0279 | 1.6911 | -0.46474 | -1.1047 | 2.2395 | 2.2258 | 2.21 | 2.1963 | 2.1784 | 2.1311 | 2.0763 | 2.01 | 1.9542 | 1.8405 | 1.4837 | -0.36263 | -1.0489 | 2.1721 | 2.1658 | 2.1563 | 2.1426 | 2.1289 | 2.0784 | 2.0247 | 1.9605 | 1.8995 | 1.7805 | 1.3953 | -0.83526 | -1.5637
| TARLAND | ABOYNE | MINIMUM HEADROOM | NO 52048 98716 | NO | YES | 0 | 15.9068 | 15.6289 | 15.3184 | 14.9668 | 14.6384 | 14.0805 | 13.5321 | 12.9879 | 12.4026 | 11.9268 | 10.0174 | 7.8637 | 5.7616 | 14.0021 | 13.6853 | 13.3326 | 12.9274 | 12.5526 | 11.9832 | 11.4253 | 10.8716 | 10.2853 | 9.8411 | 8.2695 | 6.3274 | 4.0811 | 14.6434 | 14.3403 | 14.0003 | 13.6118 | 13.2508 | 12.6466 | 12.0539 | 11.4634 | 10.8297 | 10.3255 | 8.3182 | 6.0213 | 3.7045
|  | ABOYNE | EE |  |  |  |  | 16.0058 | 15.8026 | 15.5353 | 15.2184 | 14.8774 | 14.3142 | 13.7079 | 13.1068 | 12.5542 | 12.1111 | 10.0174 | 7.8637 | 5.7616 | 14.1137 | 13.8832 | 13.5811 | 13.2179 | 12.8253 | 12.2642 | 11.6726 | 11.0884 | 10.5453 | 10.1389 | 8.2811 | 6.3432 | 4.0811 | 14.7508 | 14.5297 | 14.2361 | 13.8866 | 13.5066 | 12.8971 | 12.2434 | 11.595 | 10.9971 | 10.5255 | 8.3182 | 6.0213 | 3.7045
|  | ABOYNE | HT |  |  |  |  | 15.9068 | 15.6289 | 15.3184 | 14.9668 | 14.6384 | 14.0805 | 13.5321 | 12.9879 | 12.4026 | 11.9268 | 10.2342 | 8.4005 | 6.6195 | 14.0021 | 13.6853 | 13.3326 | 12.9274 | 12.5526 | 11.9832 | 11.4253 | 10.8716 | 10.2853 | 9.8411 | 8.2695 | 6.3274 | 4.3705 | 14.6434 | 14.3403 | 14.0003 | 13.6118 | 13.2508 | 12.6466 | 12.0539 | 11.4634 | 10.8297 | 10.3255 | 8.5287 | 6.455 | 4.4371
|  | ABOYNE | HE |  |  |  |  | 16.1405 | 16.0026 | 15.8258 | 15.6005 | 15.3489 | 14.7858 | 14.2711 | 13.8026 | 13.3405 | 12.9921 | 11.6079 | 9.8363 | 7.4711 | 14.2663 | 14.1084 | 13.9042 | 13.6421 | 13.3474 | 12.7884 | 12.2674 | 11.8032 | 11.3474 | 11.0316 | 9.8242 | 8.0747 | 5.6726 | 14.6434 | 14.3403 | 14.0003 | 13.6118 | 13.2508 | 12.6466 | 12.0539 | 11.4634 | 10.8297 | 10.3255 | 8.5287 | 6.455 | 4.4371
|  | ABOYNE | CF |  |  |  |  | 16.2174 | 16.1374 | 16.0489 | 15.9353 | 15.8142 | 15.5805 | 15.3521 | 15.1142 | 14.8995 | 14.7637 | 14.0542 | 12.8416 | 11.4311 | 14.3526 | 14.26 | 14.16 | 14.0284 | 13.8863 | 13.6495 | 13.4137 | 13.1653 | 12.94 | 12.8042 | 12.1505 | 10.9189 | 9.3547 | 14.9803 | 14.8918 | 14.795 | 14.6697 | 14.5339 | 14.2792 | 14.0287 | 13.7676 | 13.5318 | 13.3866 | 12.6339 | 11.3003 | 9.6918
| GRUDIE BRIDGE | ACHILTIBUIE | MINIMUM HEADROOM | NC 01618 09557 | YES | NO | 0 | 0.38421 | 0.37263 | 0.36 | 0.34737 | 0.33368 | 0.32105 | 0.30737 | 0.29579 | 0.28211 | 0.27053 | 0.21158 | -0.30211 | -0.36316 | 0.47158 | 0.45158 | 0.42947 | 0.40737 | 0.38632 | 0.36526 | 0.34526 | 0.32632 | 0.30632 | 0.28632 | 0.19895 | -0.21895 | -0.28421 | 0.40947 | 0.39474 | 0.37895 | 0.36421 | 0.34842 | 0.33368 | 0.31684 | 0.30211 | 0.28737 | 0.27368 | 0.19684 | -0.32737 | -0.39684
|  | ACHILTIBUIE | EE |  |  |  |  | 0.39053 | 0.38 | 0.36947 | 0.35789 | 0.34632 | 0.33368 | 0.32421 | 0.31263 | 0.30316 | 0.29263 | 0.25368 | -0.23474 | -0.28211 | 0.48211 | 0.46526 | 0.44842 | 0.43053 | 0.41368 | 0.39579 | 0.38105 | 0.36421 | 0.34947 | 0.33474 | 0.26526 | -0.13895 | -0.18737 | 0.41684 | 0.40421 | 0.39053 | 0.37684 | 0.36211 | 0.34842 | 0.33579 | 0.32316 | 0.31158 | 0.29895 | 0.24842 | -0.25474 | -0.30737
|  | ACHILTIBUIE | HT |  |  |  |  | 0.38421 | 0.37263 | 0.36 | 0.34737 | 0.33368 | 0.32105 | 0.30737 | 0.29579 | 0.28211 | 0.27053 | 0.21158 | -0.30211 | -0.36316 | 0.47158 | 0.45158 | 0.42947 | 0.40737 | 0.38632 | 0.36526 | 0.34526 | 0.32632 | 0.30632 | 0.28632 | 0.19895 | -0.21895 | -0.28421 | 0.40947 | 0.39474 | 0.37895 | 0.36421 | 0.34842 | 0.33368 | 0.31684 | 0.30211 | 0.28737 | 0.27368 | 0.19684 | -0.32737 | -0.39684
|  | ACHILTIBUIE | HE |  |  |  |  | 0.39684 | 0.39053 | 0.38421 | 0.37684 | 0.36842 | 0.36105 | 0.35263 | 0.34632 | 0.33895 | 0.33368 | 0.31158 | 0.10105 | 0.093684 | 0.49579 | 0.48632 | 0.47684 | 0.46421 | 0.45368 | 0.44211 | 0.43158 | 0.42105 | 0.41158 | 0.40316 | 0.36947 | 0.17053 | 0.14421 | 0.40947 | 0.39474 | 0.37895 | 0.36421 | 0.34842 | 0.33368 | 0.31684 | 0.30211 | 0.28737 | 0.27368 | 0.19684 | -0.32737 | -0.39684
|  | ACHILTIBUIE | CF |  |  |  |  | 0.40105 | 0.39684 | 0.39368 | 0.39053 | 0.38632 | 0.38211 | 0.37895 | 0.37579 | 0.37158 | 0.36842 | 0.35263 | 0.34526 | 0.33895 | 0.50316 | 0.49684 | 0.49053 | 0.48421 | 0.47895 | 0.47263 | 0.46632 | 0.46 | 0.45263 | 0.44737 | 0.41789 | 0.4 | 0.38421 | 0.42947 | 0.42526 | 0.42105 | 0.41684 | 0.41158 | 0.40737 | 0.40316 | 0.39895 | 0.39474 | 0.39053 | 0.37053 | 0.36 | 0.35158
| BEAULY | AIGAS | MINIMUM HEADROOM | NH 45362 40529 | YES | YES | 0 | 0.53474 | 0.53158 | 0.52316 | 0.51368 | 0.50632 | 0.43263 | 0.34105 | 0.24632 | 0.15684 | 0.018947 | -0.76211 | -1.7095 | -2.4611 | 0.52421 | 0.52 | 0.51158 | 0.50316 | 0.49579 | 0.43474 | 0.35158 | 0.26211 | 0.18 | 0.042105 | -0.71263 | -1.7105 | -2.46 | 0.52632 | 0.52211 | 0.51263 | 0.50316 | 0.49474 | 0.42632 | 0.34211 | 0.25684 | 0.18105 | 0.027368 | -0.86105 | -1.9 | -2.7579
|  | AIGAS | EE |  |  |  |  | 0.53684 | 0.53474 | 0.52526 | 0.51684 | 0.50632 | 0.43684 | 0.35263 | 0.26632 | 0.19158 | 0.078947 | -0.76211 | -1.7095 | -2.4611 | 0.52632 | 0.52421 | 0.51474 | 0.50632 | 0.49895 | 0.44526 | 0.37789 | 0.30737 | 0.24737 | 0.14105 | -0.69053 | -1.6379 | -2.46 | 0.52947 | 0.52526 | 0.51579 | 0.50632 | 0.49684 | 0.42632 | 0.34211 | 0.25684 | 0.18105 | 0.062105 | -0.86105 | -1.9 | -2.7579
|  | AIGAS | HT |  |  |  |  | 0.53474 | 0.53158 | 0.52316 | 0.51368 | 0.50632 | 0.44737 | 0.38842 | 0.31789 | 0.22526 | 0.062105 | -0.71368 | -1.6179 | -2.24 | 0.52421 | 0.52 | 0.51158 | 0.50316 | 0.49579 | 0.45158 | 0.40316 | 0.34211 | 0.25684 | 0.093684 | -0.71263 | -1.7105 | -2.4158 | 0.52632 | 0.52211 | 0.51263 | 0.50316 | 0.49474 | 0.43684 | 0.37789 | 0.30526 | 0.20632 | 0.027368 | -0.83579 | -1.8705 | -2.5905
|  | AIGAS | HE |  |  |  |  | 0.53789 | 0.53684 | 0.53368 | 0.53158 | 0.52842 | 0.43263 | 0.34105 | 0.24632 | 0.15684 | 0.018947 | -0.56316 | -1.3095 | -2.12 | 0.52737 | 0.52632 | 0.52421 | 0.52211 | 0.51895 | 0.43474 | 0.35158 | 0.26211 | 0.18 | 0.042105 | -0.53263 | -1.3042 | -2.1453 | 0.52632 | 0.52211 | 0.51263 | 0.50316 | 0.49474 | 0.43684 | 0.37789 | 0.30526 | 0.20632 | 0.027368 | -0.83579 | -1.8705 | -2.5905
|  | AIGAS | CF |  |  |  |  | 0.53895 | 0.53789 | 0.53684 | 0.53474 | 0.53368 | 0.50632 | 0.48 | 0.42526 | 0.36632 | 0.29684 | -0.0084211 | -0.47789 | -1.0084 | 0.52842 | 0.52737 | 0.52737 | 0.52526 | 0.52421 | 0.50316 | 0.48421 | 0.42421 | 0.36105 | 0.28526 | -0.027368 | -0.51684 | -1.0979 | 0.53368 | 0.53263 | 0.53158 | 0.52842 | 0.52526 | 0.49684 | 0.47158 | 0.40947 | 0.34421 | 0.26632 | -0.071579 | -0.59579 | -1.2011
| ARDMORE | AIRD | MINIMUM HEADROOM | NF 79163 53853 | NO | YES | 0 | 7.5421 | 7.5095 | 7.4758 | 7.4421 | 7.4084 | 7.3716 | 7.3358 | 7.3011 | 7.2684 | 7.2368 | 7.1326 | 7.0621 | 6.2032 | 7.2347 | 7.1705 | 7.1063 | 7.0432 | 6.9832 | 6.92 | 6.86 | 6.8011 | 6.7463 | 6.6926 | 6.4779 | 6.3 | 5.5284 | 7.4979 | 7.4337 | 7.3695 | 7.3063 | 7.2453 | 7.1832 | 7.1232 | 7.0642 | 7.0095 | 6.9558 | 6.74 | 6.5632 | 5.6116
|  | AIRD | EE |  |  |  |  | 7.5526 | 7.5263 | 7.4989 | 7.4705 | 7.4411 | 7.4105 | 7.3811 | 7.3537 | 7.3274 | 7.3021 | 7.2032 | 7.1495 | 6.3947 | 7.2621 | 7.2116 | 7.1611 | 7.1105 | 7.06 | 7.0095 | 6.9621 | 6.9147 | 6.8716 | 6.8295 | 6.6474 | 6.5137 | 5.78 | 7.5095 | 7.4747 | 7.4242 | 7.3737 | 7.3232 | 7.2726 | 7.2253 | 7.1779 | 7.1347 | 7.0916 | 6.9105 | 6.7768 | 5.8684
|  | AIRD | HT |  |  |  |  | 7.5421 | 7.5095 | 7.4758 | 7.4421 | 7.4084 | 7.3716 | 7.3358 | 7.3011 | 7.2684 | 7.2368 | 7.1326 | 7.0621 | 6.2032 | 7.2347 | 7.1705 | 7.1063 | 7.0432 | 6.9832 | 6.92 | 6.86 | 6.8011 | 6.7463 | 6.6926 | 6.4779 | 6.3 | 5.5284 | 7.4979 | 7.4337 | 7.3695 | 7.3063 | 7.2453 | 7.1832 | 7.1232 | 7.0642 | 7.0095 | 6.9558 | 6.74 | 6.5632 | 5.6116
|  | AIRD | HE |  |  |  |  | 7.5716 | 7.5537 | 7.5347 | 7.5137 | 7.4916 | 7.4684 | 7.4474 | 7.4263 | 7.4063 | 7.3884 | 7.3284 | 7.2979 | 6.9253 | 7.3032 | 7.2716 | 7.24 | 7.2063 | 7.1726 | 7.1379 | 7.1063 | 7.0747 | 7.0453 | 7.0179 | 6.9168 | 6.8463 | 6.4863 | 7.4979 | 7.4337 | 7.3695 | 7.3063 | 7.2453 | 7.1832 | 7.1232 | 7.0642 | 7.0095 | 6.9558 | 6.74 | 6.5632 | 5.6116
|  | AIRD | CF |  |  |  |  | 7.5811 | 7.5716 | 7.5611 | 7.5505 | 7.54 | 7.5295 | 7.5179 | 7.5063 | 7.4958 | 7.4842 | 7.4379 | 7.4137 | 7.4032 | 7.3232 | 7.3042 | 7.2842 | 7.2653 | 7.2453 | 7.2253 | 7.2053 | 7.1853 | 7.1653 | 7.1453 | 7.0579 | 6.9958 | 6.9505 | 7.54 | 7.5305 | 7.5189 | 7.5084 | 7.4968 | 7.4863 | 7.4684 | 7.4484 | 7.4284 | 7.4084 | 7.3211 | 7.2589 | 7.2137
| PORT ANN | AIRIGH-NA-BRODAIG | MINIMUM HEADROOM | NR 85849 74792 | YES | YES | 0 | 0.32763 | 0.32658 | 0.32342 | 0.32026 | 0.31395 | 0.26237 | 0.20237 | 0.14237 | 0.084474 | -0.005 | -0.50184 | -3.7882 | -4.2408 | 0.32342 | 0.32132 | 0.31816 | 0.31605 | 0.31079 | 0.26447 | 0.20974 | 0.15395 | 0.10132 | 0.011842 | -0.46184 | -3.1987 | -3.7018 | 0.32447 | 0.32237 | 0.31921 | 0.31605 | 0.31079 | 0.26974 | 0.215 | 0.16132 | 0.11395 | 0.011842 | -0.56289 | -3.9018 | -4.4418
|  | AIRIGH-NA-BRODAIG | EE |  |  |  |  | 0.32763 | 0.32763 | 0.32342 | 0.32026 | 0.31395 | 0.27184 | 0.21816 | 0.16342 | 0.11711 | 0.038158 | -0.50184 | -3.7882 | -4.2408 | 0.32342 | 0.32237 | 0.31816 | 0.31605 | 0.31079 | 0.27816 | 0.235 | 0.19184 | 0.15395 | 0.081316 | -0.45342 | -3.1987 | -3.7018 | 0.32447 | 0.32342 | 0.31921 | 0.31605 | 0.31079 | 0.26974 | 0.215 | 0.16132 | 0.11395 | 0.029737 | -0.56289 | -3.9018 | -4.4418
|  | AIRIGH-NA-BRODAIG | HT |  |  |  |  | 0.32763 | 0.32658 | 0.32342 | 0.32026 | 0.31816 | 0.28237 | 0.24658 | 0.195 | 0.135 | 0.031842 | -0.46395 | -3.1566 | -3.5461 | 0.32342 | 0.32132 | 0.31921 | 0.31605 | 0.31395 | 0.28553 | 0.25711 | 0.21079 | 0.15711 | 0.052895 | -0.46184 | -2.7734 | -3.1976 | 0.32447 | 0.32237 | 0.32026 | 0.31711 | 0.31395 | 0.27921 | 0.24237 | 0.18868 | 0.12553 | 0.011842 | -0.54184 | -3.3239 | -3.7745
|  | AIRIGH-NA-BRODAIG | HE |  |  |  |  | 0.32763 | 0.32763 | 0.32658 | 0.32553 | 0.32447 | 0.26237 | 0.20237 | 0.14237 | 0.084474 | -0.005 | -0.37763 | -2.1797 | -2.6976 | 0.32342 | 0.32342 | 0.32237 | 0.32132 | 0.32026 | 0.26447 | 0.20974 | 0.15395 | 0.10132 | 0.011842 | -0.35658 | -1.9018 | -2.4282 | 0.32447 | 0.32237 | 0.32026 | 0.31711 | 0.31395 | 0.27921 | 0.24237 | 0.18868 | 0.12553 | 0.011842 | -0.54184 | -3.3239 | -3.7745
|  | AIRIGH-NA-BRODAIG | CF |  |  |  |  | 0.32974 | 0.32763 | 0.32658 | 0.32658 | 0.32553 | 0.30974 | 0.29395 | 0.25395 | 0.21605 | 0.17184 | -0.022895 | -1.6503 | -1.985 | 0.32447 | 0.32342 | 0.32237 | 0.32237 | 0.32237 | 0.30763 | 0.295 | 0.25395 | 0.215 | 0.16763 | -0.032368 | -1.4018 | -1.7576 | 0.32658 | 0.32447 | 0.32342 | 0.32342 | 0.32237 | 0.30658 | 0.28974 | 0.24658 | 0.20342 | 0.15289 | -0.062895 | -1.7282 | -2.1113
| COUPAR ANGUS | ALYTH | MINIMUM HEADROOM | NO 23579 48311 | NO | YES | 0.196 | 4.8893 | 4.6556 | 4.3745 | 4.0493 | 3.6082 | 2.884 | 2.5914 | 2.0829 | 1.8145 | 1.1851 | -1.3665 | -5.6876 | -9.1413 | 4.9093 | 4.6124 | 4.2577 | 3.8419 | 3.264 | 2.4661 | 2.0861 | 1.5819 | 1.2335 | 0.604 | -1.4276 | -5.0592 | -8.5065 | 5.0187 | 4.724 | 4.3724 | 3.9619 | 3.3935 | 2.5314 | 2.1608 | 1.5851 | 1.2451 | 0.52611 | -2.1181 | -5.0992 | -8.4581
|  | ALYTH | EE |  |  |  |  | 4.9472 | 4.7535 | 4.5166 | 4.2366 | 3.8598 | 3.0672 | 2.6766 | 2.0914 | 1.9251 | 1.3629 | -1.3665 | -4.176 | -7.1928 | 4.9777 | 4.7335 | 4.4366 | 4.0808 | 3.5903 | 2.7282 | 2.204 | 1.6766 | 1.4629 | 0.93558 | -1.4276 | -4.0013 | -7.2086 | 5.0882 | 4.8419 | 4.5461 | 4.1924 | 3.7072 | 2.7619 | 2.2514 | 1.6093 | 1.4019 | 0.77453 | -2.1181 | -5.0992 | -8.4581
|  | ALYTH | HT |  |  |  |  | 4.8893 | 4.6556 | 4.3745 | 4.0493 | 3.6082 | 2.884 | 2.5914 | 2.0829 | 1.8145 | 1.1851 | -0.68758 | -3.5781 | -6.0402 | 4.9093 | 4.6124 | 4.2577 | 3.8419 | 3.264 | 2.4661 | 2.0861 | 1.5819 | 1.2335 | 0.604 | -0.98232 | -4.0718 | -6.8128 | 5.0187 | 4.724 | 4.3724 | 3.9619 | 3.3935 | 2.5314 | 2.1608 | 1.5851 | 1.2451 | 0.52611 | -1.4255 | -4.6276 | -7.4423
|  | ALYTH | HE |  |  |  |  | 5.0114 | 4.8451 | 4.6503 | 4.4061 | 4.0451 | 3.2303 | 2.8619 | 2.3672 | 2.1745 | 1.6861 | -0.011789 | -5.6876 | -9.1413 | 5.0514 | 4.8408 | 4.5851 | 4.2608 | 3.7766 | 2.8903 | 2.3903 | 1.9114 | 1.6566 | 1.1829 | -0.21389 | -5.0592 | -8.5065 | 5.0187 | 4.724 | 4.3724 | 3.9619 | 3.3935 | 2.5314 | 2.1608 | 1.5851 | 1.2451 | 0.52611 | -1.4255 | -4.6276 | -7.4423
|  | ALYTH | CF |  |  |  |  | 5.0672 | 4.9903 | 4.8987 | 4.8008 | 4.6766 | 4.3998 | 4.2745 | 4.0366 | 3.9324 | 3.6903 | 2.6966 | -2.0286 | -4.1455 | 5.1198 | 5.0229 | 4.9103 | 4.7861 | 4.6251 | 4.3335 | 4.1661 | 3.9198 | 3.7808 | 3.4956 | 2.5061 | -1.6602 | -3.8971 | 5.2324 | 5.1335 | 5.0177 | 4.8924 | 4.7335 | 4.4093 | 4.2461 | 3.9703 | 3.8345 | 3.5366 | 2.3998 | -2.7002 | -5.0792
| FORT WILLIAM | ANNAT | MINIMUM HEADROOM | NN 08452 76751 | YES | NO | 0 | 7.0621 | 7.0189 | 6.9726 | 6.9274 | 6.8811 | 6.8063 | 6.7042 | 6.6011 | 6.4979 | 6.4021 | 5.9747 | 5.6537 | 5.4189 | 6.7074 | 6.6274 | 6.5463 | 6.4674 | 6.3884 | 6.2895 | 6.1916 | 6.0958 | 6.0011 | 5.9126 | 5.5137 | 5.2095 | 4.9737 | 6.8558 | 6.8105 | 6.7453 | 6.6789 | 6.6126 | 6.5158 | 6.4232 | 6.3305 | 6.2368 | 6.1411 | 5.6895 | 5.3516 | 5.1011
|  | ANNAT | EE |  |  |  |  | 7.0779 | 7.0421 | 7.0021 | 6.9589 | 6.9179 | 6.8495 | 6.7758 | 6.7021 | 6.6084 | 6.5168 | 6.0779 | 5.6853 | 5.46 | 6.7421 | 6.6768 | 6.6105 | 6.5432 | 6.4768 | 6.3926 | 6.3053 | 6.2147 | 6.1305 | 6.0495 | 5.6632 | 5.3253 | 5.1137 | 6.8726 | 6.8347 | 6.7916 | 6.7337 | 6.6737 | 6.5863 | 6.4947 | 6.3989 | 6.3126 | 6.2263 | 5.7968 | 5.38 | 5.14
|  | ANNAT | HT |  |  |  |  | 7.0621 | 7.0189 | 6.9726 | 6.9274 | 6.8811 | 6.8063 | 6.7042 | 6.6011 | 6.4979 | 6.4021 | 5.9747 | 5.6537 | 5.4189 | 6.7074 | 6.6274 | 6.5463 | 6.4674 | 6.3884 | 6.2895 | 6.1916 | 6.0958 | 6.0011 | 5.9126 | 5.5137 | 5.2095 | 4.9737 | 6.8558 | 6.8105 | 6.7453 | 6.6789 | 6.6126 | 6.5158 | 6.4232 | 6.3305 | 6.2368 | 6.1411 | 5.6895 | 5.3516 | 5.1011
|  | ANNAT | HE |  |  |  |  | 7.1021 | 7.0779 | 7.0526 | 7.0253 | 6.9947 | 6.9358 | 6.8821 | 6.8305 | 6.78 | 6.7305 | 6.5347 | 6.3379 | 6.0547 | 6.7916 | 6.7516 | 6.7116 | 6.6695 | 6.6263 | 6.56 | 6.5011 | 6.4389 | 6.3768 | 6.3253 | 6.1116 | 5.9389 | 5.6789 | 6.8558 | 6.8105 | 6.7453 | 6.6789 | 6.6126 | 6.5158 | 6.4232 | 6.3305 | 6.2368 | 6.1411 | 5.6895 | 5.3516 | 5.1011
|  | ANNAT | CF |  |  |  |  | 7.1137 | 7.1011 | 7.0874 | 7.0716 | 7.0579 | 7.0326 | 7.0095 | 6.9853 | 6.96 | 6.94 | 6.8326 | 6.7379 | 6.6305 | 6.8158 | 6.7926 | 6.7674 | 6.7411 | 6.7158 | 6.68 | 6.6484 | 6.6158 | 6.58 | 6.5505 | 6.4053 | 6.2821 | 6.1747 | 6.9116 | 6.8968 | 6.8821 | 6.8674 | 6.8526 | 6.8274 | 6.8032 | 6.78 | 6.7495 | 6.7221 | 6.5779 | 6.4474 | 6.3432
| KILLIN | ARDCHYLE | MINIMUM HEADROOM | NN 52734 29223 | YES | YES | 0 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.094737 | 0.088421 | 0.081053 | 0.075789 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.093684 | 0.088421 | 0.08 | 0.073684 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.093684 | 0.087368 | 0.078947 | 0.072632
|  | ARDCHYLE | EE |  |  |  |  | 0.098947 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.094737 | 0.089474 | 0.083158 | 0.076842 | 0.098947 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.095789 | 0.089474 | 0.083158 | 0.075789 | 0.098947 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.094737 | 0.088421 | 0.082105 | 0.074737
|  | ARDCHYLE | HT |  |  |  |  | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.094737 | 0.088421 | 0.081053 | 0.075789 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.093684 | 0.088421 | 0.08 | 0.073684 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.093684 | 0.087368 | 0.078947 | 0.072632
|  | ARDCHYLE | HE |  |  |  |  | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.095789 | 0.095789 | 0.095789 | 0.095789 | 0.090526 | 0.086316 | 0.08 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.095789 | 0.095789 | 0.095789 | 0.094737 | 0.090526 | 0.084211 | 0.078947 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.093684 | 0.087368 | 0.078947 | 0.072632
|  | ARDCHYLE | CF |  |  |  |  | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.093684 | 0.090526 | 0.086316 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.093684 | 0.090526 | 0.086316 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.093684 | 0.089474 | 0.085263
| NAIRN | ARDERSIER | MINIMUM HEADROOM | NH 80475 55905 | NO | YES | 0.05 | 5.6121 | 5.5584 | 5.4889 | 5.4184 | 5.35 | 4.5911 | 3.8332 | 3.0763 | 2.2889 | 1.5047 | 0.19421 | -1.0805 | -1.9795 | 5.2889 | 5.2353 | 5.1637 | 5.09 | 5.0184 | 4.1858 | 3.3542 | 2.5237 | 1.6721 | 0.82368 | -0.21 | -1.2574 | -2.1637 | 5.3163 | 5.2826 | 5.2405 | 5.1763 | 5.1047 | 4.2837 | 3.4311 | 2.5658 | 1.6711 | 0.77947 | -0.55421 | -1.8458 | -2.8342
|  | ARDERSIER | EE |  |  |  |  | 5.6258 | 5.5984 | 5.5374 | 5.4742 | 5.4111 | 5.1911 | 4.9342 | 4.1174 | 3.3321 | 2.5447 | 0.19421 | -1.0805 | -1.9795 | 5.3026 | 5.2753 | 5.2174 | 5.1542 | 5.0911 | 4.9016 | 4.6858 | 3.8142 | 2.9689 | 2.1195 | -0.21 | -1.2574 | -2.1637 | 5.33 | 5.3026 | 5.2616 | 5.2205 | 5.1679 | 4.9363 | 4.6668 | 3.7826 | 2.9205 | 2.0258 | -0.55421 | -1.8458 | -2.8342
|  | ARDERSIER | HT |  |  |  |  | 5.6121 | 5.5584 | 5.4889 | 5.4184 | 5.35 | 4.5911 | 3.8332 | 3.0763 | 2.2889 | 1.5047 | 0.57526 | -0.054211 | -1.2984 | 5.2889 | 5.2353 | 5.1637 | 5.09 | 5.0184 | 4.1858 | 3.3542 | 2.5237 | 1.6721 | 0.82368 | 0.016316 | -0.53421 | -1.9195 | 5.3163 | 5.2826 | 5.2405 | 5.1763 | 5.1047 | 4.2837 | 3.4311 | 2.5658 | 1.6711 | 0.77947 | -0.19211 | -0.84474 | -2.2679
|  | ARDERSIER | HE |  |  |  |  | 5.6447 | 5.6268 | 5.6047 | 5.5805 | 5.5521 | 5.33 | 5.0953 | 4.7847 | 4.4279 | 4.0795 | 2.4089 | 0.82053 | -0.97421 | 5.3216 | 5.3037 | 5.2826 | 5.2605 | 5.2342 | 5.0489 | 4.8353 | 4.5321 | 4.1763 | 3.8289 | 2.1626 | 0.57316 | -1.2321 | 5.3163 | 5.2826 | 5.2405 | 5.1763 | 5.1047 | 4.2837 | 3.4311 | 2.5658 | 1.6711 | 0.77947 | -0.19211 | -0.84474 | -2.2679
|  | ARDERSIER | CF |  |  |  |  | 5.6553 | 5.6447 | 5.6321 | 5.6184 | 5.6058 | 5.5311 | 5.4542 | 5.3563 | 5.2026 | 5.0353 | 4.1584 | 3.1405 | 1.9079 | 5.3321 | 5.3216 | 5.31 | 5.2974 | 5.2847 | 5.2321 | 5.1626 | 5.0721 | 4.9153 | 4.7342 | 3.8247 | 2.7889 | 1.4521 | 5.3595 | 5.3489 | 5.3363 | 5.3237 | 5.31 | 5.2416 | 5.1784 | 5.1079 | 4.9437 | 4.7616 | 3.8174 | 2.7037 | 1.2963
| FORT AUGUSTUS | ARDOCHY | MINIMUM HEADROOM | NH 47714 12561 | YES | YES | 0 | 0.098947 | 0.097895 | 0.095789 | 0.094737 | 0.092632 | 0.066316 | 0.037895 | 0.010526 | -0.017895 | -0.058947 | -0.29474 | -0.57684 | -0.79368 | 0.098947 | 0.097895 | 0.096842 | 0.094737 | 0.093684 | 0.069474 | 0.044211 | 0.018947 | -0.0063158 | -0.046316 | -0.26526 | -0.54632 | -0.77895 | 0.098947 | 0.097895 | 0.095789 | 0.093684 | 0.092632 | 0.070526 | 0.043158 | 0.015789 | -0.0073684 | -0.051579 | -0.32 | -0.62947 | -0.87579
|  | ARDOCHY | EE |  |  |  |  | 0.1 | 0.097895 | 0.095789 | 0.094737 | 0.092632 | 0.071579 | 0.044211 | 0.016842 | -0.0063158 | -0.042105 | -0.29474 | -0.57684 | -0.79368 | 0.1 | 0.097895 | 0.096842 | 0.094737 | 0.093684 | 0.076842 | 0.053684 | 0.031579 | 0.013684 | -0.02 | -0.26526 | -0.54421 | -0.77895 | 0.1 | 0.097895 | 0.095789 | 0.093684 | 0.092632 | 0.070526 | 0.043158 | 0.015789 | -0.0073684 | -0.045263 | -0.32 | -0.62947 | -0.87579
|  | ARDOCHY | HT |  |  |  |  | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.093684 | 0.076842 | 0.058947 | 0.034737 | 0.0063158 | -0.043158 | -0.26947 | -0.53053 | -0.70737 | 0.098947 | 0.097895 | 0.096842 | 0.096842 | 0.093684 | 0.08 | 0.065263 | 0.044211 | 0.018947 | -0.030526 | -0.26105 | -0.54632 | -0.74421 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.093684 | 0.075789 | 0.057895 | 0.032632 | 0.0031579 | -0.051579 | -0.30211 | -0.6 | -0.80421
|  | ARDOCHY | HE |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.096842 | 0.096842 | 0.066316 | 0.037895 | 0.010526 | -0.017895 | -0.058947 | -0.23368 | -0.45263 | -0.69263 | 0.1 | 0.1 | 0.1 | 0.096842 | 0.096842 | 0.069474 | 0.044211 | 0.018947 | -0.0063158 | -0.046316 | -0.21684 | -0.44 | -0.68526 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.093684 | 0.075789 | 0.057895 | 0.032632 | 0.0031579 | -0.051579 | -0.30211 | -0.6 | -0.80421
|  | ARDOCHY | CF |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.088421 | 0.08 | 0.063158 | 0.045263 | 0.025263 | -0.063158 | -0.20105 | -0.35579 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.090526 | 0.084211 | 0.066316 | 0.048421 | 0.026316 | -0.063158 | -0.20526 | -0.37263 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.088421 | 0.08 | 0.061053 | 0.041053 | 0.018947 | -0.08 | -0.23263 | -0.40842
| FORT WILLIAM | ARISAIG | MINIMUM HEADROOM | NM 66564 86619 | YES | NO | 0 | 2.6011 | 2.5747 | 2.5474 | 2.5211 | 2.4968 | 2.4705 | 2.4453 | 2.4211 | 2.3979 | 2.3768 | 2.2916 | 2.2232 | 2.1674 | 2.5653 | 2.5358 | 2.5074 | 2.4789 | 2.4526 | 2.4242 | 2.3968 | 2.3716 | 2.3474 | 2.3242 | 2.2316 | 2.1568 | 2.0958 | 2.5326 | 2.5053 | 2.4768 | 2.4495 | 2.4242 | 2.3958 | 2.3695 | 2.3453 | 2.3211 | 2.2989 | 2.2095 | 2.1368 | 2.0779
|  | ARISAIG | EE |  |  |  |  | 2.6137 | 2.5926 | 2.5716 | 2.5505 | 2.5305 | 2.5116 | 2.4916 | 2.4726 | 2.4558 | 2.4379 | 2.3684 | 2.3179 | 2.2789 | 2.5779 | 2.5558 | 2.5337 | 2.5105 | 2.4895 | 2.4684 | 2.4474 | 2.4274 | 2.4095 | 2.3905 | 2.3158 | 2.26 | 2.2168 | 2.5463 | 2.5242 | 2.5021 | 2.48 | 2.4589 | 2.4389 | 2.4189 | 2.3989 | 2.3811 | 2.3632 | 2.2905 | 2.2368 | 2.1947
|  | ARISAIG | HT |  |  |  |  | 2.6011 | 2.5747 | 2.5474 | 2.5211 | 2.4968 | 2.4705 | 2.4453 | 2.4211 | 2.3979 | 2.3768 | 2.2916 | 2.2232 | 2.1674 | 2.5653 | 2.5358 | 2.5074 | 2.4789 | 2.4526 | 2.4242 | 2.3968 | 2.3716 | 2.3474 | 2.3242 | 2.2316 | 2.1568 | 2.0958 | 2.5326 | 2.5053 | 2.4768 | 2.4495 | 2.4242 | 2.3958 | 2.3695 | 2.3453 | 2.3211 | 2.2989 | 2.2095 | 2.1368 | 2.0779
|  | ARISAIG | HE |  |  |  |  | 2.6305 | 2.6179 | 2.6042 | 2.5916 | 2.5779 | 2.5642 | 2.5516 | 2.5389 | 2.5263 | 2.5158 | 2.4768 | 2.4505 | 2.4326 | 2.5968 | 2.5832 | 2.5695 | 2.5558 | 2.5411 | 2.5263 | 2.5126 | 2.5 | 2.4863 | 2.4758 | 2.4337 | 2.4042 | 2.3853 | 2.5326 | 2.5053 | 2.4768 | 2.4495 | 2.4242 | 2.3958 | 2.3695 | 2.3453 | 2.3211 | 2.2989 | 2.2095 | 2.1368 | 2.0779
|  | ARISAIG | CF |  |  |  |  | 2.6379 | 2.6316 | 2.6242 | 2.6158 | 2.6074 | 2.6 | 2.5926 | 2.5853 | 2.5768 | 2.5695 | 2.5368 | 2.5137 | 2.4979 | 2.6042 | 2.5979 | 2.5895 | 2.5811 | 2.5726 | 2.5642 | 2.5558 | 2.5484 | 2.5389 | 2.5316 | 2.4958 | 2.4695 | 2.4516 | 2.5716 | 2.5653 | 2.5568 | 2.5484 | 2.54 | 2.5326 | 2.5242 | 2.5168 | 2.5084 | 2.5 | 2.4653 | 2.4411 | 2.4242
| ELGIN | ASHGROVE | MINIMUM HEADROOM | NJ 22458 62130 | YES | YES | 0.035 | 9.7018 | 9.5597 | 37.5061 | 37.3513 | 37.1945 | 36.9387 | 35.905 | 35.0113 | 33.9892 | 32.7513 | 26.9661 | 24.0239 | 22.7534 | 11.1261 | 10.5766 | 36.6892 | 35.9692 | 35.1113 | 34.0829 | 32.8871 | 31.8976 | 30.7629 | 29.3724 | 22.8366 | 19.5513 | 18.1439 | 11.3376 | 10.8597 | 37.9839 | 37.2566 | 36.3892 | 35.3376 | 34.1187 | 33.1071 | 31.945 | 30.5261 | 23.8797 | 20.5292 | 19.0955
|  | ASHGROVE | EE |  |  |  |  | 9.7566 | 9.6418 | 37.6134 | 37.4808 | 37.3418 | 37.0976 | 36.5029 | 35.7576 | 35.0113 | 34.2008 | 28.0818 | 24.6492 | 22.9061 | 11.2029 | 10.7587 | 36.9376 | 36.2692 | 35.4597 | 34.4724 | 33.5829 | 32.7808 | 31.9682 | 31.0818 | 24.2408 | 20.5503 | 18.6261 | 11.3924 | 11.0334 | 38.2334 | 37.5566 | 36.7376 | 35.7187 | 34.7966 | 33.9618 | 33.1197 | 32.2018 | 25.1955 | 21.3334 | 19.3534
|  | ASHGROVE | HT |  |  |  |  | 9.7018 | 9.5597 | 37.5061 | 37.3513 | 37.1945 | 36.9387 | 35.905 | 35.0113 | 33.9892 | 32.7513 | 26.9661 | 24.0239 | 22.7534 | 11.1261 | 10.5766 | 36.6892 | 35.9692 | 35.1113 | 34.0829 | 32.8871 | 31.8976 | 30.7629 | 29.3724 | 22.8366 | 19.5513 | 18.1439 | 11.3376 | 10.8597 | 37.9839 | 37.2566 | 36.3892 | 35.3376 | 34.1187 | 33.1071 | 31.945 | 30.5261 | 23.8797 | 20.5292 | 19.0955
|  | ASHGROVE | HE |  |  |  |  | 9.8355 | 9.7587 | 37.7713 | 37.6797 | 37.5797 | 37.3587 | 37.1208 | 36.3545 | 35.5113 | 34.5797 | 29.2166 | 26.3313 | 24.8892 | 11.3124 | 11.0092 | 37.2776 | 36.6903 | 35.9597 | 35.0334 | 34.2408 | 33.3955 | 32.4566 | 31.4124 | 25.3408 | 22.1608 | 20.6776 | 11.3376 | 10.8597 | 37.9839 | 37.2566 | 36.3892 | 35.3376 | 34.1187 | 33.1071 | 31.945 | 30.5261 | 23.8797 | 20.5292 | 19.0955
|  | ASHGROVE | CF |  |  |  |  | 9.8787 | 9.8334 | 37.885 | 37.8366 | 37.7861 | 37.6913 | 37.6029 | 37.5145 | 37.4313 | 37.3576 | 35.1092 | 32.9355 | 31.6555 | 11.3618 | 11.2713 | 37.8408 | 37.5755 | 37.2566 | 36.8618 | 36.4913 | 36.2092 | 35.8576 | 35.4555 | 31.9387 | 29.4955 | 28.0766 | 11.5145 | 11.4692 | 39.1039 | 38.8555 | 38.5555 | 38.1461 | 37.7629 | 37.4703 | 37.1082 | 36.6966 | 33.1282 | 30.6208 | 29.1555
| MILTON OF CRAIGIE | ASHLUDIE | MINIMUM HEADROOM | NO 49222 33584 | NO | YES | 0.31 | 12.3426 | 11.95 | 11.5237 | 30.21 | 29.8563 | 29.2879 | 28.6879 | 28.0868 | 27.4237 | 26.7037 | 24.6447 | 22.1353 | 19.4553 | 11.0395 | 10.5711 | 10.0626 | 27.1795 | 26.8047 | 26.2668 | 25.6911 | 25.1142 | 24.4847 | 23.7868 | 21.8142 | 19.5795 | 17.2511 | 11.2247 | 10.7668 | 10.2616 | 28.1326 | 27.7526 | 27.1632 | 26.5337 | 25.9042 | 25.2084 | 24.4442 | 22.2916 | 19.7284 | 16.9968
|  | ASHLUDIE | EE |  |  |  |  | 12.4932 | 12.1795 | 11.8142 | 30.5647 | 30.2847 | 29.7437 | 29.15 | 28.5247 | 27.9595 | 27.3784 | 24.8437 | 22.1353 | 19.6984 | 11.2153 | 10.8405 | 10.4079 | 27.5974 | 27.2858 | 26.7921 | 26.2637 | 25.6984 | 25.1795 | 24.6426 | 22.2816 | 19.8511 | 17.2511 | 11.3805 | 11.0321 | 10.5995 | 28.54 | 28.2263 | 27.6642 | 27.0526 | 26.4053 | 25.8179 | 25.2126 | 22.5568 | 19.7284 | 16.9968
|  | ASHLUDIE | HT |  |  |  |  | 12.3426 | 11.95 | 11.5237 | 30.21 | 29.8563 | 29.2879 | 28.6879 | 28.0868 | 27.4237 | 26.7037 | 24.6668 | 22.47 | 20.3605 | 11.0395 | 10.5711 | 10.0626 | 27.1795 | 26.8047 | 26.2668 | 25.6911 | 25.1142 | 24.4847 | 23.7868 | 21.8142 | 19.5795 | 17.2584 | 11.2247 | 10.7668 | 10.2616 | 28.1326 | 27.7526 | 27.1632 | 26.5337 | 25.9042 | 25.2084 | 24.4442 | 22.2916 | 19.9 | 17.5179
|  | ASHLUDIE | HE |  |  |  |  | 12.6942 | 12.4732 | 12.2205 | 31.0753 | 30.8942 | 30.4237 | 30.0174 | 29.5711 | 29.1089 | 28.6426 | 24.6447 | 22.1868 | 19.4553 | 11.4479 | 11.1837 | 10.8795 | 28.1858 | 27.9837 | 27.5605 | 27.1847 | 26.7679 | 26.3437 | 25.9121 | 22.55 | 20.1268 | 17.4037 | 11.2247 | 10.7668 | 10.2616 | 28.1326 | 27.7526 | 27.1632 | 26.5337 | 25.9042 | 25.2084 | 24.4442 | 22.2916 | 19.9 | 17.5179
|  | ASHLUDIE | CF |  |  |  |  | 12.7816 | 12.6816 | 12.5416 | 31.5079 | 31.4058 | 31.1984 | 31.0026 | 30.8121 | 30.6226 | 30.4563 | 29.3995 | 27.9026 | 26.2111 | 11.5805 | 11.4289 | 11.2626 | 28.7047 | 28.5889 | 28.3879 | 28.1974 | 28.01 | 27.8195 | 27.6479 | 26.5963 | 25.1205 | 23.3247 | 11.7026 | 11.5732 | 11.4268 | 29.64 | 29.5274 | 29.3011 | 29.0874 | 28.8779 | 28.6695 | 28.4842 | 27.3274 | 25.7021 | 23.8063
| GRUDIE BRIDGE | AULTBEA | MINIMUM HEADROOM | NG 87458 88885 | YES | NO | 0 | 1.3116 | 1.2758 | 1.2242 | 1.1705 | 1.1189 | 1.0621 | 1.0063 | 0.95684 | 0.90947 | 0.86526 | 0.67579 | 0.5 | 0.34211 | 1.0853 | 1.0505 | 0.99053 | 0.92526 | 0.86316 | 0.79474 | 0.72632 | 0.66632 | 0.61053 | 0.55789 | 0.31368 | 0.11053 | -0.067368 | 1.1379 | 1.0726 | 1.0095 | 0.94526 | 0.88316 | 0.81474 | 0.74842 | 0.68947 | 0.63263 | 0.58105 | 0.34 | 0.14211 | -0.031579
|  | AULTBEA | EE |  |  |  |  | 1.3253 | 1.2979 | 1.2684 | 1.2263 | 1.1821 | 1.1389 | 1.0989 | 1.0589 | 1.0211 | 0.98632 | 0.82526 | 0.70632 | 0.59053 | 1.1 | 1.0716 | 1.0432 | 0.99895 | 0.94632 | 0.89579 | 0.84842 | 0.80211 | 0.75789 | 0.71684 | 0.51684 | 0.35684 | 0.22 | 1.1611 | 1.1168 | 1.0663 | 1.0147 | 0.96211 | 0.91158 | 0.86421 | 0.81789 | 0.77263 | 0.73158 | 0.53158 | 0.37263 | 0.23579
|  | AULTBEA | HT |  |  |  |  | 1.3116 | 1.2758 | 1.2242 | 1.1705 | 1.1189 | 1.0621 | 1.0063 | 0.95684 | 0.90947 | 0.86526 | 0.67579 | 0.5 | 0.34211 | 1.0853 | 1.0505 | 0.99053 | 0.92526 | 0.86316 | 0.79474 | 0.72632 | 0.66632 | 0.61053 | 0.55789 | 0.31368 | 0.11053 | -0.067368 | 1.1379 | 1.0726 | 1.0095 | 0.94526 | 0.88316 | 0.81474 | 0.74842 | 0.68947 | 0.63263 | 0.58105 | 0.34 | 0.14211 | -0.031579
|  | AULTBEA | HE |  |  |  |  | 1.3442 | 1.3274 | 1.3074 | 1.2874 | 1.2663 | 1.2421 | 1.2189 | 1.1926 | 1.1674 | 1.1442 | 1.06 | 1.0074 | 0.97158 | 1.12 | 1.1021 | 1.0832 | 1.0621 | 1.04 | 1.0158 | 0.99474 | 0.96737 | 0.93895 | 0.91263 | 0.81368 | 0.74526 | 0.69579 | 1.1379 | 1.0726 | 1.0095 | 0.94526 | 0.88316 | 0.81474 | 0.74842 | 0.68947 | 0.63263 | 0.58105 | 0.34 | 0.14211 | -0.031579
|  | AULTBEA | CF |  |  |  |  | 1.3547 | 1.3453 | 1.3358 | 1.3263 | 1.3158 | 1.3063 | 1.2958 | 1.2853 | 1.2747 | 1.2632 | 1.1968 | 1.1526 | 1.1232 | 1.1305 | 1.1211 | 1.1116 | 1.1011 | 1.0905 | 1.08 | 1.0695 | 1.0589 | 1.0474 | 1.0368 | 0.96105 | 0.90211 | 0.86 | 1.1905 | 1.1811 | 1.1716 | 1.1611 | 1.1505 | 1.1368 | 1.1179 | 1.0989 | 1.08 | 1.0621 | 0.98 | 0.92105 | 0.88
| BOAT OF GARTEN | AVIEMORE | MINIMUM HEADROOM | NH 89856 11394 | NO | YES | 0 | 18.3074 | 18.2021 | 18.0947 | 17.9842 | 17.6779 | 17.18 | 16.6884 | 16.2442 | 15.9 | 15.7326 | 15 | 14.4147 | 13.9158 | 17.22 | 17.0116 | 16.6853 | 16.3295 | 15.9168 | 15.3526 | 14.7958 | 14.2937 | 13.9084 | 13.7305 | 12.9295 | 12.2842 | 11.7274 | 17.3232 | 17.2179 | 16.9947 | 16.6568 | 16.2663 | 15.7347 | 15.2021 | 14.6989 | 14.3137 | 14.1358 | 13.3347 | 12.6884 | 12.1305
|  | AVIEMORE | EE |  |  |  |  | 18.3463 | 18.2621 | 18.1747 | 18.0832 | 17.9147 | 17.5516 | 17.1979 | 16.7895 | 16.3884 | 16.1684 | 15.5705 | 15.1189 | 14.7474 | 17.2611 | 17.1484 | 16.8663 | 16.5516 | 16.1747 | 15.7653 | 15.3663 | 14.9021 | 14.4463 | 14.2021 | 13.5568 | 13.0568 | 12.64 | 17.3621 | 17.2779 | 17.1684 | 16.8705 | 16.5137 | 16.1263 | 15.7505 | 15.3084 | 14.8526 | 14.6074 | 13.9611 | 13.4611 | 13.0442
|  | AVIEMORE | HT |  |  |  |  | 18.3074 | 18.2021 | 18.0947 | 17.9842 | 17.6779 | 17.18 | 16.6884 | 16.2442 | 15.9 | 15.7326 | 15 | 14.4147 | 13.9158 | 17.22 | 17.0116 | 16.6853 | 16.3295 | 15.9168 | 15.3526 | 14.7958 | 14.2937 | 13.9084 | 13.7305 | 12.9295 | 12.2842 | 11.7274 | 17.3232 | 17.2179 | 16.9947 | 16.6568 | 16.2663 | 15.7347 | 15.2021 | 14.6989 | 14.3137 | 14.1358 | 13.3347 | 12.6884 | 12.1305
|  | AVIEMORE | HE |  |  |  |  | 18.4042 | 18.3484 | 18.2874 | 18.2211 | 18.1495 | 17.9253 | 17.62 | 17.2905 | 16.9653 | 16.82 | 16.4168 | 16.2126 | 16.0547 | 17.3221 | 17.26 | 17.1168 | 16.8579 | 16.5337 | 16.1716 | 15.8253 | 15.4505 | 15.08 | 14.9189 | 14.4789 | 14.2579 | 14.0811 | 17.3232 | 17.2179 | 16.9947 | 16.6568 | 16.2663 | 15.7347 | 15.2021 | 14.6989 | 14.3137 | 14.1358 | 13.3347 | 12.6884 | 12.1305
|  | AVIEMORE | CF |  |  |  |  | 18.4368 | 18.4042 | 18.3705 | 18.3358 | 18.3 | 18.2642 | 18.2284 | 18.1916 | 18.0947 | 17.9968 | 17.6263 | 17.4442 | 17.3105 | 17.3589 | 17.3232 | 17.2853 | 17.2463 | 17.1337 | 16.9621 | 16.7779 | 16.5842 | 16.3568 | 16.2484 | 15.84 | 15.64 | 15.4895 | 17.4526 | 17.42 | 17.3863 | 17.3516 | 17.3158 | 17.2642 | 17.0905 | 16.9084 | 16.6947 | 16.5916 | 16.2021 | 16.0105 | 15.8684
| ALNESS | BALALDIE | MINIMUM HEADROOM | NH 87017 79720 | YES | YES | 0 | 1.4811 | 1.3779 | 1.2695 | 1.1663 | 1.0758 | 0.86526 | 0.65263 | 0.41158 | 0.21895 | 0.024211 | -0.46947 | -0.79263 | -1.0768 | 1.1189 | 0.99895 | 0.87474 | 0.75579 | 0.65368 | 0.39053 | 0.12632 | -0.14737 | -0.36421 | -0.58316 | -1.0958 | -1.4537 | -1.7716 | 1.0137 | 0.9 | 0.78316 | 0.67053 | 0.57263 | 0.31895 | 0.053684 | -0.22 | -0.43579 | -0.65579 | -1.1884 | -1.5474 | -1.8653
|  | BALALDIE | EE |  |  |  |  | 1.5211 | 1.4368 | 1.3495 | 1.2632 | 1.1874 | 1.1084 | 1.0379 | 0.85263 | 0.66947 | 0.45368 | -0.16947 | -0.40737 | -0.60105 | 1.1653 | 1.0684 | 0.96632 | 0.86842 | 0.78421 | 0.69579 | 0.61789 | 0.38316 | 0.14632 | -0.098947 | -0.76526 | -1.0295 | -1.2463 | 1.0568 | 0.96632 | 0.86947 | 0.77684 | 0.69579 | 0.61158 | 0.53579 | 0.31053 | 0.073684 | -0.17158 | -0.85895 | -1.1221 | -1.34
|  | BALALDIE | HT |  |  |  |  | 1.4811 | 1.3779 | 1.2695 | 1.1663 | 1.0758 | 0.86526 | 0.65263 | 0.41158 | 0.21895 | 0.024211 | -0.46947 | -0.79263 | -1.0768 | 1.1189 | 0.99895 | 0.87474 | 0.75579 | 0.65368 | 0.39053 | 0.12632 | -0.14737 | -0.36421 | -0.58316 | -1.0958 | -1.4537 | -1.7716 | 1.0137 | 0.9 | 0.78316 | 0.67053 | 0.57263 | 0.31895 | 0.053684 | -0.22 | -0.43579 | -0.65579 | -1.1884 | -1.5474 | -1.8653
|  | BALALDIE | HE |  |  |  |  | 1.5779 | 1.5221 | 1.46 | 1.3979 | 1.3474 | 1.2895 | 1.2421 | 1.0895 | 0.94105 | 0.79474 | 0.33474 | 0.22842 | 0.14105 | 1.2305 | 1.1663 | 1.0947 | 1.0242 | 0.96842 | 0.90526 | 0.85263 | 0.66211 | 0.47158 | 0.28 | -0.22842 | -0.34421 | -0.44211 | 1.0137 | 0.9 | 0.78316 | 0.67053 | 0.57263 | 0.31895 | 0.053684 | -0.22 | -0.43579 | -0.65579 | -1.1884 | -1.5474 | -1.8653
|  | BALALDIE | CF |  |  |  |  | 1.6126 | 1.58 | 1.5411 | 1.5042 | 1.4737 | 1.4432 | 1.4137 | 1.3832 | 1.2979 | 1.2074 | 0.87474 | 0.78421 | 0.71474 | 1.2716 | 1.2337 | 1.1884 | 1.1453 | 1.1105 | 1.0758 | 1.0421 | 1.0084 | 0.90105 | 0.78737 | 0.36105 | 0.25684 | 0.17895 | 1.1579 | 1.1221 | 1.0789 | 1.0389 | 1.0053 | 0.97263 | 0.94105 | 0.90842 | 0.80947 | 0.70632 | 0.28947 | 0.18526 | 0.10632
| ABERNETHY | BALBEGGIE | MINIMUM HEADROOM | NO 17499 29606 | YES | YES | 0.19 | 7.2142 | 7.1405 | 6.9711 | 6.7889 | 6.5784 | 5.9468 | 5.1879 | 4.3932 | 3.6784 | 2.9353 | -2.7595 | -9.5668 | -14.4763 | 6.1911 | 6.0311 | 5.8247 | 5.6258 | 5.3932 | 4.8426 | 4.2426 | 3.5868 | 3.0037 | 2.3784 | -3.0163 | -9.6205 | -14.9163 | 6.4416 | 6.2847 | 6.0763 | 5.8732 | 5.6384 | 4.97 | 4.17 | 3.3521 | 2.6311 | 1.8774 | -4.2732 | -11.65 | -17.1416
|  | BALBEGGIE | EE |  |  |  |  | 7.2458 | 7.1889 | 7.0974 | 6.9479 | 6.7689 | 6.03 | 5.1879 | 4.3932 | 3.6784 | 2.9353 | -2.7595 | -9.5668 | -14.4763 | 6.2584 | 6.1405 | 5.9826 | 5.8174 | 5.6247 | 4.9826 | 4.2426 | 3.5868 | 3.0037 | 2.3784 | -3.0163 | -9.6205 | -14.9163 | 6.5068 | 6.3921 | 6.2268 | 6.0542 | 5.8542 | 5.0668 | 4.17 | 3.3521 | 2.6311 | 1.8774 | -4.2732 | -11.65 | -17.1416
|  | BALBEGGIE | HT |  |  |  |  | 7.2142 | 7.1405 | 6.9711 | 6.7889 | 6.5784 | 5.9468 | 5.3511 | 4.7489 | 4.0184 | 3.2237 | -2.1489 | -8.1405 | -12.1521 | 6.1911 | 6.0311 | 5.8247 | 5.6258 | 5.3932 | 4.8426 | 4.3226 | 3.7889 | 3.1553 | 2.4637 | -2.9732 | -9.4047 | -13.8847 | 6.4416 | 6.2847 | 6.0763 | 5.8732 | 5.6384 | 4.97 | 4.3405 | 3.7016 | 2.9374 | 2.1132 | -3.7868 | -10.5047 | -15.1079
|  | BALBEGGIE | HE |  |  |  |  | 7.2868 | 7.2489 | 7.2026 | 7.15 | 7.0268 | 6.2826 | 5.6447 | 5.0542 | 4.35 | 3.3668 | -0.90053 | -6.0647 | -11.6763 | 6.3374 | 6.2584 | 6.1521 | 6.0353 | 5.8795 | 5.2426 | 4.6784 | 4.17 | 3.5447 | 2.5658 | -1.5289 | -6.7163 | -12.3616 | 6.4416 | 6.2847 | 6.0763 | 5.8732 | 5.6384 | 4.97 | 4.3405 | 3.7016 | 2.9374 | 2.1132 | -3.7868 | -10.5047 | -15.1079
|  | BALBEGGIE | CF |  |  |  |  | 7.3068 | 7.2889 | 7.2626 | 7.2353 | 7.2068 | 6.9868 | 6.7542 | 6.4911 | 6.0984 | 5.6532 | 3.5111 | 0.26158 | -3.2447 | 6.3574 | 6.3395 | 6.2984 | 6.2468 | 6.1868 | 5.9532 | 5.7237 | 5.4858 | 5.0732 | 4.5753 | 2.3995 | -0.88474 | -4.6153 | 6.6026 | 6.5847 | 6.5437 | 6.4921 | 6.4321 | 6.1405 | 5.8616 | 5.5784 | 5.1311 | 4.6121 | 2.2384 | -1.3195 | -5.2468
| MILTON OF CRAIGIE | BALDOVIE | MINIMUM HEADROOM | NO 45279 32147 | NO | YES | 0.11 | 22.5216 | 22.25 | 21.9742 | 21.5447 | 20.9226 | 20.0953 | 18.7489 | 18.31 | 17.9026 | 17.4837 | 16.8742 | 16.5626 | 16.2953 | 22.0553 | 21.7521 | 21.4458 | 20.9458 | 20.2047 | 19.2332 | 18.3647 | 17.8658 | 17.3868 | 16.9247 | 16.2679 | 15.6511 | 15.1542 | 22.1258 | 21.8226 | 21.5163 | 21.0153 | 20.2742 | 19.2974 | 18.7079 | 18.0511 | 17.4416 | 17.1942 | 16.2963 | 15.6658 | 15.1658
|  | BALDOVIE | EE |  |  |  |  | 22.6458 | 22.4342 | 22.2205 | 21.8437 | 21.3384 | 20.6816 | 20.1805 | 19.6921 | 19.2353 | 18.7605 | 17.8595 | 17.3142 | 16.9542 | 22.1953 | 21.9605 | 21.7247 | 21.2826 | 20.6826 | 19.9016 | 19.3195 | 18.7689 | 18.2595 | 17.7311 | 16.81 | 16.2732 | 15.8984 | 22.2595 | 22.0311 | 21.7942 | 21.3521 | 20.7521 | 19.9647 | 19.3826 | 18.8258 | 18.31 | 17.7763 | 16.8237 | 16.2521 | 15.8668
|  | BALDOVIE | HT |  |  |  |  | 22.5216 | 22.25 | 21.9742 | 21.5447 | 20.9226 | 20.0953 | 19.5774 | 18.9953 | 18.4489 | 18.2121 | 17.3595 | 16.7637 | 16.2953 | 22.0553 | 21.7521 | 21.4458 | 20.9458 | 20.2047 | 19.2332 | 18.6437 | 17.9911 | 17.3868 | 17.1458 | 16.2679 | 15.6511 | 15.1542 | 22.1258 | 21.8226 | 21.5163 | 21.0153 | 20.2742 | 19.2974 | 18.7079 | 18.0511 | 17.4416 | 17.1942 | 16.2963 | 15.6658 | 15.1658
|  | BALDOVIE | HE |  |  |  |  | 22.7763 | 22.6511 | 22.4205 | 22.0995 | 21.6416 | 21.0247 | 18.7489 | 18.31 | 17.9026 | 17.4837 | 16.8742 | 16.5626 | 16.3142 | 22.3763 | 22.2026 | 21.9353 | 21.5563 | 21.0058 | 20.2668 | 18.3647 | 17.8658 | 17.4037 | 16.9247 | 16.2942 | 15.9879 | 15.7468 | 22.1258 | 21.8226 | 21.5163 | 21.0153 | 20.2742 | 19.2974 | 18.7079 | 18.0511 | 17.4416 | 17.1942 | 16.2963 | 15.6658 | 15.1658
|  | BALDOVIE | CF |  |  |  |  | 22.8226 | 22.7679 | 22.7068 | 22.6163 | 22.5258 | 22.4258 | 22.2721 | 22.0837 | 21.8879 | 21.6668 | 20.7342 | 20.1279 | 19.9721 | 22.4595 | 22.3637 | 22.2668 | 22.1668 | 22.0668 | 21.9595 | 21.7837 | 21.5647 | 21.3353 | 21.0732 | 19.9774 | 19.2879 | 19.1279 | 22.5142 | 22.4216 | 22.3279 | 22.2311 | 22.1342 | 22.0279 | 21.85 | 21.63 | 21.3984 | 21.1342 | 20.0289 | 19.3279 | 19.1595
| TARLAND | BALLATER | MINIMUM HEADROOM | NO 37542 97131 | NO | YES | 0 | 11.9895 | 11.9063 | 11.8189 | 11.6568 | 11.4189 | 11.2032 | 10.9758 | 10.7495 | 10.4789 | 10.1537 | 5.88 | 5.46 | 5.0737 | 12.2042 | 11.98 | 11.7337 | 11.4695 | 11.1884 | 10.9411 | 10.6821 | 10.4179 | 10.0979 | 9.7116 | 6.1358 | 5.6726 | 5.24 | 11.8937 | 11.6884 | 11.46 | 11.2084 | 10.9389 | 10.6968 | 10.4368 | 10.1716 | 9.8537 | 9.4663 | 5.0705 | 4.6105 | 4.1811
|  | BALLATER | EE |  |  |  |  | 12.0232 | 11.9568 | 11.8863 | 11.8126 | 11.7126 | 11.5211 | 11.2895 | 11.1253 | 10.9526 | 10.7484 | 6.2042 | 5.8853 | 5.6158 | 12.28 | 12.1137 | 11.9474 | 11.7558 | 11.5484 | 11.3168 | 11.0442 | 10.8568 | 10.6589 | 10.42 | 6.4926 | 6.1463 | 5.8453 | 11.9558 | 11.8105 | 11.6568 | 11.4768 | 11.2779 | 11.0568 | 10.7926 | 10.6084 | 10.4074 | 10.1674 | 5.4168 | 5.0663 | 4.7653
|  | BALLATER | HT |  |  |  |  | 11.9895 | 11.9063 | 11.8189 | 11.6568 | 11.4189 | 11.2032 | 10.9758 | 10.7495 | 10.4789 | 10.1537 | 5.88 | 5.46 | 5.0737 | 12.2042 | 11.98 | 11.7337 | 11.4695 | 11.1884 | 10.9411 | 10.6821 | 10.4179 | 10.0979 | 9.7116 | 6.1358 | 5.6726 | 5.24 | 11.8937 | 11.6884 | 11.46 | 11.2084 | 10.9389 | 10.6968 | 10.4368 | 10.1716 | 9.8537 | 9.4663 | 5.0705 | 4.6105 | 4.1811
|  | BALLATER | HE |  |  |  |  | 12.0705 | 12.0274 | 11.9789 | 11.9274 | 11.8737 | 11.74 | 11.5284 | 11.3505 | 11.1442 | 10.8937 | 8.6221 | 8.4642 | 8.3284 | 12.3832 | 12.2653 | 12.1284 | 11.9632 | 11.7695 | 11.5537 | 11.2979 | 11.0853 | 10.8368 | 10.5358 | 8.5474 | 8.3758 | 8.2242 | 11.8937 | 11.6884 | 11.46 | 11.2084 | 10.9389 | 10.6968 | 10.4368 | 10.1716 | 9.8537 | 9.4663 | 5.0705 | 4.6105 | 4.1811
|  | BALLATER | CF |  |  |  |  | 12.0968 | 12.0726 | 12.0474 | 12.0211 | 11.9947 | 11.9674 | 11.94 | 11.9126 | 11.8842 | 11.8568 | 11.1253 | 10.9895 | 10.8947 | 12.4347 | 12.3863 | 12.3295 | 12.2695 | 12.2042 | 12.1379 | 12.0558 | 11.9579 | 11.8674 | 11.7379 | 10.7905 | 10.6389 | 10.5274 | 12.0295 | 12.0053 | 11.98 | 11.9526 | 11.8926 | 11.8326 | 11.7579 | 11.6705 | 11.5863 | 11.4653 | 10.5484 | 10.3937 | 10.2811
| CARRADALE 1 | BALLIEKINE | MINIMUM HEADROOM | NR 87179 38819 | YES | YES | 0 | 0.96526 | 0.94526 | 0.92316 | 0.90105 | 0.87684 | 0.82842 | 0.77579 | 0.72316 | 0.67474 | 0.62737 | 0.38421 | 0.14947 | 0.038947 | 0.96947 | 0.94842 | 0.92526 | 0.90316 | 0.88 | 0.84421 | 0.80632 | 0.76211 | 0.72 | 0.67895 | 0.46947 | 0.27579 | 0.17789 | 0.96211 | 0.94 | 0.91474 | 0.89263 | 0.86737 | 0.81895 | 0.76526 | 0.71158 | 0.66421 | 0.61474 | 0.35895 | 0.11579 | -0.0031579
|  | BALLIEKINE | EE |  |  |  |  | 0.97368 | 0.95053 | 0.92737 | 0.90105 | 0.87684 | 0.82842 | 0.77579 | 0.72316 | 0.67474 | 0.62737 | 0.38421 | 0.14947 | 0.038947 | 0.97895 | 0.95895 | 0.93684 | 0.91263 | 0.89053 | 0.85053 | 0.80737 | 0.76211 | 0.72 | 0.67895 | 0.46947 | 0.27579 | 0.17789 | 0.97158 | 0.94737 | 0.92105 | 0.89368 | 0.86737 | 0.81895 | 0.76526 | 0.71158 | 0.66421 | 0.61474 | 0.35895 | 0.11579 | -0.0031579
|  | BALLIEKINE | HT |  |  |  |  | 0.96526 | 0.94526 | 0.92316 | 0.90211 | 0.88 | 0.84 | 0.79895 | 0.76 | 0.71368 | 0.66842 | 0.49053 | 0.36421 | 0.28632 | 0.96947 | 0.94842 | 0.92526 | 0.90316 | 0.88 | 0.84421 | 0.80632 | 0.77053 | 0.72947 | 0.69158 | 0.53895 | 0.42947 | 0.35895 | 0.96211 | 0.94 | 0.91474 | 0.89263 | 0.86842 | 0.82842 | 0.78526 | 0.74526 | 0.69895 | 0.65474 | 0.46947 | 0.33579 | 0.25263
|  | BALLIEKINE | HE |  |  |  |  | 0.98526 | 0.97474 | 0.96211 | 0.94947 | 0.93895 | 0.89684 | 0.86316 | 0.82737 | 0.79368 | 0.76211 | 0.61158 | 0.47895 | 0.34 | 0.99263 | 0.98211 | 0.97053 | 0.95684 | 0.94632 | 0.91263 | 0.88316 | 0.85474 | 0.82632 | 0.79789 | 0.67053 | 0.56105 | 0.44842 | 0.96211 | 0.94 | 0.91474 | 0.89263 | 0.86842 | 0.82842 | 0.78526 | 0.74526 | 0.69895 | 0.65474 | 0.46947 | 0.33579 | 0.25263
|  | BALLIEKINE | CF |  |  |  |  | 0.99053 | 0.98526 | 0.98 | 0.97263 | 0.96737 | 0.95053 | 0.93474 | 0.92105 | 0.90842 | 0.89684 | 0.82842 | 0.75053 | 0.69263 | 0.99895 | 0.99368 | 0.98737 | 0.98 | 0.97368 | 0.96105 | 0.94526 | 0.93263 | 0.92 | 0.91158 | 0.84947 | 0.78211 | 0.73579 | 0.98947 | 0.98421 | 0.97895 | 0.97053 | 0.96526 | 0.94947 | 0.93158 | 0.91789 | 0.90421 | 0.89263 | 0.82421 | 0.74421 | 0.68421
| BOAT OF GARTEN | BALLINDALLOCH | MINIMUM HEADROOM | NJ 19279 34652 | NO | YES | 0.1 | 14.2692 | 14.1924 | 14.0976 | 14.0071 | 13.9176 | 13.5724 | 13.1292 | 12.6482 | 12.2303 | 11.725 | 7.8124 | 3.3534 | -0.0055263 | 12.0653 | 11.9821 | 11.8874 | 11.7926 | 11.7011 | 11.42 | 11.0705 | 10.6674 | 10.3168 | 9.7368 | 6.1284 | 1.7789 | -1.8063 | 13.5936 | 13.5125 | 13.4136 | 13.3178 | 13.2241 | 12.8599 | 12.4072 | 11.9178 | 11.4904 | 11.0146 | 6.7862 | 1.9262 | -1.8296
|  | BALLINDALLOCH | EE |  |  |  |  | 14.2861 | 14.245 | 14.1587 | 14.0745 | 13.9892 | 13.5987 | 13.1292 | 12.6482 | 12.2303 | 11.805 | 7.8124 | 3.3534 | -0.0055263 | 12.0821 | 12.0389 | 11.9558 | 11.8737 | 11.7895 | 11.4674 | 11.0705 | 10.6674 | 10.3168 | 9.9579 | 6.1284 | 1.7863 | -1.8063 | 13.6104 | 13.5683 | 13.4788 | 13.3904 | 13.2988 | 12.8883 | 12.4072 | 11.9178 | 11.4904 | 11.0557 | 6.7862 | 1.9262 | -1.8296
|  | BALLINDALLOCH | HT |  |  |  |  | 14.2692 | 14.1924 | 14.0976 | 14.0071 | 13.9176 | 13.5724 | 13.2271 | 12.8745 | 12.4597 | 11.7955 | 8.1682 | 4.0997 | 1.3418 | 12.0653 | 11.9821 | 11.8874 | 11.7926 | 11.7011 | 11.42 | 11.1158 | 10.8126 | 10.4611 | 9.8284 | 6.1789 | 1.7789 | -1.3263 | 13.5936 | 13.5125 | 13.4136 | 13.3178 | 13.2241 | 12.8599 | 12.4999 | 12.1388 | 11.7167 | 11.0146 | 7.0525 | 2.4725 | -0.70224
|  | BALLINDALLOCH | HE |  |  |  |  | 14.3071 | 14.2892 | 14.2639 | 14.2292 | 14.1839 | 13.7808 | 13.3145 | 12.8366 | 12.3797 | 11.725 | 8.9387 | 5.5018 | 1.7618 | 12.1032 | 12.0853 | 12.0611 | 12.0263 | 11.9811 | 11.6516 | 11.2253 | 10.7884 | 10.3747 | 9.7368 | 7.0663 | 3.6011 | -0.17579 | 13.5936 | 13.5125 | 13.4136 | 13.3178 | 13.2241 | 12.8599 | 12.4999 | 12.1388 | 11.7167 | 11.0146 | 7.0525 | 2.4725 | -0.70224
|  | BALLINDALLOCH | CF |  |  |  |  | 14.3187 | 14.3082 | 14.2934 | 14.2808 | 14.265 | 14.1155 | 13.9776 | 13.7682 | 13.4882 | 13.1734 | 11.7376 | 9.5703 | 7.185 | 12.1147 | 12.1042 | 12.0905 | 12.0789 | 12.0642 | 11.9495 | 11.8337 | 11.6347 | 11.3526 | 11.0253 | 9.5937 | 7.3968 | 4.8274 | 13.643 | 13.6325 | 13.6178 | 13.6041 | 13.5883 | 13.4304 | 13.2841 | 13.062 | 12.7599 | 12.4199 | 10.8725 | 8.4914 | 5.8146
| CARRADALE 1 | BALLURE | MINIMUM HEADROOM | NR 71425 49944 | YES | YES | 0 | 2.2337 | 2.2168 | 2.1895 | 2.1621 | 1.5989 | 1.5705 | 1.5368 | 1.5053 | 1.3095 | 1.04 | -0.58105 | -2.4411 | -3.3095 | 2.1558 | 2.1253 | 2.0853 | 2.0453 | 1.5095 | 1.4716 | 1.4326 | 1.3968 | 1.2316 | 1.0095 | -0.35684 | -1.96 | -2.7989 | 2.0779 | 2.0453 | 2.0011 | 1.9579 | 1.3179 | 1.2768 | 1.2347 | 1.1958 | 1 | 0.73684 | -0.89053 | -2.8 | -3.7505
|  | BALLURE | EE |  |  |  |  | 2.24 | 2.2263 | 2.1979 | 2.1674 | 1.6021 | 1.5716 | 1.5421 | 1.5095 | 1.3789 | 1.1074 | -0.58105 | -2.4411 | -3.3095 | 2.1705 | 2.1453 | 2.1074 | 2.0684 | 1.5337 | 1.4958 | 1.46 | 1.4242 | 1.3105 | 1.0821 | -0.35684 | -1.96 | -2.7989 | 2.0937 | 2.0674 | 2.0242 | 1.9821 | 1.3421 | 1.3 | 1.26 | 1.2211 | 1.0863 | 0.81579 | -0.89053 | -2.8 | -3.7505
|  | BALLURE | HT |  |  |  |  | 2.2337 | 2.2168 | 2.1895 | 2.1621 | 1.5989 | 1.5705 | 1.5368 | 1.5053 | 1.3095 | 1.04 | -0.23684 | -1.3021 | -1.9021 | 2.1558 | 2.1253 | 2.0853 | 2.0453 | 1.5095 | 1.4716 | 1.4326 | 1.3968 | 1.2316 | 1.0095 | -0.11895 | -1.1463 | -1.7568 | 2.0779 | 2.0453 | 2.0011 | 1.9579 | 1.3179 | 1.2768 | 1.2347 | 1.1958 | 1 | 0.73684 | -0.59053 | -1.7653 | -2.4432
|  | BALLURE | HE |  |  |  |  | 2.2495 | 2.2411 | 2.2295 | 2.2158 | 1.9326 | 1.9189 | 1.7695 | 1.5726 | 1.56 | 1.3063 | 0.092632 | -1.1484 | -2.4842 | 2.1895 | 2.1747 | 2.1579 | 2.1379 | 1.8705 | 1.8516 | 1.7063 | 1.5032 | 1.4705 | 1.2379 | 0.19684 | -0.89789 | -2.0947 | 2.0779 | 2.0453 | 2.0011 | 1.9579 | 1.3179 | 1.2768 | 1.2347 | 1.1958 | 1 | 0.73684 | -0.59053 | -1.7653 | -2.4432
|  | BALLURE | CF |  |  |  |  | 2.2547 | 2.2505 | 2.2432 | 2.2347 | 2.2274 | 2.1389 | 2.0621 | 1.9842 | 1.9179 | 1.8684 | 1.38 | 0.62 | -0.042105 | 2.1989 | 2.1916 | 2.18 | 2.1684 | 2.1568 | 2.0705 | 1.9947 | 1.9179 | 1.8347 | 1.7516 | 1.2779 | 0.60316 | -0.022105 | 2.1242 | 2.1158 | 2.1032 | 2.0905 | 2.0779 | 1.9758 | 1.8853 | 1.7947 | 1.6979 | 1.6011 | 1.0432 | 0.24632 | -0.47579
| DYCE | BALMEDIE | MINIMUM HEADROOM | NJ 95546 18627 | NO | YES | 0 | 5.3947 | 5.2032 | 4.6042 | 3.6705 | 2.4916 | 1.0874 | -0.26526 | -1.0611 | -1.64 | -4.5063 | -6.0979 | -7.1895 | -7.8568 | 4.5211 | 4.3084 | 3.7211 | 2.6684 | 1.2947 | -0.24421 | -1.6726 | -2.44 | -2.9737 | -5.1211 | -6.5042 | -7.4863 | -8.1474 | 5.0632 | 4.9347 | 4.2274 | 3.1232 | 1.7232 | 0.097895 | -1.4495 | -2.3158 | -2.9326 | -5.74 | -7.36 | -8.4905 | -9.2105
|  | BALMEDIE | EE |  |  |  |  | 5.4295 | 5.3663 | 5.0284 | 4.2747 | 3.2032 | 1.5811 | -0.26526 | -1.0611 | -1.64 | -1.8021 | -4.0074 | -6.0937 | -6.9379 | 4.5684 | 4.4853 | 4.1716 | 3.3611 | 2.1295 | 0.35895 | -1.6726 | -2.44 | -2.9737 | -3.1526 | -4.9421 | -6.6568 | -7.4126 | 5.0979 | 5.0347 | 4.7358 | 3.8358 | 2.5642 | 0.68632 | -1.4495 | -2.3158 | -2.9326 | -3.1126 | -5.3568 | -7.4495 | -8.3263
|  | BALMEDIE | HT |  |  |  |  | 5.3947 | 5.2032 | 4.6042 | 3.6705 | 2.4916 | 1.0874 | 0.23053 | -0.61684 | -1.3042 | -4.5063 | -6.0979 | -7.1895 | -7.8568 | 4.5211 | 4.3084 | 3.7211 | 2.6684 | 1.2947 | -0.24421 | -1.1432 | -2.0274 | -2.6926 | -5.1211 | -6.5042 | -7.4863 | -8.1474 | 5.0632 | 4.9347 | 4.2274 | 3.1232 | 1.7232 | 0.097895 | -0.86526 | -1.8168 | -2.5611 | -5.74 | -7.36 | -8.4905 | -9.2105
|  | BALMEDIE | HE |  |  |  |  | 5.4758 | 5.4358 | 5.3884 | 4.9474 | 4.2 | 2.9821 | 1.7505 | 0.96526 | 0.40211 | -1.7063 | -3.5326 | -5.1937 | -6.9084 | 4.6316 | 4.5789 | 4.4526 | 4.0821 | 3.2526 | 1.9768 | 0.64947 | -0.15158 | -0.69368 | -2.2811 | -3.9368 | -5.4421 | -6.9821 | 5.0632 | 4.9347 | 4.2274 | 3.1232 | 1.7232 | 0.097895 | -0.86526 | -1.8168 | -2.5611 | -5.74 | -7.36 | -8.4905 | -9.2105
|  | BALMEDIE | CF |  |  |  |  | 5.5011 | 5.4779 | 5.4516 | 5.4253 | 5.3168 | 4.9516 | 4.4516 | 3.9032 | 3.5768 | 1.5968 | 0.40105 | -0.64421 | -1.4653 | 4.6642 | 4.6337 | 4.5968 | 4.5337 | 4.4147 | 4.1379 | 3.6316 | 3.0495 | 2.7105 | 1.2253 | 0.038947 | -0.92105 | -1.6958 | 5.1695 | 5.1463 | 5.12 | 5.0937 | 5.0516 | 4.6463 | 4.0653 | 3.4295 | 3.06 | 1.0695 | -0.24421 | -1.3474 | -2.2263
| CLAYHILLS | BALNAGASK | MINIMUM HEADROOM | NJ 96055 05234 | YES | YES | 0.947 | 10.3867 | 10.3298 | 10.273 | 10.2151 | 10.1551 | 10.0898 | 10.0235 | 9.9604 | 9.8951 | 9.833 | 9.5856 | 9.3825 | 9.213 | 10.433 | 10.3709 | 10.3077 | 10.2446 | 10.1804 | 10.1098 | 10.0404 | 9.973 | 9.9035 | 9.8372 | 9.5719 | 9.3477 | 9.1562 | 10.293 | 10.2319 | 10.1719 | 10.1098 | 10.0467 | 9.9772 | 9.9077 | 9.8414 | 9.773 | 9.7077 | 9.4446 | 9.2256 | 9.0414
|  | BALNAGASK | EE |  |  |  |  | 10.4067 | 10.3741 | 10.3319 | 10.2877 | 10.2435 | 10.193 | 10.1414 | 10.0898 | 10.0425 | 9.9951 | 9.773 | 9.6046 | 9.4783 | 10.4541 | 10.4193 | 10.373 | 10.3246 | 10.2751 | 10.2225 | 10.1688 | 10.1151 | 10.0656 | 10.0141 | 9.7835 | 9.6035 | 9.4604 | 10.3141 | 10.2793 | 10.2341 | 10.1877 | 10.1404 | 10.0867 | 10.033 | 9.9793 | 9.9298 | 9.8783 | 9.6467 | 9.4646 | 9.3256
|  | BALNAGASK | HT |  |  |  |  | 10.3867 | 10.3298 | 10.273 | 10.2151 | 10.1551 | 10.0898 | 10.0235 | 9.9604 | 9.8951 | 9.833 | 9.5856 | 9.3825 | 9.213 | 10.433 | 10.3709 | 10.3077 | 10.2446 | 10.1804 | 10.1098 | 10.0404 | 9.973 | 9.9035 | 9.8372 | 9.5719 | 9.3477 | 9.1562 | 10.293 | 10.2319 | 10.1719 | 10.1098 | 10.0467 | 9.9772 | 9.9077 | 9.8414 | 9.773 | 9.7077 | 9.4446 | 9.2256 | 9.0414
|  | BALNAGASK | HE |  |  |  |  | 10.4162 | 10.393 | 10.3688 | 10.3383 | 10.3014 | 10.2583 | 10.2183 | 10.1804 | 10.1425 | 10.1077 | 9.9698 | 9.8709 | 9.793 | 10.4635 | 10.4404 | 10.4162 | 10.3846 | 10.3446 | 10.3004 | 10.2604 | 10.2204 | 10.1814 | 10.1456 | 10.0025 | 9.8983 | 9.8151 | 10.293 | 10.2319 | 10.1719 | 10.1098 | 10.0467 | 9.9772 | 9.9077 | 9.8414 | 9.773 | 9.7077 | 9.4446 | 9.2256 | 9.0414
|  | BALNAGASK | CF |  |  |  |  | 10.4204 | 10.4035 | 10.3867 | 10.3688 | 10.3498 | 10.3277 | 10.3014 | 10.2741 | 10.2477 | 10.2225 | 10.1046 | 10.0256 | 9.9698 | 10.4677 | 10.4509 | 10.4341 | 10.4162 | 10.3972 | 10.3741 | 10.3456 | 10.3183 | 10.2909 | 10.2635 | 10.1404 | 10.0541 | 9.993 | 10.3277 | 10.3109 | 10.2941 | 10.2762 | 10.2572 | 10.233 | 10.2056 | 10.1783 | 10.1498 | 10.1235 | 10.0004 | 9.9151 | 9.8551
| KINTORE | BANCHORY | MINIMUM HEADROOM | NO 69262 96297 | NO | YES | 0.08 | 16 | 15.4789 | 14.8042 | 38.5432 | 37.8737 | 36.9221 | 36.0558 | 35.2821 | 34.4558 | 33.6484 | 30.4242 | 24.8695 | 23.2926 | 13.3379 | 12.7337 | 11.9453 | 34.9421 | 34.1705 | 33.2 | 32.3326 | 31.5832 | 30.8053 | 30.0526 | 27.4705 | 22.9958 | 21.4716 | 14.2626 | 13.6837 | 12.9258 | 36.6105 | 35.8747 | 34.8526 | 33.9295 | 33.1084 | 32.2379 | 31.3905 | 28.1558 | 22.5379 | 20.8495
|  | BANCHORY | EE |  |  |  |  | 16.1653 | 15.7642 | 15.2 | 39.0642 | 38.4116 | 37.4232 | 36.3789 | 35.5442 | 34.8042 | 34.0421 | 30.4242 | 24.8695 | 23.2926 | 13.5253 | 13.0589 | 12.4053 | 35.5558 | 34.7926 | 33.8032 | 32.7884 | 32.0368 | 31.3674 | 30.6726 | 27.5032 | 22.9958 | 21.4716 | 14.4437 | 13.9974 | 13.3637 | 37.1926 | 36.4568 | 35.3968 | 34.2989 | 33.4358 | 32.6705 | 31.8789 | 28.1558 | 22.5379 | 20.8495
|  | BANCHORY | HT |  |  |  |  | 16 | 15.4789 | 14.8042 | 38.5432 | 37.8737 | 36.9221 | 36.0558 | 35.2821 | 34.4558 | 33.6484 | 30.8211 | 26.6242 | 25.0653 | 13.3379 | 12.7337 | 11.9453 | 34.9421 | 34.1705 | 33.2 | 32.3326 | 31.5832 | 30.8053 | 30.0526 | 27.4705 | 23.9032 | 22.2074 | 14.2626 | 13.6837 | 12.9258 | 36.6105 | 35.8747 | 34.8526 | 33.9295 | 33.1084 | 32.2379 | 31.3905 | 28.4421 | 24.1453 | 22.3768
|  | BANCHORY | HE |  |  |  |  | 16.3905 | 16.0947 | 15.6558 | 39.6337 | 39.0905 | 38.0589 | 37.18 | 36.5453 | 35.9484 | 35.3779 | 33.0274 | 29.9284 | 27.0116 | 13.7779 | 13.4316 | 12.9084 | 36.1758 | 35.5263 | 34.4863 | 33.5874 | 33.0053 | 32.4695 | 31.9653 | 29.9653 | 27.4674 | 24.6789 | 14.2626 | 13.6837 | 12.9258 | 36.6105 | 35.8747 | 34.8526 | 33.9295 | 33.1084 | 32.2379 | 31.3905 | 28.4421 | 24.1453 | 22.3768
|  | BANCHORY | CF |  |  |  |  | 16.5295 | 16.3642 | 16.1632 | 40.4505 | 40.2305 | 39.8474 | 39.4611 | 39.0989 | 38.8084 | 38.5368 | 37.1916 | 35.8926 | 34.1642 | 13.9389 | 13.7442 | 13.5084 | 37.1526 | 36.8926 | 36.5105 | 36.1126 | 35.7442 | 35.4579 | 35.1747 | 33.8947 | 32.7779 | 30.9579 | 14.8437 | 14.6563 | 14.43 | 38.7358 | 38.4874 | 38.0768 | 37.6579 | 37.2663 | 36.9579 | 36.6642 | 35.2484 | 33.9147 | 32.0032
| TAYNUILT | BARCALDINE | MINIMUM HEADROOM | NM 96356 42181 | YES | YES | 0.18 | -0.67263 | -0.72 | -0.76842 | -0.91158 | -1.0842 | -1.2568 | -1.4042 | -1.5516 | -1.6821 | -1.7958 | -2.6095 | -3.3684 | -3.5547 | -0.21579 | -0.26211 | -0.36211 | -0.52105 | -0.70421 | -0.89263 | -1.0558 | -1.2211 | -1.3653 | -1.4905 | -2.1568 | -2.7642 | -2.9653 | -0.38737 | -0.48737 | -0.6 | -0.76947 | -0.96526 | -1.1611 | -1.3263 | -1.4926 | -1.6389 | -1.7663 | -2.5811 | -3.3368 | -3.5453
|  | BARCALDINE | EE |  |  |  |  | -0.65368 | -0.69579 | -0.74 | -0.83158 | -0.98842 | -1.1516 | -1.3105 | -1.4263 | -1.5337 | -1.6474 | -0.66737 | -1.4011 | -1.5621 | -0.19684 | -0.23474 | -0.29263 | -0.43368 | -0.6 | -0.77158 | -0.94 | -1.0611 | -1.1768 | -1.3011 | 0.37895 | -0.24105 | -0.39053 | -0.34632 | -0.43368 | -0.52947 | -0.68105 | -0.85895 | -1.0453 | -1.2284 | -1.3579 | -1.4768 | -1.6074 | -0.38211 | -1.1126 | -1.2926
|  | BARCALDINE | HT |  |  |  |  | -0.67263 | -0.72 | -0.76842 | -0.91158 | -1.0842 | -1.2568 | -1.4042 | -1.5516 | -1.6821 | -1.7958 | -2.6095 | -3.3684 | -3.5547 | -0.21579 | -0.26211 | -0.36211 | -0.52105 | -0.70421 | -0.89263 | -1.0558 | -1.2211 | -1.3653 | -1.4905 | -2.1568 | -2.7642 | -2.9653 | -0.38737 | -0.48737 | -0.6 | -0.76947 | -0.96526 | -1.1611 | -1.3263 | -1.4926 | -1.6389 | -1.7663 | -2.5811 | -3.3368 | -3.5453
|  | BARCALDINE | HE |  |  |  |  | -0.62842 | -0.65158 | -0.67895 | -0.70842 | -0.82842 | -0.98316 | -1.1368 | -1.2326 | -1.3189 | -1.3832 | -1.7895 | -2.1537 | -2.2253 | -0.17158 | -0.19368 | -0.22 | -0.29053 | -0.43684 | -0.60211 | -0.77158 | -0.87684 | -0.97368 | -1.0442 | -1.3716 | -1.6558 | -1.7284 | -0.38737 | -0.48737 | -0.6 | -0.76947 | -0.96526 | -1.1611 | -1.3263 | -1.4926 | -1.6389 | -1.7663 | -2.5811 | -3.3368 | -3.5453
|  | BARCALDINE | CF |  |  |  |  | -0.61368 | -0.62632 | -0.63895 | -0.65263 | -0.66632 | -0.68105 | -0.70105 | -0.76526 | -0.81474 | -0.87368 | -1.0368 | -1.1063 | -1.1579 | -0.15684 | -0.16947 | -0.18211 | -0.19474 | -0.20842 | -0.25263 | -0.30316 | -0.37158 | -0.42526 | -0.48842 | -0.65895 | -0.73158 | -0.78947 | -0.26316 | -0.29263 | -0.32316 | -0.37579 | -0.44 | -0.48842 | -0.54211 | -0.61474 | -0.67263 | -0.74 | -0.92211 | -0.99895 | -1.0589
| STORNOWAY | BARVAS | MINIMUM HEADROOM | NB 35613 48891 | NO | YES | 0 | 2.6989 | 2.6389 | 6.3779 | 6.3147 | 6.2516 | 6.1821 | 6.1158 | 6.0526 | 5.9916 | 5.9 | 5.5337 | 5.2389 | 4.9884 | 2.4558 | 2.3958 | 6.1347 | 6.06 | 5.9453 | 5.8295 | 5.7168 | 5.6105 | 5.5063 | 5.4074 | 5.0032 | 4.6747 | 4.3926 | 2.5947 | 2.5347 | 6.2737 | 6.1884 | 6.0747 | 5.9589 | 5.8463 | 5.74 | 5.6358 | 5.5368 | 5.1337 | 4.8063 | 4.5242
|  | BARVAS | EE |  |  |  |  | 2.72 | 2.6716 | 6.4211 | 6.3674 | 6.3126 | 6.2568 | 6.2032 | 6.1516 | 6.1032 | 6.0568 | 5.8242 | 5.6032 | 5.4221 | 2.4768 | 2.4284 | 6.1779 | 6.1242 | 6.0695 | 5.9968 | 5.9084 | 5.8232 | 5.7421 | 5.6632 | 5.3274 | 5.0811 | 4.8758 | 2.6158 | 2.5674 | 6.3168 | 6.2632 | 6.2084 | 6.1263 | 6.0379 | 5.9526 | 5.8716 | 5.7937 | 5.4568 | 5.2116 | 5.0074
|  | BARVAS | HT |  |  |  |  | 2.6989 | 2.6389 | 6.3779 | 6.3147 | 6.2516 | 6.1821 | 6.1158 | 6.0526 | 5.9916 | 5.9 | 5.5337 | 5.2389 | 4.9884 | 2.4558 | 2.3958 | 6.1347 | 6.06 | 5.9453 | 5.8295 | 5.7168 | 5.6105 | 5.5063 | 5.4074 | 5.0032 | 4.6747 | 4.3926 | 2.5947 | 2.5347 | 6.2737 | 6.1884 | 6.0747 | 5.9589 | 5.8463 | 5.74 | 5.6358 | 5.5368 | 5.1337 | 4.8063 | 4.5242
|  | BARVAS | HE |  |  |  |  | 2.7547 | 2.7221 | 6.4863 | 6.4484 | 6.4074 | 6.3653 | 6.3253 | 6.2863 | 6.2495 | 6.2168 | 6.1063 | 6.0516 | 6.0242 | 2.5116 | 2.4789 | 6.2432 | 6.2053 | 6.1642 | 6.1221 | 6.0821 | 6.0432 | 6.0063 | 5.9737 | 5.8253 | 5.6989 | 5.6053 | 2.5947 | 2.5347 | 6.2737 | 6.1884 | 6.0747 | 5.9589 | 5.8463 | 5.74 | 5.6358 | 5.5368 | 5.1337 | 4.8063 | 4.5242
|  | BARVAS | CF |  |  |  |  | 2.7726 | 2.7537 | 6.5347 | 6.5147 | 6.4947 | 6.4747 | 6.4537 | 6.4326 | 6.4126 | 6.3916 | 6.3032 | 6.26 | 6.2389 | 2.5295 | 2.5105 | 6.2916 | 6.2716 | 6.2516 | 6.2316 | 6.2105 | 6.1895 | 6.1695 | 6.1484 | 6.06 | 5.9589 | 5.8737 | 2.6684 | 2.6495 | 6.4305 | 6.4105 | 6.3905 | 6.3705 | 6.3495 | 6.3284 | 6.3084 | 6.2874 | 6.1989 | 6.0884 | 6.0042
| STORNOWAY | BATTERY POINT | MINIMUM HEADROOM | NB 43147 32182 | NO | YES | 0 | 16.6074 | 29.7537 | 29.32 | 28.9253 | 28.5684 | 28.14 | 27.6063 | 27.0674 | 26.4526 | 25.7189 | 23.7032 | 22.5263 | 21.6168 | 15.5432 | 27.9295 | 27.4411 | 27.0021 | 26.6095 | 26.1705 | 25.5947 | 25.0116 | 24.3389 | 23.5126 | 21.3305 | 20.08 | 19.0611 | 15.2779 | 28.0089 | 27.5142 | 27.0689 | 26.6732 | 26.2132 | 25.6142 | 25.0058 | 24.3026 | 23.4437 | 21.1479 | 19.8289 | 18.7774
|  | BATTERY POINT | EE |  |  |  |  | 16.7874 | 30.0137 | 29.6495 | 29.28 | 28.9558 | 28.5705 | 28.1884 | 27.7516 | 27.3284 | 26.8674 | 39.2737 | 38.02 | 37.2579 | 15.7516 | 28.2295 | 27.82 | 27.4053 | 27.0495 | 26.6611 | 26.2842 | 25.8379 | 25.3979 | 24.9116 | 41.8295 | 40.6147 | 39.7926 | 15.4884 | 28.3121 | 27.8963 | 27.4753 | 27.1153 | 26.7026 | 26.2953 | 25.8174 | 25.3489 | 24.8311 | 38.7447 | 37.3984 | 36.5363
|  | BATTERY POINT | HT |  |  |  |  | 16.6074 | 29.7537 | 29.32 | 28.9253 | 28.5684 | 28.14 | 27.6063 | 27.0674 | 26.4526 | 25.7189 | 23.7032 | 22.5263 | 21.6168 | 15.5432 | 27.9295 | 27.4411 | 27.0021 | 26.6095 | 26.1705 | 25.5947 | 25.0116 | 24.3389 | 23.5126 | 21.3305 | 20.08 | 19.0611 | 15.2779 | 28.0089 | 27.5142 | 27.0689 | 26.6732 | 26.2132 | 25.6142 | 25.0058 | 24.3026 | 23.4437 | 21.1479 | 19.8289 | 18.7774
|  | BATTERY POINT | HE |  |  |  |  | 16.9726 | 30.3453 | 30.0747 | 29.8179 | 29.6063 | 29.3084 | 29.0442 | 28.6916 | 28.3116 | 27.9063 | 26.2611 | 25.3989 | 24.7842 | 16.0042 | 28.6021 | 28.2926 | 28.0053 | 27.7747 | 27.4895 | 27.2347 | 26.8663 | 26.4632 | 26.0253 | 24.2463 | 23.3947 | 22.8421 | 15.2779 | 28.0089 | 27.5142 | 27.0689 | 26.6732 | 26.2132 | 25.6142 | 25.0058 | 24.3026 | 23.4437 | 21.1479 | 19.8289 | 18.7774
|  | BATTERY POINT | CF |  |  |  |  | 17.0663 | 30.5579 | 30.4632 | 30.3284 | 30.1947 | 30.0337 | 29.8695 | 29.7063 | 29.5411 | 29.3632 | 28.18 | 27.4347 | 27.0537 | 16.1537 | 28.9 | 28.7505 | 28.5874 | 28.4368 | 28.2716 | 28.1 | 27.9284 | 27.7516 | 27.5579 | 26.2232 | 25.4316 | 25.0484 | 15.8947 | 28.9889 | 28.8395 | 28.6732 | 28.5205 | 28.3447 | 28.1637 | 27.9826 | 27.7974 | 27.5974 | 26.2068 | 25.3532 | 24.9279
| DOUNREAY | BETTYHILL | MINIMUM HEADROOM | NC 70763 61645 | YES | YES | 0 | 1.0737 | 1.0484 | 1.0179 | 0.98526 | 0.95263 | 0.79474 | 0.57474 | 0.35158 | 0.15789 | -0.12842 | -4.2779 | -6.4368 | -8.9811 | 1.0642 | 1.0295 | 0.98947 | 0.94842 | 0.90842 | 0.78105 | 0.63053 | 0.45053 | 0.25368 | -0.06 | -3.6074 | -5.7168 | -8.1874 | 1.0916 | 1.0547 | 1.0147 | 0.97158 | 0.93053 | 0.77579 | 0.56947 | 0.34737 | 0.15263 | -0.14316 | -4.4716 | -6.8389 | -9.6147
|  | BETTYHILL | EE |  |  |  |  | 1.0853 | 1.0653 | 1.0337 | 1 | 0.96947 | 0.79579 | 0.57474 | 0.35158 | 0.15789 | -0.057895 | -4.2779 | -6.4368 | -8.9811 | 1.0811 | 1.0526 | 1.0168 | 0.97895 | 0.94316 | 0.79895 | 0.63053 | 0.45474 | 0.29579 | 0.11368 | -3.6074 | -5.7168 | -8.1874 | 1.1074 | 1.0789 | 1.0389 | 0.99789 | 0.95895 | 0.78211 | 0.56947 | 0.34737 | 0.15263 | -0.066316 | -4.4716 | -6.8389 | -9.6147
|  | BETTYHILL | HT |  |  |  |  | 1.0737 | 1.0484 | 1.0179 | 0.98526 | 0.95263 | 0.79474 | 0.63684 | 0.47474 | 0.28421 | -0.092632 | -3.6632 | -5.6589 | -7.9211 | 1.0642 | 1.0295 | 0.98947 | 0.94842 | 0.90842 | 0.78105 | 0.65263 | 0.52526 | 0.37474 | -0.0063158 | -3.2295 | -5.4021 | -7.6337 | 1.0916 | 1.0547 | 1.0147 | 0.97158 | 0.93053 | 0.77579 | 0.62 | 0.46316 | 0.27368 | -0.14316 | -3.9126 | -6.1842 | -8.6568
|  | BETTYHILL | HE |  |  |  |  | 1.1 | 1.0874 | 1.0737 | 1.0579 | 1.0411 | 0.85895 | 0.63579 | 0.40632 | 0.18842 | -0.12842 | -2.4663 | -4.1326 | -6.4084 | 1.1021 | 1.0863 | 1.0695 | 1.0495 | 1.0295 | 0.85895 | 0.65789 | 0.45053 | 0.25368 | -0.06 | -2.1379 | -3.8463 | -6.0705 | 1.0916 | 1.0547 | 1.0147 | 0.97158 | 0.93053 | 0.77579 | 0.62 | 0.46316 | 0.27368 | -0.14316 | -3.9126 | -6.1842 | -8.6568
|  | BETTYHILL | CF |  |  |  |  | 1.1074 | 1.1011 | 1.0926 | 1.0842 | 1.0747 | 1.0116 | 0.95474 | 0.85474 | 0.71684 | 0.56105 | -1.2589 | -2.3095 | -3.4853 | 1.1095 | 1.1042 | 1.0947 | 1.0821 | 1.0716 | 1.0147 | 0.96211 | 0.84737 | 0.70526 | 0.53579 | -1.0274 | -2.1126 | -3.3832 | 1.1379 | 1.1305 | 1.12 | 1.1084 | 1.0958 | 1.0253 | 0.96105 | 0.83579 | 0.68526 | 0.51158 | -1.3768 | -2.5442 | -3.8811
| GRUDIE BRIDGE | BIDEN CLAN RAONAILD | MINIMUM HEADROOM | NH 06927 58342 | YES | NO | 0 | 0.098463 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154
|  | BIDEN CLAN RAONAILD | EE |  |  |  |  | 0.098463 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154
|  | BIDEN CLAN RAONAILD | HT |  |  |  |  | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154
|  | BIDEN CLAN RAONAILD | HE |  |  |  |  | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154
|  | BIDEN CLAN RAONAILD | CF |  |  |  |  | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154 | 0.10154
| ELGIN | BILBOHALL | MINIMUM HEADROOM | NJ 20782 61556 | YES | YES | 0.07 | 12.1689 | 12.1174 | 23.3332 | 23.2679 | 23.17 | 23.0605 | 22.6995 | 22.2774 | 21.7121 | 21.1374 | 18.6511 | 14.7795 | 11.8089 | 11.6647 | 11.4711 | 21.4374 | 21.3258 | 21.2132 | 21.0995 | 20.7584 | 20.3668 | 19.8289 | 19.2837 | 16.7889 | 12.8437 | 9.9932 | 11.9121 | 11.7921 | 22.3595 | 22.2479 | 22.1321 | 22.0174 | 21.6342 | 21.1868 | 20.5816 | 19.9679 | 17.2679 | 13.1311 | 9.7584
|  | BILBOHALL | EE |  |  |  |  | 12.1889 | 12.1479 | 23.3679 | 23.3037 | 23.2384 | 23.1668 | 22.8321 | 22.3584 | 21.9237 | 21.4237 | 18.6921 | 14.7795 | 11.8089 | 11.7111 | 11.5395 | 21.5226 | 21.4237 | 21.3226 | 21.2247 | 20.9447 | 20.5416 | 20.1616 | 19.7079 | 17.0879 | 13.2416 | 9.9932 | 11.9321 | 11.8584 | 22.4384 | 22.3363 | 22.2332 | 22.1321 | 21.7858 | 21.2932 | 20.8374 | 20.3089 | 17.3784 | 13.1311 | 9.7584
|  | BILBOHALL | HT |  |  |  |  | 12.1689 | 12.1174 | 23.3332 | 23.2679 | 23.17 | 23.0605 | 22.6995 | 22.2774 | 21.7121 | 21.1374 | 18.6511 | 15.0374 | 12.5753 | 11.6647 | 11.4711 | 21.4374 | 21.3258 | 21.2132 | 21.0995 | 20.7584 | 20.3668 | 19.8289 | 19.2837 | 16.7889 | 12.8437 | 10.0763 | 11.9121 | 11.7921 | 22.3595 | 22.2479 | 22.1321 | 22.0174 | 21.6342 | 21.1868 | 20.5816 | 19.9679 | 17.2679 | 13.1605 | 10.3289
|  | BILBOHALL | HE |  |  |  |  | 12.2174 | 12.1911 | 23.4384 | 23.4016 | 23.3637 | 23.3237 | 23.0774 | 22.7311 | 22.31 | 21.7837 | 19.5595 | 16.5342 | 13.27 | 11.7742 | 11.6353 | 21.6584 | 21.5995 | 21.5384 | 21.4753 | 21.2374 | 20.8837 | 20.4984 | 19.9879 | 17.7858 | 14.6879 | 11.3468 | 11.9121 | 11.7921 | 22.3595 | 22.2479 | 22.1321 | 22.0174 | 21.6342 | 21.1868 | 20.5816 | 19.9679 | 17.2679 | 13.1605 | 10.3289
|  | BILBOHALL | CF |  |  |  |  | 12.2332 | 12.2184 | 23.4795 | 23.4605 | 23.4405 | 23.4205 | 23.3247 | 23.2195 | 23.1268 | 22.8742 | 21.7353 | 19.8311 | 17.7353 | 11.8321 | 11.7563 | 21.8016 | 21.7668 | 21.7311 | 21.6942 | 21.5932 | 21.4837 | 21.2753 | 20.9679 | 19.7774 | 17.8195 | 15.5574 | 11.9763 | 11.9616 | 22.6226 | 22.6037 | 22.5837 | 22.5647 | 22.4732 | 22.3458 | 22.1247 | 21.8132 | 20.5595 | 18.45 | 16.0742
| RANNOCH | BLACKMOUNT | MINIMUM HEADROOM | NN 30077 41404 | YES | YES | 0 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.034211 | 0.034211 | 0.034211 | 0.033158 | 0.031053 | 0.028947 | 0.026842 | 0.037368 | 0.036316 | 0.036316 | 0.035263 | 0.035263 | 0.034211 | 0.033158 | 0.033158 | 0.033158 | 0.032105 | 0.028947 | 0.026842 | 0.023684 | 0.045789 | 0.043684 | 0.043684 | 0.042632 | 0.042632 | 0.041579 | 0.040526 | 0.040526 | 0.040526 | 0.039474 | 0.036316 | 0.034211 | 0.031053
|  | BLACKMOUNT | EE |  |  |  |  | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.034211 | 0.034211 | 0.033158 | 0.031053 | 0.028947 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.035263 | 0.034211 | 0.033158 | 0.033158 | 0.032105 | 0.028947 | 0.026842 | 0.045789 | 0.044737 | 0.043684 | 0.043684 | 0.043684 | 0.042632 | 0.042632 | 0.041579 | 0.040526 | 0.040526 | 0.039474 | 0.036316 | 0.034211
|  | BLACKMOUNT | HT |  |  |  |  | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.034211 | 0.034211 | 0.034211 | 0.033158 | 0.031053 | 0.028947 | 0.026842 | 0.037368 | 0.036316 | 0.036316 | 0.035263 | 0.035263 | 0.034211 | 0.033158 | 0.033158 | 0.033158 | 0.032105 | 0.028947 | 0.026842 | 0.023684 | 0.045789 | 0.043684 | 0.043684 | 0.042632 | 0.042632 | 0.041579 | 0.040526 | 0.040526 | 0.040526 | 0.039474 | 0.036316 | 0.034211 | 0.031053
|  | BLACKMOUNT | HE |  |  |  |  | 0.037368 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.034211 | 0.034211 | 0.034211 | 0.037368 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.033158 | 0.033158 | 0.033158 | 0.045789 | 0.043684 | 0.043684 | 0.042632 | 0.042632 | 0.041579 | 0.040526 | 0.040526 | 0.040526 | 0.039474 | 0.036316 | 0.034211 | 0.031053
|  | BLACKMOUNT | CF |  |  |  |  | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.037368 | 0.036316 | 0.036316 | 0.036316 | 0.035263 | 0.035263 | 0.034211 | 0.045789 | 0.045789 | 0.045789 | 0.045789 | 0.045789 | 0.045789 | 0.045789 | 0.043684 | 0.043684 | 0.043684 | 0.042632 | 0.042632 | 0.041579
| BEAULY | BLACKSTAND | MINIMUM HEADROOM | NH 71036 59151 | YES | YES | 0 | 6.4137 | 6.2832 | 6.1484 | 6.0063 | 5.86 | 5.6947 | 5.5368 | 5.3842 | 5.2842 | 5.1895 | 4.7695 | 4.4284 | 4.1421 | 6.1842 | 6.0411 | 5.8937 | 5.7368 | 5.5758 | 5.3926 | 5.2189 | 5.0505 | 4.9432 | 4.8421 | 4.3789 | 4.0021 | 3.6811 | 6.34 | 6.1979 | 6.0516 | 5.8958 | 5.7358 | 5.5547 | 5.3821 | 5.2147 | 5.1074 | 5.0074 | 4.5484 | 4.1737 | 3.8537
|  | BLACKSTAND | EE |  |  |  |  | 6.4632 | 6.3568 | 6.2463 | 6.1253 | 6 | 5.8611 | 5.7316 | 5.6 | 5.5232 | 5.4484 | 5.1021 | 4.8526 | 4.66 | 6.2389 | 6.1211 | 5.9989 | 5.8663 | 5.7274 | 5.5737 | 5.4295 | 5.2853 | 5.2021 | 5.1211 | 4.7453 | 4.4684 | 4.2516 | 6.3937 | 6.2779 | 6.1558 | 6.0242 | 5.8863 | 5.7337 | 5.5916 | 5.4474 | 5.3653 | 5.2853 | 4.9116 | 4.6358 | 4.4221
|  | BLACKSTAND | HT |  |  |  |  | 6.4137 | 6.2832 | 6.1484 | 6.0063 | 5.86 | 5.6947 | 5.5368 | 5.3842 | 5.2842 | 5.1895 | 4.7695 | 4.4284 | 4.1421 | 6.1842 | 6.0411 | 5.8937 | 5.7368 | 5.5758 | 5.3926 | 5.2189 | 5.0505 | 4.9432 | 4.8421 | 4.3789 | 4.0021 | 3.6811 | 6.34 | 6.1979 | 6.0516 | 5.8958 | 5.7358 | 5.5547 | 5.3821 | 5.2147 | 5.1074 | 5.0074 | 4.5484 | 4.1737 | 3.8537
|  | BLACKSTAND | HE |  |  |  |  | 6.5305 | 6.4579 | 6.3768 | 6.2863 | 6.1884 | 6.0758 | 5.9726 | 5.8663 | 5.8126 | 5.7621 | 5.5905 | 5.4811 | 5.3937 | 6.3116 | 6.2316 | 6.1421 | 6.0411 | 5.9326 | 5.8074 | 5.6926 | 5.5737 | 5.5168 | 5.4642 | 5.2789 | 5.1611 | 5.0632 | 6.34 | 6.1979 | 6.0516 | 5.8958 | 5.7358 | 5.5547 | 5.3821 | 5.2147 | 5.1074 | 5.0074 | 4.5484 | 4.1737 | 3.8537
|  | BLACKSTAND | CF |  |  |  |  | 6.5747 | 6.5358 | 6.4874 | 6.4368 | 6.3842 | 6.3242 | 6.2653 | 6.2116 | 6.1758 | 6.1411 | 5.9916 | 5.8937 | 5.8253 | 6.3611 | 6.3168 | 6.2642 | 6.2074 | 6.1484 | 6.0821 | 6.0158 | 5.9547 | 5.9168 | 5.8789 | 5.7168 | 5.6095 | 5.5316 | 6.5116 | 6.4705 | 6.4189 | 6.3621 | 6.3042 | 6.2379 | 6.1726 | 6.1126 | 6.0747 | 6.0379 | 5.8768 | 5.7695 | 5.6926
| COUPAR ANGUS | BLAIRGOWRIE | MINIMUM HEADROOM | NO 18741 44551 | NO | YES | 0.628 | 23.3104 | 23.0641 | 22.7852 | 22.4988 | 22.0936 | 21.2167 | 20.4315 | 19.6157 | 18.6831 | 17.7062 | 15.2536 | 8.6999 | 5.7767 | 20.8173 | 20.5425 | 20.2383 | 19.9278 | 19.4552 | 18.4973 | 17.6562 | 16.8109 | 15.8783 | 14.8973 | 12.6657 | 6.6878 | 3.3994 | 21.7207 | 21.4586 | 21.1649 | 20.8638 | 20.4217 | 19.4544 | 18.5554 | 17.6523 | 16.6459 | 15.5912 | 13.0407 | 6.1175 | 2.7944
|  | BLAIRGOWRIE | EE |  |  |  |  | 23.3883 | 23.2315 | 23.0146 | 22.7925 | 22.5567 | 21.7115 | 20.8262 | 19.9946 | 19.1936 | 18.3399 | 15.2841 | 12.3704 | 8.9578 | 20.8962 | 20.7309 | 20.4994 | 20.2625 | 20.0067 | 19.1067 | 18.1888 | 17.3531 | 16.5625 | 15.7278 | 13.0415 | 10.3373 | 6.5909 | 21.7996 | 21.6365 | 21.4091 | 21.1744 | 20.9249 | 20.0017 | 19.0196 | 18.0881 | 17.2154 | 16.2965 | 13.1365 | 10.0502 | 6.1881
|  | BLAIRGOWRIE | HT |  |  |  |  | 23.3104 | 23.0641 | 22.7852 | 22.4988 | 22.0936 | 21.2167 | 20.4315 | 19.6157 | 18.6831 | 17.7062 | 15.2536 | 8.6999 | 5.7767 | 20.8173 | 20.5425 | 20.2383 | 19.9278 | 19.4552 | 18.4973 | 17.6562 | 16.8109 | 15.8783 | 14.8973 | 12.6657 | 6.6878 | 3.3994 | 21.7207 | 21.4586 | 21.1649 | 20.8638 | 20.4217 | 19.4544 | 18.5554 | 17.6523 | 16.6459 | 15.5912 | 13.0407 | 6.1175 | 2.7944
|  | BLAIRGOWRIE | HE |  |  |  |  | 23.4809 | 23.3894 | 23.2873 | 23.162 | 23.0136 | 22.2715 | 21.5494 | 20.8725 | 20.1788 | 19.4588 | 17.5157 | 12.6178 | 8.9062 | 20.9888 | 20.8983 | 20.7952 | 20.6657 | 20.5078 | 19.752 | 18.9794 | 18.2667 | 17.5278 | 16.8078 | 15.1604 | 10.7794 | 6.9646 | 21.7207 | 21.4586 | 21.1649 | 20.8638 | 20.4217 | 19.4544 | 18.5554 | 17.6523 | 16.6459 | 15.5912 | 13.0407 | 6.1175 | 2.7944
|  | BLAIRGOWRIE | CF |  |  |  |  | 23.5304 | 23.4767 | 23.4167 | 23.3536 | 23.2936 | 23.0852 | 22.882 | 22.6736 | 22.3988 | 22.0757 | 20.9631 | 17.0452 | 14.6788 | 21.0383 | 20.9846 | 20.9246 | 20.8646 | 20.8057 | 20.6278 | 20.4436 | 20.2541 | 19.9552 | 19.5678 | 18.4741 | 14.9352 | 12.3657 | 21.9417 | 21.8881 | 21.8281 | 21.7649 | 21.7049 | 21.4923 | 21.2817 | 21.0659 | 20.7638 | 20.3986 | 19.2144 | 15.0259 | 12.3544
| STRATHLEVEN | BLAIRLINNANS | MINIMUM HEADROOM | NS 40709 85121 | YES | YES | 0.931 | -0.56047 | -0.56574 | -0.571 | -0.57732 | -0.58258 | -0.591 | -0.59732 | -0.60468 | -0.60995 | -0.61732 | -0.64363 | -0.72995 | -0.74574 | -0.73732 | -0.74363 | -0.74889 | -0.75521 | -0.76153 | -0.76889 | -0.77626 | -0.78363 | -0.78889 | -0.79626 | -0.82258 | -0.89416 | -0.911 | -0.72574 | -0.731 | -0.73732 | -0.74363 | -0.74889 | -0.75837 | -0.76468 | -0.77205 | -0.77837 | -0.78574 | -0.81416 | -0.90258 | -0.92047
|  | BLAIRLINNANS | EE |  |  |  |  | -0.55837 | -0.56153 | -0.56574 | -0.56995 | -0.57521 | -0.58153 | -0.58784 | -0.59311 | -0.60047 | -0.60468 | -0.631 | -0.70995 | -0.72047 | -0.73521 | -0.73942 | -0.74363 | -0.74784 | -0.75311 | -0.75942 | -0.76679 | -0.771 | -0.77732 | -0.78258 | -0.80784 | -0.871 | -0.88363 | -0.72363 | -0.72784 | -0.731 | -0.73626 | -0.74153 | -0.74784 | -0.75416 | -0.76047 | -0.76784 | -0.77205 | -0.80047 | -0.88047 | -0.89311
|  | BLAIRLINNANS | HT |  |  |  |  | -0.56047 | -0.56574 | -0.571 | -0.57732 | -0.58258 | -0.591 | -0.59732 | -0.60468 | -0.60995 | -0.61732 | -0.64363 | -0.72995 | -0.74574 | -0.73732 | -0.74363 | -0.74889 | -0.75521 | -0.76153 | -0.76889 | -0.77626 | -0.78363 | -0.78889 | -0.79626 | -0.82258 | -0.89416 | -0.911 | -0.72574 | -0.731 | -0.73732 | -0.74363 | -0.74889 | -0.75837 | -0.76468 | -0.77205 | -0.77837 | -0.78574 | -0.81416 | -0.90258 | -0.92047
|  | BLAIRLINNANS | HE |  |  |  |  | -0.55626 | -0.55837 | -0.56047 | -0.56258 | -0.56574 | -0.571 | -0.57521 | -0.57837 | -0.58363 | -0.58679 | -0.60363 | -0.63732 | -0.64363 | -0.73311 | -0.73521 | -0.73732 | -0.74047 | -0.74363 | -0.74784 | -0.75311 | -0.75521 | -0.75942 | -0.76258 | -0.77942 | -0.80889 | -0.81521 | -0.72574 | -0.731 | -0.73732 | -0.74363 | -0.74889 | -0.75837 | -0.76468 | -0.77205 | -0.77837 | -0.78574 | -0.81416 | -0.90258 | -0.92047
|  | BLAIRLINNANS | CF |  |  |  |  | -0.55521 | -0.55626 | -0.55732 | -0.55837 | -0.55942 | -0.56153 | -0.56258 | -0.56574 | -0.56784 | -0.56995 | -0.58047 | -0.58784 | -0.59521 | -0.73205 | -0.73311 | -0.73416 | -0.73521 | -0.73626 | -0.73837 | -0.74047 | -0.74258 | -0.74574 | -0.74784 | -0.75732 | -0.76574 | -0.77205 | -0.72047 | -0.72153 | -0.72258 | -0.72363 | -0.72468 | -0.72679 | -0.72889 | -0.731 | -0.73416 | -0.73626 | -0.74679 | -0.75521 | -0.76258
| BOAT OF GARTEN | BOAT OF GARTEN | MINIMUM HEADROOM | NH 95609 19427 | NO | YES | 0 | 8.6253 | 8.5505 | 8.4747 | 8.3842 | 8.2958 | 8.1274 | 7.9611 | 7.7895 | 7.6968 | 7.6116 | 7.2453 | 6.9611 | 6.7347 | 8.2621 | 8.1611 | 8.06 | 7.96 | 7.8621 | 7.6684 | 7.4758 | 7.2758 | 7.1779 | 7.0874 | 6.6821 | 6.3621 | 6.1 | 8.3147 | 8.22 | 8.1253 | 8.0263 | 7.9284 | 7.7305 | 7.5358 | 7.3337 | 7.2326 | 7.14 | 6.7263 | 6.3989 | 6.1337
|  | BOAT OF GARTEN | EE |  |  |  |  | 8.6589 | 8.6011 | 8.54 | 8.4789 | 8.4105 | 8.3326 | 8.2568 | 8.1084 | 7.9653 | 7.8179 | 7.4968 | 7.2474 | 7.0705 | 8.3084 | 8.2316 | 8.1516 | 8.0726 | 7.9937 | 7.9116 | 7.8295 | 7.66 | 7.4937 | 7.32 | 6.9789 | 6.7095 | 6.5084 | 8.3579 | 8.2853 | 8.2105 | 8.1358 | 8.0589 | 7.9758 | 7.8916 | 7.7179 | 7.5495 | 7.3716 | 7.0189 | 6.7379 | 6.5305
|  | BOAT OF GARTEN | HT |  |  |  |  | 8.6253 | 8.5505 | 8.4747 | 8.3842 | 8.2958 | 8.1274 | 7.9611 | 7.7895 | 7.6968 | 7.6116 | 7.2453 | 6.9611 | 6.7347 | 8.2621 | 8.1611 | 8.06 | 7.96 | 7.8621 | 7.6684 | 7.4758 | 7.2758 | 7.1779 | 7.0874 | 6.6821 | 6.3621 | 6.1 | 8.3147 | 8.22 | 8.1253 | 8.0263 | 7.9284 | 7.7305 | 7.5358 | 7.3337 | 7.2326 | 7.14 | 6.7263 | 6.3989 | 6.1337
|  | BOAT OF GARTEN | HE |  |  |  |  | 8.7053 | 8.6695 | 8.6305 | 8.5895 | 8.5474 | 8.4947 | 8.4474 | 8.3432 | 8.2263 | 8.0937 | 7.9211 | 7.8011 | 7.6989 | 8.3737 | 8.3263 | 8.2768 | 8.2263 | 8.1747 | 8.1147 | 8.06 | 7.9221 | 7.7853 | 7.6284 | 7.4505 | 7.3263 | 7.22 | 8.3147 | 8.22 | 8.1253 | 8.0263 | 7.9284 | 7.7305 | 7.5358 | 7.3337 | 7.2326 | 7.14 | 6.7263 | 6.3989 | 6.1337
|  | BOAT OF GARTEN | CF |  |  |  |  | 8.7284 | 8.7063 | 8.6853 | 8.6632 | 8.64 | 8.6126 | 8.5874 | 8.5611 | 8.5147 | 8.4547 | 8.2674 | 8.1684 | 8.0989 | 8.4042 | 8.3758 | 8.3463 | 8.3168 | 8.2874 | 8.2526 | 8.22 | 8.1874 | 8.1105 | 8.0337 | 7.8211 | 7.7158 | 7.6379 | 8.4474 | 8.42 | 8.3926 | 8.3653 | 8.3368 | 8.3042 | 8.2737 | 8.2411 | 8.1726 | 8.0968 | 7.8811 | 7.7705 | 7.6895
| PETERHEAD SHELL | BODDAM | MINIMUM HEADROOM | NK 12219 42512 | YES | NO | 0.349 | 6.1647 | 6.1142 | 6.0542 | 5.991 | 5.9226 | 5.6826 | 5.4436 | 5.1721 | 4.8626 | 4.6899 | 3.8615 | 3.1531 | 2.8605 | 5.6826 | 5.6089 | 5.5215 | 5.4289 | 5.3257 | 4.971 | 4.6194 | 4.2005 | 3.7205 | 3.5173 | 2.6994 | 2.0468 | 1.7457 | 6.1226 | 6.0794 | 6.0289 | 5.9763 | 5.9173 | 5.7205 | 5.5236 | 5.3036 | 5.0542 | 4.8889 | 4.0794 | 3.2594 | 2.9078
|  | BODDAM | EE |  |  |  |  | 6.1752 | 6.1426 | 6.091 | 6.0363 | 5.9773 | 5.7678 | 5.5121 | 5.2478 | 4.9868 | 4.6899 | 3.8615 | 3.1531 | 2.8605 | 5.6931 | 5.651 | 5.5794 | 5.5005 | 5.4142 | 5.1405 | 4.7963 | 4.4352 | 4.0531 | 3.6078 | 2.6994 | 2.0468 | 1.7457 | 6.1331 | 6.1047 | 6.0594 | 6.0131 | 5.9626 | 5.7836 | 5.5678 | 5.3457 | 5.131 | 4.8889 | 4.0794 | 3.2594 | 2.9078
|  | BODDAM | HT |  |  |  |  | 6.1647 | 6.1142 | 6.0542 | 5.991 | 5.9226 | 5.6826 | 5.4436 | 5.1721 | 4.8626 | 4.6899 | 4.0468 | 3.6731 | 3.3194 | 5.6826 | 5.6089 | 5.5215 | 5.4289 | 5.3257 | 4.971 | 4.6194 | 4.2005 | 3.7205 | 3.5173 | 2.7594 | 2.3552 | 1.8973 | 6.1226 | 6.0794 | 6.0289 | 5.9763 | 5.9173 | 5.7205 | 5.5236 | 5.3036 | 5.0542 | 4.9015 | 4.2215 | 3.7584 | 3.2773
|  | BODDAM | HE |  |  |  |  | 6.1889 | 6.1699 | 6.1447 | 6.1131 | 6.071 | 5.8647 | 5.6478 | 5.4289 | 5.1931 | 4.9268 | 4.3247 | 3.8963 | 3.4247 | 5.7068 | 5.6836 | 5.651 | 5.6036 | 5.5394 | 5.2752 | 4.9699 | 4.6521 | 4.3005 | 3.8847 | 3.2026 | 2.8089 | 2.3521 | 6.1226 | 6.0794 | 6.0289 | 5.9763 | 5.9173 | 5.7205 | 5.5236 | 5.3036 | 5.0542 | 4.9015 | 4.2215 | 3.7584 | 3.2773
|  | BODDAM | CF |  |  |  |  | 6.2005 | 6.191 | 6.1805 | 6.1689 | 6.1563 | 6.0973 | 6.0342 | 5.9605 | 5.8836 | 5.8036 | 5.3794 | 4.9836 | 4.7899 | 5.7226 | 5.7121 | 5.6994 | 5.6857 | 5.6721 | 5.6121 | 5.5352 | 5.4394 | 5.331 | 5.2047 | 4.5921 | 4.0868 | 3.8994 | 6.1573 | 6.1478 | 6.1384 | 6.1278 | 6.1163 | 6.0626 | 6.0068 | 5.9447 | 5.8794 | 5.8163 | 5.4668 | 5.1268 | 4.9489
| TUMMEL BRIDGE | BONSKEID | MINIMUM HEADROOM | NN 90919 60658 | YES | YES | 0 | 1.6 | 1.5684 | 1.5316 | 1.4926 | 1.4526 | 1.3863 | 1.3263 | 1.2663 | 1.2053 | 1.0842 | 0.71474 | 0.46316 | 0.31789 | 1.0958 | 1.0032 | 0.87895 | 0.73895 | 0.58211 | 0.43053 | 0.30842 | 0.18632 | 0.032632 | -0.16526 | -0.54316 | -0.76842 | -0.93474 | 1.4274 | 1.3316 | 1.2021 | 1.0547 | 0.89158 | 0.73053 | 0.60105 | 0.47158 | 0.30737 | 0.10105 | -0.30105 | -0.55789 | -0.71474
|  | BONSKEID | EE |  |  |  |  | 1.6137 | 1.5895 | 1.5621 | 1.5337 | 1.5053 | 1.4484 | 1.3874 | 1.3284 | 1.2747 | 1.2211 | 0.76316 | 0.46316 | 0.31789 | 1.1242 | 1.0589 | 0.98842 | 0.89474 | 0.77789 | 0.58105 | 0.38737 | 0.28947 | 0.18421 | 0.064211 | -0.47053 | -0.74632 | -0.89158 | 1.4568 | 1.3895 | 1.3137 | 1.2179 | 1.0947 | 0.88526 | 0.67895 | 0.57053 | 0.45789 | 0.32842 | -0.24526 | -0.55789 | -0.71474
|  | BONSKEID | HT |  |  |  |  | 1.6 | 1.5684 | 1.5316 | 1.4926 | 1.4526 | 1.3863 | 1.3263 | 1.2663 | 1.2053 | 1.0842 | 0.71474 | 0.49158 | 0.33684 | 1.0958 | 1.0032 | 0.87895 | 0.73895 | 0.58211 | 0.43053 | 0.30842 | 0.18632 | 0.032632 | -0.16526 | -0.54316 | -0.76842 | -0.93474 | 1.4274 | 1.3316 | 1.2021 | 1.0547 | 0.89158 | 0.73053 | 0.60105 | 0.47158 | 0.30737 | 0.10105 | -0.30105 | -0.54 | -0.71263
|  | BONSKEID | HE |  |  |  |  | 1.6316 | 1.6147 | 1.5979 | 1.5779 | 1.5579 | 1.5063 | 1.4621 | 1.4179 | 1.3747 | 1.3337 | 1.0853 | 0.91158 | 0.74526 | 1.16 | 1.1126 | 1.0484 | 0.96 | 0.85474 | 0.66 | 0.51158 | 0.41158 | 0.29789 | 0.16316 | -0.13895 | -0.29684 | -0.44737 | 1.4274 | 1.3316 | 1.2021 | 1.0547 | 0.89158 | 0.73053 | 0.60105 | 0.47158 | 0.30737 | 0.10105 | -0.30105 | -0.54 | -0.71263
|  | BONSKEID | CF |  |  |  |  | 1.6411 | 1.6316 | 1.6221 | 1.6116 | 1.6021 | 1.5811 | 1.5611 | 1.5411 | 1.5232 | 1.5063 | 1.4179 | 1.3326 | 1.2758 | 1.1768 | 1.16 | 1.1389 | 1.1137 | 1.0832 | 1.0337 | 0.96737 | 0.89263 | 0.83895 | 0.72105 | 0.42316 | 0.31053 | 0.22842 | 1.5137 | 1.4947 | 1.4716 | 1.4453 | 1.4137 | 1.36 | 1.2895 | 1.2095 | 1.1537 | 1.0274 | 0.70947 | 0.58526 | 0.49263
| PORT ANN | BOWMORE | MINIMUM HEADROOM | NR 32021 60211 | NO | YES | 0 | 8.8926 | 8.8053 | 8.6863 | 8.5537 | 8.3979 | 8.2368 | 8.0337 | 7.8832 | 7.7905 | 7.7095 | 7.1084 | 6.8537 | 6.5568 | 7.9516 | 7.8716 | 7.7642 | 7.6453 | 7.4695 | 7.2789 | 7.0337 | 6.8568 | 6.7526 | 6.6632 | 6.1021 | 5.8074 | 5.4505 | 8.3663 | 8.2726 | 8.1389 | 7.9874 | 7.8063 | 7.6179 | 7.3737 | 7.1968 | 7.0916 | 7.0021 | 6.3726 | 6.0779 | 5.7211
|  | BOWMORE | EE |  |  |  |  | 8.9442 | 8.8705 | 8.7779 | 8.6621 | 8.5105 | 8.3589 | 8.1547 | 8.0211 | 7.9505 | 7.8821 | 11.4274 | 11.2768 | 11.1274 | 7.9989 | 7.9305 | 7.8463 | 7.7432 | 7.5989 | 7.4168 | 7.1684 | 7.0095 | 6.9305 | 6.8526 | 11.4726 | 11.2653 | 11.0905 | 8.4221 | 8.3453 | 8.2432 | 8.1116 | 7.9347 | 7.7547 | 7.5074 | 7.3495 | 7.2695 | 7.1926 | 11.2126 | 11.0074 | 10.8337
|  | BOWMORE | HT |  |  |  |  | 8.8926 | 8.8053 | 8.6863 | 8.5537 | 8.3979 | 8.2368 | 8.0337 | 7.8832 | 7.7905 | 7.7095 | 7.1084 | 6.8537 | 6.5568 | 7.9516 | 7.8716 | 7.7642 | 7.6453 | 7.4695 | 7.2789 | 7.0337 | 6.8568 | 6.7526 | 6.6632 | 6.1021 | 5.8074 | 5.4505 | 8.3663 | 8.2726 | 8.1389 | 7.9874 | 7.8063 | 7.6179 | 7.3737 | 7.1968 | 7.0916 | 7.0021 | 6.3726 | 6.0779 | 5.7211
|  | BOWMORE | HE |  |  |  |  | 8.9989 | 8.9516 | 8.8779 | 8.78 | 8.6526 | 8.5221 | 8.3432 | 8.2158 | 8.1653 | 8.1211 | 7.8242 | 7.7305 | 7.6621 | 8.0484 | 8.0042 | 7.9389 | 7.8516 | 7.74 | 7.6021 | 7.3821 | 7.2284 | 7.1716 | 7.1232 | 6.8526 | 6.7453 | 6.6642 | 8.3663 | 8.2726 | 8.1389 | 7.9874 | 7.8063 | 7.6179 | 7.3737 | 7.1968 | 7.0916 | 7.0021 | 6.3726 | 6.0779 | 5.7211
|  | BOWMORE | CF |  |  |  |  | 9.0389 | 9.0116 | 8.9758 | 8.9368 | 8.8737 | 8.8105 | 8.7221 | 8.6463 | 8.6105 | 8.5716 | 8.4253 | 8.3411 | 8.28 | 8.0842 | 8.0589 | 8.0263 | 7.9905 | 7.9358 | 7.88 | 7.8042 | 7.7379 | 7.7053 | 7.66 | 7.4947 | 7.3968 | 7.3232 | 8.4947 | 8.4758 | 8.4526 | 8.4137 | 8.3453 | 8.2737 | 8.1684 | 8.0789 | 8.04 | 7.9958 | 7.8316 | 7.7337 | 7.6611
| SHETLAND | BRAE | MINIMUM HEADROOM | HU3604068816 | YES | YES | 0 | 1.4663 | 1.4032 | 1.3379 | -0.89263 | -0.94737 | -1.0179 | -1.1484 | -1.2958 | -1.4537 | -1.5832 | -1.8284 | -1.9926 | -2.0811 | 1.2137 | 1.1358 | 1.0558 | -0.72526 | -0.78632 | -0.85789 | -1.0116 | -1.1737 | -1.3495 | -1.4979 | -1.7411 | -1.8937 | -1.9811 | 1.2989 | 1.26 | 1.2179 | -1.0958 | -1.1537 | -1.2284 | -1.3768 | -1.5484 | -1.7305 | -1.8811 | -2.14 | -2.3116 | -2.4042
|  | BRAE | EE |  |  |  |  | 1.4937 | 1.4432 | 1.3895 | -0.89263 | -0.94737 | -1.0179 | -1.1484 | -1.2958 | -1.4537 | -1.5832 | -1.8284 | -1.9926 | -2.0811 | 1.2495 | 1.1874 | 1.1232 | -0.72526 | -0.78632 | -0.85789 | -1.0116 | -1.1737 | -1.3495 | -1.4979 | -1.7411 | -1.8937 | -1.9811 | 1.3137 | 1.2811 | 1.2453 | -1.0958 | -1.1537 | -1.2284 | -1.3768 | -1.5484 | -1.7305 | -1.8811 | -2.14 | -2.3116 | -2.4042
|  | BRAE | HT |  |  |  |  | 1.4663 | 1.4032 | 1.3379 | 1.2737 | 1.2095 | 1.1295 | 0.98947 | 0.81895 | 0.62526 | 0.57053 | -0.48947 | -1.3937 | -1.4863 | 1.2137 | 1.1358 | 1.0558 | 0.97789 | 0.90105 | 0.80632 | 0.61895 | 0.40842 | 0.18105 | 0.12842 | -0.73158 | -1.4642 | -1.5632 | 1.2989 | 1.26 | 1.2179 | 1.1526 | 1.0758 | 0.98105 | 0.79684 | 0.59053 | 0.36737 | 0.31158 | -0.75263 | -1.6916 | -1.7895
|  | BRAE | HE |  |  |  |  | 1.5337 | 1.5011 | 1.4674 | 1.4316 | 1.3937 | 1.3137 | 1.1979 | 1.0821 | 0.94632 | 0.82842 | 0.28842 | -0.15368 | -0.18632 | 1.2958 | 1.2611 | 1.2211 | 1.1789 | 1.1368 | 1.0337 | 0.86947 | 0.71263 | 0.54316 | 0.40526 | -0.049474 | -0.40632 | -0.44 | 1.2989 | 1.26 | 1.2179 | 1.1526 | 1.0758 | 0.98105 | 0.79684 | 0.59053 | 0.36737 | 0.31158 | -0.75263 | -1.6916 | -1.7895
|  | BRAE | CF |  |  |  |  | 1.5537 | 1.5337 | 1.5126 | 1.4916 | 1.4695 | 1.4453 | 1.42 | 1.3937 | 1.3705 | 1.3305 | 1.1389 | 1.0032 | 0.96 | 1.3084 | 1.2958 | 1.2747 | 1.2495 | 1.2232 | 1.1937 | 1.1663 | 1.1368 | 1.1084 | 1.0547 | 0.79789 | 0.62842 | 0.58632 | 1.3484 | 1.3358 | 1.3232 | 1.3095 | 1.2947 | 1.2779 | 1.26 | 1.2421 | 1.2253 | 1.2084 | 0.96947 | 0.79895 | 0.75368
| BRIDGE OF DUN | BRECHIN | MINIMUM HEADROOM | NO 60998 59682 | NO | YES | 0 | 13.1555 | 13.0271 | 12.8787 | 12.6218 | 12.2692 | 11.6755 | 11.0987 | 10.5082 | 9.8155 | 9.0155 | 6.0082 | 0.82605 | -3.1403 | 11.4905 | 11.2579 | 10.8 | 10.3874 | 10.0063 | 9.4442 | 8.9011 | 8.3442 | 7.6895 | 6.9116 | 4.06 | -1.2737 | -5.1684 | 12.1799 | 11.9514 | 11.4999 | 11.0872 | 10.7051 | 10.0746 | 9.463 | 8.8346 | 8.0957 | 7.2336 | 4.0514 | -1.6391 | -6.1033
|  | BRECHIN | EE |  |  |  |  | 13.2082 | 13.1071 | 12.9755 | 12.8376 | 12.6661 | 12.0313 | 11.2755 | 10.6082 | 9.9924 | 9.2787 | 6.0082 | 0.82605 | -3.1403 | 11.5474 | 11.4368 | 11.1053 | 10.7674 | 10.4547 | 9.8642 | 9.16 | 8.5621 | 8.0011 | 7.3274 | 4.3568 | -0.82421 | -5.1684 | 12.2325 | 12.1314 | 11.8009 | 11.4578 | 11.142 | 10.4662 | 9.6588 | 8.9536 | 8.2988 | 7.5336 | 4.0514 | -1.6391 | -6.1033
|  | BRECHIN | HT |  |  |  |  | 13.1555 | 13.0271 | 12.8787 | 12.6218 | 12.2692 | 11.6755 | 11.0987 | 10.5082 | 9.8155 | 9.0155 | 6.0692 | 1.1829 | -2.1676 | 11.4905 | 11.2579 | 10.8 | 10.3874 | 10.0063 | 9.4442 | 8.9011 | 8.3442 | 7.6895 | 6.9116 | 4.06 | -1.2737 | -5.0221 | 12.1799 | 11.9514 | 11.4999 | 11.0872 | 10.7051 | 10.0746 | 9.463 | 8.8346 | 8.0957 | 7.2336 | 4.0546 | -1.4275 | -5.2159
|  | BRECHIN | HE |  |  |  |  | 13.2713 | 13.1997 | 13.1166 | 13.0271 | 12.9324 | 12.4261 | 11.825 | 11.2892 | 10.7197 | 10.0682 | 7.4934 | 3.5145 | -0.76237 | 11.6137 | 11.5347 | 11.3884 | 11.1168 | 10.8621 | 10.28 | 9.7105 | 9.2168 | 8.6842 | 8.0516 | 5.6368 | 1.5253 | -2.9053 | 12.1799 | 11.9514 | 11.4999 | 11.0872 | 10.7051 | 10.0746 | 9.463 | 8.8346 | 8.0957 | 7.2336 | 4.0546 | -1.4275 | -5.2159
|  | BRECHIN | CF |  |  |  |  | 13.3071 | 13.2629 | 13.2134 | 13.1618 | 13.1113 | 12.9303 | 12.7661 | 12.6018 | 12.4566 | 12.3376 | 10.8271 | 8.2976 | 5.5324 | 11.6526 | 11.6053 | 11.5537 | 11.5011 | 11.4495 | 11.3305 | 11.1105 | 10.8684 | 10.6547 | 10.4158 | 8.7295 | 6.1 | 3.1021 | 12.3314 | 12.2872 | 12.2378 | 12.1872 | 12.1357 | 11.9599 | 11.7199 | 11.4578 | 11.2262 | 10.9746 | 9.1557 | 6.3483 | 3.2388
| PERSLEY | BRIDGE OF DON | MINIMUM HEADROOM | NJ 94130 10184 | NO | NO | 0.443 | 17.8912 | 17.4238 | 16.807 | 16.0838 | 15.2923 | 14.4512 | 13.5744 | 12.6217 | 11.547 | 10.2617 | 7.7049 | 6.447 | 5.3986 | 15.5538 | 14.6054 | 13.8328 | 12.977 | 12.0444 | 11.0886 | 10.0844 | 9.0317 | 7.8654 | 6.4591 | 3.7738 | 2.4717 | 1.3486 | 16.2825 | 15.752 | 14.9615 | 14.0825 | 13.1278 | 12.1373 | 11.0973 | 10.0067 | 8.7931 | 7.3352 | 4.5446 | 3.1804 | 2.0183
|  | BRIDGE OF DON | EE |  |  |  |  | 17.9817 | 17.7144 | 17.1681 | 16.5333 | 15.8417 | 15.0659 | 14.2186 | 13.5238 | 12.8133 | 12.0302 | 8.3133 | 7.0849 | 6.2459 | 15.7328 | 14.9581 | 14.2686 | 13.4875 | 12.6728 | 11.7917 | 10.8286 | 10.0549 | 9.2791 | 8.4381 | 4.4538 | 3.3033 | 2.4338 | 16.3709 | 16.112 | 15.4036 | 14.6025 | 13.7657 | 12.8488 | 11.8436 | 11.0341 | 10.2204 | 9.3425 | 5.1667 | 3.9141 | 2.9952
|  | BRIDGE OF DON | HT |  |  |  |  | 17.8912 | 17.4238 | 16.807 | 16.0838 | 15.2923 | 14.4512 | 13.5744 | 12.6217 | 11.547 | 10.2617 | 7.7049 | 6.447 | 5.3986 | 15.5538 | 14.6054 | 13.8328 | 12.977 | 12.0444 | 11.0886 | 10.0844 | 9.0317 | 7.8654 | 6.4591 | 3.7738 | 2.4717 | 1.3486 | 16.2825 | 15.752 | 14.9615 | 14.0825 | 13.1278 | 12.1373 | 11.0973 | 10.0067 | 8.7931 | 7.3352 | 4.5446 | 3.1804 | 2.0183
|  | BRIDGE OF DON | HE |  |  |  |  | 18.0965 | 17.9502 | 17.5912 | 17.1123 | 16.5723 | 15.9154 | 15.2302 | 14.6154 | 14.0291 | 13.4786 | 11.8038 | 10.6175 | 9.5481 | 15.9665 | 15.3033 | 14.7728 | 14.1612 | 13.5023 | 12.7633 | 11.9802 | 11.2823 | 10.6181 | 9.9959 | 8.2486 | 7.0181 | 5.9307 | 16.2825 | 15.752 | 14.9615 | 14.0825 | 13.1278 | 12.1373 | 11.0973 | 10.0067 | 8.7931 | 7.3352 | 4.5446 | 3.1804 | 2.0183
|  | BRIDGE OF DON | CF |  |  |  |  | 18.1659 | 18.0796 | 17.9986 | 17.9133 | 17.747 | 17.5017 | 17.2354 | 16.9217 | 16.6217 | 16.3007 | 15.1249 | 14.2638 | 13.5491 | 16.1012 | 15.8265 | 15.5759 | 15.2717 | 14.9865 | 14.6949 | 14.3707 | 13.9833 | 13.6233 | 13.2496 | 11.9275 | 10.9865 | 10.1823 | 16.5509 | 16.4688 | 16.3909 | 16.3088 | 16.1383 | 15.8341 | 15.4973 | 15.0941 | 14.7215 | 14.3352 | 12.9562 | 11.9562 | 11.1067
| BRIDGE OF DUN | BRIDGE OF DUN | MINIMUM HEADROOM | NO 66018 58883 | YES | YES | 0.66 | 0.30211 | 0.28 | 0.24947 | 0.22 | 0.18947 | 0.0021053 | -0.22947 | -0.46842 | -0.68211 | -1.0368 | -3.0926 | -5.5095 | -7.3811 | 0.31684 | 0.28947 | 0.25684 | 0.22421 | 0.19263 | 0.061053 | -0.13789 | -0.36842 | -0.58526 | -0.93053 | -2.8642 | -5.3358 | -7.2674 | 0.35474 | 0.32737 | 0.29474 | 0.26211 | 0.22842 | 0.042105 | -0.19158 | -0.43053 | -0.63895 | -0.97158 | -3.2642 | -5.9074 | -8.0453
|  | BRIDGE OF DUN | EE |  |  |  |  | 0.31158 | 0.29263 | 0.26211 | 0.22947 | 0.19579 | 0.0021053 | -0.22947 | -0.46842 | -0.67368 | -0.92421 | -3.0926 | -5.5095 | -7.3811 | 0.32842 | 0.30632 | 0.27684 | 0.24421 | 0.21263 | 0.061053 | -0.12842 | -0.32211 | -0.49158 | -0.72526 | -2.8379 | -5.2284 | -7.2674 | 0.36421 | 0.34421 | 0.31053 | 0.27474 | 0.23895 | 0.042105 | -0.19158 | -0.43053 | -0.63895 | -0.90947 | -3.2642 | -5.9074 | -8.0453
|  | BRIDGE OF DUN | HT |  |  |  |  | 0.30211 | 0.28 | 0.24947 | 0.22 | 0.18947 | 0.025263 | -0.14 | -0.30526 | -0.53368 | -0.95579 | -2.9305 | -5.1874 | -6.7305 | 0.31684 | 0.28947 | 0.25684 | 0.22421 | 0.19263 | 0.062105 | -0.073684 | -0.21158 | -0.42211 | -0.84105 | -2.8642 | -5.3358 | -7.0821 | 0.35474 | 0.32737 | 0.29474 | 0.26211 | 0.22842 | 0.061053 | -0.10632 | -0.27368 | -0.51789 | -0.97158 | -3.1642 | -5.7358 | -7.5168
|  | BRIDGE OF DUN | HE |  |  |  |  | 0.32526 | 0.31368 | 0.3 | 0.28632 | 0.27053 | 0.037895 | -0.19789 | -0.44632 | -0.68211 | -1.0368 | -2.5326 | -4.4084 | -6.4547 | 0.34632 | 0.33263 | 0.31684 | 0.30211 | 0.28632 | 0.084211 | -0.13789 | -0.36842 | -0.58526 | -0.93053 | -2.3916 | -4.3158 | -6.4179 | 0.35474 | 0.32737 | 0.29474 | 0.26211 | 0.22842 | 0.061053 | -0.10632 | -0.27368 | -0.51789 | -0.97158 | -3.1642 | -5.7358 | -7.5168
|  | BRIDGE OF DUN | CF |  |  |  |  | 0.33158 | 0.32526 | 0.31684 | 0.30842 | 0.3 | 0.22211 | 0.15263 | 0.031579 | -0.12211 | -0.29684 | -1.0726 | -2.2558 | -3.5768 | 0.35368 | 0.34632 | 0.33684 | 0.32842 | 0.31895 | 0.25895 | 0.20526 | 0.065263 | -0.093684 | -0.28421 | -1.0747 | -2.2979 | -3.7337 | 0.38737 | 0.38 | 0.37053 | 0.36211 | 0.35263 | 0.27263 | 0.20316 | 0.061053 | -0.10316 | -0.30105 | -1.1611 | -2.4789 | -3.98
| ABERNETHY | BRIDGE OF EARN | MINIMUM HEADROOM | NO 13343 17764 | NO | YES | 0 | 15.1995 | 14.9668 | 14.6353 | 14.2416 | 13.8679 | 13.2942 | 12.7395 | 12.1858 | 11.6037 | 11.01 | 7.59 | 6.5289 | 4.7995 | 13.8789 | 13.6053 | 13.2253 | 12.7705 | 12.3432 | 11.7453 | 11.1653 | 10.5884 | 9.9916 | 9.3832 | 6.5884 | 5.6526 | 3.9526 | 14.3034 | 14.0434 | 13.6834 | 13.2529 | 12.8476 | 12.2266 | 11.6161 | 11.0076 | 10.3708 | 9.7213 | 7.5445 | 5.8329 | 4.2708
|  | BRIDGE OF EARN | EE |  |  |  |  | 15.2342 | 15.0574 | 14.7532 | 14.39 | 14.0489 | 13.4795 | 12.8805 | 12.2795 | 11.7142 | 11.1405 | 8.9942 | 7.3426 | 5.9447 | 13.9147 | 13.7032 | 13.3558 | 12.9358 | 12.5432 | 11.9621 | 11.3589 | 10.7568 | 10.1821 | 9.5989 | 7.4789 | 6.0726 | 4.5779 | 14.3382 | 14.1382 | 13.8076 | 13.4108 | 13.0382 | 12.4266 | 11.7739 | 11.1182 | 10.5013 | 9.8718 | 7.5445 | 5.8329 | 4.2708
|  | BRIDGE OF EARN | HT |  |  |  |  | 15.1995 | 14.9668 | 14.6353 | 14.2416 | 13.8679 | 13.2942 | 12.7395 | 12.1858 | 11.6037 | 11.01 | 9.1553 | 8.1689 | 6.2563 | 13.8789 | 13.6053 | 13.2253 | 12.7705 | 12.3432 | 11.7453 | 11.1653 | 10.5884 | 9.9916 | 9.3832 | 7.4505 | 6.5084 | 4.32 | 14.3034 | 14.0434 | 13.6834 | 13.2529 | 12.8476 | 12.2266 | 11.6161 | 11.0076 | 10.3708 | 9.7213 | 7.6803 | 6.6297 | 4.4445
|  | BRIDGE OF EARN | HE |  |  |  |  | 15.2732 | 15.1679 | 14.9153 | 14.5953 | 14.2953 | 13.7447 | 13.2342 | 12.7268 | 12.2247 | 11.7163 | 7.59 | 6.5289 | 4.7995 | 13.9537 | 13.8295 | 13.5305 | 13.1537 | 12.8042 | 12.2474 | 11.7211 | 11.1989 | 10.6811 | 10.1558 | 6.5884 | 5.6526 | 3.9526 | 14.3034 | 14.0434 | 13.6834 | 13.2529 | 12.8476 | 12.2266 | 11.6161 | 11.0076 | 10.3708 | 9.7213 | 7.6803 | 6.6297 | 4.4445
|  | BRIDGE OF EARN | CF |  |  |  |  | 15.3121 | 15.2847 | 15.2026 | 15.0595 | 14.9226 | 14.6974 | 14.4689 | 14.23 | 13.9889 | 13.7479 | 10.4658 | 9.7889 | 8.3542 | 13.9979 | 13.9684 | 13.8716 | 13.6968 | 13.54 | 13.3074 | 13.0684 | 12.8158 | 12.5579 | 12.2905 | 9.4884 | 8.8821 | 7.3347 | 14.4192 | 14.3908 | 14.2982 | 14.135 | 13.9866 | 13.7434 | 13.4992 | 13.2413 | 12.9813 | 12.7192 | 9.3255 | 8.6171 | 6.9918
| RANNOCH | BRIDGE OF GAUR | MINIMUM HEADROOM | NN 50676 57767 | YES | YES | 0 | 0.89053 | 0.88316 | 0.86947 | 0.85474 | 0.83789 | 0.76421 | 0.68526 | 0.60105 | 0.52947 | 0.44316 | -0.20211 | -0.90316 | -1.3821 | 0.88526 | 0.87789 | 0.86526 | 0.85053 | 0.83579 | 0.77579 | 0.70947 | 0.64 | 0.58 | 0.50737 | -0.054737 | -0.72211 | -1.2453 | 0.95579 | 0.94632 | 0.93053 | 0.91263 | 0.89684 | 0.82105 | 0.73684 | 0.64842 | 0.57263 | 0.48 | -0.22947 | -1.0011 | -1.5632
|  | BRIDGE OF GAUR | EE |  |  |  |  | 0.89158 | 0.88316 | 0.86947 | 0.85474 | 0.83789 | 0.76421 | 0.68526 | 0.60105 | 0.52947 | 0.44316 | -0.20211 | -0.90316 | -1.3821 | 0.88842 | 0.87895 | 0.86526 | 0.85053 | 0.83579 | 0.77579 | 0.70947 | 0.64 | 0.58 | 0.50737 | -0.054737 | -0.72211 | -1.2453 | 0.95895 | 0.94632 | 0.93053 | 0.91263 | 0.89684 | 0.82105 | 0.73684 | 0.64842 | 0.57263 | 0.48 | -0.22947 | -1.0011 | -1.5632
|  | BRIDGE OF GAUR | HT |  |  |  |  | 0.89053 | 0.88526 | 0.87684 | 0.86526 | 0.85684 | 0.79789 | 0.74526 | 0.68842 | 0.61579 | 0.50211 | -0.033684 | -0.60211 | -0.99263 | 0.88526 | 0.87789 | 0.86842 | 0.85684 | 0.85053 | 0.80421 | 0.75895 | 0.71263 | 0.64947 | 0.54105 | 0.014737 | -0.60737 | -1.0379 | 0.95579 | 0.94737 | 0.93579 | 0.92421 | 0.91474 | 0.85368 | 0.79579 | 0.73789 | 0.66 | 0.52842 | -0.073684 | -0.73263 | -1.1821
|  | BRIDGE OF GAUR | HE |  |  |  |  | 0.89368 | 0.89053 | 0.88632 | 0.88105 | 0.87684 | 0.80105 | 0.73053 | 0.65579 | 0.58421 | 0.48526 | 0.049474 | -0.46 | -1.0137 | 0.89158 | 0.88947 | 0.88316 | 0.87789 | 0.87263 | 0.81053 | 0.74526 | 0.68 | 0.61579 | 0.52526 | 0.12737 | -0.38947 | -0.95053 | 0.95579 | 0.94737 | 0.93579 | 0.92421 | 0.91474 | 0.85368 | 0.79579 | 0.73789 | 0.66 | 0.52842 | -0.073684 | -0.73263 | -1.1821
|  | BRIDGE OF GAUR | CF |  |  |  |  | 0.89474 | 0.89368 | 0.89053 | 0.88947 | 0.88737 | 0.86526 | 0.84211 | 0.80526 | 0.76737 | 0.72737 | 0.52211 | 0.20842 | -0.12842 | 0.89368 | 0.89158 | 0.88842 | 0.88632 | 0.88421 | 0.86421 | 0.84526 | 0.80947 | 0.76842 | 0.72211 | 0.51474 | 0.19895 | -0.16105 | 0.96421 | 0.96105 | 0.95895 | 0.95579 | 0.95263 | 0.92632 | 0.90105 | 0.85895 | 0.81263 | 0.76211 | 0.52737 | 0.17263 | -0.21368
| BROADFORD | BROADFORD | MINIMUM HEADROOM | NG 62656 24360 | YES | YES | 0 | 5.6232 | 5.5821 | 5.5368 | 5.4747 | 5.4116 | 5.2232 | 5.0421 | 4.8568 | 4.7411 | 4.6274 | 4.0116 | 2.9432 | 2.1653 | 5.2326 | 5.1674 | 5.1021 | 5.0368 | 4.9716 | 4.7863 | 4.6095 | 4.4295 | 4.3295 | 4.2337 | 3.6505 | 2.4695 | 1.6253 | 5.38 | 5.3453 | 5.2968 | 5.2295 | 5.1621 | 4.9547 | 4.7579 | 4.5558 | 4.4358 | 4.32 | 3.6558 | 2.4389 | 1.5811
|  | BROADFORD | EE |  |  |  |  | 5.64 | 5.6084 | 5.5705 | 5.5316 | 5.4863 | 5.3789 | 5.2589 | 5.0663 | 4.8863 | 4.7011 | 4.0789 | 3.0274 | 2.1653 | 5.2621 | 5.2126 | 5.16 | 5.1053 | 5.0526 | 4.9611 | 4.8632 | 4.6842 | 4.5137 | 4.3368 | 3.7958 | 2.7274 | 1.7695 | 5.3947 | 5.3674 | 5.3347 | 5.2989 | 5.2432 | 5.1326 | 5.0105 | 4.8011 | 4.6063 | 4.4042 | 3.7537 | 2.5947 | 1.6084
|  | BROADFORD | HT |  |  |  |  | 5.6232 | 5.5821 | 5.5368 | 5.4747 | 5.4116 | 5.2232 | 5.0421 | 4.8568 | 4.7411 | 4.6274 | 4.0116 | 2.9432 | 2.1958 | 5.2326 | 5.1674 | 5.1021 | 5.0368 | 4.9716 | 4.7863 | 4.6095 | 4.4295 | 4.3295 | 4.2337 | 3.6505 | 2.4695 | 1.6253 | 5.38 | 5.3453 | 5.2968 | 5.2295 | 5.1621 | 4.9547 | 4.7579 | 4.5558 | 4.4358 | 4.32 | 3.6558 | 2.4389 | 1.5811
|  | BROADFORD | HE |  |  |  |  | 5.66 | 5.6421 | 5.6221 | 5.5979 | 5.5716 | 5.4811 | 5.4042 | 5.2779 | 5.1358 | 4.9968 | 4.3821 | 3.5558 | 2.6674 | 5.3032 | 5.2726 | 5.24 | 5.2084 | 5.1737 | 5.0947 | 5.0263 | 4.8905 | 4.7579 | 4.6284 | 4.0568 | 3.1895 | 2.2526 | 5.38 | 5.3453 | 5.2968 | 5.2295 | 5.1621 | 4.9547 | 4.7579 | 4.5558 | 4.4358 | 4.32 | 3.6558 | 2.4389 | 1.5811
|  | BROADFORD | CF |  |  |  |  | 5.6705 | 5.6611 | 5.6495 | 5.64 | 5.6274 | 5.5916 | 5.5579 | 5.5232 | 5.4842 | 5.4147 | 5.0463 | 4.52 | 3.9253 | 5.3242 | 5.3053 | 5.2853 | 5.2674 | 5.2474 | 5.2126 | 5.1789 | 5.1442 | 5.0779 | 5.0042 | 4.6411 | 4.1147 | 3.4663 | 5.4263 | 5.4168 | 5.4053 | 5.3958 | 5.3832 | 5.3537 | 5.3253 | 5.2958 | 5.2474 | 5.1653 | 4.7589 | 4.1674 | 3.4895
| CARRADALE 1 | BRODICK | MINIMUM HEADROOM | NS 01976 35459 | NO | YES | 0.18 | 8.6137 | 8.5253 | 8.4358 | 8.3347 | 8.2495 | 8.1495 | 8.0326 | 7.8821 | 7.7368 | 7.5968 | 7.0474 | 3.8221 | 3.5505 | 7.5232 | 7.4358 | 7.3474 | 7.1916 | 7.0179 | 6.8421 | 6.6705 | 6.5042 | 6.3463 | 6.1926 | 5.5989 | 3.2211 | 2.8211 | 8.0368 | 7.9432 | 7.8463 | 7.6958 | 7.5221 | 7.3453 | 7.1737 | 7.0084 | 6.8484 | 6.6958 | 6.0989 | 2.8737 | 2.5611
|  | BRODICK | EE |  |  |  |  | 8.6474 | 8.5737 | 8.4958 | 8.3347 | 8.2516 | 8.1663 | 8.0853 | 8.0063 | 7.9095 | 7.7958 | 7.3053 | 3.8221 | 3.5505 | 7.5568 | 7.4863 | 7.4116 | 7.3 | 7.1716 | 7.0263 | 6.8863 | 6.7505 | 6.6221 | 6.4989 | 5.9832 | 3.2337 | 2.9358 | 8.0726 | 7.9926 | 7.9084 | 7.7137 | 7.5968 | 7.4474 | 7.3053 | 7.1653 | 7.0326 | 6.9063 | 6.3716 | 2.8737 | 2.5611
|  | BRODICK | HT |  |  |  |  | 8.6137 | 8.5253 | 8.4358 | 8.3432 | 8.2495 | 8.1495 | 8.0326 | 7.8821 | 7.7368 | 7.5968 | 7.0474 | 4.1211 | 3.7705 | 7.5232 | 7.4358 | 7.3474 | 7.1916 | 7.0179 | 6.8421 | 6.6705 | 6.5042 | 6.3463 | 6.1926 | 5.5989 | 3.2211 | 2.8211 | 8.0368 | 7.9432 | 7.8463 | 7.6958 | 7.5221 | 7.3453 | 7.1737 | 7.0084 | 6.8484 | 6.6958 | 6.0989 | 3.1326 | 2.7284
|  | BRODICK | HE |  |  |  |  | 8.6958 | 8.6484 | 8.5979 | 8.5421 | 8.4832 | 8.4221 | 8.3642 | 8.3074 | 8.2547 | 8.2063 | 8.0432 | 6.3526 | 6.2316 | 7.6053 | 7.5589 | 7.5095 | 7.4547 | 7.3968 | 7.3358 | 7.28 | 7.2242 | 7.1474 | 7.0653 | 6.7674 | 5.3895 | 5.2547 | 8.0368 | 7.9432 | 7.8463 | 7.6958 | 7.5221 | 7.3453 | 7.1737 | 7.0084 | 6.8484 | 6.6958 | 6.0989 | 3.1326 | 2.7284
|  | BRODICK | CF |  |  |  |  | 8.7232 | 8.6979 | 8.6705 | 8.6432 | 8.6147 | 8.5863 | 8.5568 | 8.5284 | 8.5 | 8.4716 | 8.3484 | 6.8032 | 6.7032 | 7.6326 | 7.6074 | 7.5811 | 7.5526 | 7.5253 | 7.4968 | 7.4684 | 7.44 | 7.4116 | 7.3832 | 7.2074 | 5.8537 | 5.7358 | 8.1537 | 8.1253 | 8.0979 | 8.0674 | 8.0389 | 8.0074 | 7.9779 | 7.9463 | 7.9158 | 7.8853 | 7.7116 | 5.9926 | 5.8747
| BRORA | BRORA | MINIMUM HEADROOM | NC 90482 04236 | NO | YES | 0 | 5.4379 | 5.3663 | 5.2853 | 5.2053 | 5.1263 | 4.8695 | 4.6116 | 4.3516 | 4.0674 | 3.7221 | 0.95474 | -2.3463 | -5.1442 | 5.2516 | 5.1726 | 5.0853 | 4.9979 | 4.9116 | 4.6642 | 4.4179 | 4.1684 | 3.9442 | 3.5389 | 0.72842 | -3.0568 | -5.7705 | 5.2779 | 5.2105 | 5.1211 | 5.0337 | 4.9453 | 4.6642 | 4.38 | 4.0926 | 3.8095 | 3.4232 | 0.39579 | -3.4442 | -6.5011
|  | BRORA | EE |  |  |  |  | 5.4684 | 5.4126 | 5.34 | 5.2663 | 5.1937 | 4.9505 | 4.6726 | 4.3516 | 4.0674 | 3.7726 | 0.95474 | -2.3463 | -5.1442 | 5.2811 | 5.2253 | 5.1526 | 5.0779 | 5.0021 | 4.7958 | 4.5611 | 4.2621 | 3.9926 | 3.7158 | 0.87368 | -2.5179 | -5.6284 | 5.2937 | 5.2589 | 5.1842 | 5.1042 | 5.0242 | 4.7663 | 4.4705 | 4.1211 | 3.8095 | 3.4884 | 0.39579 | -3.2884 | -6.5011
|  | BRORA | HT |  |  |  |  | 5.4379 | 5.3663 | 5.2853 | 5.2053 | 5.1263 | 4.8695 | 4.6116 | 4.3516 | 4.0968 | 3.7347 | 1.1242 | -2.2663 | -4.6442 | 5.2516 | 5.1726 | 5.0853 | 4.9979 | 4.9116 | 4.6642 | 4.4179 | 4.1684 | 3.9442 | 3.5863 | 0.72842 | -3.0568 | -5.7705 | 5.2779 | 5.2105 | 5.1211 | 5.0337 | 4.9453 | 4.6642 | 4.38 | 4.0926 | 3.82 | 3.4232 | 0.44211 | -3.4442 | -6.1958
|  | BRORA | HE |  |  |  |  | 5.5137 | 5.4779 | 5.44 | 5.3989 | 5.3568 | 5.1053 | 4.8042 | 4.4968 | 4.2063 | 3.7221 | 1.6842 | -0.95579 | -3.8411 | 5.3053 | 5.2832 | 5.2568 | 5.2147 | 5.1705 | 4.9632 | 4.6579 | 4.3432 | 4.0484 | 3.5389 | 1.4674 | -1.3326 | -4.3926 | 5.2779 | 5.2105 | 5.1211 | 5.0337 | 4.9453 | 4.6642 | 4.38 | 4.0926 | 3.82 | 3.4232 | 0.44211 | -3.4442 | -6.1958
|  | BRORA | CF |  |  |  |  | 5.5368 | 5.5147 | 5.4926 | 5.4684 | 5.4432 | 5.3484 | 5.26 | 5.1137 | 4.9147 | 4.6863 | 3.6 | 1.9274 | -0.021053 | 5.3189 | 5.3063 | 5.2926 | 5.2789 | 5.2642 | 5.1895 | 5.1147 | 4.9558 | 4.7168 | 4.4253 | 3.2526 | 1.46 | -0.69789 | 5.3316 | 5.3189 | 5.3042 | 5.2884 | 5.2726 | 5.1937 | 5.1042 | 4.9347 | 4.6937 | 4.4042 | 3.1558 | 1.2589 | -0.97053
| MILTON OF CRAIGIE | BROUGHTY FERRY | MINIMUM HEADROOM | NO 46658 30758 | NO | YES | 0 | 11.6516 | 11.5126 | 11.3695 | 11.2253 | 11.0747 | 10.8979 | 10.7263 | 10.5589 | 10.3958 | 10.24 | 9.4947 | 8.6274 | 7.9432 | 11.1526 | 11.0074 | 10.86 | 10.7095 | 10.5558 | 10.3863 | 10.2221 | 10.0632 | 9.9084 | 9.6884 | 8.3895 | 7.44 | 6.6853 | 11.2095 | 11.0705 | 10.9221 | 10.7716 | 10.6168 | 10.4432 | 10.2726 | 10.1084 | 9.9484 | 9.7947 | 8.5832 | 7.6347 | 6.8842
|  | BROUGHTY FERRY | EE |  |  |  |  | 11.7105 | 11.6032 | 11.4916 | 11.3747 | 11.2526 | 11.1168 | 10.9811 | 10.8453 | 10.7179 | 10.5947 | 10.0695 | 9.5884 | 9.0705 | 11.2158 | 11.1032 | 10.9884 | 10.8653 | 10.74 | 10.6063 | 10.4758 | 10.3505 | 10.2316 | 10.1158 | 9.2811 | 8.5147 | 7.9442 | 11.2684 | 11.1611 | 11.0495 | 10.9295 | 10.8021 | 10.6632 | 10.5253 | 10.3926 | 10.2684 | 10.1463 | 9.4558 | 8.6768 | 8.1074
|  | BROUGHTY FERRY | HT |  |  |  |  | 11.6516 | 11.5126 | 11.3695 | 11.2253 | 11.0747 | 10.8979 | 10.7263 | 10.5589 | 10.3958 | 10.24 | 9.4947 | 8.6274 | 7.9432 | 11.1526 | 11.0074 | 10.86 | 10.7095 | 10.5558 | 10.3863 | 10.2221 | 10.0632 | 9.9084 | 9.6884 | 8.3895 | 7.44 | 6.6853 | 11.2095 | 11.0705 | 10.9221 | 10.7716 | 10.6168 | 10.4432 | 10.2726 | 10.1084 | 9.9484 | 9.7947 | 8.5832 | 7.6347 | 6.8842
|  | BROUGHTY FERRY | HE |  |  |  |  | 11.78 | 11.7042 | 11.6242 | 11.5368 | 11.4411 | 11.3316 | 11.2316 | 11.1316 | 11.0368 | 10.9516 | 10.6263 | 10.4337 | 10.3042 | 11.2895 | 11.2105 | 11.1284 | 11.0379 | 10.9411 | 10.8347 | 10.7379 | 10.6389 | 10.5484 | 10.4653 | 10.1663 | 9.8947 | 9.5674 | 11.2095 | 11.0705 | 10.9221 | 10.7716 | 10.6168 | 10.4432 | 10.2726 | 10.1084 | 9.9484 | 9.7947 | 8.5832 | 7.6347 | 6.8842
|  | BROUGHTY FERRY | CF |  |  |  |  | 11.8158 | 11.7705 | 11.7232 | 11.6747 | 11.6242 | 11.5705 | 11.5147 | 11.4611 | 11.4074 | 11.3547 | 11.1189 | 10.9726 | 10.8895 | 11.3263 | 11.2789 | 11.2305 | 11.18 | 11.1284 | 11.0737 | 11.0189 | 10.9653 | 10.9105 | 10.8568 | 10.62 | 10.4905 | 10.4211 | 11.3737 | 11.3284 | 11.2811 | 11.2326 | 11.1821 | 11.1284 | 11.0737 | 11.02 | 10.9663 | 10.9137 | 10.6674 | 10.5232 | 10.4442
| DUNOON | BRUCHAG | MINIMUM HEADROOM | NS 11372 57191 | NO | YES | 3.5 | 26.1589 | 26.0842 | 26.0053 | 25.9253 | 25.8474 | 25.7295 | 25.6116 | 25.4916 | 25.3653 | 25.2411 | 24.7505 | 24.3316 | 24.0726 | 24.2747 | 24.2253 | 24.1726 | 24.1189 | 24.0274 | 23.9021 | 23.7811 | 23.66 | 23.5347 | 23.4095 | 22.9095 | 22.5158 | 22.2084 | 25.1595 | 25.11 | 25.0553 | 24.9711 | 24.8805 | 24.7511 | 24.6258 | 24.5005 | 24.3689 | 24.2384 | 23.7111 | 23.2826 | 22.9553
|  | BRUCHAG | EE |  |  |  |  | 26.1937 | 26.1358 | 26.0726 | 26.0063 | 25.94 | 25.8316 | 25.7147 | 25.5947 | 25.4853 | 25.3726 | 24.8263 | 24.3316 | 24.0726 | 24.2958 | 24.2568 | 24.2147 | 24.1695 | 24.1221 | 24.0295 | 23.9116 | 23.7916 | 23.6832 | 23.5747 | 23.0442 | 22.5663 | 22.2937 | 25.1805 | 25.1416 | 25.0974 | 25.05 | 24.9942 | 24.8753 | 24.7511 | 24.6237 | 24.5089 | 24.3953 | 23.8268 | 23.2858 | 22.9858
|  | BRUCHAG | HT |  |  |  |  | 26.1589 | 26.0842 | 26.0053 | 25.9253 | 25.8474 | 25.7295 | 25.6116 | 25.4916 | 25.3653 | 25.2411 | 24.7505 | 24.3726 | 24.0758 | 24.2747 | 24.2253 | 24.1726 | 24.1189 | 24.0274 | 23.9021 | 23.7811 | 23.66 | 23.5347 | 23.4095 | 22.9095 | 22.5158 | 22.2084 | 25.1595 | 25.11 | 25.0553 | 24.9711 | 24.8805 | 24.7511 | 24.6258 | 24.5005 | 24.3689 | 24.2384 | 23.7111 | 23.2826 | 22.9553
|  | BRUCHAG | HE |  |  |  |  | 26.2347 | 26.1937 | 26.1505 | 26.1053 | 26.0589 | 25.9611 | 25.8737 | 25.7895 | 25.7053 | 25.6253 | 25.2832 | 24.9947 | 24.6811 | 24.3189 | 24.2895 | 24.2579 | 24.2221 | 24.1863 | 24.1274 | 24.0737 | 24.02 | 23.9368 | 23.8579 | 23.5253 | 23.2516 | 22.9463 | 25.1595 | 25.11 | 25.0553 | 24.9711 | 24.8805 | 24.7511 | 24.6258 | 24.5005 | 24.3689 | 24.2384 | 23.7111 | 23.2826 | 22.9553
|  | BRUCHAG | CF |  |  |  |  | 26.2505 | 26.2221 | 26.1926 | 26.1642 | 26.1326 | 26.0853 | 26.0389 | 25.9926 | 25.9474 | 25.9063 | 25.6947 | 25.4937 | 25.3442 | 24.3295 | 24.3105 | 24.2905 | 24.2695 | 24.2463 | 24.2179 | 24.1895 | 24.1621 | 24.1326 | 24.1063 | 23.9053 | 23.7011 | 23.5495 | 25.2142 | 25.1942 | 25.1742 | 25.1532 | 25.1311 | 25.0932 | 25.0574 | 25.0216 | 24.9868 | 24.9574 | 24.7384 | 24.5216 | 24.3626
| KEITH 1 | BUCKIE | MINIMUM HEADROOM | NJ 43291 64802 | NO | YES | 0.05 | 25.1942 | 25.0005 | 24.7868 | 24.55 | 23.9953 | 22.9416 | 21.9468 | 20.9553 | 19.6542 | 18.4068 | 14.5047 | 11.5637 | 10.2879 | 23.6563 | 23.4626 | 22.9089 | 22.2163 | 21.4447 | 20.3847 | 19.3626 | 18.3311 | 16.9605 | 15.6626 | 11.8479 | 9.4984 | 8.2911 | 24.3858 | 24.1921 | 23.5984 | 22.8847 | 22.0942 | 20.9416 | 19.8563 | 18.7732 | 17.3426 | 15.9826 | 11.8163 | 8.8079 | 7.4563
|  | BUCKIE | EE |  |  |  |  | 25.27 | 25.1153 | 24.9342 | 24.7437 | 24.4721 | 23.4184 | 22.2489 | 21.2774 | 20.2647 | 19.2258 | 14.5047 | 11.5637 | 10.2879 | 23.7321 | 23.5774 | 23.2489 | 22.6395 | 21.9711 | 20.9153 | 19.7468 | 18.8026 | 17.7784 | 16.7174 | 12.0447 | 9.4984 | 8.2911 | 24.4616 | 24.3068 | 23.9468 | 23.3121 | 22.6205 | 21.47 | 20.1942 | 19.1511 | 18.0468 | 16.9121 | 11.8163 | 8.8079 | 7.4563
|  | BUCKIE | HT |  |  |  |  | 25.1942 | 25.0005 | 24.7868 | 24.55 | 23.9953 | 22.9416 | 21.9468 | 20.9553 | 19.6542 | 18.4068 | 14.5953 | 12.6363 | 11.4332 | 23.6563 | 23.4626 | 22.9089 | 22.2163 | 21.4447 | 20.3847 | 19.3626 | 18.3311 | 16.9605 | 15.6626 | 11.8479 | 9.9374 | 8.7016 | 24.3858 | 24.1921 | 23.5984 | 22.8847 | 22.0942 | 20.9416 | 19.8563 | 18.7732 | 17.3426 | 15.9826 | 11.9247 | 9.8374 | 8.5405
|  | BUCKIE | HE |  |  |  |  | 25.3774 | 25.2742 | 25.1584 | 25.0321 | 24.8837 | 24.0605 | 23.0332 | 22.1563 | 21.1111 | 20.1911 | 16.8426 | 14.9437 | 13.2963 | 23.8395 | 23.7363 | 23.6226 | 23.1995 | 22.6205 | 21.5858 | 20.5384 | 19.6616 | 18.5668 | 17.6121 | 14.2837 | 12.5721 | 11.19 | 24.3858 | 24.1921 | 23.5984 | 22.8847 | 22.0942 | 20.9416 | 19.8563 | 18.7732 | 17.3426 | 15.9826 | 11.9247 | 9.8374 | 8.5405
|  | BUCKIE | CF |  |  |  |  | 25.4363 | 25.3774 | 25.3121 | 25.2468 | 25.1784 | 24.9995 | 24.8342 | 24.6605 | 24.4616 | 23.9911 | 21.8037 | 20.4942 | 19.6953 | 23.8984 | 23.8395 | 23.7763 | 23.7121 | 23.6458 | 23.3195 | 22.9268 | 22.4847 | 22.0479 | 21.5489 | 19.2889 | 18.0732 | 17.3616 | 24.6279 | 24.5689 | 24.5037 | 24.4395 | 24.3711 | 23.9942 | 23.5679 | 23.09 | 22.6205 | 22.0921 | 19.6637 | 18.2784 | 17.4447
| FORT AUGUSTUS | BUNOICH | MINIMUM HEADROOM | NH 37662 09672 | YES | YES | 0 | 2.0263 | 2.0116 | 1.9968 | 1.9821 | 1.9674 | 1.9516 | 1.9347 | 1.9179 | 1.9021 | 1.8853 | 1.82 | 1.7621 | 1.7105 | 2.0042 | 1.9884 | 1.9726 | 1.9568 | 1.9411 | 1.9253 | 1.9063 | 1.8884 | 1.8705 | 1.8537 | 1.7821 | 1.7179 | 1.66 | 2.0253 | 2.0126 | 1.9968 | 1.9821 | 1.9663 | 1.9505 | 1.9326 | 1.9147 | 1.8979 | 1.8811 | 1.8095 | 1.7474 | 1.6895
|  | BUNOICH | EE |  |  |  |  | 2.0326 | 2.0211 | 2.0105 | 1.9979 | 1.9863 | 1.9747 | 1.9653 | 1.9516 | 1.94 | 1.9274 | 1.8716 | 1.8295 | 1.7905 | 2.0116 | 1.9989 | 1.9874 | 1.9747 | 1.9621 | 1.9495 | 1.9389 | 1.9253 | 1.9116 | 1.8989 | 1.8389 | 1.7916 | 1.7484 | 2.0284 | 2.0221 | 2.0105 | 1.9989 | 1.9863 | 1.9747 | 1.9642 | 1.9505 | 1.9379 | 1.9253 | 1.8653 | 1.82 | 1.7768
|  | BUNOICH | HT |  |  |  |  | 2.0263 | 2.0116 | 1.9968 | 1.9821 | 1.9674 | 1.9516 | 1.9347 | 1.9179 | 1.9021 | 1.8853 | 1.82 | 1.7621 | 1.7105 | 2.0042 | 1.9884 | 1.9726 | 1.9568 | 1.9411 | 1.9253 | 1.9063 | 1.8884 | 1.8705 | 1.8537 | 1.7821 | 1.7179 | 1.66 | 2.0253 | 2.0126 | 1.9968 | 1.9821 | 1.9663 | 1.9505 | 1.9326 | 1.9147 | 1.8979 | 1.8811 | 1.8095 | 1.7474 | 1.6895
|  | BUNOICH | HE |  |  |  |  | 2.04 | 2.0347 | 2.0274 | 2.0211 | 2.0137 | 2.0042 | 1.9968 | 1.9905 | 1.9832 | 1.9768 | 1.9484 | 1.9242 | 1.9042 | 2.02 | 2.0147 | 2.0053 | 1.9989 | 1.9905 | 1.9821 | 1.9737 | 1.9663 | 1.96 | 1.9526 | 1.9221 | 1.8947 | 1.8726 | 2.0253 | 2.0126 | 1.9968 | 1.9821 | 1.9663 | 1.9505 | 1.9326 | 1.9147 | 1.8979 | 1.8811 | 1.8095 | 1.7474 | 1.6895
|  | BUNOICH | CF |  |  |  |  | 2.0421 | 2.04 | 2.0379 | 2.0337 | 2.0295 | 2.0242 | 2.02 | 2.0158 | 2.0116 | 2.0063 | 1.9874 | 1.9705 | 1.9558 | 2.0221 | 2.02 | 2.0168 | 2.0126 | 2.0074 | 2.0032 | 1.9979 | 1.9926 | 1.9895 | 1.9832 | 1.9632 | 1.9453 | 1.9274 | 2.0368 | 2.0347 | 2.0316 | 2.0284 | 2.0263 | 2.0232 | 2.0211 | 2.0168 | 2.0126 | 2.0074 | 1.9874 | 1.9695 | 1.9537
| THURSO | BURGARHILL | MINIMUM HEADROOM | HY 34441 26078 | YES | YES | 0 | -1.5074 | -1.5379 | -1.5684 | -1.6011 | -1.6337 | -1.6821 | -1.7295 | -3.7221 | -3.7632 | -3.8032 | -3.9621 | -4.0989 | -4.9389 | -1.7642 | -1.8189 | -1.8726 | -1.9326 | -1.9895 | -2.0621 | -2.1253 | -3.6947 | -3.74 | -3.7842 | -3.9526 | -4.1095 | -4.7979 | -3.5147 | -3.5695 | -3.6242 | -3.6874 | -3.7442 | -3.8221 | -3.8895 | -4.7116 | -4.7347 | -4.7558 | -4.8758 | -4.9853 | -6.1811
|  | BURGARHILL | EE |  |  |  |  | -1.4958 | -1.52 | -1.5463 | -1.5737 | -1.6032 | -1.6495 | -1.6989 | -1.7232 | -1.7663 | -1.8105 | -2.0189 | -2.4042 | -3.8095 | -1.7411 | -1.7832 | -1.8263 | -1.8779 | -1.9263 | -1.9905 | -2.0632 | -2.1011 | -2.1547 | -2.2147 | -2.4968 | -2.8453 | -3.9979 | -3.4905 | -3.5337 | -3.5779 | -3.6295 | -3.6811 | -3.7505 | -3.8295 | -3.8674 | -3.9263 | -3.9926 | -4.3042 | -4.7053 | -6.1126
|  | BURGARHILL | HT |  |  |  |  | -1.5074 | -1.5379 | -1.5684 | -1.6011 | -1.6337 | -1.6821 | -1.7295 | -1.7611 | -1.8095 | -1.8589 | -2.0768 | -2.5463 | -3.8463 | -1.7642 | -1.8189 | -1.8726 | -1.9326 | -1.9895 | -2.0621 | -2.1253 | -2.1789 | -2.2495 | -2.3168 | -2.5789 | -3.0053 | -4.0926 | -3.5147 | -3.5695 | -3.6242 | -3.6874 | -3.7442 | -3.8221 | -3.8895 | -3.9442 | -4.02 | -4.0926 | -4.3758 | -4.8674 | -6.1811
|  | BURGARHILL | HE |  |  |  |  | -1.4789 | -1.4937 | -1.5116 | -1.5316 | -1.5505 | -1.5716 | -1.6063 | -3.7221 | -3.7632 | -3.8032 | -3.9621 | -4.0989 | -4.9389 | -1.7074 | -1.7326 | -1.7611 | -1.7884 | -1.8168 | -1.8516 | -1.9021 | -3.6947 | -3.74 | -3.7842 | -3.9526 | -4.1095 | -4.7979 | -3.5147 | -3.5695 | -3.6242 | -3.6874 | -3.7442 | -3.8221 | -3.8895 | -3.9442 | -4.02 | -4.0926 | -4.3758 | -4.8674 | -6.1811
|  | BURGARHILL | CF |  |  |  |  | -1.4695 | -1.4789 | -1.4884 | -1.4989 | -1.5084 | -1.5189 | -1.5347 | -2.5811 | -2.5989 | -2.6158 | -2.7063 | -2.7905 | -2.8537 | -1.6905 | -1.7063 | -1.7221 | -1.7389 | -1.7568 | -1.7758 | -1.8032 | -2.7379 | -2.76 | -2.78 | -2.8895 | -2.9874 | -3.0705 | -3.4379 | -3.4547 | -3.4705 | -3.4884 | -3.5063 | -3.5253 | -3.5547 | -4.7116 | -4.7347 | -4.7558 | -4.8758 | -4.9853 | -5.0758
| ELGIN | BURGHEAD | MINIMUM HEADROOM | NJ 12666 68781 | NO | YES | 0 | 17.4279 | 17.3279 | 17.21 | 17.0532 | 16.8132 | 16.3963 | 15.9921 | 15.5921 | 15.1595 | 14.7258 | 12.7711 | 10.8837 | 9.2826 | 15.9726 | 15.7716 | 15.5284 | 15.2758 | 15.0116 | 14.6147 | 14.2326 | 13.8547 | 13.4579 | 13.0589 | 11.4147 | 9.7642 | 8.1189 | 16.9466 | 16.8055 | 16.5803 | 16.3455 | 16.1003 | 15.675 | 15.2603 | 14.8382 | 14.3876 | 13.935 | 11.9329 | 9.9855 | 8.1982
|  | BURGHEAD | EE |  |  |  |  | 17.4689 | 17.39 | 17.29 | 17.1847 | 17.0426 | 16.6163 | 16.1405 | 15.6879 | 15.3005 | 14.9216 | 12.7711 | 10.8837 | 9.2826 | 16.0558 | 15.8958 | 15.7011 | 15.4947 | 15.2747 | 14.8821 | 14.4516 | 14.0495 | 13.7074 | 13.3716 | 11.4147 | 9.7642 | 8.1189 | 17.0034 | 16.8929 | 16.735 | 16.5424 | 16.335 | 15.8992 | 15.4161 | 14.9539 | 14.5592 | 14.1739 | 11.9329 | 9.9855 | 8.1982
|  | BURGHEAD | HT |  |  |  |  | 17.4279 | 17.3279 | 17.21 | 17.0532 | 16.8132 | 16.3963 | 15.9921 | 15.5921 | 15.1595 | 14.7258 | 13.0616 | 11.61 | 10.3037 | 15.9726 | 15.7716 | 15.5284 | 15.2758 | 15.0116 | 14.6147 | 14.2326 | 13.8547 | 13.4579 | 13.0589 | 11.5221 | 10.06 | 8.6126 | 16.9466 | 16.8055 | 16.5803 | 16.3455 | 16.1003 | 15.675 | 15.2603 | 14.8382 | 14.3876 | 13.935 | 12.1897 | 10.6013 | 9.1045
|  | BURGHEAD | HE |  |  |  |  | 17.5268 | 17.4742 | 17.4142 | 17.3468 | 17.2753 | 16.95 | 16.5795 | 16.2268 | 15.8995 | 15.5837 | 14.13 | 12.59 | 10.6732 | 16.1695 | 16.0642 | 15.9284 | 15.7747 | 15.6042 | 15.2379 | 14.8968 | 14.5779 | 14.2874 | 14.0053 | 12.6905 | 11.2495 | 9.4 | 16.9466 | 16.8055 | 16.5803 | 16.3455 | 16.1003 | 15.675 | 15.2603 | 14.8382 | 14.3876 | 13.935 | 12.1897 | 10.6013 | 9.1045
|  | BURGHEAD | CF |  |  |  |  | 17.5574 | 17.5279 | 17.4953 | 17.4605 | 17.4258 | 17.3047 | 17.1942 | 17.0837 | 16.9879 | 16.9089 | 16.0942 | 15.1489 | 14.0163 | 16.2284 | 16.1674 | 16.0968 | 16.0211 | 15.9432 | 15.7937 | 15.6453 | 15.4905 | 15.3642 | 15.2516 | 14.4484 | 13.5653 | 12.3789 | 17.1266 | 17.0834 | 17.0361 | 16.9845 | 16.9329 | 16.7918 | 16.635 | 16.4687 | 16.3318 | 16.2129 | 15.3634 | 14.3855 | 13.1139
| BURGHMUIR | BURGHMUIR | MINIMUM HEADROOM | NO 08256 23702 | NO | YES | 1.468 | 12.5854 | 12.2791 | 11.8907 | 11.3802 | 10.7875 | 9.9002 | 9.0991 | 8.2928 | 7.3633 | 6.2917 | 1.6917 | -2.5167 | -6.1777 | 10.4699 | 10.0899 | 9.5941 | 8.9836 | 8.3267 | 7.4299 | 6.6278 | 5.8173 | 4.8846 | 3.7825 | -1.0469 | -5.248 | -8.9617 | 11.3898 | 11.0677 | 10.6056 | 10.0413 | 9.4371 | 8.5308 | 7.7171 | 6.8508 | 5.8508 | 4.6834 | -0.39129 | -4.9081 | -9.0671
|  | BURGHMUIR | EE |  |  |  |  | 12.7223 | 12.4938 | 12.2128 | 11.8844 | 11.5033 | 10.6728 | 9.6854 | 8.9328 | 8.2338 | 7.4938 | 2.6402 | -2.5167 | -6.1777 | 10.6436 | 10.3594 | 10.0099 | 9.5867 | 9.1267 | 8.3067 | 7.3215 | 6.6204 | 5.9573 | 5.2467 | 0.36253 | -4.8827 | -8.9448 | 11.4782 | 11.3192 | 10.9887 | 10.594 | 10.1656 | 9.3182 | 8.3077 | 7.5413 | 6.8266 | 6.0392 | 0.75608 | -4.9081 | -9.0671
|  | BURGHMUIR | HT |  |  |  |  | 12.5854 | 12.2791 | 11.8907 | 11.3802 | 10.7875 | 9.9002 | 9.0991 | 8.2928 | 7.3633 | 6.2917 | 1.6917 | -2.1756 | -5.4251 | 10.4699 | 10.0899 | 9.5941 | 8.9836 | 8.3267 | 7.4299 | 6.6278 | 5.8173 | 4.8846 | 3.7825 | -1.0469 | -5.248 | -8.9617 | 11.3898 | 11.0677 | 10.6056 | 10.0413 | 9.4371 | 8.5308 | 7.7171 | 6.8508 | 5.8508 | 4.6834 | -0.39129 | -4.725 | -8.4902
|  | BURGHMUIR | HE |  |  |  |  | 12.8612 | 12.7496 | 12.5538 | 12.2959 | 12.0054 | 11.1907 | 10.3159 | 9.6075 | 8.837 | 7.9812 | 4.0044 | 0.32016 | -3.3504 | 10.8088 | 10.6888 | 10.4352 | 10.0846 | 9.6857 | 8.8488 | 7.9499 | 7.2478 | 6.4699 | 5.5878 | 1.4709 | -2.3691 | -6.1691 | 11.3898 | 11.0677 | 10.6056 | 10.0413 | 9.4371 | 8.5308 | 7.7171 | 6.8508 | 5.8508 | 4.6834 | -0.39129 | -4.725 | -8.4902
|  | BURGHMUIR | CF |  |  |  |  | 12.9212 | 12.8612 | 12.7907 | 12.6833 | 12.5675 | 12.3181 | 12.0654 | 11.7981 | 11.5654 | 11.3265 | 9.1254 | 6.3507 | 3.8686 | 10.872 | 10.812 | 10.7352 | 10.5994 | 10.4509 | 10.1952 | 9.9204 | 9.6173 | 9.3594 | 9.0678 | 6.7173 | 3.7457 | 1.0246 | 11.6371 | 11.5792 | 11.5161 | 11.4487 | 11.3792 | 11.1277 | 10.8424 | 10.5319 | 10.2666 | 9.9824 | 7.6961 | 4.5856 | 1.7729
| CLACHAN | BUTTERBRIDGE | MINIMUM HEADROOM | NN 19306 09936 | YES | YES | 0 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.093684 | 0.090526 | 0.085263 | 0.082105 | 0.075789 | 0.041053 | -0.0042105 | -0.043158 | 0.097895 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.092632 | 0.090526 | 0.085263 | 0.082105 | 0.075789 | 0.038947 | -0.012632 | -0.049474 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.092632 | 0.090526 | 0.086316 | 0.083158 | 0.075789 | 0.034737 | -0.017895 | -0.058947
|  | BUTTERBRIDGE | EE |  |  |  |  | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.093684 | 0.091579 | 0.086316 | 0.084211 | 0.08 | 0.041053 | -0.0042105 | -0.043158 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.095789 | 0.092632 | 0.090526 | 0.087368 | 0.085263 | 0.082105 | 0.043158 | -0.0031579 | -0.046316 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.093684 | 0.090526 | 0.086316 | 0.083158 | 0.08 | 0.036842 | -0.013684 | -0.058947
|  | BUTTERBRIDGE | HT |  |  |  |  | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.093684 | 0.092632 | 0.088421 | 0.085263 | 0.077895 | 0.041053 | -0.0042105 | -0.036842 | 0.097895 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.092632 | 0.091579 | 0.088421 | 0.086316 | 0.077895 | 0.038947 | -0.012632 | -0.049474 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.092632 | 0.091579 | 0.088421 | 0.085263 | 0.075789 | 0.034737 | -0.017895 | -0.055789
|  | BUTTERBRIDGE | HE |  |  |  |  | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.094737 | 0.090526 | 0.085263 | 0.082105 | 0.075789 | 0.048421 | 0.011579 | -0.027368 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.093684 | 0.090526 | 0.085263 | 0.082105 | 0.075789 | 0.048421 | 0.0094737 | -0.032632 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.092632 | 0.091579 | 0.088421 | 0.085263 | 0.075789 | 0.034737 | -0.017895 | -0.055789
|  | BUTTERBRIDGE | CF |  |  |  |  | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.095789 | 0.093684 | 0.091579 | 0.087368 | 0.071579 | 0.049474 | 0.023158 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.092632 | 0.089474 | 0.086316 | 0.070526 | 0.046316 | 0.017895 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.092632 | 0.090526 | 0.086316 | 0.069474 | 0.044211 | 0.013684
| BRACO | CALLANDER | MINIMUM HEADROOM | NN 62995 07081 | NO | YES | 0 | 8.5042 | 8.3495 | 8.1653 | 7.9358 | 7.6842 | 7.4021 | 7.12 | 6.8253 | 6.5368 | 6.2474 | 4.8274 | 3.5684 | 2.3968 | 7.0495 | 6.8695 | 6.6632 | 6.4053 | 6.1179 | 5.7989 | 5.4789 | 5.1421 | 4.8158 | 4.4863 | 2.8726 | 1.4221 | 0.064211 | 8.2505 | 8.0874 | 7.88 | 7.6211 | 7.3316 | 7.0126 | 6.6916 | 6.3537 | 6.0232 | 5.6926 | 4.0621 | 2.6063 | 1.2463
|  | CALLANDER | EE |  |  |  |  | 8.5568 | 8.4389 | 8.2842 | 8.0905 | 7.8726 | 7.6326 | 7.4011 | 7.1432 | 6.9021 | 6.6589 | 5.4242 | 4.3453 | 3.3589 | 7.1179 | 6.9705 | 6.8021 | 6.5863 | 6.3432 | 6.0747 | 5.8168 | 5.5274 | 5.2547 | 4.9811 | 3.5926 | 2.3663 | 1.24 | 8.3095 | 8.18 | 8.0116 | 7.7926 | 7.5453 | 7.2705 | 7.0074 | 6.7116 | 6.4337 | 6.1547 | 4.7358 | 3.4895 | 2.3453
|  | CALLANDER | HT |  |  |  |  | 8.5042 | 8.3495 | 8.1653 | 7.9358 | 7.6842 | 7.4021 | 7.12 | 6.8253 | 6.5368 | 6.2474 | 4.8274 | 3.5684 | 2.3968 | 7.0495 | 6.8695 | 6.6632 | 6.4053 | 6.1179 | 5.7989 | 5.4789 | 5.1421 | 4.8158 | 4.4863 | 2.8726 | 1.4221 | 0.064211 | 8.2505 | 8.0874 | 7.88 | 7.6211 | 7.3316 | 7.0126 | 6.6916 | 6.3537 | 6.0232 | 5.6926 | 4.0621 | 2.6063 | 1.2463
|  | CALLANDER | HE |  |  |  |  | 8.6274 | 8.5505 | 8.4526 | 8.3021 | 8.1232 | 7.9179 | 7.7274 | 7.5063 | 7.2979 | 7.0863 | 6.0726 | 5.1432 | 4.2863 | 7.2095 | 7.1084 | 6.9821 | 6.8116 | 6.6074 | 6.3758 | 6.1589 | 5.9053 | 5.6642 | 5.4232 | 4.2474 | 3.1768 | 2.1884 | 8.2505 | 8.0874 | 7.88 | 7.6211 | 7.3316 | 7.0126 | 6.6916 | 6.3537 | 6.0232 | 5.6926 | 4.0621 | 2.6063 | 1.2463
|  | CALLANDER | CF |  |  |  |  | 8.6653 | 8.6211 | 8.5716 | 8.5116 | 8.4347 | 8.3432 | 8.2526 | 8.1484 | 8.0411 | 7.9284 | 7.3105 | 6.7579 | 6.2579 | 7.2589 | 7.2 | 7.1316 | 7.0495 | 6.9568 | 6.8547 | 6.7505 | 6.6326 | 6.5095 | 6.3779 | 5.6611 | 5.0126 | 4.4211 | 8.4305 | 8.38 | 8.3232 | 8.2547 | 8.1747 | 8.0716 | 7.9663 | 7.8484 | 7.7253 | 7.5926 | 6.8726 | 6.2221 | 5.6295
| STORNOWAY | CALLANISH | MINIMUM HEADROOM | NB 22040 33554 | YES | YES | 0 | 2.0526 | 2.02 | 1.9874 | 1.9537 | 1.9189 | 1.8821 | 1.8463 | 1.8126 | 1.7789 | 1.7337 | 1.5368 | 0.59579 | 0.45789 | 2.08 | 2.0474 | 2.0147 | 1.9684 | 1.9074 | 1.8442 | 1.7842 | 1.7263 | 1.6705 | 1.6168 | 1.4032 | 0.61263 | 0.46211 | 2.0558 | 2 | 1.9379 | 1.8758 | 1.8147 | 1.7537 | 1.6937 | 1.6368 | 1.5811 | 1.5284 | 1.3168 | 0.32526 | 0.17368
|  | CALLANISH | EE |  |  |  |  | 2.0632 | 2.0368 | 2.0095 | 1.9811 | 1.9516 | 1.9211 | 1.8926 | 1.8642 | 1.8379 | 1.8126 | 1.6905 | 0.78737 | 0.68842 | 2.0905 | 2.0642 | 2.0368 | 2.0084 | 1.9789 | 1.9337 | 1.8863 | 1.8389 | 1.7958 | 1.7537 | 1.5716 | 0.81789 | 0.71263 | 2.0737 | 2.0358 | 1.9905 | 1.9411 | 1.8905 | 1.8411 | 1.7937 | 1.7474 | 1.7042 | 1.6621 | 1.4832 | 0.53474 | 0.42632
|  | CALLANISH | HT |  |  |  |  | 2.0526 | 2.02 | 1.9874 | 1.9537 | 1.9189 | 1.8821 | 1.8463 | 1.8126 | 1.7789 | 1.7337 | 1.5368 | 0.59579 | 0.45789 | 2.08 | 2.0474 | 2.0147 | 1.9684 | 1.9074 | 1.8442 | 1.7842 | 1.7263 | 1.6705 | 1.6168 | 1.4032 | 0.61263 | 0.46211 | 2.0558 | 2 | 1.9379 | 1.8758 | 1.8147 | 1.7537 | 1.6937 | 1.6368 | 1.5811 | 1.5284 | 1.3168 | 0.32526 | 0.17368
|  | CALLANISH | HE |  |  |  |  | 2.0821 | 2.0642 | 2.0453 | 2.0242 | 2.0021 | 1.9789 | 1.9579 | 1.9368 | 1.9168 | 1.8989 | 1.8389 | 1.4526 | 1.4368 | 2.1095 | 2.0916 | 2.0726 | 2.0516 | 2.0295 | 2.0063 | 1.9853 | 1.9642 | 1.9442 | 1.9263 | 1.8411 | 1.4674 | 1.4158 | 2.0558 | 2 | 1.9379 | 1.8758 | 1.8147 | 1.7537 | 1.6937 | 1.6368 | 1.5811 | 1.5284 | 1.3168 | 0.32526 | 0.17368
|  | CALLANISH | CF |  |  |  |  | 2.0916 | 2.0821 | 2.0716 | 2.0611 | 2.0505 | 2.0389 | 2.0284 | 2.0168 | 2.0063 | 1.9947 | 1.9474 | 1.9242 | 1.9126 | 2.1189 | 2.1095 | 2.0989 | 2.0884 | 2.0779 | 2.0663 | 2.0558 | 2.0442 | 2.0337 | 2.0221 | 1.9747 | 1.9189 | 1.8737 | 2.1063 | 2.0968 | 2.0863 | 2.0747 | 2.06 | 2.0432 | 2.0284 | 2.0126 | 1.9958 | 1.9747 | 1.8874 | 1.8274 | 1.7821
| TUMMEL BRIDGE | CALVINE | MINIMUM HEADROOM | NN 80186 65270 | YES | YES | 0.144 | 0.73284 | 0.71284 | 0.69179 | 0.67179 | 0.64968 | 0.59705 | 0.54547 | 0.48232 | 0.42442 | 0.36653 | -0.097684 | -0.74189 | -1.2661 | 0.97705 | 0.96758 | 0.95705 | 0.94547 | 0.93495 | 0.90653 | 0.88337 | 0.85705 | 0.81495 | 0.77074 | 0.376 | -0.31663 | -0.80926 | 0.72968 | 0.71074 | 0.68968 | 0.66968 | 0.64758 | 0.596 | 0.54653 | 0.48653 | 0.43179 | 0.37705 | -0.089263 | -0.77032 | -1.3293
|  | CALVINE | EE |  |  |  |  | 0.736 | 0.72337 | 0.70758 | 0.68863 | 0.66968 | 0.61179 | 0.54968 | 0.48232 | 0.42442 | 0.36653 | -0.097684 | -0.74189 | -1.2661 | 0.98021 | 0.97179 | 0.96442 | 0.956 | 0.94547 | 0.91811 | 0.88863 | 0.85705 | 0.81495 | 0.77074 | 0.41705 | -0.22611 | -0.79874 | 0.73389 | 0.72126 | 0.70547 | 0.68547 | 0.66547 | 0.60968 | 0.55074 | 0.48653 | 0.43179 | 0.37705 | -0.086105 | -0.75032 | -1.3293
|  | CALVINE | HT |  |  |  |  | 0.73284 | 0.71284 | 0.69179 | 0.67179 | 0.64968 | 0.59705 | 0.54547 | 0.49284 | 0.43495 | 0.37389 | -0.087158 | -0.72189 | -1.1598 | 0.97705 | 0.96758 | 0.95705 | 0.94547 | 0.93495 | 0.90653 | 0.88337 | 0.85705 | 0.82547 | 0.77811 | 0.376 | -0.31663 | -0.80926 | 0.72968 | 0.71074 | 0.68968 | 0.66968 | 0.64758 | 0.596 | 0.54653 | 0.496 | 0.44021 | 0.38337 | -0.089263 | -0.77032 | -1.2587
|  | CALVINE | HE |  |  |  |  | 0.74021 | 0.73495 | 0.72863 | 0.72232 | 0.71074 | 0.65811 | 0.61179 | 0.56547 | 0.52126 | 0.46863 | 0.066526 | -0.43874 | -0.98926 | 0.98442 | 0.98021 | 0.97495 | 0.96968 | 0.96232 | 0.93705 | 0.91495 | 0.89284 | 0.87284 | 0.85074 | 0.55179 | 0.026526 | -0.54611 | 0.72968 | 0.71074 | 0.68968 | 0.66968 | 0.64758 | 0.596 | 0.54653 | 0.496 | 0.44021 | 0.38337 | -0.089263 | -0.77032 | -1.2587
|  | CALVINE | CF |  |  |  |  | 0.74337 | 0.74021 | 0.73811 | 0.73389 | 0.73074 | 0.71074 | 0.69179 | 0.67179 | 0.65495 | 0.63916 | 0.45705 | 0.136 | -0.22505 | 0.98758 | 0.98442 | 0.98232 | 0.98021 | 0.97705 | 0.96547 | 0.95705 | 0.94758 | 0.94021 | 0.93284 | 0.86653 | 0.57179 | 0.18021 | 0.74126 | 0.73811 | 0.736 | 0.73179 | 0.72863 | 0.70863 | 0.69074 | 0.67179 | 0.65495 | 0.64126 | 0.46337 | 0.12968 | -0.25032
| CARRADALE 1 | CAMPBELTOWN | MINIMUM HEADROOM | NR 71509 20746 | NO | YES | 0 | 14.5837 | 14.4574 | 14.2479 | 14.0216 | 13.6953 | 13.3226 | 12.9542 | 10.6068 | 10.2805 | 9.9847 | 8.8837 | 8.0132 | 7.4268 | 13.6611 | 13.4274 | 13.1853 | 12.9463 | 12.5947 | 12.2032 | 11.8179 | 10.1526 | 9.8011 | 9.4905 | 8.5147 | 7.7305 | 7.1547 | 13.4834 | 13.2455 | 12.9961 | 12.7529 | 12.3939 | 11.9887 | 11.5866 | 9.2266 | 8.8718 | 8.5529 | 7.3813 | 6.4561 | 5.815
|  | CAMPBELTOWN | EE |  |  |  |  | 14.6279 | 14.5142 | 14.3837 | 14.1679 | 13.8942 | 13.5174 | 13.1016 | 10.6068 | 10.2805 | 9.9847 | 8.8837 | 8.0132 | 7.4268 | 13.7589 | 13.56 | 13.3526 | 13.1389 | 12.8579 | 12.4768 | 12.0505 | 10.1526 | 9.8274 | 9.5379 | 8.5147 | 7.7305 | 7.1726 | 13.5824 | 13.3666 | 13.1424 | 12.9108 | 12.6118 | 12.1982 | 11.7424 | 9.2266 | 8.8718 | 8.5529 | 7.3813 | 6.4561 | 5.815
|  | CAMPBELTOWN | HT |  |  |  |  | 14.5837 | 14.4574 | 14.2479 | 14.0216 | 13.6953 | 13.3226 | 12.9542 | 10.8595 | 10.4963 | 10.1921 | 9.2489 | 8.49 | 7.8721 | 13.6611 | 13.4274 | 13.1853 | 12.9463 | 12.5947 | 12.2032 | 11.8179 | 10.1779 | 9.8011 | 9.4905 | 8.5611 | 7.7958 | 7.1547 | 13.4834 | 13.2455 | 12.9961 | 12.7529 | 12.3939 | 11.9887 | 11.5866 | 9.4634 | 9.0697 | 8.7413 | 7.7382 | 6.9182 | 6.2413
|  | CAMPBELTOWN | HE |  |  |  |  | 14.6837 | 14.6142 | 14.5374 | 14.4542 | 14.31 | 13.9784 | 13.6237 | 12.2711 | 12.0311 | 11.8511 | 11.2668 | 10.8058 | 10.4258 | 13.8874 | 13.7642 | 13.6274 | 13.4884 | 13.2611 | 12.9147 | 12.5379 | 11.4716 | 11.2295 | 11.0526 | 10.5179 | 10.1032 | 9.7653 | 13.4834 | 13.2455 | 12.9961 | 12.7529 | 12.3939 | 11.9887 | 11.5866 | 9.4634 | 9.0697 | 8.7413 | 7.7382 | 6.9182 | 6.2413
|  | CAMPBELTOWN | CF |  |  |  |  | 14.7132 | 14.6732 | 14.6311 | 14.5879 | 14.5458 | 14.4816 | 14.4047 | 13.1637 | 13.0184 | 12.8753 | 12.3963 | 12.0721 | 11.8511 | 13.9474 | 13.8737 | 13.7958 | 13.72 | 13.6274 | 13.5 | 13.3611 | 12.4032 | 12.2505 | 12.0968 | 11.6042 | 11.2937 | 11.0737 | 13.7708 | 13.6961 | 13.6161 | 13.5403 | 13.4445 | 13.3108 | 13.1645 | 11.9108 | 11.7518 | 11.595 | 11.0782 | 10.735 | 10.495
| COUPAR ANGUS | CAPUTH | MINIMUM HEADROOM | NO 09277 40265 | NO | YES | 0.05 | 12.9889 | 12.8742 | 12.6384 | 12.4026 | 12.1416 | 10.9963 | 9.5384 | 7.9911 | 6.6226 | 4.9311 | -7.4974 | -21.7195 | -32.2911 | 12.17 | 11.9742 | 11.7353 | 11.4942 | 11.2289 | 10.2374 | 9.1037 | 7.8289 | 6.6763 | 4.6742 | -6.7195 | -20.6153 | -32.0511 | 12.3153 | 12.1268 | 11.8805 | 11.6289 | 11.3532 | 10.1468 | 8.6026 | 7.0026 | 5.6047 | 3.9774 | -9.5626 | -24.9942 | -36.8111
|  | CAPUTH | EE |  |  |  |  | 13.0289 | 12.95 | 12.7826 | 12.5647 | 12.3268 | 11.0247 | 9.5384 | 7.9911 | 6.6226 | 5.2332 | -7.4974 | -21.7195 | -32.2911 | 12.2479 | 12.1079 | 11.8995 | 11.6889 | 11.4542 | 10.3511 | 9.1037 | 7.8289 | 6.6763 | 5.5058 | -6.7195 | -20.6153 | -32.0511 | 12.3553 | 12.2542 | 12.03 | 11.8026 | 11.55 | 10.1742 | 8.6026 | 7.0026 | 5.6047 | 4.1837 | -9.5626 | -24.9942 | -36.8111
|  | CAPUTH | HT |  |  |  |  | 12.9889 | 12.8742 | 12.6384 | 12.4026 | 12.1416 | 10.9963 | 9.8942 | 8.7795 | 7.4542 | 5.1679 | -6.3553 | -19.15 | -27.7995 | 12.17 | 11.9742 | 11.7353 | 11.4942 | 11.2289 | 10.2374 | 9.2847 | 8.3247 | 7.2174 | 5.0026 | -6.7016 | -20.5247 | -30.1942 | 12.3153 | 12.1268 | 11.8805 | 11.6289 | 11.3532 | 10.1468 | 8.9847 | 7.8121 | 6.4405 | 3.9774 | -8.6395 | -23.0258 | -32.9763
|  | CAPUTH | HE |  |  |  |  | 13.0837 | 13.0321 | 12.9658 | 12.8911 | 12.81 | 11.4289 | 9.97 | 8.4668 | 7.0195 | 4.9311 | -3.9447 | -14.8342 | -26.6805 | 12.3058 | 12.2532 | 12.1795 | 12.0668 | 11.9258 | 10.7458 | 9.4037 | 8.0237 | 6.7216 | 4.6742 | -3.8784 | -14.9068 | -26.9289 | 12.3153 | 12.1268 | 11.8805 | 11.6289 | 11.3532 | 10.1468 | 8.9847 | 7.8121 | 6.4405 | 3.9774 | -8.6395 | -23.0258 | -32.9763
|  | CAPUTH | CF |  |  |  |  | 13.1132 | 13.0837 | 13.0437 | 13.0037 | 12.9626 | 12.5258 | 12.0668 | 11.3637 | 10.4774 | 9.4932 | 4.9616 | -1.8921 | -9.3995 | 12.3363 | 12.3058 | 12.2711 | 12.2353 | 12.1626 | 11.7258 | 11.3321 | 10.6521 | 9.7405 | 8.6784 | 4.1016 | -2.8858 | -10.9047 | 12.4395 | 12.4089 | 12.37 | 12.33 | 12.2889 | 11.7553 | 11.2689 | 10.5153 | 9.5353 | 8.4311 | 3.4637 | -4.0595 | -12.4742
| ARBROATH | CARNOUSTIE | MINIMUM HEADROOM | NO 55631 35403 | NO | YES | 0.076 | 16.1308 | 15.9498 | 15.7572 | 15.4824 | 15.1519 | 14.7298 | 14.3172 | 13.9161 | 13.5003 | 13.0929 | 11.4856 | 10.2677 | 9.3456 | 14.9272 | 14.364 | 13.8314 | 13.4766 | 13.124 | 12.7008 | 12.2903 | 11.8903 | 11.4798 | 11.0787 | 9.4745 | 8.2261 | 7.2366 | 15.5811 | 15.079 | 14.5664 | 14.2095 | 13.8558 | 13.4095 | 12.9758 | 12.5516 | 12.1137 | 11.6832 | 9.9716 | 8.6516 | 7.6327
|  | CARNOUSTIE | EE |  |  |  |  | 16.2035 | 16.0603 | 15.9024 | 15.7361 | 15.5098 | 15.1203 | 14.7203 | 14.3351 | 13.9835 | 13.6382 | 11.9529 | 10.4803 | 9.6508 | 15.1387 | 14.6556 | 14.184 | 13.8345 | 13.5103 | 13.1282 | 12.7408 | 12.3714 | 12.0314 | 11.6977 | 10.1019 | 8.7356 | 7.8882 | 15.6537 | 15.3601 | 14.9043 | 14.5653 | 14.2411 | 13.8306 | 13.4095 | 13.0053 | 12.6358 | 12.2727 | 10.5179 | 8.9779 | 8.0737
|  | CARNOUSTIE | HT |  |  |  |  | 16.1308 | 15.9498 | 15.7572 | 15.4824 | 15.1519 | 14.7298 | 14.3172 | 13.9161 | 13.5003 | 13.0929 | 11.4856 | 10.2677 | 9.3456 | 14.9272 | 14.364 | 13.8314 | 13.4766 | 13.124 | 12.7008 | 12.2903 | 11.8903 | 11.4798 | 11.0787 | 9.4745 | 8.2261 | 7.2366 | 15.5811 | 15.079 | 14.5664 | 14.2095 | 13.8558 | 13.4095 | 12.9758 | 12.5516 | 12.1137 | 11.6832 | 9.9716 | 8.6516 | 7.6327
|  | CARNOUSTIE | HE |  |  |  |  | 16.3035 | 16.2087 | 16.1024 | 15.9877 | 15.8656 | 15.6193 | 15.4024 | 15.1887 | 14.9624 | 14.7172 | 13.6624 | 12.8351 | 12.0698 | 15.2861 | 14.9787 | 14.5903 | 14.3493 | 14.1387 | 13.8419 | 13.5798 | 13.3251 | 13.0798 | 12.8451 | 11.8503 | 11.0987 | 10.4219 | 15.5811 | 15.079 | 14.5664 | 14.2095 | 13.8558 | 13.4095 | 12.9758 | 12.5516 | 12.1137 | 11.6832 | 9.9716 | 8.6516 | 7.6327
|  | CARNOUSTIE | CF |  |  |  |  | 16.3582 | 16.3024 | 16.2435 | 16.1845 | 16.1224 | 16.0182 | 15.9172 | 15.8182 | 15.7235 | 15.6393 | 15.1929 | 14.6614 | 14.2361 | 15.3451 | 15.284 | 15.1682 | 15.0282 | 14.8819 | 14.7061 | 14.5251 | 14.3451 | 14.1893 | 14.0398 | 13.3535 | 12.7924 | 12.3787 | 15.8085 | 15.7527 | 15.6948 | 15.6348 | 15.5737 | 15.3916 | 15.2043 | 15.019 | 14.859 | 14.7074 | 13.9864 | 13.3674 | 12.9137
| KILLIN | CASHLIE | MINIMUM HEADROOM | NN 50711 42144 | YES | YES | 0 | 1.0242 | 1.0221 | 1.02 | 1.0158 | 1.0126 | 1 | 0.98842 | 0.97474 | 0.96105 | 0.94737 | 0.88632 | 0.81895 | 0.78737 | 1.0168 | 1.0147 | 1.0116 | 1.0032 | 0.99579 | 0.98316 | 0.97158 | 0.95895 | 0.94737 | 0.93368 | 0.88 | 0.82632 | 0.79579 | 1.0179 | 1.0137 | 1.0074 | 0.99789 | 0.99053 | 0.97579 | 0.96316 | 0.94947 | 0.93474 | 0.92 | 0.85895 | 0.78947 | 0.75579
|  | CASHLIE | EE |  |  |  |  | 1.0253 | 1.0232 | 1.02 | 1.0189 | 1.0158 | 1.0074 | 0.99579 | 0.98105 | 0.96842 | 0.95474 | 0.88632 | 0.81895 | 0.78737 | 1.0179 | 1.0158 | 1.0137 | 1.0126 | 1.0074 | 0.99474 | 0.98211 | 0.96842 | 0.95789 | 0.94632 | 0.88526 | 0.82632 | 0.79579 | 1.02 | 1.0168 | 1.0116 | 1.0074 | 1.0011 | 0.98737 | 0.97158 | 0.95684 | 0.94421 | 0.92947 | 0.85895 | 0.78947 | 0.75579
|  | CASHLIE | HT |  |  |  |  | 1.0242 | 1.0221 | 1.02 | 1.0158 | 1.0126 | 1 | 0.98842 | 0.97474 | 0.96105 | 0.94737 | 0.88947 | 0.84632 | 0.81789 | 1.0168 | 1.0147 | 1.0116 | 1.0032 | 0.99579 | 0.98316 | 0.97158 | 0.95895 | 0.94737 | 0.93368 | 0.88 | 0.83789 | 0.80842 | 1.0179 | 1.0137 | 1.0074 | 0.99789 | 0.99053 | 0.97579 | 0.96316 | 0.94947 | 0.93474 | 0.92 | 0.85895 | 0.81263 | 0.78105
|  | CASHLIE | HE |  |  |  |  | 1.0263 | 1.0253 | 1.0242 | 1.0232 | 1.0211 | 1.0116 | 1.0032 | 0.99579 | 0.98842 | 0.98105 | 0.93789 | 0.89789 | 0.85579 | 1.0189 | 1.0179 | 1.0168 | 1.0158 | 1.0137 | 1.0084 | 1.0021 | 0.99263 | 0.98526 | 0.97579 | 0.93579 | 0.90211 | 0.86421 | 1.0179 | 1.0137 | 1.0074 | 0.99789 | 0.99053 | 0.97579 | 0.96316 | 0.94947 | 0.93474 | 0.92 | 0.85895 | 0.81263 | 0.78105
|  | CASHLIE | CF |  |  |  |  | 1.0274 | 1.0263 | 1.0263 | 1.0253 | 1.0242 | 1.0211 | 1.0179 | 1.0137 | 1.0116 | 1.0084 | 0.99368 | 0.97263 | 0.95158 | 1.02 | 1.0189 | 1.0189 | 1.0179 | 1.0168 | 1.0158 | 1.0126 | 1.0105 | 1.0095 | 1.0063 | 0.98632 | 0.96421 | 0.94526 | 1.0232 | 1.0221 | 1.0211 | 1.02 | 1.0189 | 1.0147 | 1.0105 | 1.0063 | 1.0021 | 0.99789 | 0.97474 | 0.94842 | 0.92632
| KILLIN | CHAORACH | MINIMUM HEADROOM | NN 45400 27553 | YES | YES | 0 | -2.0526 | -2.0537 | -2.0558 | -2.0589 | -2.0611 | -2.0642 | -2.0663 | -2.0684 | -2.0716 | -2.0737 | -2.0853 | -2.0937 | -2.1021 | -1.6537 | -1.6547 | -1.6558 | -1.6568 | -1.6579 | -1.66 | -1.6611 | -1.6621 | -1.6632 | -1.6642 | -1.6695 | -1.6726 | -1.6758 | -1.9611 | -1.9632 | -1.9653 | -1.9695 | -1.9768 | -1.9842 | -1.9916 | -1.9989 | -2.0063 | -2.0126 | -2.0516 | -2.0874 | -2.1242
|  | CHAORACH | EE |  |  |  |  | -2.0526 | -2.0537 | -2.0558 | -2.0589 | -2.0611 | -2.0642 | -2.0663 | -2.0684 | -2.0716 | -2.0737 | -2.0853 | -2.0937 | -2.1021 | -1.6537 | -1.6547 | -1.6558 | -1.6568 | -1.6579 | -1.66 | -1.6611 | -1.6621 | -1.6632 | -1.6642 | -1.6695 | -1.6726 | -1.6758 | -1.96 | -1.9632 | -1.9653 | -1.9684 | -1.9758 | -1.9842 | -1.9884 | -1.9947 | -2.0032 | -2.0116 | -2.0516 | -2.0874 | -2.1242
|  | CHAORACH | HT |  |  |  |  | -2.0526 | -2.0537 | -2.0558 | -2.0568 | -2.0579 | -2.06 | -2.0621 | -2.0632 | -2.0663 | -2.0663 | -2.0747 | -2.0811 | -2.0863 | -1.6537 | -1.6547 | -1.6558 | -1.6558 | -1.6579 | -1.6589 | -1.66 | -1.6611 | -1.6621 | -1.6621 | -1.6663 | -1.6695 | -1.6716 | -1.9611 | -1.9632 | -1.9642 | -1.9695 | -1.9768 | -1.9842 | -1.9916 | -1.9989 | -2.0063 | -2.0126 | -2.0484 | -2.0821 | -2.1147
|  | CHAORACH | HE |  |  |  |  | -2.0516 | -2.0526 | -2.0537 | -2.0537 | -2.0547 | -2.0579 | -2.0579 | -2.06 | -2.0611 | -2.0611 | -2.0674 | -2.0737 | -2.0779 | -1.6526 | -1.6537 | -1.6537 | -1.6537 | -1.6558 | -1.6568 | -1.6568 | -1.6579 | -1.6579 | -1.6579 | -1.6611 | -1.6632 | -1.6642 | -1.9611 | -1.9632 | -1.9642 | -1.9695 | -1.9768 | -1.9842 | -1.9916 | -1.9989 | -2.0063 | -2.0126 | -2.0484 | -2.0821 | -2.1147
|  | CHAORACH | CF |  |  |  |  | -2.0516 | -2.0516 | -2.0516 | -2.0526 | -2.0526 | -2.0526 | -2.0526 | -2.0537 | -2.0547 | -2.0558 | -2.0579 | -2.0611 | -2.0632 | -1.6526 | -1.6526 | -1.6526 | -1.6537 | -1.6537 | -1.6537 | -1.6537 | -1.6547 | -1.6547 | -1.6547 | -1.6558 | -1.6579 | -1.6579 | -1.9579 | -1.9579 | -1.9589 | -1.9611 | -1.9611 | -1.9611 | -1.9621 | -1.9653 | -1.9684 | -1.9716 | -1.9905 | -2.0105 | -2.0284
| ARBROATH | CHARLES AVENUE | MINIMUM HEADROOM | NO 62954 41097 | NO | YES | 0.23 | 12.4142 | 12.2626 | 12.1068 | 11.9458 | 11.8068 | 11.6037 | 11.4026 | 11.1268 | 10.8532 | 10.5826 | 9.4511 | 8.5237 | 7.7279 | 11.7437 | 11.5837 | 11.4205 | 11.2532 | 11.0205 | 10.7047 | 10.3963 | 10.0963 | 9.8005 | 9.5068 | 8.2868 | 7.2942 | 6.4237 | 11.9616 | 11.8016 | 11.6384 | 11.4689 | 11.33 | 11.0132 | 10.7005 | 10.3942 | 10.0911 | 9.79 | 8.5426 | 7.5216 | 6.6374
|  | CHARLES AVENUE | EE |  |  |  |  | 12.4742 | 12.3553 | 12.2289 | 12.0953 | 11.9574 | 11.7837 | 11.6332 | 11.4605 | 11.3016 | 11.1363 | 10.0974 | 9.2395 | 8.6195 | 11.8079 | 11.6826 | 11.5521 | 11.4142 | 11.2711 | 11.0837 | 10.8837 | 10.63 | 10.3921 | 10.1616 | 9.0647 | 8.1784 | 7.4963 | 12.0258 | 11.9005 | 11.7679 | 11.6289 | 11.4847 | 11.3089 | 11.1679 | 10.9089 | 10.6658 | 10.4279 | 9.2837 | 8.3437 | 7.6511
|  | CHARLES AVENUE | HT |  |  |  |  | 12.4142 | 12.2626 | 12.1068 | 11.9458 | 11.8068 | 11.6037 | 11.4026 | 11.1268 | 10.8532 | 10.5826 | 9.4511 | 8.5237 | 7.7279 | 11.7437 | 11.5837 | 11.4205 | 11.2532 | 11.0205 | 10.7047 | 10.3963 | 10.0963 | 9.8005 | 9.5068 | 8.2868 | 7.2942 | 6.4237 | 11.9616 | 11.8016 | 11.6384 | 11.4689 | 11.33 | 11.0132 | 10.7005 | 10.3942 | 10.0911 | 9.79 | 8.5426 | 7.5216 | 6.6374
|  | CHARLES AVENUE | HE |  |  |  |  | 12.55 | 12.4658 | 12.3732 | 12.2742 | 12.1679 | 12.0195 | 11.8858 | 11.7553 | 11.6079 | 11.4911 | 11.0595 | 10.7342 | 10.3679 | 11.8879 | 11.8016 | 11.7068 | 11.6047 | 11.4932 | 11.3637 | 11.2437 | 11.1268 | 10.9847 | 10.8816 | 10.2668 | 9.7995 | 9.4132 | 11.9616 | 11.8016 | 11.6384 | 11.4689 | 11.33 | 11.0132 | 10.7005 | 10.3942 | 10.0911 | 9.79 | 8.5426 | 7.5216 | 6.6374
|  | CHARLES AVENUE | CF |  |  |  |  | 12.5911 | 12.5384 | 12.4837 | 12.4289 | 12.3721 | 12.3016 | 12.2321 | 12.1626 | 12.0942 | 12.03 | 11.7279 | 11.5268 | 11.3868 | 11.9289 | 11.8763 | 11.8216 | 11.7647 | 11.7037 | 11.6395 | 11.5742 | 11.5079 | 11.4426 | 11.3795 | 11.0911 | 10.7058 | 10.4163 | 12.1447 | 12.0921 | 12.0374 | 11.9816 | 11.9216 | 11.85 | 11.7784 | 11.7079 | 11.6384 | 11.5721 | 11.2626 | 10.9584 | 10.6616
| CHARLESTON | CHARLESTON | MINIMUM HEADROOM | NO 35734 31818 | NO | YES | 0 | 16.3889 | 16.3405 | 16.2889 | 16.2311 | 16.0563 | 15.89 | 15.7321 | 15.5668 | 15.4321 | 15.3279 | 14.9489 | 14.6458 | 14.3984 | 15.2705 | 15.2221 | 15.1695 | 15.1116 | 14.9316 | 14.7232 | 14.5221 | 14.3126 | 14.1463 | 14.0211 | 13.5863 | 13.2558 | 12.9811 | 15.7792 | 15.7382 | 15.6424 | 15.4255 | 15.1834 | 14.9834 | 14.7939 | 14.5939 | 14.4339 | 14.3139 | 13.8897 | 13.555 | 13.2792
|  | CHARLESTON | EE |  |  |  |  | 16.4068 | 16.37 | 16.33 | 16.2868 | 16.2374 | 16.0984 | 15.8447 | 15.7079 | 15.5889 | 15.4774 | 15.0858 | 14.8321 | 14.6363 | 15.2895 | 15.2526 | 15.2116 | 15.1674 | 15.1168 | 14.9916 | 14.6547 | 14.4832 | 14.3326 | 14.1947 | 13.7368 | 13.4674 | 13.2526 | 15.795 | 15.7634 | 15.7276 | 15.6361 | 15.4571 | 15.2371 | 14.9203 | 14.7561 | 14.6118 | 14.4792 | 14.0318 | 13.7571 | 13.5403
|  | CHARLESTON | HT |  |  |  |  | 16.3889 | 16.3405 | 16.2889 | 16.2311 | 16.0563 | 15.89 | 15.7321 | 15.5668 | 15.4321 | 15.3279 | 14.9489 | 14.6458 | 14.3984 | 15.2705 | 15.2221 | 15.1695 | 15.1116 | 14.9316 | 14.7232 | 14.5221 | 14.3126 | 14.1463 | 14.0211 | 13.5863 | 13.2558 | 12.9811 | 15.7792 | 15.7382 | 15.6424 | 15.4255 | 15.1834 | 14.9834 | 14.7939 | 14.5939 | 14.4339 | 14.3139 | 13.8897 | 13.555 | 13.2792
|  | CHARLESTON | HE |  |  |  |  | 16.4279 | 16.3995 | 16.3668 | 16.3289 | 16.2858 | 16.1395 | 15.8942 | 15.7511 | 15.6595 | 15.6026 | 15.3995 | 15.2595 | 15.1416 | 15.3105 | 15.2821 | 15.2484 | 15.2095 | 15.1653 | 15.0263 | 14.6989 | 14.5126 | 14.3979 | 14.3316 | 14.0979 | 13.9347 | 13.8032 | 15.7792 | 15.7382 | 15.6424 | 15.4255 | 15.1834 | 14.9834 | 14.7939 | 14.5939 | 14.4339 | 14.3139 | 13.8897 | 13.555 | 13.2792
|  | CHARLESTON | CF |  |  |  |  | 16.4384 | 16.4216 | 16.4047 | 16.3847 | 16.3658 | 16.3426 | 16.3184 | 16.2858 | 16.2605 | 16.1963 | 15.9363 | 15.8279 | 15.7458 | 15.3211 | 15.3042 | 15.2874 | 15.2674 | 15.2474 | 15.2253 | 15.2011 | 15.1684 | 15.1432 | 15.1074 | 14.7811 | 14.6537 | 14.5516 | 15.8234 | 15.8076 | 15.7918 | 15.7739 | 15.7571 | 15.7371 | 15.7097 | 15.5603 | 15.4624 | 15.3466 | 15.0361 | 14.9097 | 14.8118
| ARDMORE | CLACHAN | MINIMUM HEADROOM | NF 81863 64360 | YES | YES | 0 | 2.3674 | 2.3021 | 2.2347 | 2.1695 | 2.1042 | 2.0379 | 1.9747 | 1.9137 | 1.8547 | 1.7979 | 1.5747 | -0.16947 | -0.32421 | 2.3558 | 2.2842 | 2.2116 | 2.1421 | 2.0726 | 2.0011 | 1.9337 | 1.8684 | 1.8053 | 1.7442 | 1.5021 | 0.093684 | -0.072632 | 2.3695 | 2.3042 | 2.2368 | 2.1716 | 2.1063 | 2.0389 | 1.9758 | 1.9147 | 1.8558 | 1.7989 | 1.5695 | -0.22211 | -0.39579
|  | CLACHAN | EE |  |  |  |  | 2.3968 | 2.3442 | 2.2916 | 2.2379 | 2.1842 | 2.1316 | 2.08 | 2.0326 | 1.9853 | 1.9421 | 1.7505 | 0.043158 | -0.061053 | 2.3874 | 2.3305 | 2.2747 | 2.2168 | 2.1589 | 2.1032 | 2.0495 | 1.9989 | 1.9484 | 1.9011 | 1.6958 | 0.32737 | 0.20842 | 2.3989 | 2.3463 | 2.2937 | 2.2389 | 2.1853 | 2.1337 | 2.0821 | 2.0347 | 1.9874 | 1.9432 | 1.7526 | 0.021053 | -0.10421
|  | CLACHAN | HT |  |  |  |  | 2.3674 | 2.3021 | 2.2347 | 2.1695 | 2.1042 | 2.0379 | 1.9747 | 1.9137 | 1.8547 | 1.7979 | 1.5747 | -0.16947 | -0.32421 | 2.3558 | 2.2842 | 2.2116 | 2.1421 | 2.0726 | 2.0011 | 1.9337 | 1.8684 | 1.8053 | 1.7442 | 1.5021 | 0.093684 | -0.072632 | 2.3695 | 2.3042 | 2.2368 | 2.1716 | 2.1063 | 2.0389 | 1.9758 | 1.9147 | 1.8558 | 1.7989 | 1.5695 | -0.22211 | -0.39579
|  | CLACHAN | HE |  |  |  |  | 2.4389 | 2.4074 | 2.3726 | 2.3368 | 2.3011 | 2.2484 | 2.2189 | 2.1884 | 2.1653 | 2.1368 | 2.0295 | 1.1758 | 1.1305 | 2.4347 | 2.4 | 2.3632 | 2.3253 | 2.2874 | 2.2295 | 2.1989 | 2.1684 | 2.1442 | 2.1137 | 1.9989 | 1.3347 | 1.2789 | 2.3695 | 2.3042 | 2.2368 | 2.1716 | 2.1063 | 2.0389 | 1.9758 | 1.9147 | 1.8558 | 1.7989 | 1.5695 | -0.22211 | -0.39579
|  | CLACHAN | CF |  |  |  |  | 2.46 | 2.4411 | 2.4211 | 2.4011 | 2.3789 | 2.3589 | 2.3379 | 2.3168 | 2.2958 | 2.2768 | 2.1832 | 2.1221 | 2.0768 | 2.4568 | 2.4368 | 2.4147 | 2.3926 | 2.3695 | 2.3484 | 2.3253 | 2.3021 | 2.28 | 2.2589 | 2.1589 | 2.0905 | 2.04 | 2.4621 | 2.4432 | 2.4232 | 2.4032 | 2.3811 | 2.3611 | 2.34 | 2.3189 | 2.2979 | 2.2779 | 2.1853 | 2.1232 | 2.0779
| CARRADALE 1 | CLAONAIG | MINIMUM HEADROOM | NR 86915 56467 | YES | YES | 0 | 0.34132 | 0.33921 | 0.33184 | 0.32447 | 0.31605 | 0.22026 | 0.10026 | -0.022895 | -0.12816 | -0.23868 | -0.93763 | -1.6913 | -2.0461 | 0.32658 | 0.32447 | 0.31816 | 0.31079 | 0.30132 | 0.22658 | 0.12974 | 0.029737 | -0.054474 | -0.14395 | -0.74816 | -1.405 | -1.7534 | 0.32868 | 0.32553 | 0.31711 | 0.30658 | 0.29605 | 0.19605 | 0.075 | -0.049211 | -0.15447 | -0.265 | -0.98289 | -1.7629 | -2.1534
|  | CLAONAIG | EE |  |  |  |  | 0.34237 | 0.34026 | 0.33184 | 0.32447 | 0.31605 | 0.22026 | 0.10026 | -0.022895 | -0.12816 | -0.23868 | -0.93763 | -1.6913 | -2.0461 | 0.32763 | 0.32553 | 0.32026 | 0.31079 | 0.30132 | 0.22658 | 0.12974 | 0.029737 | -0.054474 | -0.14395 | -0.74816 | -1.405 | -1.7534 | 0.32974 | 0.32763 | 0.31711 | 0.30763 | 0.29605 | 0.19605 | 0.075 | -0.049211 | -0.15447 | -0.265 | -0.98289 | -1.7629 | -2.1534
|  | CLAONAIG | HT |  |  |  |  | 0.34132 | 0.33921 | 0.33289 | 0.32658 | 0.31921 | 0.23816 | 0.15711 | 0.073947 | -0.029211 | -0.14921 | -0.67026 | -1.1092 | -1.3566 | 0.32658 | 0.32447 | 0.31816 | 0.31079 | 0.30237 | 0.23921 | 0.17184 | 0.10447 | 0.022368 | -0.082895 | -0.55342 | -0.97553 | -1.225 | 0.32868 | 0.32553 | 0.31711 | 0.30658 | 0.29921 | 0.215 | 0.13079 | 0.047632 | -0.054474 | -0.17974 | -0.725 | -1.2039 | -1.4776
|  | CLAONAIG | HE |  |  |  |  | 0.34342 | 0.34237 | 0.34026 | 0.33711 | 0.335 | 0.23395 | 0.13816 | 0.042368 | -0.054474 | -0.16184 | -0.65132 | -1.1566 | -1.7018 | 0.32868 | 0.32763 | 0.32658 | 0.32342 | 0.32237 | 0.23816 | 0.15816 | 0.078158 | -0.0039474 | -0.096579 | -0.51868 | -0.97342 | -1.4639 | 0.32868 | 0.32553 | 0.31711 | 0.30658 | 0.29921 | 0.215 | 0.13079 | 0.047632 | -0.054474 | -0.17974 | -0.725 | -1.2039 | -1.4776
|  | CLAONAIG | CF |  |  |  |  | 0.34447 | 0.34342 | 0.34132 | 0.34132 | 0.33921 | 0.30447 | 0.27395 | 0.23395 | 0.19289 | 0.15605 | -0.057632 | -0.36605 | -0.64395 | 0.32974 | 0.32868 | 0.32763 | 0.32658 | 0.32553 | 0.29921 | 0.27289 | 0.23816 | 0.20132 | 0.16658 | -0.025 | -0.30289 | -0.565 | 0.33184 | 0.33079 | 0.32868 | 0.32868 | 0.32658 | 0.28658 | 0.25184 | 0.21079 | 0.16763 | 0.12868 | -0.095526 | -0.42079 | -0.71974
| CLAYHILLS | CLAYHILLS | MINIMUM HEADROOM | NJ 94047 05518 | NO | YES | 0.05 | 27.4616 | 27.2911 | 27.1132 | 26.9342 | 26.7458 | 26.5321 | 26.3237 | 26.1184 | 25.9163 | 25.6995 | 24.9216 | 23.8732 | 22.8132 | 25.2532 | 25.0753 | 24.8911 | 24.7058 | 24.5089 | 24.2911 | 24.0763 | 23.8626 | 23.6384 | 23.2637 | 21.8637 | 20.6121 | 19.4058 | 25.9342 | 25.7637 | 25.5858 | 25.4068 | 25.2184 | 24.9963 | 24.7774 | 24.5605 | 24.3468 | 24.0984 | 22.69 | 21.4332 | 20.2279
|  | CLAYHILLS | EE |  |  |  |  | 27.5447 | 27.4174 | 27.2837 | 27.1426 | 26.9942 | 26.83 | 26.6679 | 26.5068 | 26.3532 | 26.2037 | 25.53 | 25.0226 | 24.3374 | 25.3395 | 25.2068 | 25.0689 | 24.9226 | 24.7679 | 24.6037 | 24.4426 | 24.2795 | 24.1247 | 23.9711 | 22.9405 | 21.9826 | 21.1384 | 26.0174 | 25.89 | 25.7563 | 25.6163 | 25.4668 | 25.3026 | 25.1416 | 24.9742 | 24.8132 | 24.6542 | 23.7563 | 22.7826 | 21.9353
|  | CLAYHILLS | HT |  |  |  |  | 27.4616 | 27.2911 | 27.1132 | 26.9342 | 26.7458 | 26.5321 | 26.3237 | 26.1184 | 25.9163 | 25.6995 | 24.9216 | 23.8732 | 22.8132 | 25.2532 | 25.0753 | 24.8911 | 24.7058 | 24.5089 | 24.2911 | 24.0763 | 23.8626 | 23.6384 | 23.2637 | 21.8637 | 20.6121 | 19.4058 | 25.9342 | 25.7637 | 25.5858 | 25.4068 | 25.2184 | 24.9963 | 24.7774 | 24.5605 | 24.3468 | 24.0984 | 22.69 | 21.4332 | 20.2279
|  | CLAYHILLS | HE |  |  |  |  | 27.6037 | 27.5005 | 27.3889 | 27.2668 | 27.1363 | 26.99 | 26.8563 | 26.7247 | 26.5984 | 26.4847 | 26.0753 | 25.8374 | 25.6711 | 25.4037 | 25.2974 | 25.1826 | 25.0574 | 24.9247 | 24.7805 | 24.6479 | 24.5153 | 24.3889 | 24.2732 | 23.8595 | 23.61 | 23.2911 | 25.9342 | 25.7637 | 25.5858 | 25.4068 | 25.2184 | 24.9963 | 24.7774 | 24.5605 | 24.3468 | 24.0984 | 22.69 | 21.4332 | 20.2279
|  | CLAYHILLS | CF |  |  |  |  | 27.6289 | 27.5532 | 27.4753 | 27.3953 | 27.3132 | 27.2247 | 27.1374 | 27.0489 | 26.9616 | 26.8763 | 26.5016 | 26.2974 | 26.1889 | 25.4289 | 25.3511 | 25.2711 | 25.1879 | 25.1037 | 25.0142 | 24.9258 | 24.8374 | 24.7489 | 24.6595 | 24.2679 | 24.0595 | 23.9226 | 26.1016 | 26.0258 | 25.9479 | 25.8679 | 25.7858 | 25.6974 | 25.6111 | 25.5226 | 25.4353 | 25.35 | 24.9626 | 24.7426 | 24.6226
| DOUNREAY | COLDBACKIE | MINIMUM HEADROOM | NC 62182 59590 | YES | YES | 0 | 1.2747 | 1.2116 | 1.1263 | 1.0326 | 0.93579 | 0.79053 | 0.64421 | 0.49474 | 0.35368 | -1.9842 | -2.8116 | -3.7074 | -4.4305 | 1.14 | 1.1011 | 1.0158 | 0.92105 | 0.82316 | 0.68737 | 0.55368 | 0.41789 | 0.28632 | -1.56 | -2.2916 | -3.0284 | -3.6516 | 1.1516 | 1.0821 | 0.99579 | 0.89684 | 0.79263 | 0.64105 | 0.48737 | 0.33263 | 0.18421 | -2.2221 | -3.1158 | -4.1063 | -4.9284
|  | COLDBACKIE | EE |  |  |  |  | 1.2853 | 1.2116 | 1.1263 | 1.0326 | 0.93579 | 0.79053 | 0.64421 | 0.49474 | 0.35368 | -1.9842 | -2.8116 | -3.7074 | -4.4305 | 1.1526 | 1.1011 | 1.0158 | 0.92105 | 0.82316 | 0.68737 | 0.55368 | 0.41789 | 0.28632 | -1.56 | -2.2916 | -3.0284 | -3.6516 | 1.1579 | 1.0821 | 0.99579 | 0.89684 | 0.79263 | 0.64105 | 0.48737 | 0.33263 | 0.18421 | -2.2221 | -3.1158 | -4.1063 | -4.9284
|  | COLDBACKIE | HT |  |  |  |  | 1.2747 | 1.2347 | 1.1895 | 1.1432 | 1.0989 | 1.0137 | 0.92947 | 0.84737 | 0.75474 | -1.6242 | -2.2505 | -2.9284 | -3.4284 | 1.14 | 1.1032 | 1.0642 | 1.0263 | 0.98632 | 0.91684 | 0.84842 | 0.77895 | 0.69684 | -1.1874 | -1.7905 | -2.4853 | -2.9779 | 1.1516 | 1.1063 | 1.0558 | 1.0084 | 0.95895 | 0.87053 | 0.78211 | 0.69368 | 0.59579 | -1.7968 | -2.4874 | -3.2758 | -3.8505
|  | COLDBACKIE | HE |  |  |  |  | 1.2989 | 1.2726 | 1.2442 | 1.2137 | 1.1821 | 1.0968 | 1.0168 | 0.92526 | 0.83263 | -0.42211 | -0.93895 | -1.5337 | -2.1884 | 1.1663 | 1.1495 | 1.1274 | 1.1032 | 1.0747 | 0.99789 | 0.92737 | 0.84947 | 0.77263 | -0.22526 | -0.69158 | -1.2568 | -1.8674 | 1.1516 | 1.1063 | 1.0558 | 1.0084 | 0.95895 | 0.87053 | 0.78211 | 0.69368 | 0.59579 | -1.7968 | -2.4874 | -3.2758 | -3.8505
|  | COLDBACKIE | CF |  |  |  |  | 1.3063 | 1.2958 | 1.2842 | 1.2737 | 1.2632 | 1.2305 | 1.2021 | 1.1716 | 1.1295 | 1.0758 | 0.83158 | 0.48632 | 0.11474 | 1.1705 | 1.1663 | 1.1589 | 1.1495 | 1.14 | 1.1116 | 1.0874 | 1.0632 | 1.0179 | 0.96211 | 0.72211 | 0.37684 | -0.014737 | 1.1705 | 1.1632 | 1.1537 | 1.1453 | 1.1368 | 1.1063 | 1.0747 | 1.0432 | 0.99263 | 0.93474 | 0.66526 | 0.28 | -0.14316
| DUNOON | COLINTRAIVE | MINIMUM HEADROOM | NS 03209 74814 | YES | YES | 0 | 0.52947 | 0.52421 | 0.51789 | 0.51053 | 0.50316 | 0.49158 | 0.48211 | 0.47263 | 0.46211 | 0.45368 | 0.41053 | 0.37684 | 0.34316 | 0.51368 | 0.50737 | 0.50421 | 0.49579 | 0.48526 | 0.47474 | 0.46526 | 0.45474 | 0.44526 | 0.43474 | 0.39158 | 0.35579 | 0.32211 | 0.52211 | 0.51579 | 0.50737 | 0.49684 | 0.48632 | 0.47368 | 0.46316 | 0.45368 | 0.44211 | 0.43158 | 0.38632 | 0.34947 | 0.31474
|  | COLINTRAIVE | EE |  |  |  |  | 0.53053 | 0.52526 | 0.51789 | 0.51053 | 0.50316 | 0.49158 | 0.48211 | 0.47263 | 0.46211 | 0.45368 | 0.41053 | 0.37684 | 0.34316 | 0.51474 | 0.51053 | 0.50526 | 0.49579 | 0.48526 | 0.47474 | 0.46526 | 0.45474 | 0.44526 | 0.43474 | 0.39158 | 0.35579 | 0.32211 | 0.52316 | 0.51579 | 0.50737 | 0.49684 | 0.48632 | 0.47368 | 0.46316 | 0.45368 | 0.44211 | 0.43158 | 0.38632 | 0.34947 | 0.31474
|  | COLINTRAIVE | HT |  |  |  |  | 0.52947 | 0.52421 | 0.52 | 0.51474 | 0.50947 | 0.50105 | 0.49368 | 0.48737 | 0.47895 | 0.47263 | 0.44316 | 0.41789 | 0.39474 | 0.51368 | 0.50737 | 0.50421 | 0.49895 | 0.49053 | 0.48316 | 0.47684 | 0.46947 | 0.46211 | 0.45579 | 0.42737 | 0.40316 | 0.37895 | 0.52211 | 0.51579 | 0.51158 | 0.50211 | 0.49263 | 0.48421 | 0.47579 | 0.46947 | 0.46 | 0.45368 | 0.42211 | 0.39474 | 0.36842
|  | COLINTRAIVE | HE |  |  |  |  | 0.53263 | 0.53053 | 0.52737 | 0.52421 | 0.52 | 0.51684 | 0.51368 | 0.51053 | 0.50737 | 0.50316 | 0.48842 | 0.47474 | 0.46105 | 0.51684 | 0.51474 | 0.51263 | 0.50947 | 0.50632 | 0.50211 | 0.5 | 0.49684 | 0.49263 | 0.48842 | 0.47053 | 0.45684 | 0.44526 | 0.52211 | 0.51579 | 0.51158 | 0.50211 | 0.49263 | 0.48421 | 0.47579 | 0.46947 | 0.46 | 0.45368 | 0.42211 | 0.39474 | 0.36842
|  | COLINTRAIVE | CF |  |  |  |  | 0.53368 | 0.53263 | 0.53263 | 0.53053 | 0.52842 | 0.52737 | 0.52526 | 0.52421 | 0.52316 | 0.52211 | 0.51684 | 0.51368 | 0.51053 | 0.51789 | 0.51684 | 0.51684 | 0.51579 | 0.51263 | 0.51158 | 0.51053 | 0.50947 | 0.50737 | 0.50632 | 0.50105 | 0.49684 | 0.49263 | 0.52632 | 0.52421 | 0.52421 | 0.52316 | 0.52 | 0.51895 | 0.51789 | 0.51579 | 0.51474 | 0.51368 | 0.50632 | 0.49789 | 0.49263
| STORNOWAY | COLL | MINIMUM HEADROOM | NB 47510 40182 | YES | YES | 0 | 2.3368 | 2.2474 | 5.9579 | 5.8695 | 5.7832 | 5.6874 | 5.5968 | 5.5074 | 5.42 | 5.3368 | 4.2684 | 4.0242 | 3.8168 | 2.3168 | 2.22 | 5.9232 | 5.8284 | 5.7358 | 5.6358 | 5.5411 | 5.4474 | 5.3579 | 5.2705 | 4.3526 | 4.0884 | 3.86 | 2.3147 | 2.2179 | 5.9221 | 5.8263 | 5.7337 | 5.6326 | 5.5368 | 5.4421 | 5.3495 | 5.2621 | 4.1674 | 3.9 | 3.6695
|  | COLL | EE |  |  |  |  | 2.3747 | 2.3053 | 6.0337 | 5.9621 | 5.8884 | 5.8116 | 5.7337 | 5.6568 | 5.5884 | 5.5189 | 4.5063 | 4.3221 | 4.1705 | 2.3589 | 2.2832 | 6.0063 | 5.9295 | 5.8526 | 5.7716 | 5.6916 | 5.6137 | 5.5432 | 5.4726 | 4.6084 | 4.4126 | 4.2463 | 2.3568 | 2.2821 | 6.0053 | 5.9284 | 5.8495 | 5.7684 | 5.6853 | 5.6053 | 5.5326 | 5.46 | 4.4263 | 4.2274 | 4.0568
|  | COLL | HT |  |  |  |  | 2.3368 | 2.2474 | 5.9579 | 5.8695 | 5.7832 | 5.6874 | 5.5968 | 5.5074 | 5.42 | 5.3368 | 4.2684 | 4.0242 | 3.8168 | 2.3168 | 2.22 | 5.9232 | 5.8284 | 5.7358 | 5.6358 | 5.5411 | 5.4474 | 5.3579 | 5.2705 | 4.3526 | 4.0884 | 3.86 | 2.3147 | 2.2179 | 5.9221 | 5.8263 | 5.7337 | 5.6326 | 5.5368 | 5.4421 | 5.3495 | 5.2621 | 4.1674 | 3.9 | 3.6695
|  | COLL | HE |  |  |  |  | 2.4295 | 2.3874 | 6.1432 | 6.0958 | 6.0474 | 5.9905 | 5.9358 | 5.8832 | 5.8358 | 5.7895 | 5.2842 | 5.1895 | 5.1189 | 2.42 | 2.3737 | 6.1263 | 6.0758 | 6.0242 | 5.9674 | 5.9116 | 5.8589 | 5.8095 | 5.7632 | 5.3316 | 5.2295 | 5.1537 | 2.3147 | 2.2179 | 5.9221 | 5.8263 | 5.7337 | 5.6326 | 5.5368 | 5.4421 | 5.3495 | 5.2621 | 4.1674 | 3.9 | 3.6695
|  | COLL | CF |  |  |  |  | 2.4558 | 2.4295 | 6.2032 | 6.1768 | 6.1495 | 6.1211 | 6.0895 | 6.0589 | 6.0274 | 5.9989 | 5.8611 | 5.7568 | 5.6821 | 2.4505 | 2.4211 | 6.1916 | 6.1621 | 6.1316 | 6.1011 | 6.0684 | 6.0358 | 6.0032 | 5.9726 | 5.8284 | 5.7211 | 5.6421 | 2.4484 | 2.4189 | 6.1895 | 6.16 | 6.1295 | 6.0989 | 6.0653 | 6.0326 | 5.9989 | 5.9684 | 5.8221 | 5.7095 | 5.6274
| CLAYHILLS | COMMERCE STREET | MINIMUM HEADROOM | NJ 94816 06282 | NO | YES | 0.175 | 25.9803 | 25.9434 | 25.9066 | 25.8687 | 25.8276 | 25.7813 | 25.735 | 25.6897 | 25.6455 | 25.6024 | 25.4497 | 25.3413 | 25.2634 | 24.1334 | 23.9818 | 23.8334 | 23.685 | 23.5376 | 23.3892 | 23.2418 | 23.0955 | 22.9545 | 22.8134 | 22.1734 | 21.5839 | 21.0271 | 25.2137 | 25.1768 | 25.14 | 25.1021 | 25.0611 | 25.0158 | 24.9695 | 24.9242 | 24.88 | 24.8368 | 24.6863 | 24.5779 | 24.5011
|  | COMMERCE STREET | EE |  |  |  |  | 25.9971 | 25.9697 | 25.9403 | 25.9097 | 25.8771 | 25.8403 | 25.8024 | 25.7666 | 25.7308 | 25.6971 | 25.5476 | 25.4487 | 25.3908 | 24.1555 | 24.0924 | 23.9766 | 23.8618 | 23.7482 | 23.6324 | 23.5166 | 23.4039 | 23.2934 | 23.1861 | 22.6671 | 22.205 | 21.7861 | 25.2305 | 25.2032 | 25.1737 | 25.1432 | 25.1105 | 25.0737 | 25.0368 | 25.0011 | 24.9663 | 24.9316 | 24.7853 | 24.6884 | 24.6305
|  | COMMERCE STREET | HT |  |  |  |  | 25.9803 | 25.9434 | 25.9066 | 25.8687 | 25.8276 | 25.7813 | 25.735 | 25.6897 | 25.6455 | 25.6024 | 25.4497 | 25.3413 | 25.2634 | 24.1334 | 23.9818 | 23.8334 | 23.685 | 23.5376 | 23.3892 | 23.2418 | 23.0955 | 22.9545 | 22.8134 | 22.1734 | 21.5839 | 21.0271 | 25.2137 | 25.1768 | 25.14 | 25.1021 | 25.0611 | 25.0158 | 24.9695 | 24.9242 | 24.88 | 24.8368 | 24.6863 | 24.5779 | 24.5011
|  | COMMERCE STREET | HE |  |  |  |  | 26.0097 | 25.9876 | 25.9645 | 25.9382 | 25.9108 | 25.8771 | 25.8466 | 25.8182 | 25.7887 | 25.7624 | 25.6666 | 25.6087 | 25.5676 | 24.1682 | 24.1461 | 24.1229 | 24.0734 | 23.9987 | 23.9176 | 23.8408 | 23.7692 | 23.6966 | 23.6292 | 23.3261 | 23.065 | 22.8271 | 25.2137 | 25.1768 | 25.14 | 25.1021 | 25.0611 | 25.0158 | 24.9695 | 24.9242 | 24.88 | 24.8368 | 24.6863 | 24.5779 | 24.5011
|  | COMMERCE STREET | CF |  |  |  |  | 26.0171 | 26.0013 | 25.9855 | 25.9697 | 25.9529 | 25.9339 | 25.9161 | 25.8971 | 25.8782 | 25.8603 | 25.7813 | 25.7339 | 25.7087 | 24.1755 | 24.1597 | 24.1439 | 24.1282 | 24.1113 | 24.0776 | 24.025 | 23.9713 | 23.9166 | 23.8639 | 23.6166 | 23.4092 | 23.2292 | 25.2505 | 25.2347 | 25.2189 | 25.2032 | 25.1863 | 25.1684 | 25.1495 | 25.1316 | 25.1116 | 25.0947 | 25.0158 | 24.9695 | 24.9453
| ST FILLANS | COMRIE | MINIMUM HEADROOM | NN 76887 22417 | YES | YES | 0 | 0.055263 | 0.054211 | 0.052105 | 0.051053 | 0.051053 | 0.039474 | 0.026842 | 0.012105 | -0.00052632 | -0.021579 | -0.13632 | -0.28158 | -0.40263 | 0.053158 | 0.053158 | 0.051053 | 0.051053 | 0.05 | 0.040526 | 0.027895 | 0.013158 | 0.0015789 | -0.020526 | -0.13737 | -0.29842 | -0.41211 | 0.054211 | 0.053158 | 0.051053 | 0.05 | 0.048947 | 0.040526 | 0.027895 | 0.016316 | 0.0057895 | -0.020526 | -0.15421 | -0.32053 | -0.45105
|  | COMRIE | EE |  |  |  |  | 0.055263 | 0.054211 | 0.053158 | 0.051053 | 0.051053 | 0.042632 | 0.03 | 0.018421 | 0.0078947 | -0.0089474 | -0.13632 | -0.28158 | -0.40263 | 0.053158 | 0.053158 | 0.052105 | 0.051053 | 0.051053 | 0.043684 | 0.033158 | 0.023684 | 0.015263 | -0.00052632 | -0.12895 | -0.27737 | -0.41 | 0.054211 | 0.053158 | 0.052105 | 0.05 | 0.05 | 0.041579 | 0.027895 | 0.016316 | 0.0057895 | -0.012105 | -0.15211 | -0.31316 | -0.45105
|  | COMRIE | HT |  |  |  |  | 0.055263 | 0.054211 | 0.052105 | 0.052105 | 0.051053 | 0.042632 | 0.035263 | 0.023684 | 0.011053 | -0.014211 | -0.13421 | -0.27737 | -0.37842 | 0.053158 | 0.053158 | 0.051053 | 0.051053 | 0.05 | 0.042632 | 0.037368 | 0.027895 | 0.015263 | -0.012105 | -0.13737 | -0.29842 | -0.41211 | 0.054211 | 0.053158 | 0.051053 | 0.051053 | 0.048947 | 0.040526 | 0.033158 | 0.021579 | 0.0078947 | -0.020526 | -0.15421 | -0.32053 | -0.43632
|  | COMRIE | HE |  |  |  |  | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.054211 | 0.039474 | 0.026842 | 0.012105 | -0.00052632 | -0.021579 | -0.11 | -0.22474 | -0.35211 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.040526 | 0.027895 | 0.013158 | 0.0015789 | -0.020526 | -0.10789 | -0.22895 | -0.36263 | 0.054211 | 0.053158 | 0.051053 | 0.051053 | 0.048947 | 0.040526 | 0.033158 | 0.021579 | 0.0078947 | -0.020526 | -0.15421 | -0.32053 | -0.43632
|  | COMRIE | CF |  |  |  |  | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.055263 | 0.051053 | 0.046842 | 0.038421 | 0.03 | 0.018421 | -0.028947 | -0.10158 | -0.18579 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.053158 | 0.051053 | 0.047895 | 0.038421 | 0.028947 | 0.016316 | -0.033158 | -0.11105 | -0.20368 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.054211 | 0.051053 | 0.045789 | 0.036316 | 0.026842 | 0.014211 | -0.039474 | -0.12158 | -0.21737
| TAYNUILT | CONNEL | MINIMUM HEADROOM | NM 91213 33970 | YES | YES | 0 | 1.1832 | 1.1295 | 1.0768 | 1.0253 | 0.97368 | 0.92105 | 0.87053 | 0.82316 | 0.77684 | 0.73263 | 0.55895 | 0.41895 | 0.3 | 0.98211 | 0.92632 | 0.87053 | 0.81474 | 0.76211 | 0.70632 | 0.65474 | 0.60526 | 0.55579 | 0.50947 | 0.32632 | 0.17684 | 0.045263 | 1.0116 | 0.95474 | 0.89895 | 0.84316 | 0.78842 | 0.73263 | 0.68 | 0.62947 | 0.58 | 0.53368 | 0.34632 | 0.19474 | 0.064211
|  | CONNEL | EE |  |  |  |  | 1.2074 | 1.1653 | 1.1221 | 1.08 | 1.0368 | 0.99474 | 0.95579 | 0.91579 | 0.87895 | 0.84421 | 0.69263 | 0.58526 | 0.49684 | 1.0084 | 0.96421 | 0.92105 | 0.87579 | 0.83263 | 0.78842 | 0.74842 | 0.70737 | 0.66947 | 0.63368 | 0.47789 | 0.36526 | 0.27053 | 1.0379 | 0.99263 | 0.94842 | 0.90211 | 0.85684 | 0.81158 | 0.76947 | 0.72947 | 0.68947 | 0.65263 | 0.49158 | 0.37368 | 0.27579
|  | CONNEL | HT |  |  |  |  | 1.1832 | 1.1295 | 1.0768 | 1.0253 | 0.97368 | 0.92105 | 0.87053 | 0.82316 | 0.77684 | 0.73263 | 0.55895 | 0.41895 | 0.3 | 0.98211 | 0.92632 | 0.87053 | 0.81474 | 0.76211 | 0.70632 | 0.65474 | 0.60526 | 0.55579 | 0.50947 | 0.32632 | 0.17684 | 0.045263 | 1.0116 | 0.95474 | 0.89895 | 0.84316 | 0.78842 | 0.73263 | 0.68 | 0.62947 | 0.58 | 0.53368 | 0.34632 | 0.19474 | 0.064211
|  | CONNEL | HE |  |  |  |  | 1.24 | 1.2147 | 1.1884 | 1.1621 | 1.1337 | 1.1053 | 1.0737 | 1.0474 | 1.0242 | 1 | 0.91684 | 0.86316 | 0.82316 | 1.0432 | 1.0168 | 0.98842 | 0.96105 | 0.93263 | 0.90316 | 0.87053 | 0.84316 | 0.81789 | 0.79474 | 0.70842 | 0.65158 | 0.60947 | 1.0116 | 0.95474 | 0.89895 | 0.84316 | 0.78842 | 0.73263 | 0.68 | 0.62947 | 0.58 | 0.53368 | 0.34632 | 0.19474 | 0.064211
|  | CONNEL | CF |  |  |  |  | 1.2558 | 1.2411 | 1.2253 | 1.2095 | 1.1926 | 1.1768 | 1.1611 | 1.1453 | 1.1295 | 1.1126 | 1.0442 | 0.99579 | 0.96105 | 1.06 | 1.0442 | 1.0284 | 1.0116 | 0.99474 | 0.97789 | 0.96105 | 0.94421 | 0.92737 | 0.90842 | 0.83579 | 0.78421 | 0.74737 | 1.0905 | 1.0747 | 1.0579 | 1.04 | 1.0232 | 1.0063 | 0.98947 | 0.97263 | 0.95579 | 0.93789 | 0.86421 | 0.81158 | 0.77368
| BEAULY | CONON BRIDGE | MINIMUM HEADROOM | NH 54996 55499 | NO | YES | 0.05 | 6.4293 | 6.2388 | 6.0367 | 5.8314 | 14.1137 | 13.5147 | 12.8789 | 12.2347 | 11.6937 | 11.1453 | 9.2168 | 7.2484 | 5.2147 | 5.6421 | 5.4189 | 5.1874 | 4.9547 | 12.77 | 12.1079 | 11.4532 | 10.79 | 10.2647 | 9.7311 | 8.0889 | 6.4237 | 4.2816 | 5.8878 | 5.672 | 5.4436 | 5.2141 | 13.2513 | 12.5671 | 11.8903 | 11.205 | 10.6355 | 10.0587 | 8.0797 | 6.0513 | 3.7724
|  | CONON BRIDGE | EE |  |  |  |  | 6.5062 | 6.3609 | 6.1872 | 6.0114 | 14.3179 | 13.9221 | 13.4832 | 12.8326 | 12.1863 | 11.54 | 9.2168 | 7.2484 | 5.2147 | 5.7379 | 5.5653 | 5.3716 | 5.1747 | 13.0226 | 12.6584 | 12.2616 | 11.5784 | 10.9321 | 10.2826 | 8.1689 | 6.4826 | 4.2816 | 5.9805 | 5.812 | 5.6162 | 5.4184 | 13.485 | 13.0692 | 12.6061 | 11.8724 | 11.1871 | 10.4976 | 8.0797 | 6.0513 | 3.7724
|  | CONON BRIDGE | HT |  |  |  |  | 6.4293 | 6.2388 | 6.0367 | 5.8314 | 14.1137 | 13.5147 | 12.8789 | 12.2347 | 11.6937 | 11.1453 | 9.3863 | 7.7526 | 6.0579 | 5.6421 | 5.4189 | 5.1874 | 4.9547 | 12.77 | 12.1079 | 11.4532 | 10.79 | 10.2647 | 9.7311 | 8.0889 | 6.4237 | 4.5321 | 5.8878 | 5.672 | 5.4436 | 5.2141 | 13.2513 | 12.5671 | 11.8903 | 11.205 | 10.6355 | 10.0587 | 8.2176 | 6.4282 | 4.4692
|  | CONON BRIDGE | HE |  |  |  |  | 6.5725 | 6.5167 | 6.4241 | 6.3125 | 14.6842 | 14.3116 | 13.9895 | 13.5253 | 13.0674 | 12.6032 | 10.7821 | 9.1126 | 6.82 | 5.8074 | 5.7516 | 5.6411 | 5.5147 | 13.43 | 13.1016 | 12.8121 | 12.3226 | 11.8405 | 11.3721 | 9.6521 | 8.0647 | 5.7563 | 5.8878 | 5.672 | 5.4436 | 5.2141 | 13.2513 | 12.5671 | 11.8903 | 11.205 | 10.6355 | 10.0587 | 8.2176 | 6.4282 | 4.4692
|  | CONON BRIDGE | CF |  |  |  |  | 6.6062 | 6.5757 | 6.5409 | 6.502 | 14.9295 | 14.7726 | 14.6284 | 14.4832 | 14.2716 | 14.0779 | 13.0347 | 12.0032 | 10.5884 | 5.8411 | 5.8105 | 5.7779 | 5.7358 | 13.71 | 13.5647 | 13.4279 | 13.29 | 13.0521 | 12.8247 | 11.7132 | 10.7258 | 9.2121 | 6.0836 | 6.0531 | 6.0184 | 5.9763 | 14.1713 | 14.0061 | 13.8513 | 13.6945 | 13.4503 | 13.2197 | 12.0555 | 10.9661 | 9.4145
| BEAULY | CONON FALLS | MINIMUM HEADROOM | NH 38745 57593 | YES | YES | 0.25 | 0.24684 | 0.24263 | 0.23737 | 0.23211 | 0.044737 | 0.018421 | -0.013158 | -0.045789 | -0.075263 | -0.10263 | -0.29526 | -0.56474 | -0.75211 | 0.25632 | 0.25 | 0.23947 | 0.23105 | 0.047895 | 0.025789 | -0.00052632 | -0.026842 | -0.052105 | -0.076316 | -0.23842 | -0.44684 | -0.64368 | 0.25316 | 0.24579 | 0.23632 | 0.22684 | 0.035263 | 0.0078947 | -0.024737 | -0.057368 | -0.087895 | -0.11737 | -0.35632 | -0.64684 | -0.85737
|  | CONON FALLS | EE |  |  |  |  | 0.25 | 0.24368 | 0.23737 | 0.23211 | 0.044737 | 0.018421 | -0.013158 | -0.045789 | -0.075263 | -0.10263 | -0.29526 | -0.56474 | -0.75211 | 0.26053 | 0.25316 | 0.24579 | 0.23737 | 0.047895 | 0.025789 | -0.00052632 | -0.026842 | -0.052105 | -0.076316 | -0.23842 | -0.44684 | -0.64368 | 0.25737 | 0.24895 | 0.24053 | 0.23105 | 0.035263 | 0.0078947 | -0.024737 | -0.057368 | -0.087895 | -0.11737 | -0.35632 | -0.64684 | -0.85737
|  | CONON FALLS | HT |  |  |  |  | 0.24684 | 0.24263 | 0.23737 | 0.23211 | 0.22474 | 0.20368 | 0.18158 | 0.16158 | 0.13526 | 0.10158 | -0.11316 | -0.33737 | -0.48684 | 0.25632 | 0.25 | 0.23947 | 0.23105 | 0.22263 | 0.20158 | 0.17947 | 0.15842 | 0.13421 | 0.10474 | -0.10684 | -0.34579 | -0.50895 | 0.25316 | 0.24579 | 0.23632 | 0.22684 | 0.21842 | 0.19211 | 0.16579 | 0.14053 | 0.11105 | 0.076316 | -0.15842 | -0.41105 | -0.58158
|  | CONON FALLS | HE |  |  |  |  | 0.25211 | 0.24895 | 0.24684 | 0.24263 | 0.23947 | 0.21421 | 0.19421 | 0.17211 | 0.14895 | 0.10895 | -0.061579 | -0.25947 | -0.47421 | 0.26579 | 0.26158 | 0.25737 | 0.25211 | 0.24895 | 0.22579 | 0.20263 | 0.17421 | 0.14895 | 0.11105 | -0.048947 | -0.24368 | -0.45632 | 0.25316 | 0.24579 | 0.23632 | 0.22684 | 0.21842 | 0.19211 | 0.16579 | 0.14053 | 0.11105 | 0.076316 | -0.15842 | -0.41105 | -0.58158
|  | CONON FALLS | CF |  |  |  |  | 0.25316 | 0.25211 | 0.25105 | 0.24789 | 0.24684 | 0.23737 | 0.22895 | 0.22053 | 0.21316 | 0.20579 | 0.12263 | -0.00052632 | -0.13211 | 0.26684 | 0.26579 | 0.26368 | 0.26053 | 0.25842 | 0.25 | 0.24158 | 0.23211 | 0.21526 | 0.19632 | 0.11211 | -0.012105 | -0.14895 | 0.26368 | 0.26263 | 0.26053 | 0.25632 | 0.25421 | 0.24368 | 0.23316 | 0.22158 | 0.20474 | 0.18474 | 0.092105 | -0.043684 | -0.19211
| DUDHOPE | CONSTABLE STREET | MINIMUM HEADROOM | NO 40903 30821 | NO | YES | 0.05 | 33.3142 | 33.1658 | 33.0079 | 32.8437 | 32.6826 | 32.4837 | 32.2868 | 32.1268 | 31.9321 | 31.6079 | 30.1521 | 29.0395 | 28.1026 | 30.0553 | 29.89 | 29.7068 | 29.51 | 29.3321 | 29.0995 | 28.8658 | 28.6826 | 28.45 | 28.2205 | 26.9079 | 25.6784 | 24.63 | 31.5737 | 31.4347 | 31.2905 | 31.0189 | 30.7747 | 30.38 | 29.9726 | 29.6316 | 29.2074 | 28.7874 | 27.4147 | 26.3674 | 25.4905
|  | CONSTABLE STREET | EE |  |  |  |  | 33.3942 | 33.2879 | 33.1711 | 33.0468 | 32.9205 | 32.7816 | 32.6437 | 32.4879 | 32.3384 | 32.2279 | 31.1384 | 30.2447 | 29.5426 | 30.1437 | 30.0247 | 29.8868 | 29.7321 | 29.5953 | 29.4489 | 29.3047 | 29.1132 | 28.9289 | 28.7995 | 27.9974 | 27.0237 | 26.2384 | 31.6484 | 31.5495 | 31.4453 | 31.3232 | 31.1337 | 30.9316 | 30.7295 | 30.3589 | 30 | 29.7189 | 28.3484 | 27.5021 | 26.8453
|  | CONSTABLE STREET | HT |  |  |  |  | 33.3142 | 33.1658 | 33.0079 | 32.8437 | 32.6826 | 32.4837 | 32.2868 | 32.1268 | 31.9321 | 31.6079 | 30.1521 | 29.0395 | 28.1026 | 30.0553 | 29.89 | 29.7068 | 29.51 | 29.3321 | 29.0995 | 28.8658 | 28.6826 | 28.45 | 28.2205 | 26.9079 | 25.6784 | 24.63 | 31.5737 | 31.4347 | 31.2905 | 31.0189 | 30.7747 | 30.38 | 29.9726 | 29.6316 | 29.2074 | 28.7874 | 27.4147 | 26.3674 | 25.4905
|  | CONSTABLE STREET | HE |  |  |  |  | 33.4384 | 33.35 | 33.2489 | 33.1353 | 33.0247 | 32.8984 | 32.7816 | 32.6563 | 32.5363 | 32.3889 | 31.9616 | 31.3679 | 30.9574 | 30.1995 | 30.1026 | 29.9858 | 29.8489 | 29.7311 | 29.6016 | 29.4826 | 29.3374 | 29.1953 | 29.0026 | 28.4595 | 28.1732 | 27.7532 | 31.5737 | 31.4347 | 31.2905 | 31.0189 | 30.7747 | 30.38 | 29.9726 | 29.6316 | 29.2074 | 28.7874 | 27.4147 | 26.3674 | 25.4905
|  | CONSTABLE STREET | CF |  |  |  |  | 33.4637 | 33.3974 | 33.3258 | 33.2511 | 33.1795 | 33.1026 | 33.0258 | 32.9468 | 32.8647 | 32.7837 | 32.4174 | 32.21 | 32.0963 | 30.2353 | 30.1626 | 30.0816 | 29.9942 | 29.9163 | 29.8353 | 29.7532 | 29.67 | 29.5763 | 29.4795 | 29.0353 | 28.7837 | 28.6437 | 31.7053 | 31.6421 | 31.5768 | 31.5095 | 31.4411 | 31.3674 | 31.2937 | 31.22 | 31.1463 | 31.0716 | 30.2558 | 29.7579 | 29.4632
| ALNESS | CONTULLICH | MINIMUM HEADROOM | NN 59226 32752 | YES | YES | 0 | 0.10737 | 0.10632 | 0.10526 | 0.10526 | 0.10421 | 0.10211 | 0.1 | 0.094737 | 0.090526 | 0.081053 | 0.025263 | -0.057895 | -0.12 | 0.10526 | 0.10316 | 0.10211 | 0.10105 | 0.1 | 0.098947 | 0.094737 | 0.090526 | 0.085263 | 0.074737 | 0.0084211 | -0.087368 | -0.16105 | 0.10526 | 0.10316 | 0.10211 | 0.10211 | 0.10105 | 0.098947 | 0.097895 | 0.096842 | 0.092632 | 0.078947 | 0.0094737 | -0.087368 | -0.16105
|  | CONTULLICH | EE |  |  |  |  | 0.10737 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10421 | 0.10211 | 0.10211 | 0.098947 | 0.095789 | 0.041053 | -0.02 | -0.089474 | 0.10526 | 0.10421 | 0.10316 | 0.10211 | 0.10211 | 0.1 | 0.098947 | 0.098947 | 0.096842 | 0.091579 | 0.029474 | -0.043158 | -0.12316 | 0.10526 | 0.10421 | 0.10316 | 0.10211 | 0.10211 | 0.10105 | 0.098947 | 0.098947 | 0.095789 | 0.092632 | 0.028421 | -0.043158 | -0.12421
|  | CONTULLICH | HT |  |  |  |  | 0.10737 | 0.10632 | 0.10526 | 0.10526 | 0.10421 | 0.10211 | 0.10105 | 0.1 | 0.095789 | 0.084211 | 0.025263 | -0.057895 | -0.12 | 0.10526 | 0.10316 | 0.10211 | 0.10105 | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.092632 | 0.078947 | 0.0084211 | -0.087368 | -0.16105 | 0.10526 | 0.10316 | 0.10211 | 0.10211 | 0.10105 | 0.098947 | 0.097895 | 0.096842 | 0.092632 | 0.078947 | 0.0094737 | -0.087368 | -0.16105
|  | CONTULLICH | HE |  |  |  |  | 0.10737 | 0.10737 | 0.10737 | 0.10632 | 0.10632 | 0.10421 | 0.1 | 0.094737 | 0.090526 | 0.081053 | 0.045263 | -0.010526 | -0.071579 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10105 | 0.094737 | 0.090526 | 0.085263 | 0.074737 | 0.032632 | -0.031579 | -0.10316 | 0.10526 | 0.10316 | 0.10211 | 0.10211 | 0.10105 | 0.098947 | 0.097895 | 0.096842 | 0.092632 | 0.078947 | 0.0094737 | -0.087368 | -0.16105
|  | CONTULLICH | CF |  |  |  |  | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10526 | 0.10316 | 0.098947 | 0.092632 | 0.070526 | 0.034737 | -0.012632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10316 | 0.098947 | 0.093684 | 0.087368 | 0.061053 | 0.017895 | -0.035789 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10316 | 0.098947 | 0.094737 | 0.088421 | 0.061053 | 0.018947 | -0.035789
| FORT WILLIAM | CORRAN | MINIMUM HEADROOM | NN 02545 63126 | YES | NO | 0 | 1.1358 | 1.1179 | 1.0968 | 0.08 | 0.06 | -0.0084211 | -0.084211 | -0.16316 | -0.23263 | -0.30105 | -0.78947 | -1.5242 | -2.0684 | 1.0537 | 1.0347 | 1.0116 | 0.10211 | 0.078947 | 0.017895 | -0.050526 | -0.12 | -0.18316 | -0.24421 | -0.65579 | -1.2158 | -1.7326 | 1.0779 | 1.0505 | 1.0221 | -0.057895 | -0.082105 | -0.15263 | -0.22947 | -0.30842 | -0.37895 | -0.44737 | -1.0095 | -1.8126 | -2.4411
|  | CORRAN | EE |  |  |  |  | 1.1432 | 1.1295 | 1.1105 | 0.08 | 0.06 | -0.0084211 | -0.084211 | -0.16316 | -0.23263 | -0.30105 | -0.78947 | -1.5242 | -2.0684 | 1.0611 | 1.0463 | 1.0295 | 0.10211 | 0.078947 | 0.017895 | -0.050526 | -0.12 | -0.18316 | -0.24421 | -0.65579 | -1.2158 | -1.7326 | 1.0884 | 1.0684 | 1.0442 | -0.057895 | -0.082105 | -0.15263 | -0.22947 | -0.30842 | -0.37895 | -0.44737 | -1.0095 | -1.8126 | -2.4411
|  | CORRAN | HT |  |  |  |  | 1.1358 | 1.1179 | 1.0968 | 1.0758 | 1.0516 | 0.97474 | 0.9 | 0.82632 | 0.74316 | 0.66105 | 0.072632 | -0.59895 | -1.0537 | 1.0537 | 1.0347 | 1.0116 | 0.97579 | 0.94105 | 0.87158 | 0.80421 | 0.73789 | 0.66316 | 0.59158 | 0.0031579 | -0.72421 | -1.2295 | 1.0779 | 1.0505 | 1.0221 | 0.99263 | 0.96421 | 0.89789 | 0.83263 | 0.75789 | 0.67263 | 0.59053 | -0.058947 | -0.83158 | -1.3621
|  | CORRAN | HE |  |  |  |  | 1.1537 | 1.1442 | 1.1337 | 1.1232 | 1.1105 | 1.0474 | 0.99368 | 0.93368 | 0.85158 | 0.74 | 0.27263 | -0.28632 | -0.88632 | 1.0716 | 1.0621 | 1.0526 | 1.0411 | 1.0284 | 0.98421 | 0.92737 | 0.85368 | 0.77895 | 0.67053 | 0.22105 | -0.34316 | -0.95579 | 1.0779 | 1.0505 | 1.0221 | 0.99263 | 0.96421 | 0.89789 | 0.83263 | 0.75789 | 0.67263 | 0.59053 | -0.058947 | -0.83158 | -1.3621
|  | CORRAN | CF |  |  |  |  | 1.1589 | 1.1547 | 1.1484 | 1.1421 | 1.1368 | 1.1116 | 1.0905 | 1.0684 | 1.0484 | 1.0074 | 0.76421 | 0.40947 | 0.027368 | 1.0779 | 1.0726 | 1.0674 | 1.06 | 1.0547 | 1.04 | 1.0263 | 1.0084 | 0.96947 | 0.91263 | 0.66737 | 0.30737 | -0.10105 | 1.1095 | 1.1053 | 1.0979 | 1.0884 | 1.08 | 1.0537 | 1.0295 | 1.0042 | 0.97263 | 0.93474 | 0.67368 | 0.27684 | -0.16105
| KILLIN | COSHIEVILLE | MINIMUM HEADROOM | NN 77193 48683 | YES | YES | 0 | 2.4063 | 2.8537 | 2.7537 | 2.6463 | 2.54 | 2.1484 | 1.6758 | 1.1579 | 0.70842 | 0.24526 | -3.3568 | -7.4674 | -10.2779 | 2.4305 | 2.8747 | 2.7695 | 2.6579 | 2.5474 | 2.2147 | 1.8632 | 1.4253 | 1.0421 | 0.65368 | -2.6863 | -6.5484 | -9.4884 | 2.4432 | 2.8884 | 2.7779 | 2.6642 | 2.5484 | 2.1432 | 1.66 | 1.1253 | 0.65579 | 0.18 | -3.6684 | -8.0916 | -11.2147
|  | COSHIEVILLE | EE |  |  |  |  | 2.4284 | 2.8853 | 2.8158 | 2.72 | 2.6221 | 2.1789 | 1.6758 | 1.1579 | 0.70842 | 0.24526 | -3.3568 | -7.4674 | -10.2779 | 2.4547 | 2.9126 | 2.8495 | 2.7547 | 2.6611 | 2.2926 | 1.8632 | 1.4253 | 1.0421 | 0.65368 | -2.6863 | -6.5484 | -9.4884 | 2.4621 | 2.9211 | 2.8484 | 2.7453 | 2.64 | 2.1811 | 1.66 | 1.1253 | 0.65579 | 0.18 | -3.6684 | -8.0916 | -11.2147
|  | COSHIEVILLE | HT |  |  |  |  | 2.4063 | 2.8537 | 2.7537 | 2.6463 | 2.54 | 2.1484 | 1.7726 | 1.3926 | 0.94947 | 0.48211 | -2.7295 | -6.1147 | -8.34 | 2.4305 | 2.8747 | 2.7695 | 2.6579 | 2.5474 | 2.2147 | 1.8937 | 1.5611 | 1.1779 | 0.77053 | -2.3737 | -5.9558 | -8.4011 | 2.4432 | 2.8884 | 2.7779 | 2.6642 | 2.5484 | 2.1432 | 1.7526 | 1.3579 | 0.89684 | 0.41158 | -3.08 | -6.8716 | -9.4179
|  | COSHIEVILLE | HE |  |  |  |  | 2.4589 | 2.9326 | 2.9053 | 2.8579 | 2.8095 | 2.3684 | 1.9337 | 1.4758 | 1.0337 | 0.43368 | -2.1495 | -5.1958 | -8.5042 | 2.48 | 2.9579 | 2.9326 | 2.8842 | 2.8347 | 2.4695 | 2.0832 | 1.6716 | 1.2789 | 0.71158 | -1.6968 | -4.6811 | -7.9442 | 2.4432 | 2.8884 | 2.7779 | 2.6642 | 2.5484 | 2.1432 | 1.7526 | 1.3579 | 0.89684 | 0.41158 | -3.08 | -6.8716 | -9.4179
|  | COSHIEVILLE | CF |  |  |  |  | 2.4726 | 2.9579 | 2.94 | 2.9168 | 2.8989 | 2.7337 | 2.5884 | 2.3768 | 2.1284 | 1.8632 | 0.58737 | -1.3158 | -3.3189 | 2.4905 | 2.9789 | 2.9642 | 2.9463 | 2.9263 | 2.7926 | 2.6663 | 2.4705 | 2.2295 | 1.9526 | 0.70316 | -1.1842 | -3.28 | 2.4853 | 2.9768 | 2.9653 | 2.9526 | 2.9358 | 2.7653 | 2.6126 | 2.3905 | 2.1211 | 1.8274 | 0.44526 | -1.6274 | -3.8747
| COUPAR ANGUS | COUPAR ANGUS | MINIMUM HEADROOM | NO 21784 39212 | NO | YES | 0 | 16.1468 | 16.0016 | 15.85 | 15.6953 | 15.4153 | 14.7753 | 14.0932 | 13.3732 | 12.7163 | 11.8542 | 7.4995 | 1.5089 | -3.1426 | 14.5716 | 14.4 | 14.2326 | 14.0632 | 13.7211 | 13.0947 | 12.5179 | 11.9253 | 11.1926 | 10.3168 | 6.1674 | 0.0063158 | -4.6316 | 15.2139 | 15.0445 | 14.8739 | 14.7013 | 14.3582 | 13.6487 | 12.9455 | 12.2066 | 11.4855 | 10.5108 | 5.9013 | -0.69132 | -5.9039
|  | COUPAR ANGUS | EE |  |  |  |  | 16.2153 | 16.0953 | 15.9574 | 15.8237 | 15.6174 | 14.9416 | 14.0932 | 13.3732 | 12.7163 | 11.9721 | 7.4995 | 1.5089 | -3.1426 | 14.6547 | 14.5105 | 14.3611 | 14.2147 | 13.9726 | 13.3263 | 12.5421 | 11.9305 | 11.3579 | 10.6768 | 6.4274 | 0.43368 | -4.6316 | 15.2971 | 15.1539 | 14.9982 | 14.8466 | 14.5992 | 13.8497 | 12.9455 | 12.2066 | 11.5255 | 10.7361 | 5.9013 | -0.69132 | -5.9039
|  | COUPAR ANGUS | HT |  |  |  |  | 16.1468 | 16.0016 | 15.85 | 15.6953 | 15.4153 | 14.7753 | 14.1563 | 13.5226 | 12.7458 | 11.8542 | 7.7637 | 2.0942 | -1.7826 | 14.5716 | 14.4 | 14.2326 | 14.0632 | 13.7211 | 13.0947 | 12.5179 | 11.9253 | 11.1926 | 10.3168 | 6.1674 | 0.0063158 | -4.34 | 15.2139 | 15.0445 | 14.8739 | 14.7013 | 14.3582 | 13.6487 | 12.9929 | 12.3171 | 11.4855 | 10.5108 | 5.9918 | -0.39132 | -4.8524
|  | COUPAR ANGUS | HE |  |  |  |  | 16.2879 | 16.2047 | 16.1258 | 16.0458 | 15.8679 | 15.1668 | 14.4489 | 13.8279 | 13.1637 | 12.4353 | 9.0605 | 4.4016 | -0.68368 | 14.74 | 14.6389 | 14.5495 | 14.4589 | 14.2368 | 13.5558 | 12.8632 | 12.2947 | 11.6674 | 10.9589 | 7.6737 | 2.8758 | -2.3411 | 15.2139 | 15.0445 | 14.8739 | 14.7013 | 14.3582 | 13.6487 | 12.9929 | 12.3171 | 11.4855 | 10.5108 | 5.9918 | -0.39132 | -4.8524
|  | COUPAR ANGUS | CF |  |  |  |  | 16.3311 | 16.2921 | 16.2468 | 16.1974 | 16.1353 | 15.9005 | 15.6721 | 15.4268 | 15.1511 | 14.7321 | 12.8163 | 9.89 | 6.6079 | 14.7916 | 14.7474 | 14.6947 | 14.6379 | 14.5632 | 14.3484 | 14.1295 | 13.8863 | 13.5905 | 13.1126 | 11.0926 | 8.0421 | 4.5084 | 15.4329 | 15.3887 | 15.335 | 15.2771 | 15.2024 | 14.9476 | 14.6929 | 14.4139 | 14.0897 | 13.5982 | 11.4245 | 8.1655 | 4.4792
| CRAIGIEBUCKLER | CRAIGIEBUCKLER | MINIMUM HEADROOM | NJ 90775 04519 | NO | YES | 1.354 | 22.5249 | 22.3555 | 22.1765 | 21.9965 | 21.8165 | 21.6113 | 21.4123 | 21.1513 | 20.846 | 20.5439 | 19.5797 | 18.8386 | 18.2102 | 21.3313 | 21.1565 | 20.9744 | 20.7934 | 20.6092 | 20.4028 | 20.2049 | 19.9271 | 19.5913 | 19.2597 | 18.2049 | 17.3786 | 16.6618 | 21.3586 | 21.1839 | 21.0018 | 20.8186 | 20.6355 | 20.4281 | 20.226 | 19.9471 | 19.6092 | 19.2744 | 18.2092 | 17.3765 | 16.6586
|  | CRAIGIEBUCKLER | EE |  |  |  |  | 22.5976 | 22.4755 | 22.3397 | 22.1965 | 22.0513 | 21.8881 | 21.7302 | 21.5776 | 21.4365 | 21.2976 | 20.3839 | 19.766 | 19.3197 | 21.4049 | 21.2797 | 21.1407 | 20.9955 | 20.8481 | 20.686 | 20.5302 | 20.3786 | 20.2386 | 20.1018 | 19.1113 | 18.4397 | 17.9355 | 21.4323 | 21.3071 | 21.1681 | 21.0218 | 20.8744 | 20.7102 | 20.5513 | 20.3944 | 20.2523 | 20.1123 | 19.106 | 18.4155 | 17.9071
|  | CRAIGIEBUCKLER | HT |  |  |  |  | 22.5249 | 22.3555 | 22.1765 | 21.9965 | 21.8165 | 21.6113 | 21.4123 | 21.1513 | 20.846 | 20.5439 | 19.5797 | 18.8386 | 18.2102 | 21.3313 | 21.1565 | 20.9744 | 20.7934 | 20.6092 | 20.4028 | 20.2049 | 19.9271 | 19.5913 | 19.2597 | 18.2049 | 17.3786 | 16.6618 | 21.3586 | 21.1839 | 21.0018 | 20.8186 | 20.6355 | 20.4281 | 20.226 | 19.9471 | 19.6092 | 19.2744 | 18.2092 | 17.3765 | 16.6586
|  | CRAIGIEBUCKLER | HE |  |  |  |  | 22.6881 | 22.6102 | 22.526 | 22.4344 | 22.3313 | 22.2071 | 22.0934 | 21.9807 | 21.8765 | 21.7776 | 21.4302 | 21.2102 | 20.9565 | 21.4955 | 21.4176 | 21.3334 | 21.2386 | 21.1334 | 21.0113 | 20.8997 | 20.7892 | 20.686 | 20.5892 | 20.2481 | 20.0323 | 19.7597 | 21.3586 | 21.1839 | 21.0018 | 20.8186 | 20.6355 | 20.4281 | 20.226 | 19.9471 | 19.6092 | 19.2744 | 18.2092 | 17.3765 | 16.6586
|  | CRAIGIEBUCKLER | CF |  |  |  |  | 22.7344 | 22.6902 | 22.6449 | 22.5986 | 22.5502 | 22.4976 | 22.4397 | 22.3828 | 22.326 | 22.2713 | 22.0197 | 21.8649 | 21.7744 | 21.5418 | 21.4976 | 21.4523 | 21.406 | 21.3576 | 21.3049 | 21.2449 | 21.1881 | 21.1323 | 21.0765 | 20.8239 | 20.6744 | 20.5849 | 21.5692 | 21.5249 | 21.4797 | 21.4334 | 21.3849 | 21.3292 | 21.2702 | 21.2123 | 21.1555 | 21.0976 | 20.8418 | 20.6849 | 20.5902
| REDMOSS | CRAIGINCHES | MINIMUM HEADROOM | NJ 94694 04089 | NO | YES | 0.92 | 24.7274 | 24.6579 | 24.5768 | 24.4295 | 24.2821 | 24.1137 | 23.9505 | 23.7884 | 23.6274 | 23.4684 | 22.8105 | 22.2505 | 21.7474 | 23.6168 | 23.4505 | 23.2832 | 23.1179 | 22.9505 | 22.7684 | 22.5905 | 22.4137 | 22.24 | 22.0695 | 21.3411 | 20.7126 | 20.1537 | 24.0632 | 23.9221 | 23.7547 | 23.5884 | 23.4211 | 23.2358 | 23.0558 | 22.8747 | 22.6968 | 22.5211 | 21.7768 | 21.1389 | 20.5768
|  | CRAIGINCHES | EE |  |  |  |  | 24.76 | 24.7074 | 24.6505 | 24.5926 | 24.4842 | 24.3495 | 24.2126 | 24.0789 | 23.9495 | 23.8232 | 23.2305 | 22.7337 | 22.36 | 23.6537 | 23.5705 | 23.4432 | 23.3137 | 23.1821 | 23.0368 | 22.8926 | 22.7495 | 22.6116 | 22.4768 | 21.8432 | 21.3084 | 20.8811 | 24.0958 | 24.0411 | 23.9126 | 23.7832 | 23.6516 | 23.5032 | 23.3537 | 23.2053 | 23.0632 | 22.9232 | 22.2632 | 21.7021 | 21.2663
|  | CRAIGINCHES | HT |  |  |  |  | 24.7274 | 24.6579 | 24.5768 | 24.4295 | 24.2821 | 24.1137 | 23.9505 | 23.7884 | 23.6274 | 23.4684 | 22.8105 | 22.2505 | 21.7474 | 23.6168 | 23.4505 | 23.2832 | 23.1179 | 22.9505 | 22.7684 | 22.5905 | 22.4137 | 22.24 | 22.0695 | 21.3411 | 20.7126 | 20.1537 | 24.0632 | 23.9221 | 23.7547 | 23.5884 | 23.4211 | 23.2358 | 23.0558 | 22.8747 | 22.6968 | 22.5211 | 21.7768 | 21.1389 | 20.5768
|  | CRAIGINCHES | HE |  |  |  |  | 24.7853 | 24.7432 | 24.6968 | 24.6463 | 24.5926 | 24.52 | 24.4526 | 24.3884 | 24.2968 | 24.2095 | 23.8453 | 23.5579 | 23.3053 | 23.6789 | 23.6368 | 23.5905 | 23.52 | 23.4263 | 23.3158 | 23.2137 | 23.1137 | 23.0168 | 22.9253 | 22.5411 | 22.2337 | 21.9642 | 24.0632 | 23.9221 | 23.7547 | 23.5884 | 23.4211 | 23.2358 | 23.0558 | 22.8747 | 22.6968 | 22.5211 | 21.7768 | 21.1389 | 20.5768
|  | CRAIGINCHES | CF |  |  |  |  | 24.8 | 24.7705 | 24.74 | 24.7095 | 24.6758 | 24.6379 | 24.6 | 24.5621 | 24.5242 | 24.4874 | 24.2474 | 24.0274 | 23.8589 | 23.6937 | 23.6642 | 23.6337 | 23.6032 | 23.5695 | 23.5189 | 23.4526 | 23.3853 | 23.3211 | 23.2547 | 22.9516 | 22.7126 | 22.5253 | 24.1358 | 24.1063 | 24.0758 | 24.0453 | 24.0116 | 23.9737 | 23.92 | 23.8526 | 23.7853 | 23.7179 | 23.4084 | 23.1589 | 22.9642
| CRAIGIEBUCKLER | CRAIGTON | MINIMUM HEADROOM | NJ 89195 03438 | NO | YES | 0.2 | 14.3084 | 13.5663 | 12.6926 | 11.6232 | 10.5463 | 9.2116 | 8.0021 | 6.7926 | 5.5211 | 4.3021 | -1.1568 | -2.2853 | -2.8758 | 14.0568 | 13.2011 | 12.1811 | 10.9263 | 9.6537 | 8.1179 | 6.7305 | 5.3442 | 3.8926 | 2.5021 | -3.7947 | -4.8768 | -5.5337 | 11.8021 | 10.9432 | 9.9284 | 8.6821 | 7.4263 | 5.8884 | 4.4968 | 3.1074 | 1.6474 | 0.24737 | -6.0558 | -7.1905 | -7.8674
|  | CRAIGTON | EE |  |  |  |  | 14.4074 | 13.6916 | 12.8905 | 11.8621 | 10.8221 | 9.5126 | 8.3305 | 7.1411 | 5.9758 | 4.7811 | -0.90737 | -2.2853 | -2.8758 | 14.1663 | 13.3337 | 12.4 | 11.1905 | 9.9611 | 8.46 | 7.1232 | 5.7789 | 4.4526 | 3.0884 | -3.3821 | -4.6568 | -5.2368 | 11.9105 | 11.0758 | 10.1453 | 8.9432 | 7.7284 | 6.2211 | 4.8674 | 3.5063 | 2.1674 | 0.79474 | -5.7337 | -7.1716 | -7.8084
|  | CRAIGTON | HT |  |  |  |  | 14.3084 | 13.5663 | 12.6926 | 11.6232 | 10.5463 | 9.2116 | 8.0021 | 6.7926 | 5.5211 | 4.3021 | -1.1568 | -2.2074 | -2.8253 | 14.0568 | 13.2011 | 12.1811 | 10.9263 | 9.6537 | 8.1179 | 6.7305 | 5.3442 | 3.8926 | 2.5021 | -3.7947 | -4.8768 | -5.5337 | 11.8021 | 10.9432 | 9.9284 | 8.6821 | 7.4263 | 5.8884 | 4.4968 | 3.1074 | 1.6474 | 0.24737 | -6.0558 | -7.1905 | -7.8674
|  | CRAIGTON | HE |  |  |  |  | 14.5432 | 13.8 | 13.1568 | 12.1937 | 11.2211 | 9.9589 | 8.8684 | 7.7589 | 6.6558 | 5.5516 | 0.31684 | -0.57579 | -1.2379 | 14.2874 | 13.4442 | 12.6905 | 11.5484 | 10.3926 | 8.9474 | 7.6979 | 6.4263 | 5.1589 | 3.8895 | -2.1632 | -3.0053 | -3.5611 | 11.8021 | 10.9432 | 9.9284 | 8.6821 | 7.4263 | 5.8884 | 4.4968 | 3.1074 | 1.6474 | 0.24737 | -6.0558 | -7.1905 | -7.8674
|  | CRAIGTON | CF |  |  |  |  | 14.7232 | 14.4 | 14.0179 | 13.5821 | 13.1589 | 12.6379 | 12.14 | 11.6032 | 11.0316 | 10.4242 | 7.1505 | 6.5389 | 6.1916 | 14.3579 | 14.1442 | 13.7 | 13.1895 | 12.6895 | 12.0958 | 11.5274 | 10.9063 | 10.2432 | 9.5295 | 5.7053 | 5.1189 | 4.8011 | 12.2663 | 11.8884 | 11.4421 | 10.9316 | 10.4337 | 9.8337 | 9.2589 | 8.6368 | 7.9737 | 7.2653 | 3.4495 | 2.8042 | 2.4442
| BRACO | CRIEFF | MINIMUM HEADROOM | NN 85626 22119 | NO | YES | 0.28 | 15.7005 | 24.2695 | 23.8705 | 23.4389 | 23.0337 | 22.1232 | 21.2537 | 20.3853 | 19.3979 | 18.4011 | 13.0558 | 5.2863 | -0.41684 | 14.6589 | 22.5263 | 22.0684 | 21.5811 | 21.1379 | 20.28 | 19.4579 | 18.6442 | 17.7558 | 16.8663 | 11.9189 | 4.2263 | -1.5305 | 14.6739 | 22.8126 | 22.3684 | 21.8958 | 21.4695 | 20.4989 | 19.5716 | 18.6453 | 17.6179 | 16.5874 | 11.0621 | 2.6295 | -3.8095
|  | CRIEFF | EE |  |  |  |  | 15.7647 | 24.3737 | 24.1232 | 23.7505 | 23.3863 | 22.4474 | 21.4432 | 20.3979 | 19.4411 | 18.4779 | 13.0558 | 5.2863 | -0.41684 | 14.8 | 22.7389 | 22.3558 | 21.9389 | 21.5368 | 20.6789 | 19.7926 | 18.8653 | 18.0284 | 17.1789 | 12.3105 | 4.7042 | -1.5305 | 14.7382 | 23.0189 | 22.6389 | 22.2305 | 21.8337 | 20.8305 | 19.7758 | 18.6695 | 17.68 | 16.6832 | 11.0621 | 2.6295 | -3.8095
|  | CRIEFF | HT |  |  |  |  | 15.7005 | 24.2695 | 23.8705 | 23.4389 | 23.0337 | 22.1232 | 21.2537 | 20.3853 | 19.3979 | 18.4011 | 13.3126 | 6.2411 | 1.4253 | 14.6589 | 22.5263 | 22.0684 | 21.5811 | 21.1379 | 20.28 | 19.4579 | 18.6442 | 17.7558 | 16.8663 | 11.9189 | 4.2263 | -1.1537 | 14.6739 | 22.8126 | 22.3684 | 21.8958 | 21.4695 | 20.4989 | 19.5716 | 18.6453 | 17.6179 | 16.5874 | 11.1505 | 3.2474 | -2.1674
|  | CRIEFF | HE |  |  |  |  | 15.8458 | 24.4947 | 24.3968 | 24.1968 | 23.9263 | 23.0189 | 22.2284 | 21.4484 | 20.6516 | 19.8653 | 15.2411 | 9.36 | 2.9768 | 14.9021 | 23.0105 | 22.7326 | 22.42 | 22.1105 | 21.3 | 20.5842 | 19.8789 | 19.1442 | 18.4537 | 14.0421 | 8.0379 | 1.5484 | 14.6739 | 22.8126 | 22.3684 | 21.8958 | 21.4695 | 20.4989 | 19.5716 | 18.6453 | 17.6179 | 16.5874 | 11.1505 | 3.2474 | -2.1674
|  | CRIEFF | CF |  |  |  |  | 15.8889 | 24.5705 | 24.5147 | 24.4568 | 24.3989 | 24.0853 | 23.7505 | 23.4084 | 23.0821 | 22.8011 | 20.4053 | 16.6853 | 12.6316 | 14.9453 | 23.1768 | 23.0789 | 22.9105 | 22.7516 | 22.4095 | 22.0842 | 21.7537 | 21.4389 | 21.1558 | 18.6884 | 14.8621 | 10.5074 | 14.8624 | 23.3189 | 23.2632 | 23.1768 | 23.0274 | 22.6274 | 22.2547 | 21.8779 | 21.5274 | 21.2221 | 18.6 | 14.5179 | 10.0011
| PORT ANN | CRINAN | MINIMUM HEADROOM | NR 79620 92347 | YES | YES | 0 | 0.96211 | 0.93474 | 0.90421 | 0.87263 | 0.84316 | 0.74 | 0.61684 | 0.47789 | 0.35474 | 0.22947 | -0.48421 | -1.3242 | -1.8158 | 0.94632 | 0.91579 | 0.88526 | 0.85368 | 0.82421 | 0.74842 | 0.64632 | 0.54316 | 0.43789 | 0.33158 | -0.29158 | -1.0589 | -1.5547 | 0.96842 | 0.93579 | 0.90105 | 0.86526 | 0.83158 | 0.72842 | 0.61158 | 0.47158 | 0.34737 | 0.22105 | -0.51368 | -1.4063 | -1.9621
|  | CRINAN | EE |  |  |  |  | 0.97474 | 0.95158 | 0.92211 | 0.89263 | 0.86211 | 0.74737 | 0.61684 | 0.47789 | 0.35474 | 0.22947 | -0.48421 | -1.3242 | -1.8158 | 0.95895 | 0.93474 | 0.90526 | 0.87684 | 0.84737 | 0.76526 | 0.66211 | 0.54316 | 0.43789 | 0.33158 | -0.29158 | -1.0589 | -1.5547 | 0.98 | 0.95579 | 0.92211 | 0.88842 | 0.85579 | 0.74105 | 0.61158 | 0.47158 | 0.34737 | 0.22105 | -0.51368 | -1.4063 | -1.9621
|  | CRINAN | HT |  |  |  |  | 0.96211 | 0.93474 | 0.90421 | 0.87263 | 0.84316 | 0.74 | 0.62737 | 0.51789 | 0.39684 | 0.27368 | -0.28105 | -0.88211 | -1.26 | 0.94632 | 0.91579 | 0.88526 | 0.85368 | 0.82421 | 0.74842 | 0.64632 | 0.54947 | 0.44421 | 0.33474 | -0.17474 | -0.78105 | -1.1874 | 0.96842 | 0.93579 | 0.90105 | 0.86526 | 0.83158 | 0.72842 | 0.61263 | 0.5 | 0.37684 | 0.25263 | -0.33368 | -1.0084 | -1.44
|  | CRINAN | HE |  |  |  |  | 0.99053 | 0.97789 | 0.96316 | 0.94632 | 0.93263 | 0.82 | 0.72632 | 0.62947 | 0.52632 | 0.40316 | -0.14 | -0.72526 | -1.3611 | 0.97684 | 0.96316 | 0.94737 | 0.93158 | 0.91579 | 0.83368 | 0.76 | 0.68211 | 0.59263 | 0.47789 | -0.013684 | -0.57053 | -1.1653 | 0.96842 | 0.93579 | 0.90105 | 0.86526 | 0.83158 | 0.72842 | 0.61263 | 0.5 | 0.37684 | 0.25263 | -0.33368 | -1.0084 | -1.44
|  | CRINAN | CF |  |  |  |  | 0.99789 | 0.99158 | 0.98316 | 0.97474 | 0.96632 | 0.92316 | 0.88316 | 0.84526 | 0.80632 | 0.75895 | 0.50211 | 0.14211 | -0.21158 | 0.98632 | 0.97895 | 0.96842 | 0.96 | 0.95158 | 0.92105 | 0.89053 | 0.85895 | 0.82842 | 0.78211 | 0.54 | 0.19263 | -0.15895 | 0.99368 | 0.98947 | 0.98316 | 0.97895 | 0.97263 | 0.92947 | 0.89053 | 0.85158 | 0.81053 | 0.75474 | 0.47895 | 0.084211 | -0.30842
| PORT ANN | CROMALT | MINIMUM HEADROOM | NN 08395 07755 | YES | YES | 0 | 2.6221 | 2.6042 | 2.5863 | 2.5695 | 3.0516 | 3.0253 | 2.9989 | 2.9716 | 2.9432 | 2.9158 | 2.7242 | 2.4684 | 2.2874 | 2.6253 | 2.6158 | 2.6021 | 2.5842 | 3.0663 | 3.0411 | 3.0158 | 2.9905 | 2.9653 | 2.94 | 2.7442 | 2.4589 | 2.2537 | 2.6337 | 2.6242 | 2.6137 | 2.6021 | 3.0832 | 3.0558 | 3.0284 | 3.0011 | 2.9726 | 2.9442 | 2.7389 | 2.4558 | 2.2547
|  | CROMALT | EE |  |  |  |  | 2.6295 | 2.6168 | 2.6011 | 2.5863 | 3.0737 | 3.0463 | 3.0168 | 2.9895 | 2.9642 | 2.9379 | 2.7474 | 2.5042 | 2.2979 | 2.6295 | 2.6221 | 2.6137 | 2.6042 | 3.0895 | 3.0653 | 3.0411 | 3.0147 | 2.9926 | 2.9695 | 2.7853 | 2.5326 | 2.3 | 2.6379 | 2.6305 | 2.6211 | 2.6126 | 3.1032 | 3.0779 | 3.0495 | 3.0211 | 2.9947 | 2.9695 | 2.7695 | 2.5053 | 2.2768
|  | CROMALT | HT |  |  |  |  | 2.6221 | 2.6042 | 2.5863 | 2.5695 | 3.0516 | 3.0253 | 2.9989 | 2.9716 | 2.9432 | 2.9158 | 2.7242 | 2.4684 | 2.2874 | 2.6253 | 2.6158 | 2.6021 | 2.5842 | 3.0663 | 3.0411 | 3.0158 | 2.9905 | 2.9653 | 2.94 | 2.7442 | 2.4589 | 2.2537 | 2.6337 | 2.6242 | 2.6137 | 2.6021 | 3.0832 | 3.0558 | 3.0284 | 3.0011 | 2.9726 | 2.9442 | 2.7389 | 2.4558 | 2.2547
|  | CROMALT | HE |  |  |  |  | 2.64 | 2.6316 | 2.6242 | 2.6147 | 3.1042 | 3.0811 | 3.0611 | 3.0411 | 3.0137 | 2.9768 | 2.8211 | 2.6284 | 2.4211 | 2.6347 | 2.6295 | 2.6242 | 2.6179 | 3.1116 | 3.0989 | 3.0853 | 3.0674 | 3.0411 | 3.0042 | 2.8495 | 2.6432 | 2.4211 | 2.6337 | 2.6242 | 2.6137 | 2.6021 | 3.0832 | 3.0558 | 3.0284 | 3.0011 | 2.9726 | 2.9442 | 2.7389 | 2.4558 | 2.2547
|  | CROMALT | CF |  |  |  |  | 2.6463 | 2.64 | 2.6347 | 2.6295 | 3.1253 | 3.1137 | 3.1032 | 3.0937 | 3.0842 | 3.0621 | 2.9737 | 2.8505 | 2.7095 | 2.6379 | 2.6347 | 2.6316 | 2.6284 | 3.1253 | 3.12 | 3.1147 | 3.1095 | 3.1032 | 3.0832 | 2.9926 | 2.8632 | 2.7063 | 2.6463 | 2.6432 | 2.64 | 2.6368 | 3.1337 | 3.1263 | 3.1179 | 3.1116 | 3.1042 | 3.0958 | 3 | 2.8642 | 2.7084
| ALNESS | CROSSHILLS | MINIMUM HEADROOM | NH 65470 70156 | NO | YES | 0 | 16.6921 | 16.4963 | 16.29 | 16.0858 | 15.7879 | 14.7216 | 13.79 | 12.8605 | 12.01 | 11.4689 | 9.4353 | 8.2658 | 6.2679 | 15.0958 | 14.9389 | 14.7011 | 14.4674 | 14.1116 | 12.9242 | 11.8989 | 10.8768 | 9.9632 | 9.3347 | 7.7895 | 6.7347 | 5.0211 | 15.775 | 15.6592 | 15.4897 | 15.2624 | 14.9192 | 13.7582 | 12.7129 | 11.6645 | 10.7066 | 10.0792 | 8.3487 | 7.115 | 5.4508
|  | CROSSHILLS | EE |  |  |  |  | 16.7679 | 16.6247 | 16.4511 | 16.2763 | 16.0132 | 15.7153 | 15.3795 | 14.4079 | 13.4805 | 12.7668 | 10.0826 | 8.5679 | 7.31 | 15.1432 | 15.0484 | 14.9 | 14.7042 | 14.3832 | 14.0389 | 13.7347 | 12.6958 | 11.6916 | 10.8484 | 8.2253 | 6.8958 | 5.5853 | 15.8203 | 15.7276 | 15.6171 | 15.4824 | 15.1729 | 14.8392 | 14.4918 | 13.4455 | 12.4076 | 11.5855 | 8.6845 | 7.115 | 5.7118
|  | CROSSHILLS | HT |  |  |  |  | 16.6921 | 16.4963 | 16.29 | 16.0858 | 15.7879 | 14.7216 | 13.79 | 12.8605 | 12.01 | 11.4689 | 9.8268 | 8.7658 | 7.2447 | 15.0958 | 14.9389 | 14.7011 | 14.4674 | 14.1116 | 12.9242 | 11.8989 | 10.8768 | 9.9632 | 9.3347 | 7.7895 | 6.7347 | 5.0211 | 15.775 | 15.6592 | 15.4897 | 15.2624 | 14.9192 | 13.7582 | 12.7129 | 11.6645 | 10.7066 | 10.0792 | 8.3487 | 7.2055 | 5.4508
|  | CROSSHILLS | HE |  |  |  |  | 16.8311 | 16.77 | 16.6942 | 16.5647 | 16.3837 | 15.95 | 15.6658 | 15.0258 | 14.3805 | 11.6742 | 9.4353 | 8.2658 | 6.2679 | 15.2105 | 15.1463 | 15.0758 | 14.9989 | 14.8084 | 14.3716 | 14.1232 | 13.4305 | 12.7463 | 10.4926 | 8.2126 | 7.0958 | 5.0747 | 15.775 | 15.6592 | 15.4897 | 15.2624 | 14.9192 | 13.7582 | 12.7129 | 11.6645 | 10.7066 | 10.0792 | 8.3487 | 7.2055 | 5.4508
|  | CROSSHILLS | CF |  |  |  |  | 16.8668 | 16.8311 | 16.7932 | 16.7532 | 16.6711 | 16.4858 | 16.3521 | 16.2216 | 15.9321 | 15.6195 | 14.1532 | 13.3226 | 11.9953 | 15.2474 | 15.2105 | 15.1716 | 15.1316 | 15.0884 | 14.9526 | 14.8274 | 14.7042 | 14.3484 | 13.9874 | 12.4 | 11.5853 | 10.1421 | 15.9192 | 15.8834 | 15.8455 | 15.8055 | 15.7655 | 15.6634 | 15.5697 | 15.4308 | 15.0803 | 14.7297 | 13.1255 | 12.2287 | 10.7308
| KEITH 1 | CULLEN | MINIMUM HEADROOM | NJ 51590 65032 | YES | YES | 0 | 7.4126 | 7.3421 | 7.2558 | 7.1705 | 7.0484 | 6.6474 | 6.2358 | 5.76 | 5.3463 | 4.9274 | 0.49263 | -3.4316 | -6.3811 | 7.2158 | 7.0495 | 6.8232 | 6.5832 | 6.3789 | 6.0137 | 5.6526 | 5.2842 | 4.9305 | 4.5716 | 0.53474 | -3.3884 | -6.4242 | 7.3095 | 7.1632 | 6.9642 | 6.7547 | 6.5716 | 6.1716 | 5.7495 | 5.2695 | 4.8516 | 4.4221 | -0.18421 | -4.4011 | -7.7916
|  | CULLEN | EE |  |  |  |  | 7.4421 | 7.3863 | 7.3084 | 7.2274 | 7.1453 | 6.7663 | 6.2358 | 5.76 | 5.3463 | 4.9274 | 0.49263 | -3.4316 | -6.3811 | 7.3011 | 7.1695 | 7.0021 | 6.7789 | 6.5726 | 6.1663 | 5.6905 | 5.2842 | 4.9305 | 4.5716 | 0.64526 | -3.2168 | -6.4242 | 7.3832 | 7.2674 | 7.1137 | 6.9168 | 6.7326 | 6.2789 | 5.7495 | 5.2695 | 4.8516 | 4.4221 | -0.18421 | -4.4011 | -7.7916
|  | CULLEN | HT |  |  |  |  | 7.4126 | 7.3421 | 7.2558 | 7.1705 | 7.0484 | 6.6474 | 6.2495 | 5.8695 | 5.4484 | 5.0305 | 0.68211 | -2.9432 | -5.4305 | 7.2158 | 7.0495 | 6.8232 | 6.5832 | 6.3789 | 6.0137 | 5.6526 | 5.3137 | 4.9442 | 4.5832 | 0.53474 | -3.3884 | -6.1632 | 7.3095 | 7.1632 | 6.9642 | 6.7547 | 6.5716 | 6.1716 | 5.7716 | 5.3811 | 4.9474 | 4.5189 | -0.047368 | -4.18 | -7.0358
|  | CULLEN | HE |  |  |  |  | 7.4832 | 7.4463 | 7.4032 | 7.3558 | 7.3053 | 6.9747 | 6.6032 | 6.2621 | 5.9274 | 5.5221 | 2.3221 | -0.67895 | -3.9495 | 7.3579 | 7.2968 | 7.1621 | 6.9716 | 6.8147 | 6.4168 | 6.0495 | 5.76 | 5.4779 | 5.1095 | 2.1358 | -0.92526 | -4.2611 | 7.3095 | 7.1632 | 6.9642 | 6.7547 | 6.5716 | 6.1716 | 5.7716 | 5.3811 | 4.9474 | 4.5189 | -0.047368 | -4.18 | -7.0358
|  | CULLEN | CF |  |  |  |  | 7.5042 | 7.4853 | 7.4621 | 7.4368 | 7.4126 | 7.2853 | 7.1716 | 7.0579 | 6.96 | 6.8821 | 5.5884 | 3.6768 | 1.5779 | 7.38 | 7.3611 | 7.3368 | 7.2821 | 7.2137 | 7.0579 | 6.8979 | 6.7105 | 6.5811 | 6.3189 | 5.0095 | 3.0632 | 0.79684 | 7.4653 | 7.4463 | 7.4232 | 7.3663 | 7.3053 | 7.1305 | 6.9579 | 6.7653 | 6.6221 | 6.3874 | 5.0484 | 2.9463 | 0.56737
| INVERNESS | CULLODEN | MINIMUM HEADROOM | NH 71240 45502 | NO | YES | 0.165 | 17.6487 | 17.0255 | 30.2497 | 29.3455 | 28.5139 | 27.4129 | 26.3329 | 25.2687 | 24.1929 | 23.6255 | 21.1403 | 19.3139 | 17.995 | 16.7297 | 15.8866 | 27.4887 | 26.4718 | 25.5403 | 24.3603 | 23.2024 | 22.0634 | 20.9234 | 20.3824 | 17.9192 | 16.0603 | 14.6518 | 16.4571 | 16.1487 | 28.4955 | 27.4755 | 26.5408 | 25.3218 | 24.1261 | 22.9461 | 21.7566 | 21.1661 | 18.5124 | 16.5376 | 15.0829
|  | CULLODEN | EE |  |  |  |  | 17.7382 | 17.2761 | 30.6055 | 29.7729 | 29.0076 | 27.9834 | 26.9297 | 25.8624 | 24.8434 | 24.3329 | 21.7782 | 19.4655 | 18.2245 | 16.9276 | 16.1834 | 27.8771 | 26.9413 | 26.0824 | 24.9971 | 23.8961 | 22.7782 | 21.7024 | 21.2234 | 18.8403 | 16.7171 | 15.4666 | 16.5466 | 16.3729 | 28.8818 | 27.9418 | 27.0797 | 25.945 | 24.7861 | 23.6082 | 22.4808 | 21.9482 | 19.2776 | 16.8482 | 15.5018
|  | CULLODEN | HT |  |  |  |  | 17.6487 | 17.0255 | 30.2497 | 29.3455 | 28.5139 | 27.4129 | 26.3329 | 25.2687 | 24.1929 | 23.6255 | 21.1403 | 19.3139 | 17.995 | 16.7297 | 15.8866 | 27.4887 | 26.4718 | 25.5403 | 24.3603 | 23.2024 | 22.0634 | 20.9234 | 20.3824 | 17.9192 | 16.0603 | 14.6518 | 16.4571 | 16.1487 | 28.4955 | 27.4755 | 26.5408 | 25.3218 | 24.1261 | 22.9461 | 21.7566 | 21.1661 | 18.5124 | 16.5376 | 15.0829
|  | CULLODEN | HE |  |  |  |  | 17.8592 | 17.6076 | 31.0961 | 30.3855 | 29.7361 | 28.7845 | 27.8908 | 26.9929 | 26.1066 | 25.7382 | 24.2108 | 22.9792 | 21.7529 | 17.1729 | 16.5771 | 28.4076 | 27.5982 | 26.8624 | 25.8634 | 24.9129 | 23.9603 | 23.0182 | 22.6803 | 21.3076 | 20.2245 | 19.1424 | 16.4571 | 16.1487 | 28.4955 | 27.4755 | 26.5408 | 25.3218 | 24.1261 | 22.9461 | 21.7566 | 21.1661 | 18.5124 | 16.5376 | 15.0829
|  | CULLODEN | CF |  |  |  |  | 17.9234 | 17.8561 | 31.8666 | 31.5129 | 31.2245 | 30.7929 | 30.3487 | 29.8782 | 29.3908 | 29.1666 | 28.2318 | 27.3624 | 26.7287 | 17.2371 | 17.1697 | 29.3855 | 28.9182 | 28.5539 | 28.095 | 27.6161 | 27.1066 | 26.5718 | 26.3403 | 25.4382 | 24.6413 | 24.0476 | 16.7318 | 16.6645 | 29.9429 | 29.8682 | 29.5629 | 29.0839 | 28.5871 | 28.0608 | 27.5113 | 27.2692 | 26.2871 | 25.3766 | 24.705
| CRAIGIEBUCKLER | CULTER | MINIMUM HEADROOM | NJ 84009 00884 | NO | YES | 0 | 17.2295 | 17.1032 | 16.7442 | 16.36 | 15.9495 | 15.4242 | 14.9958 | 14.5579 | 14.0684 | 13.5232 | 11.7758 | 9.7979 | 7.5368 | 16.7358 | 16.4063 | 15.9884 | 15.5684 | 15.1179 | 14.5916 | 14.1779 | 13.7526 | 13.2789 | 12.7421 | 11.0705 | 8.9968 | 6.7705 | 16.9253 | 16.5558 | 16.1979 | 15.8337 | 15.3989 | 14.8411 | 14.3895 | 13.9284 | 13.4105 | 12.8263 | 10.98 | 8.7863 | 6.3926
|  | CULTER | EE |  |  |  |  | 17.2842 | 17.1853 | 16.9495 | 16.6084 | 16.2368 | 15.7232 | 15.3126 | 14.8737 | 14.4705 | 14.0526 | 11.8189 | 9.8589 | 7.5368 | 16.7926 | 16.5779 | 16.2116 | 15.84 | 15.4316 | 14.9284 | 14.5589 | 14.1579 | 13.7853 | 13.3958 | 11.3042 | 9.5295 | 7.0021 | 16.98 | 16.7074 | 16.3916 | 16.0737 | 15.6989 | 15.1611 | 14.7368 | 14.2811 | 13.8632 | 13.4284 | 11.08 | 9.0242 | 6.3926
|  | CULTER | HT |  |  |  |  | 17.2295 | 17.1032 | 16.7442 | 16.36 | 15.9495 | 15.4242 | 14.9958 | 14.5579 | 14.0684 | 13.5232 | 11.7758 | 9.7979 | 7.7916 | 16.7358 | 16.4063 | 15.9884 | 15.5684 | 15.1179 | 14.5916 | 14.1779 | 13.7526 | 13.2789 | 12.7421 | 11.0705 | 8.9968 | 6.7705 | 16.9253 | 16.5558 | 16.1979 | 15.8337 | 15.3989 | 14.8411 | 14.3895 | 13.9284 | 13.4105 | 12.8263 | 10.98 | 8.7863 | 6.4989
|  | CULTER | HE |  |  |  |  | 17.3537 | 17.2874 | 17.2147 | 16.9589 | 16.6611 | 16.1895 | 15.8937 | 15.5516 | 15.1937 | 14.8242 | 13.3253 | 11.5989 | 9.1463 | 16.8663 | 16.7884 | 16.5284 | 16.2116 | 15.8789 | 15.4274 | 15.1632 | 14.8453 | 14.5084 | 14.1558 | 12.7621 | 11.0642 | 8.5389 | 16.9253 | 16.5558 | 16.1979 | 15.8337 | 15.3989 | 14.8411 | 14.3895 | 13.9284 | 13.4105 | 12.8263 | 10.98 | 8.7863 | 6.4989
|  | CULTER | CF |  |  |  |  | 17.3884 | 17.3505 | 17.3084 | 17.2653 | 17.2211 | 17.08 | 16.9358 | 16.7905 | 16.6463 | 16.5105 | 15.5611 | 14.4547 | 12.8568 | 16.9042 | 16.86 | 16.8137 | 16.7358 | 16.5747 | 16.3726 | 16.2379 | 16.1021 | 15.9632 | 15.8284 | 14.8821 | 13.7853 | 12.0611 | 17.0842 | 17.0463 | 16.9832 | 16.8484 | 16.7116 | 16.5095 | 16.3653 | 16.2211 | 16.0779 | 15.9463 | 15 | 13.8295 | 12.02
| ELGIN | CUMMING STREET | MINIMUM HEADROOM | NJ 21542 63007 | NO | YES | 0.113 | 23.9317 | 23.7696 | 23.5244 | 23.2149 | 22.9559 | 22.7738 | 22.5959 | 22.4223 | 22.2444 | 22.0728 | 21.4581 | 20.8317 | 20.3086 | 23.6491 | 23.5459 | 23.4396 | 23.3302 | 23.2207 | 23.0902 | 22.9302 | 22.7249 | 22.5154 | 22.3123 | 21.5375 | 20.5554 | 19.6691 | 24.4841 | 24.3809 | 24.2736 | 24.1641 | 23.9757 | 23.7536 | 23.5325 | 23.3178 | 23.0988 | 22.8873 | 22.0841 | 21.1031 | 20.2294
|  | CUMMING STREET | EE |  |  |  |  | 23.997 | 23.8675 | 23.6791 | 23.4181 | 23.1738 | 22.9833 | 22.8086 | 22.6559 | 22.5128 | 22.3717 | 21.7265 | 21.3012 | 20.9023 | 23.6902 | 23.6091 | 23.5238 | 23.4344 | 23.3407 | 23.2354 | 23.1312 | 23.0228 | 22.8565 | 22.6944 | 21.9333 | 21.4333 | 20.8017 | 24.5252 | 24.4441 | 24.3588 | 24.2673 | 24.1736 | 24.0315 | 23.8041 | 23.6188 | 23.4441 | 23.2725 | 22.462 | 21.9336 | 21.2862
|  | CUMMING STREET | HT |  |  |  |  | 23.9317 | 23.7696 | 23.5244 | 23.2149 | 22.9559 | 22.7738 | 22.5959 | 22.4223 | 22.2444 | 22.0728 | 21.4581 | 20.8317 | 20.3086 | 23.6491 | 23.5459 | 23.4396 | 23.3302 | 23.2207 | 23.0902 | 22.9302 | 22.7249 | 22.5154 | 22.3123 | 21.5375 | 20.5554 | 19.6691 | 24.4841 | 24.3809 | 24.2736 | 24.1641 | 23.9757 | 23.7536 | 23.5325 | 23.3178 | 23.0988 | 22.8873 | 22.0841 | 21.1031 | 20.2294
|  | CUMMING STREET | HE |  |  |  |  | 24.0802 | 23.9896 | 23.8307 | 23.5959 | 23.3812 | 23.237 | 23.1159 | 23.0044 | 22.8959 | 22.7949 | 22.4002 | 22.0612 | 21.8349 | 23.7417 | 23.6838 | 23.6217 | 23.5533 | 23.4807 | 23.3923 | 23.3123 | 23.2344 | 23.1596 | 23.0912 | 22.7975 | 22.3754 | 22.1144 | 24.4841 | 24.3809 | 24.2736 | 24.1641 | 23.9757 | 23.7536 | 23.5325 | 23.3178 | 23.0988 | 22.8873 | 22.0841 | 21.1031 | 20.2294
|  | CUMMING STREET | CF |  |  |  |  | 24.1202 | 24.0633 | 23.9886 | 23.8875 | 23.7981 | 23.7212 | 23.6412 | 23.5612 | 23.4907 | 23.4202 | 23.1075 | 22.8917 | 22.7423 | 23.7691 | 23.7333 | 23.6965 | 23.6586 | 23.6196 | 23.5765 | 23.5323 | 23.4881 | 23.4449 | 23.4038 | 23.2175 | 23.1081 | 23.0481 | 24.6041 | 24.5683 | 24.5315 | 24.4925 | 24.4536 | 24.4062 | 24.3588 | 24.3115 | 24.2652 | 24.222 | 24.0167 | 23.8831 | 23.8052
| ST FILLANS | DALCHONZIE | MINIMUM HEADROOM | NN 74079 21921 | YES | YES | 0 | 6.4537 | 6.4063 | 6.2926 | 6.1389 | 5.9779 | 5.7242 | 5.4958 | 5.2358 | 4.9905 | 4.7389 | 3.4389 | 1.9726 | 1.0579 | 6.1874 | 6.0832 | 5.9263 | 5.7516 | 5.5726 | 5.3474 | 5.1463 | 4.9495 | 4.72 | 4.4968 | 3.4442 | 2.1611 | 1.2284 | 6.28 | 6.1568 | 6.0011 | 5.8274 | 5.6484 | 5.3874 | 5.1526 | 4.8916 | 4.6432 | 4.3874 | 3.0789 | 1.5632 | 0.53368
|  | DALCHONZIE | EE |  |  |  |  | 6.4726 | 6.4368 | 6.3895 | 6.2716 | 6.1421 | 5.8326 | 5.52 | 5.2358 | 4.9905 | 4.7389 | 3.4389 | 1.9726 | 1.0579 | 6.2211 | 6.1432 | 6.0421 | 5.9063 | 5.76 | 5.4779 | 5.2042 | 4.9653 | 4.7589 | 4.5421 | 3.4442 | 2.1611 | 1.2284 | 6.3 | 6.2316 | 6.1147 | 5.9789 | 5.8305 | 5.5053 | 5.1821 | 4.8916 | 4.6432 | 4.3884 | 3.0789 | 1.5632 | 0.53368
|  | DALCHONZIE | HT |  |  |  |  | 6.4537 | 6.4063 | 6.2926 | 6.1389 | 5.9779 | 5.7242 | 5.4958 | 5.2695 | 5.0063 | 4.7474 | 3.7695 | 2.7316 | 2.0042 | 6.1874 | 6.0832 | 5.9263 | 5.7516 | 5.5726 | 5.3474 | 5.1463 | 4.9495 | 4.72 | 4.4968 | 3.6411 | 2.6179 | 1.84 | 6.28 | 6.1568 | 6.0011 | 5.8274 | 5.6484 | 5.3874 | 5.1526 | 4.9211 | 4.6516 | 4.3874 | 3.3842 | 2.2558 | 1.4442
|  | DALCHONZIE | HE |  |  |  |  | 6.4989 | 6.4747 | 6.4474 | 6.3958 | 6.2874 | 5.9937 | 5.7716 | 5.5674 | 5.3653 | 5.1642 | 4.2853 | 3.1737 | 1.9474 | 6.2663 | 6.2084 | 6.1421 | 6.0368 | 5.9095 | 5.6474 | 5.4568 | 5.2874 | 5.1168 | 4.9474 | 4.2147 | 3.1737 | 2.0274 | 6.28 | 6.1568 | 6.0011 | 5.8274 | 5.6484 | 5.3874 | 5.1526 | 4.9211 | 4.6516 | 4.3874 | 3.3842 | 2.2558 | 1.4442
|  | DALCHONZIE | CF |  |  |  |  | 6.5126 | 6.4989 | 6.4842 | 6.4684 | 6.4526 | 6.3747 | 6.3 | 6.1905 | 6.1042 | 6.0316 | 5.5989 | 4.9137 | 4.2379 | 6.2916 | 6.2653 | 6.2358 | 6.2032 | 6.1695 | 6.0863 | 5.9842 | 5.8811 | 5.8042 | 5.7337 | 5.3516 | 4.7063 | 4.0347 | 6.3421 | 6.3274 | 6.3126 | 6.2947 | 6.2589 | 6.1432 | 6.0274 | 5.9095 | 5.8211 | 5.7421 | 5.2968 | 4.5589 | 3.8158
| NAIRN | DALCROSS | MINIMUM HEADROOM | NH 76333 51847 | NO | YES | 0.05 | 15.3442 | 15.0758 | 14.7232 | 14.2937 | 13.7137 | 12.7074 | 11.7032 | 10.6884 | 9.7011 | 9.3274 | 7.9158 | 6.5832 | 6.1042 | 14.2258 | 13.9142 | 13.4984 | 12.99 | 12.2995 | 11.1616 | 10.0237 | 8.8774 | 7.7805 | 7.4258 | 6.3637 | 5.3195 | 4.9121 | 14.7503 | 14.4545 | 14.0555 | 13.5576 | 12.8766 | 11.7061 | 10.5345 | 9.3524 | 8.2124 | 7.8113 | 6.4187 | 5.0924 | 4.6039
|  | DALCROSS | EE |  |  |  |  | 15.3674 | 15.1105 | 14.7621 | 14.3368 | 13.7611 | 12.9253 | 12.0463 | 10.9716 | 9.9305 | 9.4874 | 7.9158 | 6.5832 | 6.1042 | 14.25 | 13.9532 | 13.5437 | 13.0416 | 12.3584 | 11.4405 | 10.4921 | 9.3068 | 8.1489 | 7.7132 | 6.3637 | 5.3195 | 4.9121 | 14.7755 | 14.4913 | 14.0976 | 13.6061 | 12.9324 | 11.9713 | 10.9692 | 9.7303 | 8.5261 | 8.0429 | 6.4187 | 5.0924 | 4.6039
|  | DALCROSS | HT |  |  |  |  | 15.3442 | 15.0758 | 14.7232 | 14.2937 | 13.7137 | 12.7074 | 11.7032 | 10.6884 | 9.7011 | 9.3274 | 8.3705 | 7.7453 | 7.4337 | 14.2258 | 13.9142 | 13.4984 | 12.99 | 12.2995 | 11.1616 | 10.0237 | 8.8774 | 7.7805 | 7.4258 | 6.6384 | 6.1089 | 5.8258 | 14.7503 | 14.4545 | 14.0555 | 13.5576 | 12.8766 | 11.7061 | 10.5345 | 9.3524 | 8.2124 | 7.8113 | 6.8429 | 6.205 | 5.8776
|  | DALCROSS | HE |  |  |  |  | 15.3989 | 15.1579 | 14.8358 | 14.4379 | 13.8874 | 13.0453 | 12.2379 | 11.3126 | 10.3874 | 10.0779 | 8.7053 | 7.9116 | 7.0705 | 14.2837 | 14.0047 | 13.6205 | 13.1447 | 12.4847 | 11.5658 | 10.6742 | 9.6374 | 8.6037 | 8.3132 | 7.0353 | 6.43 | 5.7858 | 14.7503 | 14.4545 | 14.0555 | 13.5576 | 12.8766 | 11.7061 | 10.5345 | 9.3524 | 8.2124 | 7.8113 | 6.8429 | 6.205 | 5.8776
|  | DALCROSS | CF |  |  |  |  | 15.5116 | 15.4189 | 15.2516 | 15.06 | 14.8105 | 14.4568 | 14.0832 | 13.6811 | 13.1926 | 13.0284 | 12.3232 | 11.7695 | 11.3621 | 14.4089 | 14.3058 | 14.1184 | 13.8889 | 13.59 | 13.2016 | 12.7816 | 12.3279 | 11.7658 | 11.5879 | 10.8932 | 10.4363 | 10.0932 | 14.9334 | 14.8303 | 14.645 | 14.4334 | 14.1471 | 13.7482 | 13.3208 | 12.8597 | 12.2861 | 12.0987 | 11.3282 | 10.765 | 10.3461
| TAYNUILT | DALMALLY | MINIMUM HEADROOM | NN 15538 26930 | YES | YES | 0 | 1.0495 | 1.0442 | 1.0368 | 1.0316 | 1.0253 | 1.0189 | 1.0137 | 1.0074 | 1.0021 | 0.99684 | 0.97579 | 0.96 | 0.94737 | 1.0253 | 1.0221 | 1.0179 | 1.0147 | 1.0105 | 1.0063 | 1 | 0.99474 | 0.98842 | 0.98211 | 0.96105 | 0.94316 | 0.92947 | 1.0316 | 1.0253 | 1.0179 | 1.0116 | 1.0053 | 0.99789 | 0.99263 | 0.98632 | 0.98 | 0.97474 | 0.95158 | 0.93474 | 0.92
|  | DALMALLY | EE |  |  |  |  | 1.0537 | 1.0484 | 1.0432 | 1.0379 | 1.0347 | 1.0295 | 1.0253 | 1.02 | 1.0158 | 1.0116 | 0.99474 | 0.98211 | 0.97368 | 1.0274 | 1.0242 | 1.0211 | 1.0179 | 1.0158 | 1.0126 | 1.0095 | 1.0063 | 1.0032 | 0.99895 | 0.98105 | 0.96737 | 0.95684 | 1.0347 | 1.0305 | 1.0242 | 1.0189 | 1.0147 | 1.0095 | 1.0053 | 1 | 0.99474 | 0.99158 | 0.97263 | 0.95895 | 0.94842
|  | DALMALLY | HT |  |  |  |  | 1.0495 | 1.0442 | 1.0368 | 1.0316 | 1.0253 | 1.0189 | 1.0137 | 1.0074 | 1.0021 | 0.99684 | 0.97579 | 0.96 | 0.94737 | 1.0253 | 1.0221 | 1.0179 | 1.0147 | 1.0105 | 1.0063 | 1 | 0.99474 | 0.98842 | 0.98211 | 0.96105 | 0.94316 | 0.92947 | 1.0316 | 1.0253 | 1.0179 | 1.0116 | 1.0053 | 0.99789 | 0.99263 | 0.98632 | 0.98 | 0.97474 | 0.95158 | 0.93474 | 0.92
|  | DALMALLY | HE |  |  |  |  | 1.0579 | 1.0537 | 1.0516 | 1.0484 | 1.0453 | 1.0421 | 1.0389 | 1.0358 | 1.0326 | 1.0295 | 1.0211 | 1.0095 | 0.99474 | 1.0295 | 1.0274 | 1.0253 | 1.0232 | 1.0211 | 1.0189 | 1.0168 | 1.0147 | 1.0126 | 1.0105 | 1.0053 | 0.99579 | 0.97895 | 1.0316 | 1.0253 | 1.0179 | 1.0116 | 1.0053 | 0.99789 | 0.99263 | 0.98632 | 0.98 | 0.97474 | 0.95158 | 0.93474 | 0.92
|  | DALMALLY | CF |  |  |  |  | 1.06 | 1.0579 | 1.0558 | 1.0537 | 1.0526 | 1.0505 | 1.0484 | 1.0474 | 1.0453 | 1.0432 | 1.0358 | 1.0305 | 1.0189 | 1.0305 | 1.0295 | 1.0284 | 1.0274 | 1.0263 | 1.0253 | 1.0242 | 1.0232 | 1.0221 | 1.0211 | 1.0168 | 1.0147 | 1.0053 | 1.0379 | 1.0368 | 1.0358 | 1.0347 | 1.0337 | 1.0326 | 1.0305 | 1.0284 | 1.0263 | 1.0242 | 1.0168 | 1.0105 | 0.99684
| TAYNUILT | DALMALLY SCHOOL | MINIMUM HEADROOM | NN 17249 27128 | YES | YES | 0 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725
|  | DALMALLY SCHOOL | EE |  |  |  |  | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.47599 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933 | 0.51933
|  | DALMALLY SCHOOL | HT |  |  |  |  | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.47625 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657 | 0.51657
|  | DALMALLY SCHOOL | HE |  |  |  |  | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.47577 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725 | 0.48725
|  | DALMALLY SCHOOL | CF |  |  |  |  | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.63079 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.47566 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445 | 0.51445
| INVERNESS | DALNEIGH | MINIMUM HEADROOM | NH 65564 44955 | YES | YES | 0 | 13.3105 | 12.9684 | 12.6484 | 12.3274 | 12.0063 | 11.64 | 11.2789 | 10.8737 | 10.4768 | 10.0958 | 8.2979 | 6.8621 | 5.6453 | 13.4989 | 13.2084 | 12.7758 | 12.3484 | 11.9221 | 11.4463 | 10.9895 | 10.5474 | 10.1263 | 9.7263 | 7.7747 | 6.1968 | 4.8389 | 13.8 | 13.5695 | 13.3337 | 13.0505 | 12.64 | 12.1737 | 11.7263 | 11.28 | 10.8547 | 10.4484 | 8.4779 | 6.8874 | 5.5263
|  | DALNEIGH | EE |  |  |  |  | 13.4411 | 13.1653 | 12.9074 | 12.6421 | 12.3726 | 12.08 | 11.7937 | 11.5063 | 11.2326 | 10.96 | 9.4663 | 8.2684 | 7.3358 | 13.5842 | 13.4011 | 13.1495 | 12.8 | 12.4484 | 12.0811 | 11.7274 | 11.3611 | 11.0105 | 10.6768 | 9.0874 | 7.8011 | 6.7653 | 13.8863 | 13.7 | 13.5084 | 13.3063 | 13.0989 | 12.7811 | 12.4316 | 12.0684 | 11.7242 | 11.3947 | 9.7737 | 8.4558 | 7.4105
|  | DALNEIGH | HT |  |  |  |  | 13.3105 | 12.9684 | 12.6484 | 12.3274 | 12.0063 | 11.64 | 11.2789 | 10.8737 | 10.4768 | 10.0958 | 8.2979 | 6.8621 | 5.6453 | 13.4989 | 13.2084 | 12.7758 | 12.3484 | 11.9221 | 11.4463 | 10.9895 | 10.5474 | 10.1263 | 9.7263 | 7.7747 | 6.1968 | 4.8389 | 13.8 | 13.5695 | 13.3337 | 13.0505 | 12.64 | 12.1737 | 11.7263 | 11.28 | 10.8547 | 10.4484 | 8.4779 | 6.8874 | 5.5263
|  | DALNEIGH | HE |  |  |  |  | 13.6232 | 13.4337 | 13.2589 | 13.0726 | 12.8789 | 12.6516 | 12.4463 | 12.2411 | 12.0421 | 11.8611 | 11.2 | 10.7674 | 10.3179 | 13.7042 | 13.5779 | 13.4421 | 13.2947 | 13.1389 | 12.9053 | 12.6589 | 12.4084 | 12.1674 | 11.9484 | 11.1337 | 10.5663 | 10.0547 | 13.8 | 13.5695 | 13.3337 | 13.0505 | 12.64 | 12.1737 | 11.7263 | 11.28 | 10.8547 | 10.4484 | 8.4779 | 6.8874 | 5.5263
|  | DALNEIGH | CF |  |  |  |  | 13.6874 | 13.6095 | 13.4947 | 13.3853 | 13.2747 | 13.1526 | 13.0316 | 12.9105 | 12.7884 | 12.6705 | 12.1358 | 11.7789 | 11.5337 | 13.7705 | 13.6926 | 13.6137 | 13.5337 | 13.4516 | 13.3642 | 13.2768 | 13.1884 | 13.0484 | 12.8916 | 12.1895 | 11.6926 | 11.3137 | 14.0663 | 13.9926 | 13.9168 | 13.8347 | 13.7516 | 13.6611 | 13.5695 | 13.4789 | 13.3884 | 13.3 | 12.8726 | 12.3821 | 12.0147
| COUPAR ANGUS | DALRULZION | MINIMUM HEADROOM | NO 13498 58153 | NO | YES | 0 | 2.8684 | 2.84 | 2.8053 | 2.7558 | 2.6884 | 2.5716 | 2.4611 | 2.3516 | 2.2358 | 2.1168 | 1.5579 | 1.1568 | 0.89895 | 2.66 | 2.6053 | 2.5463 | 2.4874 | 2.4137 | 2.3042 | 2.2 | 2.0968 | 1.9905 | 1.8821 | 1.38 | 1.1 | 0.83684 | 2.6726 | 2.6211 | 2.5653 | 2.5095 | 2.44 | 2.3211 | 2.2095 | 2.0958 | 1.9768 | 1.8516 | 1.2653 | 0.86 | 0.57895
|  | DALRULZION | EE |  |  |  |  | 2.8811 | 2.8558 | 2.8263 | 2.7968 | 2.7653 | 2.6632 | 2.5453 | 2.4274 | 2.3211 | 2.2147 | 1.6747 | 1.1568 | 0.89895 | 2.6789 | 2.6432 | 2.5968 | 2.5495 | 2.5053 | 2.4158 | 2.3126 | 2.2095 | 2.1147 | 2.0221 | 1.5558 | 1.1 | 0.85158 | 2.6853 | 2.6558 | 2.6095 | 2.5642 | 2.5189 | 2.4137 | 2.2937 | 2.1726 | 2.0642 | 1.9547 | 1.3989 | 0.86 | 0.57895
|  | DALRULZION | HT |  |  |  |  | 2.8684 | 2.84 | 2.8053 | 2.7558 | 2.6884 | 2.5716 | 2.4611 | 2.3516 | 2.2358 | 2.1168 | 1.5579 | 1.2979 | 1.0495 | 2.66 | 2.6053 | 2.5463 | 2.4874 | 2.4137 | 2.3042 | 2.2 | 2.0968 | 1.9905 | 1.8821 | 1.38 | 1.1011 | 0.83684 | 2.6726 | 2.6211 | 2.5653 | 2.5095 | 2.44 | 2.3211 | 2.2095 | 2.0958 | 1.9768 | 1.8516 | 1.2653 | 0.97684 | 0.70211
|  | DALRULZION | HE |  |  |  |  | 2.8968 | 2.8821 | 2.8642 | 2.8453 | 2.8274 | 2.7505 | 2.6853 | 2.62 | 2.5568 | 2.4821 | 2.1326 | 1.8242 | 1.5137 | 2.6958 | 2.6811 | 2.6653 | 2.64 | 2.6116 | 2.54 | 2.4758 | 2.4137 | 2.3526 | 2.2905 | 1.9937 | 1.7263 | 1.4568 | 2.6726 | 2.6211 | 2.5653 | 2.5095 | 2.44 | 2.3211 | 2.2095 | 2.0958 | 1.9768 | 1.8516 | 1.2653 | 0.97684 | 0.70211
|  | DALRULZION | CF |  |  |  |  | 2.9053 | 2.8979 | 2.8874 | 2.88 | 2.8705 | 2.84 | 2.8126 | 2.7853 | 2.7621 | 2.7411 | 2.6011 | 2.4011 | 2.2495 | 2.7042 | 2.6968 | 2.6874 | 2.68 | 2.6705 | 2.64 | 2.6095 | 2.5789 | 2.5526 | 2.5263 | 2.3842 | 2.2095 | 2.0747 | 2.7095 | 2.7021 | 2.6916 | 2.6842 | 2.6758 | 2.6442 | 2.6095 | 2.5747 | 2.5442 | 2.5158 | 2.3505 | 2.1474 | 1.9905
| BOAT OF GARTEN | DALWHINNIE | MINIMUM HEADROOM | NN 63711 84671 | YES | YES | 0 | 1.2947 | 1.2863 | 1.2705 | 1.2547 | 1.2368 | 1.08 | 0.87895 | 0.67158 | 0.47579 | 0.18737 | -1.5158 | -3.4968 | -4.9789 | 1.1379 | 1.1221 | 1.1 | 1.0779 | 1.0558 | 0.93789 | 0.75579 | 0.56632 | 0.38632 | 0.10105 | -1.4632 | -3.4116 | -5.0284 | 1.2147 | 1.1989 | 1.1758 | 1.1516 | 1.1274 | 0.96947 | 0.76842 | 0.56 | 0.38105 | 0.11053 | -1.7926 | -3.9516 | -5.6379
|  | DALWHINNIE | EE |  |  |  |  | 1.2979 | 1.2916 | 1.2737 | 1.2558 | 1.2368 | 1.08 | 0.87895 | 0.67158 | 0.49263 | 0.26737 | -1.5158 | -3.4968 | -4.9789 | 1.1453 | 1.1326 | 1.1116 | 1.0895 | 1.0663 | 0.93895 | 0.78105 | 0.62 | 0.48 | 0.28211 | -1.4632 | -3.4116 | -5.0284 | 1.2211 | 1.2095 | 1.1853 | 1.16 | 1.1347 | 0.96947 | 0.76842 | 0.56 | 0.38105 | 0.14632 | -1.7926 | -3.9516 | -5.6379
|  | DALWHINNIE | HT |  |  |  |  | 1.2947 | 1.2863 | 1.2705 | 1.2547 | 1.2379 | 1.0968 | 0.95368 | 0.80842 | 0.60632 | 0.26421 | -1.3242 | -3.1211 | -4.3379 | 1.1379 | 1.1221 | 1.1 | 1.0779 | 1.0558 | 0.94211 | 0.82632 | 0.71053 | 0.53684 | 0.19263 | -1.44 | -3.3863 | -4.7453 | 1.2147 | 1.1989 | 1.1758 | 1.1516 | 1.1274 | 0.98421 | 0.84 | 0.69263 | 0.48632 | 0.11053 | -1.6463 | -3.6916 | -5.0947
|  | DALWHINNIE | HE |  |  |  |  | 1.3021 | 1.2979 | 1.2916 | 1.2853 | 1.2779 | 1.0895 | 0.88526 | 0.67684 | 0.47579 | 0.18737 | -1.0432 | -2.5642 | -4.2305 | 1.1547 | 1.1474 | 1.1389 | 1.1295 | 1.1189 | 0.93789 | 0.75579 | 0.56632 | 0.38632 | 0.10105 | -1.0926 | -2.6474 | -4.3432 | 1.2147 | 1.1989 | 1.1758 | 1.1516 | 1.1274 | 0.98421 | 0.84 | 0.69263 | 0.48632 | 0.11053 | -1.6463 | -3.6916 | -5.0947
|  | DALWHINNIE | CF |  |  |  |  | 1.3053 | 1.3032 | 1.2979 | 1.2947 | 1.2905 | 1.2326 | 1.1842 | 1.0737 | 0.95158 | 0.81368 | 0.18842 | -0.77263 | -1.8337 | 1.16 | 1.1558 | 1.1484 | 1.1432 | 1.1368 | 1.0842 | 1.04 | 0.91895 | 0.79263 | 0.64316 | 0.0073684 | -0.97789 | -2.1137 | 1.2347 | 1.2316 | 1.2242 | 1.2189 | 1.2126 | 1.1432 | 1.0863 | 0.95684 | 0.82421 | 0.66842 | -0.022105 | -1.0895 | -2.2905
| WILLOWDALE | DENBURN | MINIMUM HEADROOM | NJ 93484 06342 | NO | YES | 0 | 24.4658 | 24.3689 | 24.2679 | 24.1605 | 24.0479 | 23.9226 | 23.7995 | 23.6784 | 23.5605 | 23.4437 | 23.0174 | 22.4963 | 21.6605 | 21.1484 | 21.0537 | 20.9558 | 20.8526 | 20.7453 | 20.6242 | 20.5084 | 20.3916 | 20.28 | 20.1684 | 19.7695 | 19.4663 | 19.2295 | 21.665 | 21.5745 | 21.4808 | 21.385 | 21.2839 | 21.1703 | 21.0587 | 20.9482 | 20.8408 | 20.7345 | 20.3618 | 20.0882 | 19.8829
|  | DENBURN | EE |  |  |  |  | 24.5163 | 24.4468 | 24.3742 | 24.2963 | 24.2121 | 24.1184 | 24.0258 | 23.9342 | 23.8447 | 23.7574 | 23.3763 | 23.1205 | 22.9174 | 21.1989 | 21.1305 | 21.0589 | 20.9842 | 20.9021 | 20.8137 | 20.7274 | 20.6411 | 20.5568 | 20.4747 | 20.12 | 19.8916 | 19.7295 | 21.7134 | 21.6482 | 21.5797 | 21.5071 | 21.4303 | 21.3461 | 21.2629 | 21.1797 | 21.0987 | 21.0197 | 20.6808 | 20.4661 | 20.3239
|  | DENBURN | HT |  |  |  |  | 24.4658 | 24.3689 | 24.2679 | 24.1605 | 24.0479 | 23.9226 | 23.7995 | 23.6784 | 23.5605 | 23.4437 | 23.0174 | 22.4963 | 21.6605 | 21.1484 | 21.0537 | 20.9558 | 20.8526 | 20.7453 | 20.6242 | 20.5084 | 20.3916 | 20.28 | 20.1684 | 19.7695 | 19.4663 | 19.2295 | 21.665 | 21.5745 | 21.4808 | 21.385 | 21.2839 | 21.1703 | 21.0587 | 20.9482 | 20.8408 | 20.7345 | 20.3618 | 20.0882 | 19.8829
|  | DENBURN | HE |  |  |  |  | 24.5458 | 24.4879 | 24.4226 | 24.3532 | 24.2805 | 24.1995 | 24.1258 | 24.0511 | 23.9816 | 23.9163 | 23.6721 | 23.5205 | 23.4216 | 21.2263 | 21.1684 | 21.1053 | 21.0368 | 20.9642 | 20.8874 | 20.8147 | 20.7453 | 20.6779 | 20.6158 | 20.3884 | 20.2537 | 20.1705 | 21.665 | 21.5745 | 21.4808 | 21.385 | 21.2839 | 21.1703 | 21.0587 | 20.9482 | 20.8408 | 20.7345 | 20.3618 | 20.0882 | 19.8829
|  | DENBURN | CF |  |  |  |  | 24.5574 | 24.5121 | 24.4647 | 24.4163 | 24.3679 | 24.3174 | 24.2658 | 24.2132 | 24.1626 | 24.1111 | 23.8879 | 23.7605 | 23.6858 | 21.2368 | 21.1926 | 21.1474 | 21.0989 | 21.0516 | 21.0011 | 20.9526 | 20.9021 | 20.8526 | 20.8021 | 20.5863 | 20.4695 | 20.4042 | 21.7492 | 21.7061 | 21.6618 | 21.6155 | 21.5692 | 21.5208 | 21.4713 | 21.4218 | 21.3734 | 21.325 | 21.1145 | 21.0029 | 20.945
| TAYNUILT | DERVAIG | MINIMUM HEADROOM | NM 42441 51227 | YES | YES | 0.18 | 3.8137 | 3.7505 | 3.6747 | 3.5789 | 3.4832 | 3.3863 | 3.2505 | 3.1379 | 3.0358 | 2.9411 | 2.5168 | 1.3947 | 1.0758 | 3.7316 | 3.6653 | 3.5811 | 3.4747 | 3.3695 | 3.2621 | 3.1105 | 2.9832 | 2.8705 | 2.7653 | 2.3116 | 1.3316 | 0.96526 | 3.7347 | 3.6853 | 3.6063 | 3.5021 | 3.3989 | 3.2937 | 3.1453 | 3.0221 | 2.9095 | 2.8074 | 2.3453 | 1.1474 | 0.78842
|  | DERVAIG | EE |  |  |  |  | 3.8411 | 3.7916 | 3.7411 | 3.6653 | 3.6053 | 3.5168 | 3.4484 | 3.3558 | 3.2653 | 3.1832 | 4.6589 | 3.6168 | 3.3758 | 3.7621 | 3.7095 | 3.6547 | 3.5716 | 3.5074 | 3.4116 | 3.3379 | 3.2326 | 3.1337 | 3.0421 | 4.9779 | 4.06 | 3.7884 | 3.7558 | 3.7158 | 3.6737 | 3.5958 | 3.5316 | 3.4368 | 3.3632 | 3.2611 | 3.1632 | 3.0726 | 4.7337 | 3.6232 | 3.3505
|  | DERVAIG | HT |  |  |  |  | 3.8137 | 3.7505 | 3.6747 | 3.5789 | 3.4832 | 3.3863 | 3.2505 | 3.1379 | 3.0358 | 2.9411 | 2.5168 | 1.3947 | 1.0758 | 3.7316 | 3.6653 | 3.5811 | 3.4747 | 3.3695 | 3.2621 | 3.1105 | 2.9832 | 2.8705 | 2.7653 | 2.3116 | 1.3316 | 0.96526 | 3.7347 | 3.6853 | 3.6063 | 3.5021 | 3.3989 | 3.2937 | 3.1453 | 3.0221 | 2.9095 | 2.8074 | 2.3453 | 1.1474 | 0.78842
|  | DERVAIG | HE |  |  |  |  | 3.8674 | 3.8463 | 3.8179 | 3.7537 | 3.7116 | 3.6274 | 3.5705 | 3.5305 | 3.4916 | 3.4579 | 3.2716 | 2.7368 | 2.6095 | 3.8042 | 3.7726 | 3.7379 | 3.6663 | 3.6221 | 3.5274 | 3.4642 | 3.4211 | 3.3789 | 3.3442 | 3.1484 | 2.6979 | 2.5526 | 3.7347 | 3.6853 | 3.6063 | 3.5021 | 3.3989 | 3.2937 | 3.1453 | 3.0221 | 2.9095 | 2.8074 | 2.3453 | 1.1474 | 0.78842
|  | DERVAIG | CF |  |  |  |  | 3.8789 | 3.8674 | 3.8558 | 3.8379 | 3.8179 | 3.7916 | 3.7684 | 3.7389 | 3.7105 | 3.6779 | 3.5568 | 3.4274 | 3.3305 | 3.8242 | 3.8042 | 3.7842 | 3.76 | 3.7379 | 3.7095 | 3.6832 | 3.6516 | 3.62 | 3.5821 | 3.4484 | 3.3032 | 3.1905 | 3.8 | 3.7853 | 3.7705 | 3.7516 | 3.7358 | 3.7168 | 3.6989 | 3.6747 | 3.6453 | 3.6084 | 3.4779 | 3.3347 | 3.2253
| BEAULY | DINGWALL | MINIMUM HEADROOM | NH 53956 59680 | NO | YES | 0 | 14.2437 | 13.9826 | 13.8405 | 13.69 | 13.5374 | 13.1332 | 12.6753 | 12.1668 | 11.5037 | 10.8468 | 8.45 | 5.6847 | 2.6142 | 13.3811 | 13.2284 | 13.0705 | 12.9021 | 12.7242 | 12.4263 | 12.0863 | 11.4305 | 10.8095 | 10.2011 | 8.4947 | 5.5979 | 2.7674 | 13.8318 | 13.4603 | 13.3182 | 13.1687 | 13.0161 | 12.6255 | 12.0476 | 11.3213 | 10.6108 | 9.9129 | 7.8245 | 4.5392 | 1.1761
|  | DINGWALL | EE |  |  |  |  | 14.3005 | 13.9826 | 13.8405 | 13.69 | 13.5374 | 13.1332 | 12.6753 | 12.2111 | 11.6689 | 10.9889 | 8.7942 | 5.6847 | 2.8121 | 13.4389 | 13.2284 | 13.0947 | 12.9484 | 12.7937 | 12.5158 | 12.2242 | 11.9284 | 11.3316 | 10.6979 | 8.6821 | 5.9453 | 2.7674 | 13.8887 | 13.4603 | 13.3182 | 13.1687 | 13.0161 | 12.6255 | 12.1824 | 11.5918 | 10.8845 | 10.155 | 7.8245 | 4.5392 | 1.1761
|  | DINGWALL | HT |  |  |  |  | 14.2437 | 14.0995 | 13.9342 | 13.7689 | 13.6016 | 13.2132 | 12.8321 | 12.1668 | 11.5037 | 10.8468 | 9.0858 | 6.3553 | 3.89 | 13.3811 | 13.2337 | 13.0705 | 12.9021 | 12.7242 | 12.4263 | 12.0863 | 11.4305 | 10.8095 | 10.2011 | 8.4947 | 5.5979 | 2.8316 | 13.8318 | 13.6866 | 13.5234 | 13.3582 | 13.1908 | 12.8139 | 12.0476 | 11.3213 | 10.6108 | 9.9129 | 8.0118 | 4.8982 | 2.0413
|  | DINGWALL | HE |  |  |  |  | 14.3784 | 14.3005 | 14.21 | 14.1142 | 14.0111 | 13.6111 | 13.2689 | 12.93 | 12.5974 | 12.2721 | 8.45 | 5.7679 | 2.6142 | 13.5168 | 13.4389 | 13.3516 | 13.2547 | 13.1389 | 12.8821 | 12.6632 | 12.4463 | 12.2347 | 12.0316 | 8.9389 | 6.2674 | 3.0305 | 13.8318 | 13.6866 | 13.5234 | 13.3582 | 13.1908 | 12.8139 | 12.0476 | 11.3213 | 10.6108 | 9.9129 | 8.0118 | 4.8982 | 2.0413
|  | DINGWALL | CF |  |  |  |  | 14.4205 | 14.3742 | 14.3237 | 14.2711 | 14.2174 | 14.0574 | 13.91 | 13.7637 | 13.6311 | 13.5205 | 12.9047 | 11.6805 | 9.7226 | 13.5589 | 13.5126 | 13.4642 | 13.4137 | 13.3589 | 13.2505 | 13.1495 | 13.0516 | 12.9568 | 12.8726 | 12.4421 | 11.1979 | 9.0189 | 14.0087 | 13.9624 | 13.9118 | 13.8592 | 13.8055 | 13.6508 | 13.5076 | 13.3655 | 13.2371 | 13.1308 | 12.5339 | 10.8445 | 8.5139
| CARRADALE 1 | DIPPEN | MINIMUM HEADROOM | NR 80026 37592 | YES | YES | 0.05 | 1.0879 | 1.0689 | 1.0437 | 1.0132 | 0.98158 | 0.94684 | 0.91316 | 0.87947 | 0.84474 | 0.80684 | 0.64789 | 0.44474 | 0.26263 | 1.0247 | 0.99737 | 0.96895 | 0.93632 | 0.90158 | 0.86684 | 0.83211 | 0.79737 | 0.76368 | 0.72474 | 0.55947 | 0.33842 | 0.13105 | 1.0111 | 0.98263 | 0.95421 | 0.92053 | 0.88684 | 0.85 | 0.81316 | 0.77737 | 0.74158 | 0.70053 | 0.52789 | 0.30368 | 0.097368
|  | DIPPEN | EE |  |  |  |  | 1.0932 | 1.0826 | 1.0658 | 1.0447 | 1.0205 | 0.99 | 0.95211 | 0.92053 | 0.89 | 0.86263 | 0.70684 | 0.52684 | 0.32474 | 1.03 | 1.0153 | 0.99421 | 0.97105 | 0.94579 | 0.91421 | 0.87632 | 0.84474 | 0.81421 | 0.78684 | 0.63211 | 0.44789 | 0.22368 | 1.0216 | 1.0005 | 0.97947 | 0.95526 | 0.93 | 0.89737 | 0.85526 | 0.82368 | 0.79105 | 0.76158 | 0.59421 | 0.39737 | 0.17105
|  | DIPPEN | HT |  |  |  |  | 1.0879 | 1.0689 | 1.0437 | 1.0132 | 0.98158 | 0.94684 | 0.91316 | 0.87947 | 0.84474 | 0.80684 | 0.64789 | 0.44474 | 0.26263 | 1.0247 | 0.99737 | 0.96895 | 0.93632 | 0.90158 | 0.86684 | 0.83211 | 0.79737 | 0.76368 | 0.72474 | 0.55947 | 0.33842 | 0.13105 | 1.0111 | 0.98263 | 0.95421 | 0.92053 | 0.88684 | 0.85 | 0.81316 | 0.77737 | 0.74158 | 0.70053 | 0.52789 | 0.30368 | 0.097368
|  | DIPPEN | HE |  |  |  |  | 1.1016 | 1.0942 | 1.0868 | 1.0774 | 1.0574 | 1.0268 | 0.99737 | 0.97316 | 0.94579 | 0.91737 | 0.80684 | 0.64368 | 0.45211 | 1.0384 | 1.0311 | 1.0237 | 1.0058 | 0.98368 | 0.95211 | 0.92263 | 0.89842 | 0.87105 | 0.84158 | 0.73105 | 0.55737 | 0.35105 | 1.0111 | 0.98263 | 0.95421 | 0.92053 | 0.88684 | 0.85 | 0.81316 | 0.77737 | 0.74158 | 0.70053 | 0.52789 | 0.30368 | 0.097368
|  | DIPPEN | CF |  |  |  |  | 1.1058 | 1.1016 | 1.0974 | 1.0942 | 1.09 | 1.0826 | 1.0763 | 1.0658 | 1.0574 | 1.0458 | 0.96368 | 0.84684 | 0.71316 | 1.0426 | 1.0384 | 1.0342 | 1.0311 | 1.0268 | 1.0205 | 1.0089 | 0.99737 | 0.98789 | 0.97526 | 0.88789 | 0.76368 | 0.61526 | 1.0458 | 1.0384 | 1.0311 | 1.0258 | 1.0184 | 1.0068 | 0.99316 | 0.97947 | 0.97105 | 0.95737 | 0.86684 | 0.73737 | 0.58474
| BRORA | DORNOCH | MINIMUM HEADROOM | NH 79721 89953 | YES | YES | 0.06 | 5.2368 | 5.1726 | 5.0779 | 4.9642 | 4.8474 | 4.5305 | 4.1979 | 3.9758 | 3.7284 | 3.4853 | 2.4126 | 1.2305 | 0.30947 | 4.6032 | 4.4895 | 4.3684 | 4.2505 | 4.1326 | 3.8411 | 3.5316 | 3.3316 | 3.1126 | 2.8958 | 2.0011 | 0.98526 | 0.12421 | 4.4758 | 4.3589 | 4.2358 | 4.1137 | 3.9926 | 3.6811 | 3.3537 | 3.1368 | 2.9011 | 2.6674 | 1.6632 | 0.45368 | -0.55895
|  | DORNOCH | EE |  |  |  |  | 5.2621 | 5.2116 | 5.1474 | 5.0737 | 4.9768 | 4.7537 | 4.5095 | 4.1621 | 3.8211 | 3.5916 | 2.4126 | 1.2305 | 0.30947 | 4.6537 | 4.5663 | 4.4674 | 4.3684 | 4.2695 | 4.0642 | 3.8432 | 3.5326 | 3.2263 | 3.0253 | 2.0011 | 0.98526 | 0.12421 | 4.5295 | 4.4389 | 4.3368 | 4.2337 | 4.1316 | 3.9105 | 3.6684 | 3.3347 | 3.0042 | 2.7853 | 1.6632 | 0.45368 | -0.55895
|  | DORNOCH | HT |  |  |  |  | 5.2368 | 5.1726 | 5.0779 | 4.9642 | 4.8474 | 4.5305 | 4.1979 | 3.9758 | 3.7284 | 3.4853 | 2.4937 | 1.6695 | 0.91579 | 4.6032 | 4.4895 | 4.3684 | 4.2505 | 4.1326 | 3.8411 | 3.5316 | 3.3316 | 3.1126 | 2.8958 | 2.0137 | 1.2579 | 0.44842 | 4.4758 | 4.3589 | 4.2358 | 4.1137 | 3.9926 | 3.6811 | 3.3537 | 3.1368 | 2.9011 | 2.6674 | 1.7137 | 0.84526 | -3.8858e-16
|  | DORNOCH | HE |  |  |  |  | 5.2989 | 5.2663 | 5.2284 | 5.1853 | 5.1421 | 4.9684 | 4.8053 | 4.5926 | 4.3821 | 4.1642 | 3.3295 | 2.2937 | 1.1832 | 4.7032 | 4.6695 | 4.6137 | 4.5526 | 4.4905 | 4.3011 | 4.1432 | 3.9432 | 3.7495 | 3.5568 | 2.8326 | 1.9158 | 0.92947 | 4.4758 | 4.3589 | 4.2358 | 4.1137 | 3.9926 | 3.6811 | 3.3537 | 3.1368 | 2.9011 | 2.6674 | 1.7137 | 0.84526 | -3.8858e-16
|  | DORNOCH | CF |  |  |  |  | 5.32 | 5.3011 | 5.2811 | 5.2589 | 5.2379 | 5.1695 | 5.1074 | 5.0442 | 4.98 | 4.8979 | 4.4516 | 3.84 | 3.1916 | 4.7242 | 4.7053 | 4.6853 | 4.6568 | 4.6242 | 4.5432 | 4.4695 | 4.3947 | 4.3053 | 4.2232 | 3.8105 | 3.2695 | 2.6842 | 4.6421 | 4.6074 | 4.5705 | 4.5347 | 4.4979 | 4.4105 | 4.3305 | 4.2495 | 4.1526 | 4.0663 | 3.6211 | 3.0316 | 2.4
| CLACHAN | DOUGLAS PIER | MINIMUM HEADROOM | NS 19396 99616 | YES | YES | 0 | 1.0637 | 1.0416 | 1.0184 | 0.98684 | 0.95421 | 0.92158 | 0.88895 | 0.85842 | 0.82895 | 0.79947 | 0.67211 | 0.56053 | 0.45737 | 1.0658 | 1.0416 | 1.0174 | 0.98158 | 0.94579 | 0.91105 | 0.87526 | 0.84158 | 0.80895 | 0.77632 | 0.63316 | 0.50684 | 0.38789 | 1.0732 | 1.0521 | 1.0279 | 0.99316 | 0.95842 | 0.92368 | 0.88789 | 0.85526 | 0.82368 | 0.79105 | 0.65211 | 0.52789 | 0.41211
|  | DOUGLAS PIER | EE |  |  |  |  | 1.0753 | 1.0574 | 1.0395 | 1.0205 | 0.99737 | 0.97211 | 0.94789 | 0.92368 | 0.89947 | 0.87842 | 0.77526 | 0.69105 | 0.61421 | 1.0763 | 1.0595 | 1.0395 | 1.0205 | 0.99526 | 0.96684 | 0.93947 | 0.91421 | 0.88684 | 0.86263 | 0.74895 | 0.65316 | 0.56368 | 1.0837 | 1.0679 | 1.05 | 1.0311 | 1.0058 | 0.97842 | 0.95211 | 0.92684 | 0.90053 | 0.87632 | 0.76474 | 0.67105 | 0.58474
|  | DOUGLAS PIER | HT |  |  |  |  | 1.0637 | 1.0416 | 1.0184 | 0.98684 | 0.95421 | 0.92158 | 0.88895 | 0.85842 | 0.82895 | 0.79947 | 0.67211 | 0.56053 | 0.45737 | 1.0658 | 1.0416 | 1.0174 | 0.98158 | 0.94579 | 0.91105 | 0.87526 | 0.84158 | 0.80895 | 0.77632 | 0.63316 | 0.50684 | 0.38789 | 1.0732 | 1.0521 | 1.0279 | 0.99316 | 0.95842 | 0.92368 | 0.88789 | 0.85526 | 0.82368 | 0.79105 | 0.65211 | 0.52789 | 0.41211
|  | DOUGLAS PIER | HE |  |  |  |  | 1.0889 | 1.0784 | 1.0668 | 1.0553 | 1.0437 | 1.0321 | 1.0205 | 1.0079 | 0.99211 | 0.97842 | 0.91947 | 0.87316 | 0.83211 | 1.0911 | 1.0805 | 1.0689 | 1.0574 | 1.0447 | 1.0332 | 1.0216 | 1.0068 | 0.99105 | 0.97526 | 0.91 | 0.85632 | 0.80895 | 1.0732 | 1.0521 | 1.0279 | 0.99316 | 0.95842 | 0.92368 | 0.88789 | 0.85526 | 0.82368 | 0.79105 | 0.65211 | 0.52789 | 0.41211
|  | DOUGLAS PIER | CF |  |  |  |  | 1.0974 | 1.0911 | 1.0837 | 1.0763 | 1.0711 | 1.0637 | 1.0563 | 1.05 | 1.0437 | 1.0363 | 0.99316 | 0.95632 | 0.92579 | 1.0995 | 1.0932 | 1.0858 | 1.0784 | 1.0721 | 1.0647 | 1.0574 | 1.0511 | 1.0447 | 1.0363 | 0.99 | 0.94789 | 0.91105 | 1.1047 | 1.0995 | 1.0921 | 1.0847 | 1.0795 | 1.0732 | 1.0658 | 1.0605 | 1.0542 | 1.0468 | 1.0016 | 0.95947 | 0.92474
| ARDMORE | DRIMORE | MINIMUM HEADROOM | NF 77377 40049 | YES | YES | 0 | 2.4568 | 2.4316 | 2.4074 | 2.3821 | 2.3579 | 2.3326 | 2.3095 | 2.2863 | 2.2642 | 2.2421 | 2.1589 | 1.7958 | 1.7368 | 2.6632 | 2.6358 | 2.6095 | 2.5832 | 2.5558 | 2.5295 | 2.5053 | 2.48 | 2.4558 | 2.4337 | 2.3432 | 2.0442 | 1.9779 | 2.4516 | 2.4253 | 2.3989 | 2.3726 | 2.3463 | 2.3189 | 2.2947 | 2.2695 | 2.2463 | 2.2232 | 2.1326 | 1.7632 | 1.6968
|  | DRIMORE | EE |  |  |  |  | 2.4663 | 2.4474 | 2.4274 | 2.4074 | 2.3863 | 2.3674 | 2.3474 | 2.3284 | 2.3116 | 2.2947 | 2.2221 | 1.8747 | 1.8326 | 2.6737 | 2.6537 | 2.6316 | 2.6095 | 2.5884 | 2.5674 | 2.5463 | 2.5263 | 2.5074 | 2.4895 | 2.4126 | 2.1337 | 2.0842 | 2.4621 | 2.4421 | 2.4211 | 2.4 | 2.3779 | 2.3568 | 2.3358 | 2.3168 | 2.2979 | 2.28 | 2.2021 | 1.8495 | 1.8021
|  | DRIMORE | HT |  |  |  |  | 2.4568 | 2.4316 | 2.4074 | 2.3821 | 2.3579 | 2.3326 | 2.3095 | 2.2863 | 2.2642 | 2.2421 | 2.1589 | 1.7958 | 1.7368 | 2.6632 | 2.6358 | 2.6095 | 2.5832 | 2.5558 | 2.5295 | 2.5053 | 2.48 | 2.4558 | 2.4337 | 2.3432 | 2.0442 | 1.9779 | 2.4516 | 2.4253 | 2.3989 | 2.3726 | 2.3463 | 2.3189 | 2.2947 | 2.2695 | 2.2463 | 2.2232 | 2.1326 | 1.7632 | 1.6968
|  | DRIMORE | HE |  |  |  |  | 2.4832 | 2.4716 | 2.4579 | 2.4442 | 2.4305 | 2.4168 | 2.4032 | 2.3916 | 2.3789 | 2.3674 | 2.3263 | 2.1537 | 2.1347 | 2.6926 | 2.68 | 2.6642 | 2.6505 | 2.6358 | 2.6221 | 2.6074 | 2.5947 | 2.5821 | 2.5695 | 2.5263 | 2.3863 | 2.3642 | 2.4516 | 2.4253 | 2.3989 | 2.3726 | 2.3463 | 2.3189 | 2.2947 | 2.2695 | 2.2463 | 2.2232 | 2.1326 | 1.7632 | 1.6968
|  | DRIMORE | CF |  |  |  |  | 2.4916 | 2.4842 | 2.4768 | 2.4695 | 2.4611 | 2.4537 | 2.4453 | 2.4379 | 2.4295 | 2.4221 | 2.3874 | 2.3632 | 2.3463 | 2.7011 | 2.6937 | 2.6853 | 2.6768 | 2.6674 | 2.66 | 2.6505 | 2.6432 | 2.6337 | 2.6263 | 2.5884 | 2.5632 | 2.5432 | 2.4884 | 2.48 | 2.4726 | 2.4642 | 2.4558 | 2.4484 | 2.44 | 2.4326 | 2.4232 | 2.4158 | 2.3789 | 2.3526 | 2.3326
| CEANNACROC | DRUMNADROCHIT | MINIMUM HEADROOM | NH 50306 29824 | YES | NO | 0 | 5.5326 | 5.4411 | 5.3379 | 5.2347 | 5.1347 | 4.8495 | 4.4884 | 4.1158 | 3.7874 | 3.4526 | 1.2326 | -2.4821 | -4.4421 | 5.6263 | 5.5316 | 5.4274 | 5.3242 | 5.2232 | 4.9895 | 4.7516 | 4.4526 | 4.1853 | 3.9158 | 1.94 | -1.3589 | -3.2326 | 5.5989 | 5.5 | 5.3905 | 5.28 | 5.1737 | 4.8832 | 4.52 | 4.1432 | 3.8053 | 3.4642 | 1.1189 | -1.3053 | -3.1779
|  | DRUMNADROCHIT | EE |  |  |  |  | 5.5716 | 5.4842 | 5.3779 | 5.2726 | 5.1632 | 4.8495 | 4.4884 | 4.1158 | 3.7874 | 3.4526 | 1.2326 | -1.0126 | -2.68 | 5.6695 | 5.5863 | 5.4884 | 5.3926 | 5.2905 | 5.0442 | 4.7516 | 4.4526 | 4.1853 | 3.9158 | 1.94 | -0.16947 | -1.8968 | 5.6379 | 5.5474 | 5.4337 | 5.32 | 5.2042 | 4.8832 | 4.52 | 4.1432 | 3.8053 | 3.4642 | 1.1189 | -1.3053 | -3.1779
|  | DRUMNADROCHIT | HT |  |  |  |  | 5.5326 | 5.4411 | 5.3379 | 5.2347 | 5.1347 | 4.8589 | 4.5832 | 4.3053 | 3.9863 | 3.6758 | 1.7979 | -0.085263 | -1.3958 | 5.6263 | 5.5316 | 5.4274 | 5.3242 | 5.2232 | 4.9895 | 4.7516 | 4.5137 | 4.2474 | 3.9874 | 2.1863 | 0.19368 | -1.2147 | 5.5989 | 5.5 | 5.3905 | 5.28 | 5.1737 | 4.8905 | 4.6095 | 4.3263 | 4.0053 | 3.6905 | 1.6653 | -0.45895 | -1.9474
|  | DRUMNADROCHIT | HE |  |  |  |  | 5.6253 | 5.5789 | 5.5274 | 5.4737 | 5.42 | 5.1189 | 4.8642 | 4.5695 | 4.2747 | 3.9011 | 2.2821 | -2.4821 | -4.4421 | 5.7274 | 5.6811 | 5.6305 | 5.5779 | 5.5242 | 5.2863 | 5.0779 | 4.8253 | 4.5716 | 4.2211 | 2.74 | -1.3589 | -3.2326 | 5.5989 | 5.5 | 5.3905 | 5.28 | 5.1737 | 4.8905 | 4.6095 | 4.3263 | 4.0053 | 3.6905 | 1.6653 | -0.45895 | -1.9474
|  | DRUMNADROCHIT | CF |  |  |  |  | 5.6537 | 5.6263 | 5.5979 | 5.5684 | 5.5389 | 5.4211 | 5.3126 | 5.2053 | 5.0737 | 4.9137 | 4.1221 | 0.75474 | -0.38632 | 5.7589 | 5.7305 | 5.7011 | 5.6695 | 5.6411 | 5.5432 | 5.4526 | 5.3632 | 5.2379 | 5.0726 | 4.3084 | 1.4579 | 0.29053 | 5.68 | 5.6642 | 5.6453 | 5.6253 | 5.6074 | 5.4884 | 5.3779 | 5.2705 | 5.1295 | 4.9516 | 4.0979 | 0.63053 | -0.63895
| GRUDIE BRIDGE | DRUMRUNIE | MINIMUM HEADROOM | NC 16664 05298 | YES | NO | 0 | 0.21579 | 0.21158 | 0.20421 | 0.19789 | 0.19263 | 0.18632 | 0.17895 | 0.17263 | 0.16526 | 0.15789 | 0.13053 | 0.10632 | 0.085263 | 0.19895 | 0.19263 | 0.18421 | 0.17789 | 0.17158 | 0.16421 | 0.15684 | 0.15053 | 0.14211 | 0.13474 | 0.10421 | 0.077895 | 0.053684 | 0.20526 | 0.19789 | 0.19053 | 0.18421 | 0.17789 | 0.17158 | 0.16421 | 0.15684 | 0.14947 | 0.14211 | 0.11158 | 0.085263 | 0.062105
|  | DRUMRUNIE | EE |  |  |  |  | 0.21684 | 0.21474 | 0.21053 | 0.20632 | 0.20105 | 0.19579 | 0.19158 | 0.18526 | 0.18105 | 0.17579 | 0.15263 | 0.13579 | 0.11895 | 0.20211 | 0.19684 | 0.19158 | 0.18632 | 0.18 | 0.17579 | 0.17053 | 0.16421 | 0.16 | 0.15368 | 0.12842 | 0.10947 | 0.090526 | 0.20737 | 0.20316 | 0.19684 | 0.19263 | 0.18632 | 0.18211 | 0.17684 | 0.17158 | 0.16632 | 0.16105 | 0.13579 | 0.11684 | 0.097895
|  | DRUMRUNIE | HT |  |  |  |  | 0.21579 | 0.21158 | 0.20421 | 0.19789 | 0.19263 | 0.18632 | 0.17895 | 0.17263 | 0.16526 | 0.15789 | 0.13053 | 0.10632 | 0.085263 | 0.19895 | 0.19263 | 0.18421 | 0.17789 | 0.17158 | 0.16421 | 0.15684 | 0.15053 | 0.14211 | 0.13474 | 0.10421 | 0.077895 | 0.053684 | 0.20526 | 0.19789 | 0.19053 | 0.18421 | 0.17789 | 0.17158 | 0.16421 | 0.15684 | 0.14947 | 0.14211 | 0.11158 | 0.085263 | 0.062105
|  | DRUMRUNIE | HE |  |  |  |  | 0.21895 | 0.21789 | 0.21579 | 0.21368 | 0.21158 | 0.20842 | 0.20526 | 0.20211 | 0.19895 | 0.19579 | 0.18526 | 0.17474 | 0.16737 | 0.20526 | 0.20421 | 0.2 | 0.19684 | 0.19263 | 0.18947 | 0.18632 | 0.18316 | 0.17895 | 0.17579 | 0.16421 | 0.15263 | 0.14421 | 0.20526 | 0.19789 | 0.19053 | 0.18421 | 0.17789 | 0.17158 | 0.16421 | 0.15684 | 0.14947 | 0.14211 | 0.11158 | 0.085263 | 0.062105
|  | DRUMRUNIE | CF |  |  |  |  | 0.22105 | 0.22 | 0.21895 | 0.21789 | 0.21684 | 0.21579 | 0.21368 | 0.21263 | 0.21158 | 0.20947 | 0.20211 | 0.19684 | 0.18947 | 0.20737 | 0.20632 | 0.20526 | 0.20316 | 0.20105 | 0.19895 | 0.19579 | 0.19368 | 0.19263 | 0.19053 | 0.18211 | 0.17579 | 0.16842 | 0.21263 | 0.21158 | 0.21053 | 0.20842 | 0.20632 | 0.20526 | 0.20211 | 0.2 | 0.19789 | 0.19579 | 0.18842 | 0.18211 | 0.17474
| STRATHLEVEN | DRYMEN | MINIMUM HEADROOM | NS 48494 88026 | YES | YES | 0 | 0.86842 | 0.78632 | 0.69579 | 0.58947 | 0.47263 | 0.32526 | 0.17368 | 0.021053 | -0.13579 | -0.27684 | -0.97263 | -1.5695 | -2.0768 | 0.91684 | 0.83579 | 0.73684 | 0.61895 | 0.48842 | 0.33263 | 0.17053 | 0.0063158 | -0.15789 | -0.29789 | -1.0495 | -1.7105 | -2.2905 | 0.95263 | 0.86211 | 0.75895 | 0.64 | 0.50842 | 0.34632 | 0.17895 | 0.0073684 | -0.16632 | -0.31263 | -1.0989 | -1.7832 | -2.3758
|  | DRYMEN | EE |  |  |  |  | 0.89895 | 0.82947 | 0.74947 | 0.65579 | 0.54737 | 0.40737 | 0.26947 | 0.11895 | -0.02 | -0.15789 | -0.84526 | -1.4853 | -1.9495 | 0.93895 | 0.88421 | 0.80316 | 0.70211 | 0.58632 | 0.44316 | 0.30526 | 0.15368 | 0.012632 | -0.12842 | -0.82 | -1.4695 | -1.9737 | 0.98632 | 0.90842 | 0.81895 | 0.71474 | 0.59263 | 0.43789 | 0.28632 | 0.12316 | -0.031579 | -0.18421 | -0.93789 | -1.6505 | -2.1874
|  | DRYMEN | HT |  |  |  |  | 0.86842 | 0.78632 | 0.69579 | 0.58947 | 0.47263 | 0.32526 | 0.17368 | 0.021053 | -0.13579 | -0.27684 | -0.97263 | -1.5695 | -2.0768 | 0.91684 | 0.83579 | 0.73684 | 0.61895 | 0.48842 | 0.33263 | 0.17053 | 0.0063158 | -0.15789 | -0.29789 | -1.0495 | -1.7105 | -2.2905 | 0.95263 | 0.86211 | 0.75895 | 0.64 | 0.50842 | 0.34632 | 0.17895 | 0.0073684 | -0.16632 | -0.31263 | -1.0989 | -1.7832 | -2.3758
|  | DRYMEN | HE |  |  |  |  | 0.94211 | 0.89895 | 0.84632 | 0.77789 | 0.69684 | 0.57474 | 0.46842 | 0.34421 | 0.23158 | 0.11789 | -0.41895 | -0.91368 | -1.3705 | 0.97053 | 0.93789 | 0.9 | 0.82632 | 0.73579 | 0.61158 | 0.50105 | 0.37263 | 0.25368 | 0.13474 | -0.43263 | -0.96632 | -1.4463 | 0.95263 | 0.86211 | 0.75895 | 0.64 | 0.50842 | 0.34632 | 0.17895 | 0.0073684 | -0.16632 | -0.31263 | -1.0989 | -1.7832 | -2.3758
|  | DRYMEN | CF |  |  |  |  | 0.96421 | 0.93895 | 0.91053 | 0.87684 | 0.84 | 0.78737 | 0.73579 | 0.68 | 0.62421 | 0.56737 | 0.26 | -0.035789 | -0.28526 | 0.98632 | 0.96842 | 0.94842 | 0.92737 | 0.89263 | 0.83895 | 0.78316 | 0.72421 | 0.66316 | 0.60105 | 0.26632 | -0.051579 | -0.32526 | 1.0547 | 1.0284 | 0.99684 | 0.96 | 0.91789 | 0.86 | 0.80105 | 0.74105 | 0.67789 | 0.61368 | 0.26526 | -0.069474 | -0.35579
| DUNVEGAN | DRYNOCH | MINIMUM HEADROOM | NG 41080 31292 | YES | YES | 0 | 2.4379 | 2.4011 | 2.3495 | 2.2716 | 2.1947 | 1.9126 | 1.5621 | 1.1758 | 0.83895 | 0.48947 | -2.8116 | -6.5063 | -9.3063 | 2.4779 | 2.4368 | 2.3558 | 2.2758 | 2.1979 | 1.9495 | 1.6874 | 1.3621 | 1.0768 | 0.74316 | -2.4653 | -6.0926 | -9.1284 | 2.4632 | 2.4 | 2.3158 | 2.2326 | 2.1516 | 1.8684 | 1.5337 | 1.1358 | 0.78211 | 0.43158 | -3.2011 | -7.2316 | -10.4316
|  | DRYNOCH | EE |  |  |  |  | 2.4537 | 2.4242 | 2.3726 | 2.3211 | 2.2526 | 1.9347 | 1.5621 | 1.1758 | 0.83895 | 0.48947 | -2.8116 | -6.5063 | -9.3063 | 2.4958 | 2.4632 | 2.4147 | 2.3421 | 2.2695 | 2 | 1.6874 | 1.3621 | 1.0768 | 0.79158 | -2.4653 | -6.0926 | -9.1284 | 2.4789 | 2.4484 | 2.3705 | 2.2937 | 2.2158 | 1.9032 | 1.5337 | 1.1358 | 0.78211 | 0.43158 | -3.2011 | -7.2316 | -10.4316
|  | DRYNOCH | HT |  |  |  |  | 2.4379 | 2.4011 | 2.3495 | 2.2716 | 2.1947 | 1.9126 | 1.6274 | 1.3421 | 1.0147 | 0.71895 | -2.2579 | -5.6611 | -7.9747 | 2.4779 | 2.4368 | 2.3558 | 2.2758 | 2.1979 | 1.9495 | 1.7021 | 1.4537 | 1.1726 | 0.82 | -2.2579 | -5.9453 | -8.5463 | 2.4632 | 2.4 | 2.3158 | 2.2326 | 2.1516 | 1.8684 | 1.5842 | 1.2989 | 0.96105 | 0.60632 | -2.7495 | -6.6179 | -9.2811
|  | DRYNOCH | HE |  |  |  |  | 2.4747 | 2.4568 | 2.4326 | 2.4053 | 2.3789 | 2.0779 | 1.7011 | 1.3189 | 1.1958 | 0.67053 | -1.3589 | -4.2105 | -7.3116 | 2.52 | 2.5 | 2.4768 | 2.4495 | 2.4242 | 2.1453 | 1.7905 | 1.4274 | 1.2811 | 0.74316 | -1.3011 | -4.1947 | -7.3621 | 2.4632 | 2.4 | 2.3158 | 2.2326 | 2.1516 | 1.8684 | 1.5842 | 1.2989 | 0.96105 | 0.60632 | -2.7495 | -6.6179 | -9.2811
|  | DRYNOCH | CF |  |  |  |  | 2.4863 | 2.4768 | 2.4632 | 2.4505 | 2.4368 | 2.3284 | 2.2316 | 2.08 | 1.9337 | 1.6832 | 0.61158 | -1.1674 | -3.1516 | 2.5337 | 2.5221 | 2.5095 | 2.4968 | 2.4832 | 2.4158 | 2.3189 | 2.1368 | 1.9611 | 1.6789 | 0.53368 | -1.3 | -3.4305 | 2.5116 | 2.5021 | 2.4884 | 2.4758 | 2.4611 | 2.3568 | 2.2432 | 2.0463 | 1.8716 | 1.5832 | 0.35368 | -1.6453 | -3.8937
| KEITH 2 | DUFFTOWN | MINIMUM HEADROOM | NJ 32060 39722 | NO | YES | 0 | 6.1284 | 6.0779 | 6.0011 | 5.8232 | 15.1763 | 14.5184 | 13.5911 | 12.7111 | 11.9542 | 11.1847 | 2.7784 | -4.4858 | -9.7184 | 5.7295 | 5.6789 | 5.6147 | 5.4432 | 14.0305 | 13.4589 | 12.72 | 11.9884 | 11.3589 | 10.72 | 3.0389 | -4.0432 | -9.5663 | 6.0926 | 6.02 | 5.8895 | 5.7537 | 14.7076 | 14.0329 | 13.1129 | 12.2287 | 11.4687 | 10.695 | 1.7603 | -6.2587 | -12.185
|  | DUFFTOWN | EE |  |  |  |  | 6.1474 | 6.1074 | 6.0253 | 5.9358 | 15.3111 | 14.5332 | 13.5911 | 12.7111 | 11.9542 | 11.1847 | 2.7784 | -4.4858 | -9.7184 | 5.7484 | 5.7084 | 5.6474 | 5.5789 | 14.2011 | 13.5347 | 12.72 | 11.9884 | 11.3589 | 10.72 | 3.0389 | -4.0432 | -9.5663 | 6.1232 | 6.0653 | 5.9505 | 5.8242 | 14.8624 | 14.0813 | 13.1129 | 12.2287 | 11.4687 | 10.695 | 1.7603 | -6.2587 | -12.185
|  | DUFFTOWN | HT |  |  |  |  | 6.1284 | 6.0779 | 6.0011 | 5.8232 | 15.1763 | 14.5184 | 13.8616 | 13.2289 | 12.4932 | 11.6058 | 3.7784 | -2.5321 | -6.8279 | 5.7295 | 5.6789 | 5.6147 | 5.4432 | 14.0305 | 13.4589 | 12.8895 | 12.3484 | 11.7305 | 10.9368 | 3.4421 | -3.3 | -8.0337 | 6.0926 | 6.02 | 5.8895 | 5.7537 | 14.7076 | 14.0329 | 13.3603 | 12.7171 | 11.975 | 11.0466 | 2.5045 | -4.6618 | -9.5934
|  | DUFFTOWN | HE |  |  |  |  | 6.1747 | 6.1484 | 6.1137 | 6.0737 | 15.5426 | 14.7289 | 14.0005 | 13.3016 | 12.5247 | 11.4605 | 5.8342 | 0.34895 | -5.7068 | 5.7758 | 5.7495 | 5.7179 | 5.6821 | 14.4179 | 13.7253 | 13.0874 | 12.4832 | 11.7842 | 10.7421 | 5.5063 | 0.0063158 | -6.0621 | 6.0926 | 6.02 | 5.8895 | 5.7537 | 14.7076 | 14.0329 | 13.3603 | 12.7171 | 11.975 | 11.0466 | 2.5045 | -4.6618 | -9.5934
|  | DUFFTOWN | CF |  |  |  |  | 6.1905 | 6.1758 | 6.1537 | 6.1326 | 15.6595 | 15.4216 | 15.2142 | 14.8826 | 14.4374 | 13.9605 | 11.6795 | 8.2658 | 4.4774 | 5.7916 | 5.7768 | 5.7579 | 5.74 | 14.52 | 14.3968 | 14.1947 | 13.8937 | 13.4453 | 12.9305 | 10.6358 | 7.1379 | 3.1621 | 6.1884 | 6.1663 | 6.1347 | 6.1042 | 15.2424 | 14.9697 | 14.7213 | 14.4424 | 13.9624 | 13.4045 | 10.8466 | 6.9897 | 2.7392
| BRACO | DUNBLANE | MINIMUM HEADROOM | NN 77907 01544 | NO | YES | 0.067 | 14.8727 | 14.6791 | 14.3033 | 13.8022 | 13.2012 | 12.1559 | 11.498 | 10.4148 | 9.2759 | 8.1233 | 2.9875 | -2.3104 | -5.5873 | 12.9035 | 12.5288 | 12.0719 | 11.5088 | 10.873 | 9.8719 | 9.1993 | 8.1309 | 7.0046 | 5.8625 | 0.67195 | -3.8291 | -7.2533 | 13.7939 | 13.4213 | 12.9634 | 12.4023 | 11.7487 | 10.6108 | 9.8666 | 8.6792 | 7.4381 | 6.1823 | 0.54761 | -4.9577 | -8.6134
|  | DUNBLANE | EE |  |  |  |  | 14.9422 | 14.8085 | 14.5412 | 14.1496 | 13.6327 | 12.6169 | 12.1022 | 10.9422 | 9.8875 | 8.8212 | 3.1927 | -2.3104 | -5.5873 | 13.0488 | 12.7519 | 12.3688 | 11.8898 | 11.3446 | 10.3877 | 9.8498 | 8.7656 | 7.773 | 6.7709 | 1.3804 | -3.8291 | -7.2365 | 13.9381 | 13.6402 | 13.2508 | 12.7644 | 12.216 | 11.1444 | 10.5466 | 9.2929 | 8.1476 | 6.9908 | 0.94234 | -4.9577 | -8.6134
|  | DUNBLANE | HT |  |  |  |  | 14.8727 | 14.6791 | 14.3033 | 13.8022 | 13.2012 | 12.1559 | 11.498 | 10.4148 | 9.2759 | 8.1233 | 2.9875 | -1.1725 | -4.4157 | 12.9035 | 12.5288 | 12.0719 | 11.5088 | 10.873 | 9.8719 | 9.1993 | 8.1309 | 7.0046 | 5.8625 | 0.67195 | -3.6786 | -7.2533 | 13.7939 | 13.4213 | 12.9634 | 12.4023 | 11.7487 | 10.6108 | 9.8666 | 8.6792 | 7.4381 | 6.1823 | 0.54761 | -4.0766 | -7.7629
|  | DUNBLANE | HE |  |  |  |  | 15.0338 | 14.9464 | 14.8464 | 14.5948 | 14.2348 | 13.2601 | 12.8338 | 11.9106 | 11.0054 | 10.0959 | 5.6906 | 1.6296 | -2.4083 | 13.2372 | 13.0309 | 12.7614 | 12.3909 | 11.9509 | 11.0425 | 10.5793 | 9.6993 | 8.8435 | 7.9835 | 3.6814 | -0.31437 | -4.2407 | 13.7939 | 13.4213 | 12.9634 | 12.4023 | 11.7487 | 10.6108 | 9.8666 | 8.6792 | 7.4381 | 6.1823 | 0.54761 | -4.0766 | -7.7629
|  | DUNBLANE | CF |  |  |  |  | 15.0822 | 15.0327 | 14.9748 | 14.918 | 14.8327 | 14.4727 | 14.3022 | 13.9212 | 13.5327 | 13.1706 | 10.9506 | 8.5538 | 5.9169 | 13.3351 | 13.2141 | 13.0677 | 12.8856 | 12.6856 | 12.313 | 12.0898 | 11.7056 | 11.3235 | 10.9572 | 8.7804 | 6.4435 | 3.6898 | 14.1202 | 14.0697 | 13.956 | 13.7729 | 13.575 | 13.1655 | 12.9444 | 12.5308 | 12.1244 | 11.7413 | 9.2623 | 6.6244 | 3.6729
| DUNOON | DUNOON | MINIMUM HEADROOM | NS 17135 77531 | NO | YES | 0 | 24.7158 | 24.4737 | 24.2211 | 23.9568 | 23.6642 | 23.3558 | 23.0516 | 22.7558 | 22.5463 | 22.3421 | 21.5432 | 20.8705 | 20.2779 | 23.9611 | 23.7611 | 23.5547 | 23.3284 | 23.0453 | 22.7453 | 22.4505 | 22.1642 | 21.9589 | 21.7589 | 20.9811 | 20.3305 | 19.7316 | 24.1263 | 24.0042 | 23.8789 | 23.7505 | 23.6105 | 23.3463 | 23.0189 | 22.7 | 22.4779 | 22.2621 | 21.4095 | 20.6832 | 20.0358
|  | DUNOON | EE |  |  |  |  | 24.7621 | 24.6232 | 24.4158 | 24.1989 | 23.9516 | 23.6884 | 23.4316 | 23.18 | 23.0137 | 22.8547 | 22.1674 | 21.6632 | 21.2358 | 24.0421 | 23.8811 | 23.7126 | 23.5368 | 23.3232 | 23.0684 | 22.82 | 22.5768 | 22.4137 | 22.2579 | 21.5874 | 21.1011 | 20.6884 | 24.1726 | 24.0747 | 23.9726 | 23.8653 | 23.7537 | 23.6305 | 23.4253 | 23.1537 | 22.9779 | 22.8095 | 22.0811 | 21.5368 | 21.0695
|  | DUNOON | HT |  |  |  |  | 24.7158 | 24.4737 | 24.2211 | 23.9568 | 23.6642 | 23.3558 | 23.0516 | 22.7558 | 22.5463 | 22.3421 | 21.5432 | 20.8705 | 20.2779 | 23.9611 | 23.7611 | 23.5547 | 23.3284 | 23.0453 | 22.7453 | 22.4505 | 22.1642 | 21.9589 | 21.7589 | 20.9811 | 20.3305 | 19.7316 | 24.1263 | 24.0042 | 23.8789 | 23.7505 | 23.6105 | 23.3463 | 23.0189 | 22.7 | 22.4779 | 22.2621 | 21.4095 | 20.6832 | 20.0358
|  | DUNOON | HE |  |  |  |  | 24.8221 | 24.7526 | 24.6684 | 24.5063 | 24.3084 | 24.0947 | 23.8842 | 23.6832 | 23.5674 | 23.46 | 23.0737 | 22.8095 | 22.6116 | 24.1463 | 24.0358 | 23.9147 | 23.7821 | 23.6253 | 23.4558 | 23.26 | 23.0653 | 22.9505 | 22.8453 | 22.4674 | 22.2116 | 22.0211 | 24.1263 | 24.0042 | 23.8789 | 23.7505 | 23.6105 | 23.3463 | 23.0189 | 22.7 | 22.4779 | 22.2621 | 21.4095 | 20.6832 | 20.0358
|  | DUNOON | CF |  |  |  |  | 24.8558 | 24.8116 | 24.7674 | 24.7211 | 24.6421 | 24.5326 | 24.4179 | 24.2947 | 24.2126 | 24.1295 | 23.7674 | 23.5253 | 23.3463 | 24.2011 | 24.1305 | 24.0579 | 23.9821 | 23.8968 | 23.8105 | 23.72 | 23.6242 | 23.5547 | 23.4842 | 23.1432 | 22.9095 | 22.7368 | 24.2663 | 24.2221 | 24.1779 | 24.1316 | 24.0842 | 24.0368 | 23.9884 | 23.94 | 23.8916 | 23.8432 | 23.6337 | 23.5211 | 23.3347
| DUNVEGAN | DUNVEGAN | MINIMUM HEADROOM | NG 27646 47150 | YES | YES | 0.9 | 2.8979 | 2.8274 | 2.0032 | 1.9263 | 1.8411 | 1.7558 | 1.6747 | 1.5905 | 1.3789 | 0.99895 | -4.7305 | -8.1368 | -10.4947 | 2.7084 | 2.6579 | 2.0126 | 1.9253 | 1.8368 | 1.7505 | 1.6684 | 1.5832 | 1.3421 | 0.94526 | -4.3158 | -8.0516 | -10.6811 | 2.7326 | 2.6611 | 1.8053 | 1.7189 | 1.6305 | 1.5411 | 1.4558 | 1.3663 | 1.1368 | 0.70632 | -5.4032 | -9.2695 | -11.9779
|  | DUNVEGAN | EE |  |  |  |  | 2.9295 | 2.8758 | 2.0032 | 1.9263 | 1.8411 | 1.7558 | 1.6747 | 1.5905 | 1.5042 | 1.1579 | -1.8116 | -5.54 | -8.3758 | 2.7295 | 2.6905 | 2.0126 | 1.9253 | 1.8368 | 1.7505 | 1.6684 | 1.5832 | 1.4968 | 1.2021 | -1.7905 | -5.4811 | -8.5747 | 2.7526 | 2.7158 | 1.8053 | 1.7189 | 1.6305 | 1.5411 | 1.4558 | 1.3663 | 1.2747 | 0.91158 | -2.3789 | -6.4474 | -9.6716
|  | DUNVEGAN | HT |  |  |  |  | 2.8979 | 2.8274 | 2.7316 | 2.6347 | 2.5411 | 2.2389 | 1.9389 | 1.8589 | 1.3789 | 0.99895 | -4.7305 | -8.1368 | -10.4947 | 2.7084 | 2.6579 | 2.5579 | 2.4558 | 2.3579 | 2.0958 | 1.8358 | 1.7474 | 1.3421 | 0.94526 | -4.3158 | -8.0516 | -10.6811 | 2.7326 | 2.6611 | 2.5558 | 2.4526 | 2.3516 | 2.04 | 1.7242 | 1.6379 | 1.1368 | 0.70632 | -5.4032 | -9.2695 | -11.9779
|  | DUNVEGAN | HE |  |  |  |  | 2.9726 | 2.94 | 2.9011 | 2.8589 | 2.8168 | 2.4926 | 2.1116 | 1.9621 | 1.5916 | 1.0579 | -2.6905 | -5.5495 | -8.6579 | 2.7568 | 2.7337 | 2.7063 | 2.6747 | 2.6421 | 2.3947 | 2.0358 | 1.86 | 1.5116 | 0.96421 | -2.4389 | -5.3695 | -8.5716 | 2.7326 | 2.6611 | 2.5558 | 2.4526 | 2.3516 | 2.04 | 1.7242 | 1.6379 | 1.1368 | 0.70632 | -5.4032 | -9.2695 | -11.9779
|  | DUNVEGAN | CF |  |  |  |  | 2.9958 | 2.9758 | 2.9537 | 2.9305 | 2.9084 | 2.7863 | 2.6758 | 2.6 | 2.4484 | 2.1926 | -0.63789 | -2.4421 | -4.4263 | 2.7726 | 2.7589 | 2.7453 | 2.7295 | 2.7147 | 2.6547 | 2.5653 | 2.4716 | 2.2853 | 1.9937 | -0.54316 | -2.4021 | -4.56 | 2.7958 | 2.7821 | 2.7663 | 2.7505 | 2.7337 | 2.6263 | 2.5011 | 2.4232 | 2.2432 | 1.9421 | -1.0895 | -3.0937 | -5.3379
| DYCE | DYCE NORTH | MINIMUM HEADROOM | NJ 89092 12705 | NO | YES | 0.325 | 26.9992 | 26.6245 | 26.2182 | 25.7918 | 25.3561 | 24.8087 | 24.5161 | 24.2329 | 23.9792 | 23.7276 | 22.6613 | 21.4392 | 20.4129 | 24.8645 | 24.4329 | 23.955 | 23.4645 | 22.9739 | 22.3971 | 22.1182 | 21.8487 | 21.6234 | 21.4003 | 20.4666 | 19.5118 | 18.3382 | 25.8403 | 25.4466 | 24.9645 | 24.4708 | 23.9666 | 23.355 | 23.0497 | 22.755 | 22.5003 | 22.2476 | 21.1939 | 19.9508 | 18.8118
|  | DYCE NORTH | EE |  |  |  |  | 27.0603 | 26.7708 | 26.4139 | 26.0329 | 25.6234 | 25.0792 | 24.7455 | 24.4255 | 24.1929 | 23.9613 | 22.6613 | 21.4392 | 20.4129 | 24.9013 | 24.6013 | 24.1813 | 23.7339 | 23.2739 | 22.7076 | 22.3982 | 22.1055 | 21.9034 | 21.7055 | 20.5613 | 19.5118 | 18.4392 | 25.8939 | 25.615 | 25.1918 | 24.7403 | 24.2708 | 23.6645 | 23.3171 | 22.9876 | 22.755 | 22.5266 | 21.1939 | 19.9508 | 18.8118
|  | DYCE NORTH | HT |  |  |  |  | 26.9992 | 26.6245 | 26.2182 | 25.7918 | 25.3561 | 24.8087 | 24.5161 | 24.2329 | 23.9792 | 23.7276 | 22.6939 | 21.8771 | 20.6592 | 24.8645 | 24.4329 | 23.955 | 23.4645 | 22.9739 | 22.3971 | 22.1182 | 21.8487 | 21.6234 | 21.4003 | 20.4666 | 19.6782 | 18.3382 | 25.8403 | 25.4466 | 24.9645 | 24.4708 | 23.9666 | 23.355 | 23.0497 | 22.755 | 22.5003 | 22.2476 | 21.2013 | 20.3361 | 18.9329
|  | DYCE NORTH | HE |  |  |  |  | 27.1108 | 26.8666 | 26.5929 | 26.2803 | 25.9266 | 25.4118 | 25.2161 | 25.0224 | 24.8308 | 24.6234 | 23.7318 | 22.9782 | 21.535 | 24.9518 | 24.7024 | 24.3771 | 24.0024 | 23.5939 | 23.0634 | 22.8939 | 22.7276 | 22.5624 | 22.3782 | 21.5961 | 20.935 | 19.4855 | 25.8403 | 25.4466 | 24.9645 | 24.4708 | 23.9666 | 23.355 | 23.0497 | 22.755 | 22.5003 | 22.2476 | 21.2013 | 20.3361 | 18.9329
|  | DYCE NORTH | CF |  |  |  |  | 27.1782 | 27.1487 | 27.1129 | 27.0392 | 26.9561 | 26.7982 | 26.635 | 26.4687 | 26.3108 | 26.1624 | 25.5476 | 24.9887 | 24.1897 | 24.9845 | 24.9539 | 24.9192 | 24.8855 | 24.8276 | 24.6666 | 24.4961 | 24.3213 | 24.1539 | 23.9918 | 23.3761 | 22.8561 | 22.0118 | 26.0529 | 26.0003 | 25.9382 | 25.8739 | 25.8055 | 25.6676 | 25.4855 | 25.2992 | 25.1224 | 24.9529 | 24.2824 | 23.6897 | 22.7887
| THURSO | EDAY | MINIMUM HEADROOM | HY 56341 33422 | YES | YES | 0 | 0.98842 | 0.98211 | 0.96947 | 0.95895 | 0.94737 | 0.84421 | -1.9042 | -4.6579 | -7.3937 | -10.1379 | -13.2726 | -13.8821 | -14.5411 | 0.98632 | 0.98 | 0.96737 | 0.95789 | 0.94632 | 0.86737 | -1.8621 | -4.5947 | -7.3126 | -10.0358 | -13.1379 | -13.7021 | -14.3137 | 0.98632 | 0.98 | 0.96737 | 0.95579 | 0.94526 | 0.84211 | -1.9137 | -4.6726 | -7.4116 | -10.1558 | -10.9947 | -11.9158 | -12.4463
|  | EDAY | EE |  |  |  |  | 0.99263 | 0.98632 | 0.97263 | 0.96105 | 0.94737 | 0.84421 | -1.9042 | -4.6579 | -7.3937 | -10.1379 | -10.9442 | -11.8158 | -12.2947 | 0.99053 | 0.98421 | 0.97263 | 0.96105 | 0.94947 | 0.86737 | -1.8621 | -4.5947 | -7.3126 | -10.0358 | -10.7537 | -11.54 | -12.0189 | 0.99053 | 0.98421 | 0.97158 | 0.95789 | 0.94632 | 0.84211 | -1.9137 | -4.6726 | -7.4116 | -10.1558 | -10.9947 | -11.9158 | -12.4463
|  | EDAY | HT |  |  |  |  | 0.98842 | 0.98211 | 0.96947 | 0.95895 | 0.94842 | 0.86316 | -1.8484 | -4.5642 | -7.2937 | -10.0695 | -10.7021 | -11.2916 | -11.6463 | 0.98632 | 0.98 | 0.96737 | 0.95789 | 0.94632 | 0.87895 | -1.8168 | -4.5179 | -7.2316 | -9.9926 | -10.5811 | -11.1684 | -11.5463 | 0.98632 | 0.98 | 0.96737 | 0.95579 | 0.94526 | 0.86105 | -1.8537 | -4.5716 | -7.3063 | -10.0874 | -10.7632 | -11.4063 | -11.8042
|  | EDAY | HE |  |  |  |  | 0.99684 | 0.99263 | 0.98842 | 0.98211 | 0.97789 | 0.86421 | 0.75789 | 0.65263 | -2.0789 | -4.8326 | -13.2726 | -13.8821 | -14.5411 | 0.99474 | 0.99158 | 0.98632 | 0.98105 | 0.97579 | 0.88421 | 0.79474 | 0.70211 | -2.0137 | -4.7558 | -13.1379 | -13.7021 | -14.3137 | 0.98632 | 0.98 | 0.96737 | 0.95579 | 0.94526 | 0.86105 | -1.8537 | -4.5716 | -7.3063 | -10.0874 | -10.7632 | -11.4063 | -11.8042
|  | EDAY | CF |  |  |  |  | 0.99895 | 0.99684 | 0.99368 | 0.98842 | 0.98632 | 0.94526 | 0.90842 | 0.86211 | 0.81263 | 0.76632 | 0.50737 | 0.13158 | -0.23053 | 0.99684 | 0.99474 | 0.99263 | 0.98842 | 0.98421 | 0.95158 | 0.92316 | 0.88211 | 0.83579 | 0.78842 | 0.55158 | 0.2 | -0.15895 | 0.99684 | 0.99474 | 0.99263 | 0.98842 | 0.98421 | 0.94421 | 0.90632 | 0.85789 | 0.80842 | 0.75684 | 0.48211 | 0.078947 | -0.31474
| THURSO | EDAY TIDAL | MINIMUM HEADROOM | HY 54226 31320 | YES | YES | 0 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158
|  | EDAY TIDAL | EE |  |  |  |  | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158
|  | EDAY TIDAL | HT |  |  |  |  | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158
|  | EDAY TIDAL | HE |  |  |  |  | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158
|  | EDAY TIDAL | CF |  |  |  |  | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | -1.0684 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.39368 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158 | 0.023158
| FIDDES | EDZELL | MINIMUM HEADROOM | NO 63500 70513 | YES | YES | 0.121 | 3.9211 | 3.779 | 3.6558 | 3.5264 | 3.4116 | 3.0748 | 2.5579 | 1.9958 | 1.2579 | 0.32637 | -2.5421 | -6.0957 | -9.441 | 3.7537 | 3.5853 | 3.4495 | 3.3043 | 3.179 | 2.8864 | 2.3632 | 1.7853 | 1.0106 | 0.030579 | -2.5199 | -6.4231 | -9.6547 | 3.8085 | 3.639 | 3.5001 | 3.3506 | 3.2211 | 2.879 | 2.3032 | 1.6727 | 0.83163 | -0.21995 | -3.2105 | -7.0968 | -10.9073
|  | EDZELL | EE |  |  |  |  | 3.9579 | 3.8485 | 3.7379 | 3.6169 | 3.4737 | 3.0927 | 2.6579 | 2.1106 | 1.5958 | 0.98742 | -2.5421 | -6.0957 | -9.441 | 3.7958 | 3.6653 | 3.5474 | 3.4158 | 3.2569 | 2.9327 | 2.5706 | 2.0706 | 1.5832 | 0.98321 | -2.5199 | -5.9842 | -9.6547 | 3.8506 | 3.7201 | 3.5969 | 3.4601 | 3.2937 | 2.9095 | 2.4727 | 1.8958 | 1.3422 | 0.67268 | -3.2105 | -7.0799 | -10.9073
|  | EDZELL | HT |  |  |  |  | 3.9211 | 3.779 | 3.6558 | 3.5264 | 3.4116 | 3.0748 | 2.5579 | 1.9958 | 1.2579 | 0.32637 | -1.8315 | -5.8326 | -8.6357 | 3.7537 | 3.5853 | 3.4495 | 3.3043 | 3.179 | 2.8864 | 2.3632 | 1.7853 | 1.0106 | 0.030579 | -2.0347 | -6.4231 | -9.6031 | 3.8085 | 3.639 | 3.5001 | 3.3506 | 3.2211 | 2.879 | 2.3032 | 1.6727 | 0.83163 | -0.21995 | -2.5315 | -7.0968 | -10.3305
|  | EDZELL | HE |  |  |  |  | 4.0074 | 3.9211 | 3.8558 | 3.7758 | 3.6632 | 3.279 | 2.9527 | 2.5369 | 2.0906 | 1.6085 | -0.94416 | -4.2294 | -7.8126 | 3.8516 | 3.7474 | 3.6737 | 3.5822 | 3.4506 | 3.1306 | 2.8579 | 2.4716 | 2.0443 | 1.5716 | -1.0052 | -4.4199 | -8.1368 | 3.8085 | 3.639 | 3.5001 | 3.3506 | 3.2211 | 2.879 | 2.3032 | 1.6727 | 0.83163 | -0.21995 | -2.5315 | -7.0968 | -10.3305
|  | EDZELL | CF |  |  |  |  | 4.0422 | 3.9937 | 3.9632 | 3.9243 | 3.8758 | 3.7064 | 3.5695 | 3.4306 | 3.2348 | 2.9358 | 1.6032 | -0.47784 | -2.8294 | 3.8906 | 3.8337 | 3.8011 | 3.7558 | 3.7011 | 3.5485 | 3.4316 | 3.3116 | 3.1106 | 2.7664 | 1.339 | -0.83784 | -3.4063 | 3.9474 | 3.8885 | 3.8558 | 3.8106 | 3.7537 | 3.5769 | 3.4379 | 3.2969 | 3.0758 | 2.7158 | 1.1758 | -1.1599 | -3.8389
| MILTON OF CRAIGIE | EDZELL STREET | MINIMUM HEADROOM | NO 47103 32070 | YES | YES | 0 | 10.4558 | 10.3695 | 10.2811 | 10.1916 | 10.0747 | 9.9305 | 9.7853 | 9.6442 | 9.5137 | 9.3821 | 8.7905 | 8.3432 | 7.9811 | 10.18 | 10.0863 | 9.9916 | 9.8432 | 9.6905 | 9.5347 | 9.3758 | 9.2232 | 9.0832 | 8.9411 | 8.2926 | 7.7989 | 7.3968 | 10.3084 | 10.1884 | 10.0337 | 9.8811 | 9.7295 | 9.5726 | 9.4126 | 9.2579 | 9.1158 | 8.9747 | 8.3211 | 7.8253 | 7.4211
|  | EDZELL STREET | EE |  |  |  |  | 10.4926 | 10.4253 | 10.3547 | 10.2821 | 10.2074 | 10.1263 | 10.0368 | 9.9211 | 9.8084 | 9.7074 | 9.2326 | 8.88 | 8.6116 | 10.2211 | 10.1484 | 10.0726 | 9.9947 | 9.9011 | 9.7768 | 9.6589 | 9.5326 | 9.4095 | 9.3 | 8.7863 | 8.4032 | 8.1021 | 10.3442 | 10.2779 | 10.18 | 10.06 | 9.9379 | 9.8137 | 9.6947 | 9.5663 | 9.4421 | 9.3316 | 8.8116 | 8.42 | 8.1168
|  | EDZELL STREET | HT |  |  |  |  | 10.4558 | 10.3695 | 10.2811 | 10.1916 | 10.0747 | 9.9305 | 9.7853 | 9.6442 | 9.5137 | 9.3821 | 8.7905 | 8.3432 | 7.9811 | 10.18 | 10.0863 | 9.9916 | 9.8432 | 9.6905 | 9.5347 | 9.3758 | 9.2232 | 9.0832 | 8.9411 | 8.2926 | 7.7989 | 7.3968 | 10.3084 | 10.1884 | 10.0337 | 9.8811 | 9.7295 | 9.5726 | 9.4126 | 9.2579 | 9.1158 | 8.9747 | 8.3211 | 7.8253 | 7.4211
|  | EDZELL STREET | HE |  |  |  |  | 10.5389 | 10.4958 | 10.4484 | 10.3968 | 10.3411 | 10.2789 | 10.2232 | 10.1653 | 10.1126 | 10.0632 | 9.8221 | 9.6242 | 9.4726 | 10.2726 | 10.2253 | 10.1758 | 10.1211 | 10.0632 | 10 | 9.9421 | 9.8821 | 9.8274 | 9.7663 | 9.4368 | 9.2158 | 9.0484 | 10.3084 | 10.1884 | 10.0337 | 9.8811 | 9.7295 | 9.5726 | 9.4126 | 9.2579 | 9.1158 | 8.9747 | 8.3211 | 7.8253 | 7.4211
|  | EDZELL STREET | CF |  |  |  |  | 10.5632 | 10.5389 | 10.5137 | 10.4874 | 10.46 | 10.4305 | 10.3989 | 10.3705 | 10.3389 | 10.3116 | 10.1821 | 10.0621 | 9.9453 | 10.3011 | 10.2737 | 10.2453 | 10.2158 | 10.1874 | 10.1547 | 10.1232 | 10.0916 | 10.06 | 10.0284 | 9.8589 | 9.6789 | 9.5432 | 10.4179 | 10.3916 | 10.3653 | 10.3389 | 10.3126 | 10.2821 | 10.2526 | 10.2232 | 10.1716 | 10.1232 | 9.8937 | 9.7116 | 9.5737
| ELGIN | ELGIN | MINIMUM HEADROOM | NJ 21256 64664 | NO | YES | 0.05 | 10.9405 | 10.6184 | 10.2542 | 9.9016 | 9.57 | 8.9005 | 7.7637 | 6.5195 | 5.0247 | 3.2195 | -3.2458 | -7.85 | -10.4521 | 9.7237 | 9.3174 | 8.89 | 8.4784 | 8.0911 | 7.3868 | 6.0774 | 4.7216 | 3.0889 | 1.0942 | -6.0332 | -11.1247 | -13.2889 | 10.2247 | 9.8605 | 9.4732 | 9.0995 | 8.7468 | 7.9974 | 6.6395 | 5.2332 | 3.5395 | 1.4826 | -5.8816 | -11.1163 | -13.8563
|  | ELGIN | EE |  |  |  |  | 10.9847 | 10.7521 | 10.4247 | 10.1026 | 9.8005 | 9.1237 | 8.2647 | 7.2553 | 6.2047 | 5.0563 | -2.0553 | -7.85 | -10.4521 | 9.8268 | 9.47 | 9.0868 | 8.7121 | 8.3626 | 7.6689 | 6.7668 | 5.6742 | 4.5595 | 3.3384 | -4.3384 | -10.4574 | -13.2889 | 10.3195 | 10.0016 | 9.6532 | 9.31 | 8.99 | 8.2616 | 7.2847 | 6.1142 | 4.9342 | 3.6458 | -4.3953 | -10.9047 | -13.8563
|  | ELGIN | HT |  |  |  |  | 10.9405 | 10.6184 | 10.2542 | 9.9016 | 9.57 | 8.9005 | 7.7637 | 6.5195 | 5.0247 | 3.2195 | -3.2458 | -7.8258 | -9.3605 | 9.7237 | 9.3174 | 8.89 | 8.4784 | 8.0911 | 7.3868 | 6.0774 | 4.7216 | 3.0889 | 1.0942 | -6.0332 | -11.1247 | -12.7974 | 10.2247 | 9.8605 | 9.4732 | 9.0995 | 8.7468 | 7.9974 | 6.6395 | 5.2332 | 3.5395 | 1.4826 | -5.8816 | -11.1163 | -12.8458
|  | ELGIN | HE |  |  |  |  | 11.0489 | 10.9363 | 10.6795 | 10.4268 | 10.1889 | 9.5332 | 8.7826 | 7.8405 | 6.83 | 5.7363 | 1.1889 | -2.2553 | -5.3174 | 9.9689 | 9.6805 | 9.3721 | 9.07 | 8.7879 | 8.1247 | 7.3079 | 6.2458 | 5.1489 | 3.9668 | -0.90579 | -4.5279 | -7.6795 | 10.2247 | 9.8605 | 9.4732 | 9.0995 | 8.7468 | 7.9974 | 6.6395 | 5.2332 | 3.5395 | 1.4826 | -5.8816 | -11.1163 | -12.8458
|  | ELGIN | CF |  |  |  |  | 11.0837 | 11.0479 | 10.9974 | 10.8711 | 10.7521 | 10.4911 | 10.1795 | 9.8447 | 9.47 | 9.0616 | 6.6237 | 4.1711 | 2.1963 | 10.0784 | 9.9163 | 9.7542 | 9.6026 | 9.4637 | 9.1963 | 8.8584 | 8.4879 | 8.0605 | 7.5774 | 4.8332 | 2.2079 | 0.068947 | 10.5479 | 10.4047 | 10.2595 | 10.1247 | 9.9984 | 9.7247 | 9.3942 | 9.0374 | 8.6374 | 8.1447 | 5.3005 | 2.5321 | 0.28895
| ARBROATH | ELLIOT DEPOT | MINIMUM HEADROOM | NO 62251 40381 | YES | YES | 0 | 2.26 | 2.22 | 2.1779 | 1.9979 | 1.8768 | 1.7716 | 1.6716 | 1.5716 | 1.4674 | 1.3653 | 0.95053 | 0.62842 | 0.41263 | 1.4295 | 1.1842 | 0.88842 | 0.58737 | 0.45263 | 0.35263 | 0.25789 | 0.16316 | 0.067368 | -0.026316 | -0.41684 | -0.71263 | -0.96 | 2.0442 | 1.9189 | 1.6168 | 1.3116 | 1.1737 | 1.0653 | 0.96 | 0.85579 | 0.74632 | 0.64211 | 0.20421 | -0.12316 | -0.38316
|  | ELLIOT DEPOT | EE |  |  |  |  | 2.2768 | 2.2453 | 2.2095 | 2.0779 | 1.9674 | 1.8726 | 1.7705 | 1.6684 | 1.5758 | 1.4842 | 1.0326 | 0.62842 | 0.42632 | 1.4653 | 1.2411 | 0.96 | 0.67579 | 0.55263 | 0.46632 | 0.37474 | 0.28526 | 0.20211 | 0.12211 | -0.27474 | -0.61895 | -0.81053 | 2.0621 | 1.9758 | 1.6895 | 1.3989 | 1.2747 | 1.1758 | 1.0705 | 0.96632 | 0.87158 | 0.77684 | 0.31053 | -0.10737 | -0.32421
|  | ELLIOT DEPOT | HT |  |  |  |  | 2.26 | 2.22 | 2.1779 | 1.9979 | 1.8768 | 1.7716 | 1.6716 | 1.5716 | 1.4674 | 1.3653 | 0.95053 | 0.64632 | 0.41263 | 1.4295 | 1.1842 | 0.88842 | 0.58737 | 0.45263 | 0.35263 | 0.25789 | 0.16316 | 0.067368 | -0.026316 | -0.41684 | -0.71263 | -0.96 | 2.0442 | 1.9189 | 1.6168 | 1.3116 | 1.1737 | 1.0653 | 0.96 | 0.85579 | 0.74632 | 0.64211 | 0.20421 | -0.12316 | -0.38316
|  | ELLIOT DEPOT | HE |  |  |  |  | 2.2979 | 2.2768 | 2.2526 | 2.1842 | 2.0937 | 2.0126 | 1.94 | 1.8684 | 1.7979 | 1.7305 | 1.4474 | 1.2158 | 0.99158 | 1.5126 | 1.3105 | 1.0526 | 0.78842 | 0.68947 | 0.61789 | 0.55368 | 0.49158 | 0.43158 | 0.37368 | 0.13263 | -0.058947 | -0.23895 | 2.0442 | 1.9189 | 1.6168 | 1.3116 | 1.1737 | 1.0653 | 0.96 | 0.85579 | 0.74632 | 0.64211 | 0.20421 | -0.12316 | -0.38316
|  | ELLIOT DEPOT | CF |  |  |  |  | 2.3095 | 2.2968 | 2.2832 | 2.2695 | 2.2558 | 2.2274 | 2.2021 | 2.1758 | 2.1516 | 2.1305 | 2.0147 | 1.9042 | 1.8305 | 1.5726 | 1.4642 | 1.3379 | 1.2158 | 1.1674 | 1.1316 | 1.0979 | 1.0632 | 1.0295 | 0.99895 | 0.84316 | 0.70211 | 0.59789 | 2.0989 | 2.0811 | 2.0611 | 1.9495 | 1.8989 | 1.8589 | 1.8221 | 1.7821 | 1.7453 | 1.7137 | 1.5368 | 1.3684 | 1.2453
| DYCE | ELLON | MINIMUM HEADROOM | NJ 95510 30054 | NO | YES | 0.71 | 13.6203 | 39.1047 | 38.4911 | 37.7711 | 36.9795 | 35.8311 | 34.7563 | 33.6247 | 32.3247 | 30.9068 | 22.7426 | 16.5963 | 14.5195 | 12.6626 | 37.3837 | 36.6553 | 35.7795 | 34.8068 | 33.6058 | 32.5058 | 31.4163 | 30.1679 | 28.7847 | 21.7489 | 16.1668 | 14.2342 | 13.132 | 38.6121 | 37.9595 | 37.1353 | 36.1974 | 34.9111 | 33.7216 | 32.5416 | 31.1637 | 29.6437 | 21.1753 | 14.75 | 12.5542
|  | ELLON | EE |  |  |  |  | 13.8224 | 39.4395 | 38.9574 | 38.4037 | 37.7226 | 36.5395 | 35.1047 | 33.9374 | 32.8563 | 31.7289 | 22.7426 | 16.5963 | 14.5195 | 12.8984 | 37.7826 | 37.2226 | 36.5679 | 35.7405 | 34.5258 | 33.0289 | 31.9647 | 30.9795 | 29.9468 | 21.7805 | 16.1668 | 14.2342 | 13.3393 | 38.9584 | 38.4584 | 37.8626 | 37.0774 | 35.7511 | 34.1237 | 32.8963 | 31.7763 | 30.6047 | 21.1753 | 14.75 | 12.5542
|  | ELLON | HT |  |  |  |  | 13.6203 | 39.1047 | 38.4911 | 37.7711 | 36.9795 | 35.8311 | 34.7563 | 33.6247 | 32.3247 | 30.9068 | 23.2342 | 19.2921 | 16.9974 | 12.6626 | 37.3837 | 36.6553 | 35.7795 | 34.8068 | 33.6058 | 32.5058 | 31.4163 | 30.1679 | 28.7847 | 21.7489 | 17.7584 | 15.3332 | 13.132 | 38.6121 | 37.9595 | 37.1353 | 36.1974 | 34.9111 | 33.7216 | 32.5416 | 31.1637 | 29.6437 | 21.6405 | 17.3374 | 14.7753
|  | ELLON | HE |  |  |  |  | 14.0939 | 39.8395 | 39.51 | 39.0837 | 38.5216 | 37.3047 | 36.1258 | 35.1953 | 34.1605 | 33.0416 | 27.0174 | 23.1142 | 19.4237 | 13.2184 | 38.2511 | 37.8553 | 37.3321 | 36.6247 | 35.3689 | 34.0995 | 33.1721 | 32.1795 | 31.0963 | 25.5079 | 21.8689 | 18.5374 | 13.132 | 38.6121 | 37.9595 | 37.1353 | 36.1974 | 34.9111 | 33.7216 | 32.5416 | 31.1637 | 29.6437 | 21.6405 | 17.3374 | 14.7753
|  | ELLON | CF |  |  |  |  | 14.2276 | 40.0753 | 39.9174 | 39.7511 | 39.5384 | 39.1247 | 38.6816 | 38.2205 | 37.8479 | 37.4816 | 34.7658 | 31.6753 | 29.6079 | 13.3721 | 38.5247 | 38.3405 | 38.1426 | 37.8847 | 37.4774 | 37.0142 | 36.5226 | 36.1384 | 35.7321 | 32.7247 | 29.6553 | 27.6279 | 13.7572 | 39.6132 | 39.4511 | 39.2774 | 39.0563 | 38.6205 | 38.1532 | 37.6595 | 37.2532 | 36.8468 | 33.7174 | 30.3847 | 28.1321
| TAYNUILT | EREDINE | MINIMUM HEADROOM | NM 97142 09376 | YES | YES | 0 | 0.22421 | 0.18421 | 0.12842 | 0.069474 | 0.0084211 | -0.094737 | -0.20105 | -0.31053 | -0.41158 | -0.51579 | -1.0326 | -1.5263 | -1.8284 | 0.21263 | 0.17684 | 0.12421 | 0.067368 | 0.0094737 | -0.082105 | -0.17263 | -0.26526 | -0.35474 | -0.44526 | -0.89158 | -1.32 | -1.5905 | 0.21684 | 0.16947 | 0.11474 | 0.054737 | -0.0063158 | -0.11368 | -0.22105 | -0.33158 | -0.43474 | -0.54105 | -1.0705 | -1.5758 | -1.8832
|  | EREDINE | EE |  |  |  |  | 0.22632 | 0.18421 | 0.12842 | 0.069474 | 0.0084211 | -0.094737 | -0.20105 | -0.31053 | -0.41158 | -0.51579 | -1.0326 | -1.5263 | -1.8284 | 0.21368 | 0.17684 | 0.12421 | 0.067368 | 0.0094737 | -0.082105 | -0.17263 | -0.26526 | -0.35474 | -0.44526 | -0.89158 | -1.32 | -1.5905 | 0.21789 | 0.16947 | 0.11474 | 0.054737 | -0.0063158 | -0.11368 | -0.22105 | -0.33158 | -0.43474 | -0.54105 | -1.0705 | -1.5758 | -1.8832
|  | EREDINE | HT |  |  |  |  | 0.22421 | 0.20947 | 0.19474 | 0.17895 | 0.16105 | 0.10737 | 0.053684 | 2.7756e-17 | -0.063158 | -0.12632 | -0.38632 | -0.57895 | -0.70632 | 0.21263 | 0.20632 | 0.18947 | 0.17263 | 0.15579 | 0.10842 | 0.063158 | 0.016842 | -0.036842 | -0.089474 | -0.31263 | -0.48211 | -0.59579 | 0.21684 | 0.20105 | 0.18316 | 0.16421 | 0.14526 | 0.089474 | 0.034737 | -0.02 | -0.085263 | -0.15053 | -0.41895 | -0.61789 | -0.74737
|  | EREDINE | HE |  |  |  |  | 0.22842 | 0.21579 | 0.20211 | 0.18842 | 0.17053 | 0.10526 | 0.049474 | -0.0094737 | -0.065263 | -0.12211 | -0.39158 | -0.64842 | -0.91895 | 0.21474 | 0.20947 | 0.19684 | 0.18105 | 0.16421 | 0.11053 | 0.062105 | 0.013684 | -0.033684 | -0.081053 | -0.31053 | -0.52947 | -0.75895 | 0.21684 | 0.20105 | 0.18316 | 0.16421 | 0.14526 | 0.089474 | 0.034737 | -0.02 | -0.085263 | -0.15053 | -0.41895 | -0.61789 | -0.74737
|  | EREDINE | CF |  |  |  |  | 0.22842 | 0.22526 | 0.22105 | 0.21789 | 0.21158 | 0.19053 | 0.16947 | 0.15158 | 0.13263 | 0.11895 | 0.027368 | -0.094737 | -0.18632 | 0.21474 | 0.21368 | 0.21158 | 0.21053 | 0.20737 | 0.19368 | 0.17579 | 0.16105 | 0.14526 | 0.13368 | 0.058947 | -0.041053 | -0.11368 | 0.21895 | 0.21579 | 0.21053 | 0.20737 | 0.20211 | 0.18105 | 0.15895 | 0.14 | 0.12211 | 0.10842 | 0.012632 | -0.11579 | -0.20842
| INVERNESS | ERROGIE | MINIMUM HEADROOM | NH 56674 22810 | YES | YES | 0 | 1.0358 | 1.0274 | 1.0032 | 0.97474 | 0.94421 | 0.76421 | 0.54737 | 0.32 | 0.098947 | -0.22632 | -2.2084 | -4.4726 | -6.2242 | 1.0337 | 1.0263 | 1.0053 | 0.98211 | 0.95263 | 0.80947 | 0.61158 | 0.40105 | 0.20105 | -0.11579 | -1.8926 | -4.1116 | -5.9937 | 1.0295 | 1.0179 | 0.99368 | 0.96842 | 0.93895 | 0.75579 | 0.53474 | 0.30737 | 0.10947 | -0.20526 | -2.4295 | -4.9032 | -6.9021
|  | ERROGIE | EE |  |  |  |  | 1.0368 | 1.0274 | 1.0032 | 0.97474 | 0.94421 | 0.76421 | 0.54737 | 0.32421 | 0.12947 | -0.17053 | -2.2084 | -4.4726 | -6.2242 | 1.0347 | 1.0263 | 1.0053 | 0.98211 | 0.95263 | 0.80947 | 0.64105 | 0.46842 | 0.31579 | 0.056842 | -1.8926 | -4.1116 | -5.9937 | 1.0305 | 1.0179 | 0.99368 | 0.96842 | 0.93895 | 0.75579 | 0.53474 | 0.30737 | 0.10947 | -0.20526 | -2.4295 | -4.9032 | -6.9021
|  | ERROGIE | HT |  |  |  |  | 1.0358 | 1.0305 | 1.0158 | 1.0032 | 0.98737 | 0.84421 | 0.7 | 0.50737 | 0.27895 | -0.10632 | -1.9126 | -3.98 | -5.3947 | 1.0337 | 1.0295 | 1.0189 | 1.0084 | 0.99789 | 0.88421 | 0.76842 | 0.59789 | 0.39474 | 0.016842 | -1.8274 | -4.0705 | -5.66 | 1.0295 | 1.0232 | 1.0095 | 0.99684 | 0.98526 | 0.84211 | 0.69579 | 0.49368 | 0.25579 | -0.16947 | -2.1747 | -4.5326 | -6.1663
|  | ERROGIE | HE |  |  |  |  | 1.0379 | 1.0347 | 1.0284 | 1.0211 | 1.0158 | 0.77684 | 0.54947 | 0.32 | 0.098947 | -0.22632 | -1.6137 | -3.3579 | -5.2632 | 1.0358 | 1.0337 | 1.0305 | 1.0242 | 1.0168 | 0.81579 | 0.61158 | 0.40105 | 0.20105 | -0.11579 | -1.46 | -3.2347 | -5.1789 | 1.0295 | 1.0232 | 1.0095 | 0.99684 | 0.98526 | 0.84211 | 0.69579 | 0.49368 | 0.25579 | -0.16947 | -2.1747 | -4.5326 | -6.1663
|  | ERROGIE | CF |  |  |  |  | 1.0389 | 1.0368 | 1.0347 | 1.0305 | 1.0284 | 0.96526 | 0.90421 | 0.76211 | 0.62316 | 0.46526 | -0.24421 | -1.3326 | -2.5505 | 1.0368 | 1.0358 | 1.0337 | 1.0316 | 1.0295 | 0.98421 | 0.93474 | 0.79158 | 0.64947 | 0.47895 | -0.23895 | -1.3589 | -2.6726 | 1.0326 | 1.0305 | 1.0284 | 1.0242 | 1.0211 | 0.96526 | 0.90526 | 0.74737 | 0.59368 | 0.41579 | -0.36947 | -1.5821 | -2.9642
| ABERNETHY | ERROL | MINIMUM HEADROOM | NO 23206 23038 | NO | YES | 0.15 | 4.9953 | 4.8321 | 4.5974 | 4.33 | 4.0121 | 3.3447 | 2.7521 | 2.1205 | 1.4921 | 0.85947 | -3.7563 | -11.6995 | -16.3626 | 4.9416 | 4.7574 | 4.5047 | 4.2142 | 3.8784 | 3.2658 | 2.73 | 2.2216 | 1.6626 | 1.0953 | -3.1879 | -11.3521 | -16.4616 | 5.0532 | 4.8721 | 4.6195 | 4.3258 | 3.9753 | 3.2721 | 2.6542 | 2.0311 | 1.3911 | 0.74368 | -4.2111 | -13.0605 | -18.3763
|  | ERROL | EE |  |  |  |  | 5.0353 | 4.9416 | 4.7395 | 4.5079 | 4.2374 | 3.5395 | 2.8163 | 2.1205 | 1.4921 | 0.85947 | -3.7563 | -11.6995 | -16.3626 | 5.0163 | 4.8774 | 4.6647 | 4.4142 | 4.1268 | 3.5111 | 2.8879 | 2.29 | 1.7447 | 1.1995 | -3.1879 | -11.3521 | -16.4616 | 5.1121 | 4.99 | 4.7732 | 4.5205 | 4.2195 | 3.4889 | 2.7416 | 2.0311 | 1.3911 | 0.74579 | -4.2111 | -13.0605 | -18.3763
|  | ERROL | HT |  |  |  |  | 4.9953 | 4.8321 | 4.5974 | 4.33 | 4.0121 | 3.3447 | 2.7521 | 2.1816 | 1.5426 | 0.90474 | -3.1784 | -8.8753 | -12.7795 | 4.9416 | 4.7574 | 4.5047 | 4.2142 | 3.8784 | 3.2658 | 2.73 | 2.2216 | 1.6626 | 1.0953 | -2.95 | -9.1995 | -13.6068 | 5.0532 | 4.8721 | 4.6195 | 4.3258 | 3.9753 | 3.2721 | 2.6542 | 2.0616 | 1.4016 | 0.74368 | -3.7121 | -10.1932 | -14.6826
|  | ERROL | HE |  |  |  |  | 5.0847 | 5.0405 | 4.95 | 4.7805 | 4.5742 | 3.8826 | 3.3184 | 2.79 | 2.2721 | 1.5647 | -2.21 | -8.7974 | -13.8574 | 5.0658 | 5.0216 | 4.8837 | 4.6942 | 4.4616 | 3.8689 | 3.3732 | 2.9205 | 2.4721 | 1.7879 | -1.8911 | -8.9268 | -14.1395 | 5.0532 | 4.8721 | 4.6195 | 4.3258 | 3.9753 | 3.2721 | 2.6542 | 2.0616 | 1.4016 | 0.74368 | -3.7121 | -10.1932 | -14.6826
|  | ERROL | CF |  |  |  |  | 5.1121 | 5.0868 | 5.0574 | 5.0047 | 4.9121 | 4.6437 | 4.4079 | 4.1805 | 3.9637 | 3.5332 | 1.5437 | -1.4068 | -4.6879 | 5.0932 | 5.0679 | 5.0395 | 4.9437 | 4.8395 | 4.6121 | 4.4163 | 4.2205 | 4.0226 | 3.5395 | 1.5111 | -1.5426 | -5.1058 | 5.1889 | 5.1637 | 5.1353 | 5.0532 | 4.9511 | 4.6816 | 4.4363 | 4.1995 | 3.9732 | 3.4753 | 1.2805 | -2.0058 | -5.7311
| FASNAKYLE | FASNAKYLE | MINIMUM HEADROOM | NH 31948 29998 | YES | YES | 0 | 0.99474 | 0.97579 | 0.95474 | 0.93474 | 0.91158 | 0.84947 | 0.77474 | 0.70316 | 0.63684 | 0.52737 | -0.24421 | -1.1705 | -1.9432 | 0.98947 | 0.96947 | 0.94842 | 0.92947 | 0.90947 | 0.86421 | 0.80842 | 0.74947 | 0.67474 | 0.54 | -0.26105 | -1.3189 | -2.0863 | 0.98526 | 0.96526 | 0.94105 | 0.92 | 0.89474 | 0.82947 | 0.75368 | 0.68105 | 0.61263 | 0.50105 | -0.36421 | -1.4516 | -2.2895
|  | FASNAKYLE | EE |  |  |  |  | 0.99895 | 0.98211 | 0.95895 | 0.93474 | 0.91158 | 0.84947 | 0.77474 | 0.70316 | 0.63684 | 0.56421 | -0.24421 | -1.1421 | -1.9432 | 0.99684 | 0.98 | 0.95895 | 0.93895 | 0.91789 | 0.86947 | 0.80842 | 0.75053 | 0.69579 | 0.63474 | -0.18105 | -1.1053 | -1.9916 | 0.99263 | 0.97158 | 0.94632 | 0.92 | 0.89474 | 0.82947 | 0.75368 | 0.68105 | 0.61263 | 0.53789 | -0.36211 | -1.3674 | -2.2895
|  | FASNAKYLE | HT |  |  |  |  | 0.99474 | 0.97579 | 0.95474 | 0.93579 | 0.91579 | 0.86316 | 0.80947 | 0.75579 | 0.69474 | 0.54105 | -0.22526 | -1.1705 | -1.8442 | 0.98947 | 0.96947 | 0.94842 | 0.92947 | 0.90947 | 0.86421 | 0.82 | 0.77684 | 0.72737 | 0.56421 | -0.26105 | -1.3189 | -2.0863 | 0.98526 | 0.96526 | 0.94105 | 0.92105 | 0.89895 | 0.84421 | 0.79053 | 0.73579 | 0.67368 | 0.50105 | -0.36421 | -1.4516 | -2.2326
|  | FASNAKYLE | HE |  |  |  |  | 1.0042 | 0.99789 | 0.99053 | 0.98105 | 0.96947 | 0.90105 | 0.82 | 0.73579 | 0.65684 | 0.52737 | -0.014737 | -0.73474 | -1.5211 | 1.0053 | 0.99895 | 0.98842 | 0.97895 | 0.96842 | 0.90947 | 0.83158 | 0.74947 | 0.67474 | 0.54 | -0.016842 | -0.78632 | -1.6284 | 0.98526 | 0.96526 | 0.94105 | 0.92105 | 0.89895 | 0.84421 | 0.79053 | 0.73579 | 0.67368 | 0.50105 | -0.36421 | -1.4516 | -2.2326
|  | FASNAKYLE | CF |  |  |  |  | 1.0074 | 1.0053 | 1 | 0.99789 | 0.99368 | 0.97053 | 0.95053 | 0.90421 | 0.84737 | 0.77684 | 0.48211 | 0.028421 | -0.51053 | 1.0084 | 1.0063 | 1.0011 | 0.99684 | 0.99053 | 0.97368 | 0.95579 | 0.90737 | 0.84211 | 0.76316 | 0.44737 | -0.043158 | -0.64632 | 1.0084 | 1.0032 | 0.99684 | 0.99158 | 0.98421 | 0.96211 | 0.94 | 0.88947 | 0.82316 | 0.74211 | 0.41158 | -0.10316 | -0.72211
| TUMMEL BRIDGE | FINCASTLE | MINIMUM HEADROOM | NN 87976 61147 | YES | YES | 0 | 0.10316 | 0.10211 | 0.1 | 0.097895 | 0.095789 | 0.077895 | 0.052632 | 0.025263 | 0.0021053 | -0.027368 | -0.23053 | -0.45789 | -0.61368 | 0.10211 | 0.10105 | 0.1 | 0.097895 | 0.095789 | 0.08 | 0.058947 | 0.036842 | 0.014737 | -0.016842 | -0.20211 | -0.41895 | -0.58737 | 0.1 | 0.098947 | 0.096842 | 0.095789 | 0.092632 | 0.074737 | 0.049474 | 0.022105 | 0 | -0.028421 | -0.25263 | -0.49895 | -0.67579
|  | FINCASTLE | EE |  |  |  |  | 0.10316 | 0.10211 | 0.10105 | 0.098947 | 0.096842 | 0.077895 | 0.052632 | 0.025263 | 0.0021053 | -0.024211 | -0.23053 | -0.45789 | -0.61368 | 0.10211 | 0.10105 | 0.10105 | 0.098947 | 0.097895 | 0.08 | 0.058947 | 0.036842 | 0.018947 | -0.0052632 | -0.20211 | -0.41895 | -0.58737 | 0.1 | 0.098947 | 0.097895 | 0.095789 | 0.093684 | 0.074737 | 0.049474 | 0.022105 | 0 | -0.028421 | -0.25263 | -0.49895 | -0.67579
|  | FINCASTLE | HT |  |  |  |  | 0.10316 | 0.10211 | 0.1 | 0.097895 | 0.095789 | 0.08 | 0.061053 | 0.044211 | 0.018947 | -0.021053 | -0.19579 | -0.38632 | -0.51579 | 0.10211 | 0.10105 | 0.1 | 0.097895 | 0.095789 | 0.08 | 0.065263 | 0.051579 | 0.029474 | -0.0094737 | -0.18632 | -0.39158 | -0.53368 | 0.1 | 0.098947 | 0.096842 | 0.095789 | 0.092632 | 0.076842 | 0.057895 | 0.041053 | 0.014737 | -0.027368 | -0.22421 | -0.44105 | -0.58737
|  | FINCASTLE | HE |  |  |  |  | 0.10421 | 0.10316 | 0.10316 | 0.10105 | 0.10105 | 0.078947 | 0.055789 | 0.029474 | 0.0052632 | -0.027368 | -0.16842 | -0.33684 | -0.52316 | 0.10316 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.081053 | 0.06 | 0.036842 | 0.014737 | -0.016842 | -0.15158 | -0.32105 | -0.50632 | 0.1 | 0.098947 | 0.096842 | 0.095789 | 0.092632 | 0.076842 | 0.057895 | 0.041053 | 0.014737 | -0.027368 | -0.22421 | -0.44105 | -0.58737
|  | FINCASTLE | CF |  |  |  |  | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10211 | 0.094737 | 0.088421 | 0.077895 | 0.065263 | 0.051579 | -0.02 | -0.12421 | -0.23895 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.097895 | 0.091579 | 0.08 | 0.066316 | 0.050526 | -0.021053 | -0.12737 | -0.24842 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.092632 | 0.086316 | 0.074737 | 0.06 | 0.044211 | -0.034737 | -0.15263 | -0.28
| SHETLAND | FIRTH | MINIMUM HEADROOM | HU4396874166 | YES | YES | 0 | 1.4811 | 1.2147 | 0.82105 | 0.3 | -0.34632 | -1.1253 | -1.4947 | -2.2505 | -3.3168 | -4.3537 | -5.1021 | -7.0811 | -7.1232 | 1.2032 | 0.88737 | 0.42526 | -0.18842 | -0.94947 | -1.8642 | -2.2968 | -3.1853 | -4.44 | -5.6653 | -6.5242 | -8.0284 | -8.0642 | 1.2326 | 0.92737 | 0.46526 | -0.14632 | -0.90632 | -1.8211 | -2.2558 | -3.1432 | -4.3958 | -5.6211 | -6.4895 | -6.6042 | -6.6453
|  | FIRTH | EE |  |  |  |  | 1.4853 | 1.2242 | 0.83158 | 0.31474 | -0.32947 | -1.1042 | -1.4737 | -2.2295 | -3.2926 | -4.3537 | -5.1021 | -5.2074 | -5.2453 | 1.2074 | 0.89789 | 0.43579 | -0.17368 | -0.93158 | -1.8432 | -2.2737 | -3.1611 | -4.4137 | -5.6653 | -6.5242 | -6.6316 | -6.6674 | 1.2368 | 0.93789 | 0.47684 | -0.13158 | -0.88947 | -1.8 | -2.2337 | -3.1211 | -4.3726 | -5.6211 | -6.4895 | -6.6042 | -6.6453
|  | FIRTH | HT |  |  |  |  | 1.4811 | 1.2147 | 0.82105 | 0.3 | -0.34632 | -1.1253 | -1.4947 | -2.2505 | -3.3168 | -4.3042 | -5.0411 | -5.1347 | -5.1758 | 1.2032 | 0.88737 | 0.42526 | -0.18842 | -0.94947 | -1.8642 | -2.2968 | -3.1853 | -4.44 | -5.6032 | -6.4568 | -6.5558 | -6.5979 | 1.2326 | 0.92737 | 0.46526 | -0.14632 | -0.90632 | -1.8211 | -2.2558 | -3.1432 | -4.3958 | -5.5589 | -6.4168 | -6.5179 | -6.5621
|  | FIRTH | HE |  |  |  |  | 1.4937 | 1.2368 | 0.85158 | 0.33789 | -0.3 | -1.0726 | -1.4368 | -2.1863 | -3.2432 | -4.3 | -5.0126 | -7.0811 | -7.1232 | 1.2158 | 0.91053 | 0.45684 | -0.14842 | -0.90211 | -1.8116 | -2.2368 | -3.1179 | -4.3642 | -5.6105 | -6.4368 | -8.0284 | -8.0642 | 1.2326 | 0.92737 | 0.46526 | -0.14632 | -0.90632 | -1.8211 | -2.2558 | -3.1432 | -4.3958 | -5.5589 | -6.4168 | -6.5179 | -6.5621
|  | FIRTH | CF |  |  |  |  | 1.5842 | 1.5147 | 1.4126 | 1.2695 | 1.0947 | 0.88105 | 0.63053 | 0.35053 | 0.032632 | -0.14632 | -0.35368 | -0.38526 | -0.40526 | 1.3284 | 1.2421 | 1.1168 | 0.94947 | 0.74316 | 0.49263 | 0.2 | -0.13158 | -0.50421 | -0.71474 | -0.95158 | -0.97895 | -0.99684 | 1.2916 | 1.2695 | 1.1547 | 0.98947 | 0.78316 | 0.53158 | 0.23895 | -0.091579 | -0.46421 | -0.67474 | -0.91474 | -0.94632 | -0.96737
| FORT WILLIAM | FISHNISH | MINIMUM HEADROOM | NM 66623 42191 | YES | NO | 0 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.19789 | 0.19789 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19684
|  | FISHNISH | EE |  |  |  |  | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.19895 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19789 | 0.19789 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.19895 | 0.19895 | 0.19895
|  | FISHNISH | HT |  |  |  |  | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.19789 | 0.19789 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19684
|  | FISHNISH | HE |  |  |  |  | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19895 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19684
|  | FISHNISH | CF |  |  |  |  | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.19895 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2
| THURSO | FLOTTA | MINIMUM HEADROOM | NC 94318 95432 | YES | YES | 0 | -1.28 | -1.2832 | -1.2874 | -1.2916 | -1.2947 | -1.2937 | -1.2958 | -1.2989 | -1.3032 | -1.2853 | 0.49158 | 0.48632 | 0.48316 | -1.2558 | -1.26 | -1.2653 | -1.2695 | -1.2726 | -1.2716 | -1.2737 | -1.2779 | -1.2832 | -1.2621 | 0.32526 | 0.32 | 0.31684 | 0.92947 | 0.92526 | 0.92105 | 0.91789 | 0.91368 | 0.91579 | 0.91263 | 0.90947 | 0.90526 | 0.92316 | 2.9768 | 2.9716 | 2.9684
|  | FLOTTA | EE |  |  |  |  | -1.2789 | -1.2811 | -1.2842 | -1.2874 | -1.2905 | -1.2937 | -1.2958 | -1.2989 | -1.3032 | 0.50316 | 0.49579 | 0.49263 | 0.49053 | -1.2547 | -1.2568 | -1.2611 | -1.2642 | -1.2684 | -1.2716 | -1.2737 | -1.2779 | -1.2832 | 0.33684 | 0.32947 | 0.32632 | 0.32421 | 0.93053 | 0.92842 | 0.92421 | 0.92211 | 0.91789 | 0.91579 | 0.91263 | 0.90947 | 0.90526 | 2.9884 | 2.9811 | 2.9779 | 2.9758
|  | FLOTTA | HT |  |  |  |  | -1.28 | -1.2832 | -1.2874 | -1.2916 | -1.2947 | 0.50737 | 0.50526 | 0.50211 | 0.5 | 0.49789 | 0.49158 | 0.48632 | 0.48316 | -1.2558 | -1.26 | -1.2653 | -1.2695 | -1.2726 | 0.34105 | 0.33895 | 0.33579 | 0.33368 | 0.33158 | 0.32526 | 0.32 | 0.31684 | 0.92947 | 0.92526 | 0.92105 | 0.91789 | 0.91368 | 2.9926 | 2.9905 | 2.9874 | 2.9853 | 2.9832 | 2.9768 | 2.9716 | 2.9684
|  | FLOTTA | HE |  |  |  |  | -1.2768 | -1.2789 | -1.28 | -1.2821 | -1.2842 | -1.2863 | -1.2874 | -1.2905 | -1.2916 | 0.50842 | 0.50421 | 0.50211 | 0.50211 | -1.2526 | -1.2547 | -1.2558 | -1.2579 | -1.26 | -1.2621 | -1.2642 | -1.2674 | -1.2684 | 0.34211 | 0.33789 | 0.33579 | 0.33579 | 0.92947 | 0.92526 | 0.92105 | 0.91789 | 0.91368 | 2.9926 | 2.9905 | 2.9874 | 2.9853 | 2.9832 | 2.9768 | 2.9716 | 2.9684
|  | FLOTTA | CF |  |  |  |  | -1.2758 | -1.2758 | -1.2768 | -1.2789 | -1.2789 | -1.28 | -1.2821 | -1.2821 | -1.2842 | -1.2853 | 0.51158 | 0.51053 | 0.50947 | -1.2505 | -1.2516 | -1.2526 | -1.2547 | -1.2547 | -1.2558 | -1.2579 | -1.2579 | -1.26 | -1.2621 | 0.34526 | 0.34421 | 0.34316 | 0.93368 | 0.93368 | 0.93263 | 0.93053 | 0.92947 | 0.92842 | 0.92737 | 0.92737 | 0.92526 | 0.92316 | 2.9968 | 2.9958 | 2.9947
| ELGIN | FOCHABERS | MINIMUM HEADROOM | NC 94318 95432 | NO | YES | 0 | 15.6847 | 15.5079 | 15.2889 | 15.07 | 14.8079 | 14.3911 | 13.8258 | 13.2553 | 12.5489 | 11.6542 | 9.0205 | 7.1637 | 5.1511 | 14.4537 | 14.2526 | 14.0021 | 13.7558 | 13.4505 | 13.0558 | 12.4663 | 11.8737 | 11.1263 | 10.1905 | 7.8074 | 6.2653 | 4.1147 | 14.9855 | 14.8003 | 14.5697 | 14.3403 | 14.0476 | 13.6108 | 12.995 | 12.3739 | 11.5971 | 10.6434 | 7.8739 | 5.9603 | 3.7571
|  | FOCHABERS | EE |  |  |  |  | 15.7542 | 15.6142 | 15.43 | 15.2563 | 15.0489 | 14.6089 | 14.0532 | 13.53 | 13.0216 | 12.4553 | 9.0205 | 7.1637 | 5.1511 | 14.5326 | 14.3726 | 14.1663 | 13.9758 | 13.7421 | 13.3379 | 12.8095 | 12.3263 | 11.8358 | 11.2758 | 7.8074 | 6.2653 | 4.1147 | 15.0592 | 14.9118 | 14.7182 | 14.5371 | 14.3182 | 13.8592 | 13.2708 | 12.7213 | 12.1792 | 11.5697 | 7.8739 | 5.9603 | 3.7571
|  | FOCHABERS | HT |  |  |  |  | 15.6847 | 15.5079 | 15.2889 | 15.07 | 14.8079 | 14.3911 | 13.8258 | 13.2553 | 12.5489 | 11.6542 | 9.3595 | 7.9068 | 5.91 | 14.4537 | 14.2526 | 14.0021 | 13.7558 | 13.4505 | 13.0558 | 12.4663 | 11.8737 | 11.1263 | 10.1905 | 7.9284 | 6.4916 | 4.2621 | 14.9855 | 14.8003 | 14.5697 | 14.3403 | 14.0476 | 13.6108 | 12.995 | 12.3739 | 11.5971 | 10.6434 | 8.2203 | 6.6466 | 4.3645
|  | FOCHABERS | HE |  |  |  |  | 15.8521 | 15.7574 | 15.6311 | 15.5047 | 15.3332 | 14.8932 | 14.4511 | 14.0658 | 13.6826 | 13.2774 | 11.4289 | 9.3405 | 6.7153 | 14.6432 | 14.5347 | 14.3895 | 14.2453 | 14.0432 | 13.6421 | 13.2116 | 12.8558 | 12.4989 | 12.1126 | 10.3474 | 8.2358 | 5.5684 | 14.9855 | 14.8003 | 14.5697 | 14.3403 | 14.0476 | 13.6108 | 12.995 | 12.3739 | 11.5971 | 10.6434 | 8.2203 | 6.6466 | 4.3645
|  | FOCHABERS | CF |  |  |  |  | 15.9058 | 15.8511 | 15.7847 | 15.7321 | 15.6689 | 15.5089 | 15.3374 | 15.1616 | 15.0016 | 14.8426 | 13.83 | 12.3995 | 10.7426 | 14.7053 | 14.6421 | 14.5663 | 14.5074 | 14.4358 | 14.2937 | 14.1295 | 13.9579 | 13.8011 | 13.6326 | 12.5937 | 11.0874 | 9.2968 | 15.2171 | 15.1603 | 15.0897 | 15.035 | 14.9687 | 14.8055 | 14.6287 | 14.4466 | 14.2803 | 14.1129 | 13.015 | 11.4339 | 9.6424
| NAIRN | FORRES | MINIMUM HEADROOM | NJ 03362 59425 | NO | YES | 0.05 | 16.9905 | 16.7484 | 16.3663 | 15.8968 | 38.9174 | 37.6942 | 36.3163 | 35.0226 | 33.5395 | 31.7911 | 24.7858 | 17.9342 | 11.0521 | 14.9237 | 14.3668 | 13.8332 | 13.1163 | 35.2679 | 34.0268 | 32.6805 | 31.4289 | 30.0047 | 28.2626 | 22.1437 | 15.3079 | 8.3353 | 15.5313 | 15.0061 | 14.4861 | 13.7955 | 36.6089 | 35.2437 | 33.7563 | 32.37 | 30.7795 | 28.8711 | 21.5679 | 14.3553 | 6.41
|  | FORRES | EE |  |  |  |  | 17.0716 | 16.9095 | 16.6032 | 16.1863 | 39.2911 | 38.1247 | 36.6668 | 35.3279 | 34.1384 | 32.8616 | 24.7858 | 17.9342 | 11.0521 | 15.0458 | 14.6405 | 14.1837 | 13.5626 | 35.8868 | 34.6268 | 33.2553 | 32.0732 | 31.0132 | 29.8542 | 22.1437 | 15.9647 | 8.3353 | 15.6124 | 15.2682 | 14.8145 | 14.2103 | 37.1795 | 35.7574 | 34.1942 | 32.8047 | 31.5711 | 30.2384 | 21.5679 | 14.3553 | 6.41
|  | FORRES | HT |  |  |  |  | 16.9905 | 16.7484 | 16.3663 | 15.8968 | 38.9174 | 37.6942 | 36.3163 | 35.0226 | 33.5395 | 31.7911 | 25.8395 | 19.1447 | 13.2963 | 14.9237 | 14.3668 | 13.8332 | 13.1163 | 35.2679 | 34.0268 | 32.6805 | 31.4289 | 30.0047 | 28.2626 | 22.4753 | 15.3079 | 8.7458 | 15.5313 | 15.0061 | 14.4861 | 13.7955 | 36.6089 | 35.2437 | 33.7563 | 32.37 | 30.7795 | 28.8711 | 22.4416 | 14.8921 | 8.1921
|  | FORRES | HE |  |  |  |  | 17.1821 | 17.0726 | 16.9463 | 16.6768 | 39.8711 | 38.7079 | 37.6279 | 36.5805 | 35.5753 | 34.5205 | 29.4268 | 22.9184 | 15.3079 | 15.1563 | 15.0068 | 14.6921 | 14.1974 | 36.6037 | 35.3774 | 34.2016 | 33.2532 | 32.3521 | 31.39 | 26.6626 | 20.0868 | 12.2605 | 15.5313 | 15.0061 | 14.4861 | 13.7955 | 36.6089 | 35.2437 | 33.7563 | 32.37 | 30.7795 | 28.8711 | 22.4416 | 14.8921 | 8.1921
|  | FORRES | CF |  |  |  |  | 17.2421 | 17.1779 | 17.1042 | 17.0316 | 40.5058 | 40.0626 | 39.6574 | 39.2721 | 38.9405 | 38.6511 | 36.0911 | 31.6184 | 26.7679 | 15.2163 | 15.1521 | 15.0826 | 14.8805 | 37.6532 | 37.1763 | 36.7416 | 36.35 | 36.0237 | 35.6963 | 32.7742 | 28.15 | 22.8605 | 15.7829 | 15.7187 | 15.6461 | 15.4955 | 38.9016 | 38.3584 | 37.8679 | 37.4163 | 37.0384 | 36.6795 | 33.5753 | 28.5921 | 23.0374
| DOUNREAY | FORSS | MINIMUM HEADROOM | ND 02614 69148 | YES | YES | 0 | 0.17579 | 0.15158 | 0.10842 | 0.065263 | 0.015789 | -0.035789 | -0.095789 | -2.4579 | -2.8432 | -4.9084 | -8.3305 | -12.6116 | -15.7432 | 0.32421 | 0.29895 | 0.25789 | 0.21789 | 0.16842 | 0.11895 | 0.023158 | -1.8253 | -2.1379 | -3.8916 | -7.2221 | -11.3568 | -14.7158 | 0.16842 | 0.14421 | 0.1 | 0.055789 | 0.0021053 | -0.051579 | -0.096842 | -2.4821 | -2.8695 | -4.9463 | -8.7211 | -13.3832 | -16.9411
|  | FORSS | EE |  |  |  |  | 0.18632 | 0.16842 | 0.12105 | 0.072632 | 0.021053 | -0.033684 | -0.082105 | -2.4579 | -2.8432 | -4.9084 | -8.3305 | -12.6116 | -15.7432 | 0.33684 | 0.31684 | 0.27579 | 0.23053 | 0.18316 | 0.13158 | 0.087368 | -1.8253 | -2.1379 | -3.8368 | -7.2221 | -11.3568 | -14.7158 | 0.17895 | 0.16211 | 0.11368 | 0.064211 | 0.010526 | -0.046316 | -0.096842 | -2.4821 | -2.8695 | -4.9463 | -8.7211 | -13.3832 | -16.9411
|  | FORSS | HT |  |  |  |  | 0.17579 | 0.15158 | 0.10842 | 0.065263 | 0.015789 | -0.035789 | -0.078947 | -2.0758 | -2.5316 | -4.8189 | -8.0032 | -11.7979 | -14.3863 | 0.32421 | 0.29895 | 0.25789 | 0.21789 | 0.16842 | 0.11895 | 0.077895 | -1.5326 | -1.9326 | -3.8916 | -7.1547 | -11.2368 | -14.12 | 0.16842 | 0.14421 | 0.1 | 0.055789 | 0.0021053 | -0.051579 | -0.096842 | -2.0947 | -2.5663 | -4.9168 | -8.4947 | -12.8 | -15.7811
|  | FORSS | HE |  |  |  |  | 0.2 | 0.18947 | 0.17368 | 0.15684 | 0.13158 | 0.04 | -0.095789 | -1.6526 | -2.0853 | -3.4747 | -5.5379 | -8.8042 | -12.3958 | 0.35263 | 0.34105 | 0.32526 | 0.30737 | 0.28316 | 0.18105 | 0.023158 | -1.2695 | -1.6621 | -2.8863 | -4.9526 | -8.2495 | -11.8916 | 0.16842 | 0.14421 | 0.1 | 0.055789 | 0.0021053 | -0.051579 | -0.096842 | -2.0947 | -2.5663 | -4.9168 | -8.4947 | -12.8 | -15.7811
|  | FORSS | CF |  |  |  |  | 0.20737 | 0.20105 | 0.19053 | 0.18105 | 0.16947 | 0.16 | 0.14737 | -0.79368 | -1.0516 | -1.3326 | -2.6105 | -4.6747 | -6.9474 | 0.36105 | 0.35368 | 0.34421 | 0.33368 | 0.32211 | 0.31263 | 0.3 | -0.49789 | -0.76316 | -1.0663 | -2.3474 | -4.4547 | -6.8811 | 0.2 | 0.19368 | 0.18421 | 0.17368 | 0.16211 | 0.15158 | 0.14 | -0.82105 | -1.1084 | -1.4379 | -2.8516 | -5.1358 | -7.7063
| BRACO | FORTEVIOT | MINIMUM HEADROOM | NO 04539 18092 | YES | YES | 1.796 | 2.7893 | 2.7524 | 2.7029 | 2.6524 | 2.6008 | 2.3966 | 2.1682 | 1.9082 | 1.6829 | 1.3577 | -0.41916 | -2.3371 | -3.5392 | 2.0366 | 1.9998 | 1.9524 | 1.904 | 1.8535 | 1.6882 | 1.5282 | 1.3261 | 1.1103 | 0.77874 | -0.77179 | -2.5518 | -3.8213 | 2.1366 | 2.0998 | 2.0503 | 2.0008 | 1.9482 | 1.7472 | 1.524 | 1.2672 | 1.044 | 0.68084 | -1.1792 | -3.2234 | -4.5665
|  | FORTEVIOT | EE |  |  |  |  | 2.804 | 2.7766 | 2.7335 | 2.6903 | 2.6472 | 2.4229 | 2.1682 | 1.9082 | 1.6829 | 1.3798 | -0.41916 | -2.3371 | -3.5392 | 2.0514 | 2.024 | 1.984 | 1.944 | 1.904 | 1.7272 | 1.5282 | 1.3261 | 1.1503 | 0.88295 | -0.77179 | -2.5518 | -3.8213 | 2.1514 | 2.124 | 2.0808 | 2.0377 | 1.9956 | 1.7745 | 1.524 | 1.2672 | 1.044 | 0.72821 | -1.1792 | -3.2234 | -4.5665
|  | FORTEVIOT | HT |  |  |  |  | 2.7893 | 2.7524 | 2.7029 | 2.6524 | 2.6008 | 2.3966 | 2.2051 | 1.9703 | 1.7114 | 1.3577 | -0.15705 | -1.6455 | -2.596 | 2.0366 | 1.9998 | 1.9524 | 1.904 | 1.8535 | 1.6882 | 1.5335 | 1.3293 | 1.1103 | 0.77874 | -0.69074 | -2.2623 | -3.3171 | 2.1366 | 2.0998 | 2.0503 | 2.0008 | 1.9482 | 1.7472 | 1.5587 | 1.3187 | 1.0556 | 0.68084 | -0.95811 | -2.6339 | -3.7286
|  | FORTEVIOT | HE |  |  |  |  | 2.8251 | 2.8061 | 2.784 | 2.7598 | 2.7335 | 2.4693 | 2.2377 | 2.0029 | 1.7766 | 1.4893 | 0.25137 | -1.1297 | -2.6192 | 2.0724 | 2.0535 | 2.0324 | 2.0082 | 1.9829 | 1.7619 | 1.5629 | 1.3608 | 1.1672 | 0.90084 | -0.22442 | -1.5602 | -3.0034 | 2.1366 | 2.0998 | 2.0503 | 2.0008 | 1.9482 | 1.7472 | 1.5587 | 1.3187 | 1.0556 | 0.68084 | -0.95811 | -2.6339 | -3.7286
|  | FORTEVIOT | CF |  |  |  |  | 4.9482 | 2.8251 | 2.8124 | 2.8008 | 2.7872 | 2.6998 | 2.6219 | 2.4935 | 2.3735 | 2.2535 | 1.6451 | 0.78189 | -0.085474 | 4.7461 | 2.0724 | 2.0608 | 2.0482 | 2.0356 | 1.9672 | 1.9061 | 1.7829 | 1.6661 | 1.5419 | 0.95874 | 0.11874 | -0.78232 | 4.8429 | 2.1724 | 2.1598 | 2.1482 | 2.1345 | 2.0482 | 1.9724 | 1.8335 | 1.7051 | 1.5714 | 0.91663 | -0.023368 | -0.996
| INVERNESS | FOYERS | MINIMUM HEADROOM | NH 49740 21044 | YES | YES | 0 | 1.0611 | 1.0537 | 1.0474 | 1.04 | 1.0316 | 1.0221 | 1.0126 | 1.0021 | 0.99368 | 0.98421 | 0.92526 | 0.83368 | 0.76842 | 1.0537 | 1.0495 | 1.0453 | 1.04 | 1.0305 | 1.0221 | 1.0116 | 1.0021 | 0.99263 | 0.98526 | 0.91895 | 0.81684 | 0.74211 | 1.0442 | 1.0368 | 1.0284 | 1.0211 | 1.0116 | 1.0021 | 0.99158 | 0.98105 | 0.97158 | 0.96316 | 0.89474 | 0.78947 | 0.71474
|  | FOYERS | EE |  |  |  |  | 1.0642 | 1.0589 | 1.0537 | 1.0463 | 1.0411 | 1.0326 | 1.0242 | 1.0147 | 1.0063 | 0.99895 | 0.94 | 0.86211 | 0.78947 | 1.0558 | 1.0526 | 1.0495 | 1.0453 | 1.0421 | 1.0326 | 1.0253 | 1.0168 | 1.0095 | 1.0011 | 0.94105 | 0.85684 | 0.77474 | 1.0484 | 1.0421 | 1.0368 | 1.0284 | 1.0232 | 1.0137 | 1.0042 | 0.99474 | 0.98737 | 0.97789 | 0.91368 | 0.82526 | 0.74
|  | FOYERS | HT |  |  |  |  | 1.0611 | 1.0537 | 1.0474 | 1.04 | 1.0316 | 1.0221 | 1.0126 | 1.0021 | 0.99368 | 0.98421 | 0.92526 | 0.83368 | 0.76842 | 1.0537 | 1.0495 | 1.0453 | 1.04 | 1.0305 | 1.0221 | 1.0116 | 1.0021 | 0.99263 | 0.98526 | 0.91895 | 0.81684 | 0.74211 | 1.0442 | 1.0368 | 1.0284 | 1.0211 | 1.0116 | 1.0021 | 0.99158 | 0.98105 | 0.97158 | 0.96316 | 0.89474 | 0.78947 | 0.71474
|  | FOYERS | HE |  |  |  |  | 1.0684 | 1.0663 | 1.0621 | 1.0589 | 1.0547 | 1.0474 | 1.0411 | 1.0347 | 1.0284 | 1.0158 | 0.96526 | 0.90211 | 0.83053 | 1.0579 | 1.0558 | 1.0537 | 1.0516 | 1.0484 | 1.0442 | 1.04 | 1.0368 | 1.0316 | 1.0189 | 0.96316 | 0.89368 | 0.81579 | 1.0442 | 1.0368 | 1.0284 | 1.0211 | 1.0116 | 1.0021 | 0.99158 | 0.98105 | 0.97158 | 0.96316 | 0.89474 | 0.78947 | 0.71474
|  | FOYERS | CF |  |  |  |  | 1.0716 | 1.0695 | 1.0674 | 1.0653 | 1.0632 | 1.06 | 1.0547 | 1.0537 | 1.0505 | 1.0442 | 1.0147 | 0.97474 | 0.92632 | 1.0589 | 1.0579 | 1.0568 | 1.0558 | 1.0547 | 1.0526 | 1.0505 | 1.0495 | 1.0474 | 1.0453 | 1.0137 | 0.96737 | 0.91263 | 1.0558 | 1.0537 | 1.0516 | 1.0495 | 1.0474 | 1.0432 | 1.0379 | 1.0358 | 1.0337 | 1.0253 | 0.99263 | 0.94421 | 0.88842
| FRASERBURGH | FRASERBURGH | MINIMUM HEADROOM | NH 51502 69028 | NO | YES | 0.699 | 39.5684 | 39.0663 | 38.4663 | 37.7726 | 36.9684 | 35.7042 | 34.6884 | 33.6221 | 32.4663 | 31.6621 | 25.8778 | 21.8273 | 20.0715 | 36.3999 | 35.8305 | 35.1463 | 34.3473 | 33.4084 | 32.0431 | 31.0084 | 29.9294 | 28.7736 | 28.0442 | 22.741 | 19.2884 | 17.5705 | 38.4157 | 37.9221 | 37.3326 | 36.6526 | 35.8073 | 34.4221 | 33.3147 | 32.1642 | 30.9157 | 30.0799 | 24.0357 | 19.7652 | 17.8799
|  | FRASERBURGH | EE |  |  |  |  | 39.6778 | 39.3568 | 38.8694 | 38.2947 | 37.6231 | 36.481 | 35.3957 | 34.3063 | 33.2842 | 32.2094 | 25.8778 | 21.8273 | 20.0715 | 36.5136 | 36.1589 | 35.6115 | 34.9557 | 34.181 | 32.9905 | 31.9084 | 30.8673 | 29.8736 | 28.8178 | 23.0084 | 19.2884 | 17.5705 | 38.5242 | 38.2073 | 37.7273 | 37.1631 | 36.4936 | 35.2884 | 34.1221 | 32.9599 | 31.8642 | 30.7063 | 24.0357 | 19.7652 | 17.8799
|  | FRASERBURGH | HT |  |  |  |  | 39.5684 | 39.0663 | 38.4663 | 37.7726 | 36.9684 | 35.7042 | 34.6884 | 33.6221 | 32.4663 | 31.6621 | 25.9978 | 23.1084 | 21.3484 | 36.3999 | 35.8305 | 35.1463 | 34.3473 | 33.4084 | 32.0431 | 31.0084 | 29.9294 | 28.7736 | 28.0442 | 22.741 | 19.7968 | 17.9305 | 38.4157 | 37.9221 | 37.3326 | 36.6526 | 35.8073 | 34.4221 | 33.3147 | 32.1642 | 30.9157 | 30.0799 | 24.0715 | 20.9347 | 19.0021
|  | FRASERBURGH | HE |  |  |  |  | 39.8084 | 39.6021 | 39.3252 | 38.9189 | 38.3747 | 37.3031 | 36.4326 | 35.5999 | 34.741 | 33.8442 | 30.0747 | 27.0284 | 24.8631 | 36.6442 | 36.4189 | 36.1094 | 35.6421 | 34.9999 | 33.901 | 33.0178 | 32.1831 | 31.3442 | 30.4557 | 27.0631 | 24.1084 | 22.2315 | 38.4157 | 37.9221 | 37.3326 | 36.6526 | 35.8073 | 34.4221 | 33.3147 | 32.1642 | 30.9157 | 30.0799 | 24.0715 | 20.9347 | 19.0021
|  | FRASERBURGH | CF |  |  |  |  | 39.8947 | 39.8063 | 39.701 | 39.5842 | 39.4515 | 39.1263 | 38.7736 | 38.4031 | 38.0357 | 37.6705 | 35.8526 | 33.7968 | 32.6968 | 36.7336 | 36.6431 | 36.5336 | 36.4105 | 36.2684 | 35.9568 | 35.6042 | 35.2252 | 34.8421 | 34.4442 | 32.5652 | 30.5421 | 29.5273 | 38.741 | 38.6526 | 38.5473 | 38.4315 | 38.2999 | 37.9694 | 37.6136 | 37.2399 | 36.8736 | 36.5115 | 34.621 | 32.4273 | 31.261
| LUNANHEAD | FRIOCKHEIM | MINIMUM HEADROOM | NO 58834 49317 | YES | YES | 0 | 5.9674 | 5.8958 | 5.7926 | 5.6389 | 5.4811 | 5.1326 | 4.7589 | 4.3095 | 3.9074 | 3.4989 | -0.82737 | -3.6695 | -5.8958 | 5.8495 | 5.7347 | 5.6105 | 5.4495 | 5.2789 | 4.98 | 4.6842 | 4.3389 | 4.0105 | 3.68 | -1.0021 | -3.8758 | -5.8221 | 5.6632 | 5.5474 | 5.4211 | 5.2537 | 5.0811 | 4.7263 | 4.3611 | 3.9063 | 3.5074 | 3.1042 | -1.7979 | -4.8558 | -7.1421
|  | FRIOCKHEIM | EE |  |  |  |  | 5.9958 | 5.9411 | 5.86 | 5.7526 | 5.6116 | 5.2126 | 4.7589 | 4.3095 | 3.9074 | 3.4989 | 0.65053 | -3.6695 | -5.8958 | 5.9011 | 5.8137 | 5.7084 | 5.5779 | 5.4326 | 5.0926 | 4.7126 | 4.3389 | 4.0105 | 3.68 | 1.0737 | -3.2189 | -5.5674 | 5.7137 | 5.6263 | 5.5147 | 5.38 | 5.2274 | 4.8211 | 4.3611 | 3.9063 | 3.5074 | 3.1042 | 0.095789 | -4.6421 | -7.1421
|  | FRIOCKHEIM | HT |  |  |  |  | 5.9674 | 5.8958 | 5.7926 | 5.6389 | 5.4811 | 5.1326 | 4.7884 | 4.4442 | 4.0484 | 3.6495 | -0.82737 | -3.5558 | -5.3379 | 5.8495 | 5.7347 | 5.6105 | 5.4495 | 5.2789 | 4.98 | 4.6842 | 4.3874 | 4.0526 | 3.7158 | -1.0021 | -3.8758 | -5.8221 | 5.6632 | 5.5474 | 5.4211 | 5.2537 | 5.0811 | 4.7263 | 4.3758 | 4.0253 | 3.6232 | 3.2189 | -1.7979 | -4.8558 | -6.8832
|  | FRIOCKHEIM | HE |  |  |  |  | 6.0389 | 6.0032 | 5.9611 | 5.9105 | 5.84 | 5.4463 | 5.1158 | 4.7916 | 4.4053 | 3.9074 | 1.7558 | -1.6821 | -4.3432 | 5.9726 | 5.92 | 5.8611 | 5.7716 | 5.66 | 5.3347 | 5.0589 | 4.7926 | 4.4579 | 3.9811 | 1.9779 | -1.56 | -4.1674 | 5.6632 | 5.5474 | 5.4211 | 5.2537 | 5.0811 | 4.7263 | 4.3758 | 4.0253 | 3.6232 | 3.2189 | -1.7979 | -4.8558 | -6.8832
|  | FRIOCKHEIM | CF |  |  |  |  | 6.0611 | 6.04 | 6.0158 | 5.9895 | 5.9621 | 5.8168 | 5.6863 | 5.5589 | 5.4063 | 5.1853 | 4.1116 | 2.5642 | 0.96947 | 6.0084 | 5.9758 | 5.9389 | 5.9 | 5.8547 | 5.7189 | 5.5926 | 5.4684 | 5.3158 | 5.0863 | 4.0421 | 2.5179 | 0.86105 | 5.8221 | 5.7884 | 5.7526 | 5.7116 | 5.6653 | 5.5021 | 5.3526 | 5.2053 | 5.0326 | 4.7863 | 3.6274 | 1.94 | 0.15895
| KINTORE | FYVIE | MINIMUM HEADROOM | NJ 76759 37635 | NO | YES | 1.5 | -6.2653 | -6.3726 | -6.5211 | -6.68 | -6.8442 | -7.5305 | -8.3547 | -10.7105 | -11.4432 | -14.3147 | -24.5832 | -33.3589 | -37.8716 | 0.20947 | 0.096842 | -0.052632 | -0.21368 | -0.38105 | -0.96842 | -1.64 | -3.6011 | -4.2211 | -6.7263 | -16.2337 | -24.8726 | -29.7505 | -2.6021 | -2.66 | -2.7474 | -2.9095 | -3.0779 | -3.74 | -4.5158 | -6.7821 | -7.5411 | -10.5274 | -21.4653 | -31.0611 | -36.1516
|  | FYVIE | EE |  |  |  |  | -6.2168 | -6.2989 | -6.4358 | -6.58 | -6.7337 | -7.4705 | -8.3547 | -10.7105 | -11.4432 | -14.3147 | -21.8242 | -31.5674 | -37.1316 | 0.25789 | 0.17474 | 0.045263 | -0.094737 | -0.24526 | -0.88 | -1.64 | -3.6011 | -4.2211 | -6.6032 | -13.6484 | -22.6958 | -28.4484 | -2.5789 | -2.6242 | -2.7126 | -2.8032 | -2.9579 | -3.6653 | -4.5158 | -6.7821 | -7.5411 | -10.5274 | -18.5179 | -28.9347 | -35.1442
|  | FYVIE | HT |  |  |  |  | -6.2653 | -6.3726 | -6.5211 | -6.68 | -6.8442 | -7.5305 | -8.0905 | -10.2137 | -10.9358 | -14.2526 | -24.5832 | -33.3589 | -37.8716 | 0.20947 | 0.096842 | -0.052632 | -0.21368 | -0.38105 | -0.96842 | -1.4558 | -3.2305 | -3.8463 | -6.7263 | -16.2337 | -24.8726 | -29.7505 | -2.6021 | -2.66 | -2.7474 | -2.9095 | -3.0779 | -3.74 | -4.2789 | -6.3042 | -7.0158 | -10.4674 | -21.4653 | -31.0611 | -36.1516
|  | FYVIE | HE |  |  |  |  | -6.1516 | -6.2032 | -6.2726 | -6.3558 | -6.4453 | -7.2053 | -8.0011 | -9.5905 | -10.3916 | -12.5842 | -19.4347 | -26.2979 | -32.6484 | 0.32211 | 0.27158 | 0.20526 | 0.12 | 0.028421 | -0.61789 | -1.3337 | -2.7158 | -3.44 | -5.4 | -11.6411 | -18.2211 | -24.4674 | -2.6021 | -2.66 | -2.7474 | -2.9095 | -3.0779 | -3.74 | -4.2789 | -6.3042 | -7.0158 | -10.4674 | -21.4653 | -31.0611 | -36.1516
|  | FYVIE | CF |  |  |  |  | -6.1189 | -6.1484 | -6.1884 | -6.2284 | -6.2705 | -6.5579 | -6.8242 | -7.2042 | -7.6853 | -8.2116 | -14.9505 | -18.6211 | -22.5926 | 0.35474 | 0.32526 | 0.28842 | 0.25053 | 0.21053 | -0.033684 | -0.26316 | -0.62105 | -1.0947 | -1.6337 | -7.5653 | -11.1884 | -15.2832 | -2.5284 | -2.5442 | -2.5674 | -2.5905 | -2.6126 | -2.8453 | -3.0495 | -3.4011 | -3.8926 | -4.4421 | -11.3379 | -15.3579 | -19.7884
| GRUDIE BRIDGE | GARBAT FOREST | MINIMUM HEADROOM | NH 41255 67993 | YES | NO | 0 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.095789 | 0.090526 | 0.086316 | 0.082105 | 0.077895 | 0.046316 | 0.011579 | -0.0094737 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.095789 | 0.091579 | 0.088421 | 0.086316 | 0.081053 | 0.051579 | 0.02 | -0.0010526 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.095789 | 0.090526 | 0.086316 | 0.082105 | 0.076842 | 0.043158 | 0.0063158 | -0.016842
|  | GARBAT FOREST | EE |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.095789 | 0.090526 | 0.086316 | 0.082105 | 0.077895 | 0.046316 | 0.011579 | -0.0094737 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.096842 | 0.092632 | 0.089474 | 0.086316 | 0.081053 | 0.051579 | 0.02 | -0.0010526 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.095789 | 0.090526 | 0.086316 | 0.082105 | 0.076842 | 0.043158 | 0.0063158 | -0.016842
|  | GARBAT FOREST | HT |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.095789 | 0.093684 | 0.089474 | 0.086316 | 0.08 | 0.054737 | 0.029474 | 0.012632 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.096842 | 0.094737 | 0.091579 | 0.087368 | 0.082105 | 0.056842 | 0.031579 | 0.013684 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.095789 | 0.093684 | 0.089474 | 0.085263 | 0.078947 | 0.050526 | 0.023158 | 0.0031579
|  | GARBAT FOREST | HE |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.095789 | 0.091579 | 0.087368 | 0.084211 | 0.078947 | 0.056842 | 0.031579 | 0.0052632 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.095789 | 0.091579 | 0.088421 | 0.086316 | 0.081053 | 0.061053 | 0.035789 | 0.011579 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.095789 | 0.093684 | 0.089474 | 0.085263 | 0.078947 | 0.050526 | 0.023158 | 0.0031579
|  | GARBAT FOREST | CF |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.097895 | 0.096842 | 0.095789 | 0.092632 | 0.091579 | 0.081053 | 0.065263 | 0.049474 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.095789 | 0.092632 | 0.092632 | 0.081053 | 0.066316 | 0.049474 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.097895 | 0.096842 | 0.094737 | 0.091579 | 0.091579 | 0.078947 | 0.062105 | 0.044211
| STORNOWAY | GISLA | MINIMUM HEADROOM | NB 12846 25823 | YES | YES | 0 | 0.95579 | 0.93368 | 0.91158 | 0.89053 | 2.3684 | 2.3463 | 2.3242 | 2.3053 | 2.2853 | 2.2663 | 2.1926 | 2.1326 | 2.0821 | 1.0189 | 0.99474 | 0.97053 | 0.94737 | 2.4232 | 2.3989 | 2.3758 | 2.3537 | 2.3326 | 2.3116 | 2.2295 | 2.1611 | 2.1021 | 1.0916 | 1.0674 | 1.0421 | 1.0189 | 2.4947 | 2.4705 | 2.4463 | 2.4253 | 2.4042 | 2.3821 | 2.3011 | 2.2326 | 2.1726
|  | GISLA | EE |  |  |  |  | 0.96526 | 0.94737 | 0.93053 | 0.91263 | 2.3947 | 2.3768 | 2.3611 | 2.3432 | 2.3295 | 2.3147 | 2.2516 | 2.2063 | 2.1695 | 1.0295 | 1.0105 | 0.99158 | 0.97263 | 2.4526 | 2.4337 | 2.4158 | 2.3979 | 2.3821 | 2.3663 | 2.2958 | 2.2442 | 2.2021 | 1.0989 | 1.0821 | 1.0642 | 1.0442 | 2.5242 | 2.5053 | 2.4874 | 2.4684 | 2.4526 | 2.4368 | 2.3674 | 2.3147 | 2.2737
|  | GISLA | HT |  |  |  |  | 0.95579 | 0.93368 | 0.91158 | 0.89053 | 2.3684 | 2.3463 | 2.3242 | 2.3053 | 2.2853 | 2.2663 | 2.1926 | 2.1326 | 2.0821 | 1.0189 | 0.99474 | 0.97053 | 0.94737 | 2.4232 | 2.3989 | 2.3758 | 2.3537 | 2.3326 | 2.3116 | 2.2295 | 2.1611 | 2.1021 | 1.0916 | 1.0674 | 1.0421 | 1.0189 | 2.4947 | 2.4705 | 2.4463 | 2.4253 | 2.4042 | 2.3821 | 2.3011 | 2.2326 | 2.1726
|  | GISLA | HE |  |  |  |  | 0.98 | 0.96842 | 0.95684 | 0.94526 | 2.4337 | 2.4211 | 2.4105 | 2.3989 | 2.3884 | 2.3779 | 2.3421 | 2.32 | 2.3032 | 1.0463 | 1.0337 | 1.0211 | 1.0084 | 2.4958 | 2.4832 | 2.4705 | 2.4589 | 2.4484 | 2.4368 | 2.3979 | 2.3726 | 2.3526 | 1.0916 | 1.0674 | 1.0421 | 1.0189 | 2.4947 | 2.4705 | 2.4463 | 2.4253 | 2.4042 | 2.3821 | 2.3011 | 2.2326 | 2.1726
|  | GISLA | CF |  |  |  |  | 0.98632 | 0.98 | 0.97263 | 0.96526 | 2.4589 | 2.4516 | 2.4453 | 2.4379 | 2.4305 | 2.4242 | 2.3937 | 2.3716 | 2.3579 | 1.0526 | 1.0463 | 1.0379 | 1.0305 | 2.5232 | 2.5147 | 2.5084 | 2.5 | 2.4926 | 2.4842 | 2.4516 | 2.4274 | 2.4105 | 1.1126 | 1.1095 | 1.1042 | 1.0989 | 2.5937 | 2.5874 | 2.58 | 2.5726 | 2.5642 | 2.5568 | 2.5232 | 2.4979 | 2.4811
| ALNESS | GLASTULLICH | MINIMUM HEADROOM | NH 78509 76508 | YES | YES | 0 | 1.45 | 1.3795 | 1.3058 | 1.2374 | 1.1668 | 1.0847 | 1.0026 | 0.92368 | 0.85105 | 0.78053 | 0.46053 | -0.47421 | -0.66368 | 1.4405 | 1.3647 | 1.2858 | 1.2121 | 1.1384 | 1.0511 | 0.96684 | 0.88474 | 0.81105 | 0.73842 | 0.40158 | -0.39526 | -0.60368 | 1.4353 | 1.3584 | 1.2805 | 1.2068 | 1.1311 | 1.0437 | 0.95632 | 0.87316 | 0.79632 | 0.72158 | 0.37421 | -0.58368 | -0.79421
|  | GLASTULLICH | EE |  |  |  |  | 1.4805 | 1.4258 | 1.3689 | 1.3121 | 1.2542 | 1.1889 | 1.1237 | 1.0542 | 0.99105 | 0.92789 | 0.65 | -0.20158 | -0.34579 | 1.4753 | 1.4153 | 1.3553 | 1.2942 | 1.2332 | 1.1658 | 1.1016 | 1.0311 | 0.96579 | 0.90158 | 0.62263 | -0.095263 | -0.25421 | 1.4689 | 1.4089 | 1.3489 | 1.2879 | 1.2268 | 1.1574 | 1.0889 | 1.0153 | 0.94789 | 0.88158 | 0.58684 | -0.28263 | -0.44474
|  | GLASTULLICH | HT |  |  |  |  | 1.45 | 1.3795 | 1.3058 | 1.2374 | 1.1668 | 1.0847 | 1.0026 | 0.92368 | 0.85105 | 0.78053 | 0.46053 | -0.47421 | -0.66368 | 1.4405 | 1.3647 | 1.2858 | 1.2121 | 1.1384 | 1.0511 | 0.96684 | 0.88474 | 0.81105 | 0.73842 | 0.40158 | -0.39526 | -0.60368 | 1.4353 | 1.3584 | 1.2805 | 1.2068 | 1.1311 | 1.0437 | 0.95632 | 0.87316 | 0.79632 | 0.72158 | 0.37421 | -0.58368 | -0.79421
|  | GLASTULLICH | HE |  |  |  |  | 1.5258 | 1.4911 | 1.4563 | 1.4195 | 1.3795 | 1.3321 | 1.2858 | 1.2426 | 1.1995 | 1.1605 | 1.0047 | 0.62368 | 0.56474 | 1.5226 | 1.4868 | 1.4489 | 1.41 | 1.3689 | 1.3216 | 1.2763 | 1.2332 | 1.1911 | 1.1521 | 0.99947 | 0.67842 | 0.61526 | 1.4353 | 1.3584 | 1.2805 | 1.2068 | 1.1311 | 1.0437 | 0.95632 | 0.87316 | 0.79632 | 0.72158 | 0.37421 | -0.58368 | -0.79421
|  | GLASTULLICH | CF |  |  |  |  | 1.5468 | 1.5258 | 1.5058 | 1.4837 | 1.4616 | 1.4353 | 1.4079 | 1.3826 | 1.3584 | 1.3332 | 1.2195 | 1.13 | 1.0647 | 1.5447 | 1.5237 | 1.5016 | 1.4784 | 1.4553 | 1.4279 | 1.4005 | 1.3742 | 1.3489 | 1.3226 | 1.2047 | 1.1142 | 1.0489 | 1.5247 | 1.5089 | 1.4932 | 1.4721 | 1.4489 | 1.4205 | 1.3921 | 1.3658 | 1.3395 | 1.3132 | 1.1911 | 1.0953 | 1.0237
| SHIN | GLEDFIELD | MINIMUM HEADROOM | NH 58876 90837 | YES | NO | 0 | 2.7674 | 2.72 | 2.6684 | 2.6158 | 2.5642 | 2.3105 | 2.0947 | 1.8874 | 1.7084 | 1.5253 | -0.35474 | -2.6147 | -4.4958 | 2.5074 | 2.4568 | 2.4021 | 2.3453 | 2.2926 | 2.0358 | 1.8421 | 1.7 | 1.5537 | 1.3316 | -0.54737 | -3.0653 | -4.8716 | 2.5947 | 2.5442 | 2.4905 | 2.4347 | 2.3811 | 2.1179 | 1.9116 | 1.72 | 1.5516 | 1.3695 | -0.68316 | -3.2158 | -5.3284
|  | GLEDFIELD | EE |  |  |  |  | 2.7874 | 2.7526 | 2.7021 | 2.6537 | 2.6063 | 2.3421 | 2.0947 | 1.8874 | 1.7084 | 1.5253 | -0.35474 | -2.6147 | -4.4958 | 2.5305 | 2.4916 | 2.4421 | 2.3947 | 2.3463 | 2.0884 | 1.8663 | 1.7 | 1.5537 | 1.4063 | -0.47789 | -2.7789 | -4.8526 | 2.6168 | 2.5789 | 2.5274 | 2.4779 | 2.4284 | 2.1568 | 1.9126 | 1.72 | 1.5516 | 1.3695 | -0.68316 | -3.1705 | -5.3284
|  | GLEDFIELD | HT |  |  |  |  | 2.7674 | 2.72 | 2.6684 | 2.6158 | 2.5642 | 2.3105 | 2.1021 | 1.9421 | 1.9011 | 1.6926 | -0.22526 | -2.5032 | -4.0916 | 2.5074 | 2.4568 | 2.4021 | 2.3453 | 2.2926 | 2.0358 | 1.8421 | 1.7042 | 1.6611 | 1.4747 | -0.54737 | -3.0653 | -4.8716 | 2.5947 | 2.5442 | 2.4905 | 2.4347 | 2.3811 | 2.1179 | 1.9116 | 1.7558 | 1.7137 | 1.5095 | -0.60737 | -3.2158 | -5.0537
|  | GLEDFIELD | HE |  |  |  |  | 2.8158 | 2.7937 | 2.7695 | 2.7442 | 2.7179 | 2.4516 | 2.2589 | 2.0863 | 1.8737 | 1.54 | 0.14947 | -1.6505 | -3.6063 | 2.5621 | 2.54 | 2.5147 | 2.4853 | 2.4589 | 2.2032 | 2.0263 | 1.8768 | 1.6768 | 1.3316 | -0.070526 | -1.9568 | -4.0137 | 2.5947 | 2.5442 | 2.4905 | 2.4347 | 2.3811 | 2.1179 | 1.9116 | 1.7558 | 1.7137 | 1.5095 | -0.60737 | -3.2158 | -5.0537
|  | GLEDFIELD | CF |  |  |  |  | 2.8305 | 2.8179 | 2.8032 | 2.7874 | 2.7737 | 2.6674 | 2.5853 | 2.5232 | 2.3874 | 2.2158 | 1.4674 | 0.32526 | -0.98632 | 2.5789 | 2.5653 | 2.5495 | 2.5337 | 2.5189 | 2.4147 | 2.3389 | 2.2863 | 2.1368 | 1.9442 | 1.1589 | -0.045263 | -1.4832 | 2.6632 | 2.6505 | 2.6337 | 2.6179 | 2.6021 | 2.4937 | 2.4126 | 2.3537 | 2.2053 | 2.0189 | 1.2305 | -0.046316 | -1.5463
| FORT AUGUSTUS | GLEN LAOGH | MINIMUM HEADROOM | NH 27430 00910 | YES | YES | 0 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.088421 | 0.076842 | 0.067368 | 0.055789 | 0.037895 | -0.064211 | -0.20526 | -0.30421 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.089474 | 0.078947 | 0.068421 | 0.057895 | 0.037895 | -0.071579 | -0.23158 | -0.34526 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.093684 | 0.085263 | 0.077895 | 0.068421 | 0.042105 | -0.083158 | -0.24632 | -0.36211
|  | GLEN LAOGH | EE |  |  |  |  | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.092632 | 0.085263 | 0.077895 | 0.071579 | 0.055789 | -0.056842 | -0.18526 | -0.30421 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.094737 | 0.088421 | 0.083158 | 0.077895 | 0.061053 | -0.056842 | -0.19158 | -0.32526 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.098947 | 0.093684 | 0.085263 | 0.077895 | 0.071579 | 0.053684 | -0.072632 | -0.21684 | -0.35368
|  | GLEN LAOGH | HT |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.093684 | 0.089474 | 0.078947 | 0.069474 | 0.047368 | -0.064211 | -0.20526 | -0.30421 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.095789 | 0.092632 | 0.082105 | 0.072632 | 0.048421 | -0.071579 | -0.23158 | -0.34526 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.094737 | 0.089474 | 0.077895 | 0.068421 | 0.042105 | -0.083158 | -0.24632 | -0.36211
|  | GLEN LAOGH | HE |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.088421 | 0.076842 | 0.067368 | 0.055789 | 0.037895 | -0.04 | -0.14632 | -0.26421 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.089474 | 0.078947 | 0.068421 | 0.057895 | 0.037895 | -0.043158 | -0.15789 | -0.28526 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.094737 | 0.089474 | 0.077895 | 0.068421 | 0.042105 | -0.083158 | -0.24632 | -0.36211
|  | GLEN LAOGH | CF |  |  |  |  | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.097895 | 0.095789 | 0.086316 | 0.077895 | 0.068421 | 0.025263 | -0.043158 | -0.12421 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.087368 | 0.077895 | 0.066316 | 0.02 | -0.053684 | -0.14632 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.097895 | 0.096842 | 0.085263 | 0.075789 | 0.064211 | 0.015789 | -0.062105 | -0.15579
| KINLOCHLEVEN | GLENCOE | MINIMUM HEADROOM | NN 10658 58797 | YES | YES | 0 | 3.2489 | 3.2205 | 3.1921 | 3.1616 | 3.1311 | 3.0953 | 3.0616 | 3.0289 | 2.9963 | 2.9637 | 2.8332 | 2.7226 | 2.5721 | 3.2468 | 3.2184 | 3.1784 | 3.1258 | 3.0753 | 3.0163 | 2.9595 | 2.9047 | 2.8553 | 2.8089 | 2.5953 | 2.4153 | 2.2584 | 3.4984 | 3.4689 | 3.4395 | 3.3847 | 3.3332 | 3.2711 | 3.2089 | 3.1511 | 3.0984 | 3.0479 | 2.8153 | 2.6205 | 2.4521
|  | GLENCOE | EE |  |  |  |  | 3.2595 | 3.2311 | 3.2026 | 3.17 | 3.1384 | 3.1026 | 3.0668 | 3.0342 | 3.0005 | 2.9689 | 2.8332 | 2.7353 | 2.5889 | 3.2584 | 3.2332 | 3.2068 | 3.1626 | 3.1163 | 3.0689 | 3.0184 | 2.9679 | 2.9174 | 2.8753 | 2.6658 | 2.49 | 2.3437 | 3.5089 | 3.4774 | 3.4458 | 3.4079 | 3.3626 | 3.3079 | 3.2521 | 3.1942 | 3.1363 | 3.0889 | 2.8479 | 2.6416 | 2.4721
|  | GLENCOE | HT |  |  |  |  | 3.2489 | 3.2205 | 3.1921 | 3.1616 | 3.1311 | 3.0953 | 3.0616 | 3.0289 | 2.9963 | 2.9637 | 2.8542 | 2.7226 | 2.5721 | 3.2468 | 3.2184 | 3.1784 | 3.1258 | 3.0753 | 3.0163 | 2.9595 | 2.9047 | 2.8553 | 2.8089 | 2.5953 | 2.4153 | 2.2584 | 3.4984 | 3.4689 | 3.4395 | 3.3847 | 3.3332 | 3.2711 | 3.2089 | 3.1511 | 3.0984 | 3.0479 | 2.8153 | 2.6205 | 2.4521
|  | GLENCOE | HE |  |  |  |  | 3.2742 | 3.2584 | 3.2416 | 3.2226 | 3.2037 | 3.1784 | 3.1563 | 3.1342 | 3.1132 | 3.0932 | 3.0174 | 2.9679 | 2.9268 | 3.2742 | 3.2584 | 3.2426 | 3.2247 | 3.2068 | 3.1847 | 3.1658 | 3.1363 | 3.1089 | 3.0847 | 2.9826 | 2.9079 | 2.8458 | 3.4984 | 3.4689 | 3.4395 | 3.3847 | 3.3332 | 3.2711 | 3.2089 | 3.1511 | 3.0984 | 3.0479 | 2.8153 | 2.6205 | 2.4521
|  | GLENCOE | CF |  |  |  |  | 3.2816 | 3.2742 | 3.2658 | 3.2563 | 3.2479 | 3.2363 | 3.2268 | 3.2153 | 3.2068 | 3.1963 | 3.1511 | 3.1226 | 3.1047 | 3.2826 | 3.2742 | 3.2658 | 3.2563 | 3.2479 | 3.2384 | 3.2289 | 3.2184 | 3.21 | 3.1995 | 3.1395 | 3.0858 | 3.0447 | 3.5311 | 3.5226 | 3.5142 | 3.5058 | 3.4963 | 3.4858 | 3.4753 | 3.4647 | 3.4553 | 3.4447 | 3.3963 | 3.3353 | 3.2889
| DUNOON | GLENDARUEL | MINIMUM HEADROOM | NN 03067 59147 | YES | YES | 0 | 0.042368 | 0.024474 | 0.0023684 | -0.018684 | -0.041842 | -0.082895 | -0.12395 | -0.16921 | -0.20921 | -0.24816 | -0.45026 | -0.64395 | -0.75342 | 0.026579 | 0.0097368 | -0.011316 | -0.034474 | -0.057632 | -0.094474 | -0.13132 | -0.17026 | -0.20711 | -0.24289 | -0.42605 | -0.60184 | -0.70816 | 0.017105 | -0.00078947 | -0.022895 | -0.047105 | -0.070263 | -0.11237 | -0.15553 | -0.20395 | -0.24605 | -0.28816 | -0.50184 | -0.70605 | -0.82289
|  | GLENDARUEL | EE |  |  |  |  | 0.044474 | 0.024474 | 0.0023684 | -0.018684 | -0.041842 | -0.082895 | -0.12395 | -0.16921 | -0.20921 | -0.24816 | -0.45026 | -0.64395 | -0.75342 | 0.028684 | 0.0097368 | -0.011316 | -0.034474 | -0.057632 | -0.094474 | -0.13132 | -0.17026 | -0.20711 | -0.24289 | -0.42605 | -0.60184 | -0.70816 | 0.020263 | -0.00078947 | -0.022895 | -0.047105 | -0.070263 | -0.11237 | -0.15553 | -0.20395 | -0.24605 | -0.28816 | -0.50184 | -0.70605 | -0.82289
|  | GLENDARUEL | HT |  |  |  |  | 0.042368 | 0.033947 | 0.022368 | 0.013947 | 0.0044737 | -0.020789 | -0.046053 | -0.071316 | -0.098684 | -0.12711 | -0.24289 | -0.34289 | -0.41447 | 0.026579 | 0.016053 | 0.0044737 | -0.005 | -0.016579 | -0.039737 | -0.063947 | -0.087105 | -0.11237 | -0.13868 | -0.24921 | -0.33026 | -0.38921 | 0.017105 | 0.0076316 | -0.005 | -0.015526 | -0.027105 | -0.054474 | -0.081842 | -0.11026 | -0.13868 | -0.17026 | -0.30079 | -0.41132 | -0.49237
|  | GLENDARUEL | HE |  |  |  |  | 0.046579 | 0.040263 | 0.031842 | 0.024474 | 0.016053 | -0.010263 | -0.036579 | -0.059737 | -0.083947 | -0.10921 | -0.22079 | -0.32184 | -0.42921 | 0.031842 | 0.024474 | 0.016053 | 0.0086842 | 0.0013158 | -0.021842 | -0.043947 | -0.065 | -0.085 | -0.10605 | -0.20289 | -0.29553 | -0.39132 | 0.017105 | 0.0076316 | -0.005 | -0.015526 | -0.027105 | -0.054474 | -0.081842 | -0.11026 | -0.13868 | -0.17026 | -0.30079 | -0.41132 | -0.49237
|  | GLENDARUEL | CF |  |  |  |  | 0.36132 | 0.35921 | 0.35816 | 0.35605 | 0.35395 | 0.34447 | 0.33605 | 0.32868 | 0.32132 | 0.31605 | 0.275 | 0.21289 | 0.16658 | 0.33921 | 0.33816 | 0.33605 | 0.335 | 0.33395 | 0.32868 | 0.32342 | 0.31921 | 0.315 | 0.30974 | 0.26553 | 0.21079 | 0.17079 | 0.35079 | 0.34868 | 0.34658 | 0.34447 | 0.34237 | 0.33395 | 0.32447 | 0.31711 | 0.30974 | 0.30447 | 0.25184 | 0.18553 | 0.13816
| ABERNETHY | GLENDEVON | MINIMUM HEADROOM | NO 00101 02760 | YES | YES | 0.14 | 2.7653 | 2.7137 | 2.6474 | 2.5811 | 2.5126 | 2.1789 | 1.7137 | 1.2874 | 0.92316 | 0.54632 | -2.2853 | -5.6895 | -7.9695 | 2.9211 | 2.8674 | 2.8011 | 2.7368 | 2.6684 | 2.3916 | 2.0032 | 1.6474 | 1.3442 | 1.0295 | -1.5853 | -4.8263 | -7.2168 | 2.7326 | 2.7021 | 2.6558 | 2.6095 | 2.5621 | 2.2442 | 1.8053 | 1.3547 | 0.96947 | 0.57263 | -2.4547 | -6.1221 | -8.6758
|  | GLENDEVON | EE |  |  |  |  | 2.7779 | 2.7442 | 2.6789 | 2.6137 | 2.5463 | 2.1789 | 1.7137 | 1.2874 | 0.92316 | 0.54632 | -2.2853 | -5.6895 | -7.9695 | 2.9347 | 2.9011 | 2.8421 | 2.7811 | 2.7189 | 2.4095 | 2.0032 | 1.6474 | 1.3442 | 1.0295 | -1.5853 | -4.8263 | -7.2168 | 2.7453 | 2.7168 | 2.6674 | 2.6168 | 2.5663 | 2.2442 | 1.8053 | 1.3547 | 0.96947 | 0.57263 | -2.4547 | -6.1221 | -8.6758
|  | GLENDEVON | HT |  |  |  |  | 2.7653 | 2.7137 | 2.6474 | 2.5811 | 2.5126 | 2.1926 | 1.8895 | 1.5853 | 1.2021 | 0.76842 | -1.7442 | -4.4968 | -6.2968 | 2.9211 | 2.8674 | 2.8011 | 2.7368 | 2.6684 | 2.3916 | 2.1316 | 1.8716 | 1.5389 | 1.1495 | -1.3126 | -4.2063 | -6.1589 | 2.7326 | 2.7021 | 2.6558 | 2.6095 | 2.5621 | 2.2884 | 1.9989 | 1.6768 | 1.2716 | 0.80947 | -1.8874 | -4.9916 | -7.0632
|  | GLENDEVON | HE |  |  |  |  | 2.7937 | 2.7789 | 2.7589 | 2.7326 | 2.7011 | 2.3095 | 1.9779 | 1.6768 | 1.3789 | 0.90526 | -1.2421 | -3.7474 | -6.4663 | 2.9505 | 2.9368 | 2.9168 | 2.8926 | 2.8611 | 2.5263 | 2.2421 | 1.9905 | 1.7432 | 1.2926 | -0.73263 | -3.2 | -5.8842 | 2.7326 | 2.7021 | 2.6558 | 2.6095 | 2.5621 | 2.2884 | 1.9989 | 1.6768 | 1.2716 | 0.80947 | -1.8874 | -4.9916 | -7.0632
|  | GLENDEVON | CF |  |  |  |  | 2.8032 | 2.7937 | 2.7832 | 2.7705 | 2.7579 | 2.6232 | 2.5021 | 2.3779 | 2.2716 | 2.1232 | 1.0674 | -0.49789 | -2.1274 | 2.96 | 2.9516 | 2.9411 | 2.9295 | 2.9179 | 2.8053 | 2.7021 | 2.5979 | 2.5063 | 2.3589 | 1.3242 | -0.22947 | -1.9221 | 2.7705 | 2.7611 | 2.7505 | 2.7389 | 2.7263 | 2.6021 | 2.4937 | 2.3853 | 2.2937 | 2.2242 | 1.1032 | -0.59053 | -2.4305
| FORT AUGUSTUS | GLENDOE | MINIMUM HEADROOM | NH 40060 08894 | YES | YES | 0 | 7.7074 | 7.6895 | 7.6642 | 7.6389 | 7.6116 | 7.3274 | 7.2842 | 7.2389 | 7.1989 | 7.16 | 6.96 | 6.6284 | 6.2347 | 7.5895 | 7.58 | 7.5674 | 7.5547 | 7.5326 | 7.2021 | 7.1695 | 7.1326 | 7.1021 | 7.0705 | 6.9147 | 6.5337 | 6.1537 | 7.7074 | 7.6863 | 7.6568 | 7.6232 | 7.5853 | 7.2137 | 7.1695 | 7.1221 | 7.0789 | 7.0358 | 6.8232 | 6.44 | 5.9632
|  | GLENDOE | EE |  |  |  |  | 7.7116 | 7.6895 | 7.6642 | 7.6389 | 7.6116 | 7.3274 | 7.2842 | 7.2389 | 7.1989 | 7.16 | 6.96 | 6.6284 | 6.2347 | 7.5926 | 7.5811 | 7.5695 | 7.5547 | 7.5326 | 7.2021 | 7.1695 | 7.1326 | 7.1021 | 7.0705 | 6.9147 | 6.5884 | 6.1537 | 7.7137 | 7.6863 | 7.6568 | 7.6232 | 7.5853 | 7.2137 | 7.1695 | 7.1221 | 7.0789 | 7.0358 | 6.8232 | 6.44 | 5.9632
|  | GLENDOE | HT |  |  |  |  | 7.7074 | 7.6937 | 7.6758 | 7.6611 | 7.6347 | 7.36 | 7.3295 | 7.2979 | 7.2632 | 7.2316 | 7.0989 | 6.7095 | 6.3789 | 7.5895 | 7.58 | 7.5674 | 7.5558 | 7.5411 | 7.2095 | 7.1832 | 7.1547 | 7.1253 | 7.0979 | 6.9832 | 6.5337 | 6.16 | 7.7074 | 7.6874 | 7.66 | 7.6284 | 7.5968 | 7.2537 | 7.22 | 7.1874 | 7.1516 | 7.1179 | 6.9768 | 6.4979 | 6.1095
|  | GLENDOE | HE |  |  |  |  | 7.7168 | 7.7074 | 7.6968 | 7.6853 | 7.6747 | 7.4074 | 7.3811 | 7.3547 | 7.3295 | 7.3053 | 7.1947 | 6.9347 | 6.5926 | 7.5979 | 7.5926 | 7.5842 | 7.5779 | 7.5695 | 7.2642 | 7.2421 | 7.2211 | 7.2 | 7.18 | 7.0937 | 6.8147 | 6.4326 | 7.7074 | 7.6874 | 7.66 | 7.6284 | 7.5968 | 7.2537 | 7.22 | 7.1874 | 7.1516 | 7.1179 | 6.9768 | 6.4979 | 6.1095
|  | GLENDOE | CF |  |  |  |  | 7.72 | 7.7158 | 7.7116 | 7.7063 | 7.7011 | 7.6116 | 7.6 | 7.5884 | 7.5789 | 7.5705 | 7.4968 | 7.3021 | 7.0737 | 7.6011 | 7.5979 | 7.5937 | 7.5895 | 7.5874 | 7.4989 | 7.4874 | 7.4789 | 7.4684 | 7.4611 | 7.3884 | 7.1684 | 6.8989 | 7.7295 | 7.7232 | 7.7168 | 7.7084 | 7.7021 | 7.56 | 7.5474 | 7.5358 | 7.5263 | 7.5147 | 7.4347 | 7.1989 | 6.9158
| BRACO | GLENEAGLES | MINIMUM HEADROOM | NN 91540 11582 | NO | YES | 2.49 | 16.0495 | 15.9084 | 15.7379 | 15.5568 | 15.2274 | 14.3916 | 13.6179 | 12.8253 | 11.88 | 10.7863 | 7.0168 | 2.1842 | -1.9768 | 14.1953 | 13.8142 | 13.3584 | 12.9321 | 12.4184 | 11.6047 | 10.8553 | 10.0858 | 9.1626 | 8.0563 | 4.9784 | 0.30684 | -4.0911 | 14.6882 | 14.5355 | 14.1155 | 13.7197 | 13.2482 | 12.3545 | 11.5134 | 10.6503 | 9.6134 | 8.3955 | 4.4018 | -0.79289 | -5.4908
|  | GLENEAGLES | EE |  |  |  |  | 16.1063 | 16 | 15.8611 | 15.6684 | 15.52 | 14.6811 | 13.6884 | 12.8284 | 12.0305 | 11.0726 | 7.0168 | 2.1842 | -1.9768 | 14.3195 | 14.0047 | 13.6121 | 13.2174 | 12.8089 | 12.01 | 11.0668 | 10.2942 | 9.5605 | 8.6279 | 4.9784 | 0.45947 | -4.0911 | 14.745 | 14.6387 | 14.3482 | 13.9334 | 13.5555 | 12.6629 | 11.5945 | 10.6745 | 9.8145 | 8.7576 | 4.4018 | -0.79289 | -5.4908
|  | GLENEAGLES | HT |  |  |  |  | 16.0495 | 15.9084 | 15.7379 | 15.5568 | 15.2274 | 14.3916 | 13.6179 | 12.8253 | 11.88 | 10.7863 | 8.0158 | 3.2895 | -0.21474 | 14.1953 | 13.8142 | 13.3584 | 12.9321 | 12.4184 | 11.6047 | 10.8553 | 10.0858 | 9.1626 | 8.0563 | 5.6226 | 0.30684 | -3.5826 | 14.6882 | 14.5355 | 14.1155 | 13.7197 | 13.2482 | 12.3545 | 11.5134 | 10.6503 | 9.6134 | 8.3955 | 5.5418 | 0.027105 | -3.9697
|  | GLENEAGLES | HE |  |  |  |  | 16.18 | 16.1095 | 16.0274 | 15.9379 | 15.8432 | 15.2063 | 14.3811 | 13.6547 | 12.8779 | 12.0326 | 9.4126 | 5.0821 | 0.43368 | 14.4121 | 14.2479 | 13.95 | 13.6795 | 13.3374 | 12.5332 | 11.7195 | 11.0332 | 10.2795 | 9.4363 | 7.1532 | 2.5721 | -2.2289 | 14.6882 | 14.5355 | 14.1155 | 13.7197 | 13.2482 | 12.3545 | 11.5134 | 10.6503 | 9.6134 | 8.3955 | 5.5418 | 0.027105 | -3.9697
|  | GLENEAGLES | CF |  |  |  |  | 16.22 | 16.1789 | 16.1316 | 16.0842 | 16.0347 | 15.8147 | 15.62 | 15.4253 | 15.2526 | 15.1168 | 13.4558 | 10.8453 | 8.02 | 14.4521 | 14.4111 | 14.2784 | 14.1353 | 13.9911 | 13.7205 | 13.4447 | 13.1405 | 12.8721 | 12.5626 | 10.8605 | 8.1258 | 4.9574 | 14.8587 | 14.8176 | 14.7703 | 14.7229 | 14.6745 | 14.3882 | 14.0818 | 13.7492 | 13.4597 | 13.1503 | 11.3282 | 8.3513 | 5.0324
| RANNOCH | GLENETIVE | MINIMUM HEADROOM | NN 25850 54886 | YES | YES | 0 | 0.27053 | 0.26 | 0.24421 | 0.22421 | 0.20211 | 0.18 | 0.16 | 0.14 | 0.12 | 0.097895 | 0.0031579 | -0.08 | -0.16526 | 0.27263 | 0.25579 | 0.23684 | 0.21474 | 0.19474 | 0.17263 | 0.15263 | 0.13474 | 0.11474 | 0.094737 | 0.0010526 | -0.078947 | -0.16211 | 0.28947 | 0.27053 | 0.24947 | 0.22842 | 0.20526 | 0.18316 | 0.16316 | 0.14316 | 0.12316 | 0.10105 | 0.0042105 | -0.078947 | -0.16421
|  | GLENETIVE | EE |  |  |  |  | 0.27053 | 0.26 | 0.24421 | 0.22421 | 0.20211 | 0.18 | 0.16 | 0.14 | 0.12 | 0.097895 | 0.0031579 | -0.08 | -0.16526 | 0.27263 | 0.25579 | 0.23684 | 0.21474 | 0.19474 | 0.17263 | 0.15263 | 0.13474 | 0.11474 | 0.094737 | 0.0010526 | -0.078947 | -0.16211 | 0.28947 | 0.27053 | 0.24947 | 0.22842 | 0.20526 | 0.18316 | 0.16316 | 0.14316 | 0.12316 | 0.10105 | 0.0042105 | -0.078947 | -0.16421
|  | GLENETIVE | HT |  |  |  |  | 0.27053 | 0.26737 | 0.26421 | 0.26 | 0.25368 | 0.24842 | 0.24211 | 0.23579 | 0.23053 | 0.22421 | 0.19368 | 0.16421 | 0.13368 | 0.27263 | 0.26632 | 0.26 | 0.25368 | 0.24737 | 0.24211 | 0.23579 | 0.22947 | 0.22316 | 0.21684 | 0.18421 | 0.15263 | 0.12105 | 0.28947 | 0.28211 | 0.27579 | 0.26947 | 0.26211 | 0.25684 | 0.24947 | 0.24316 | 0.23789 | 0.23158 | 0.19789 | 0.16421 | 0.13053
|  | GLENETIVE | HE |  |  |  |  | 0.27053 | 0.26737 | 0.26421 | 0.26 | 0.25684 | 0.25263 | 0.24632 | 0.24105 | 0.23684 | 0.23053 | 0.2 | 0.16842 | 0.13579 | 0.27263 | 0.26737 | 0.26316 | 0.25789 | 0.25158 | 0.24737 | 0.24 | 0.23368 | 0.22842 | 0.22316 | 0.19158 | 0.16 | 0.12842 | 0.28947 | 0.28211 | 0.27579 | 0.26947 | 0.26211 | 0.25684 | 0.24947 | 0.24316 | 0.23789 | 0.23158 | 0.19789 | 0.16421 | 0.13053
|  | GLENETIVE | CF |  |  |  |  | 0.27053 | 0.26947 | 0.26842 | 0.26737 | 0.26737 | 0.26632 | 0.26526 | 0.26526 | 0.26421 | 0.26316 | 0.26 | 0.25474 | 0.24842 | 0.27263 | 0.27158 | 0.27053 | 0.26842 | 0.26737 | 0.26632 | 0.26421 | 0.26316 | 0.26211 | 0.26 | 0.25368 | 0.24737 | 0.24211 | 0.28947 | 0.28842 | 0.28632 | 0.28526 | 0.28316 | 0.28211 | 0.28105 | 0.27895 | 0.27684 | 0.27579 | 0.26947 | 0.26316 | 0.25579
| FORT WILLIAM | GLENUIG | MINIMUM HEADROOM | NM 67224 77119 | YES | NO | 0 | 0.12105 | 0.12105 | 0.12 | 0.11895 | 0.11789 | 0.11684 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.10737 | 0.10421 | 0.098947 | 0.11158 | 0.11158 | 0.11053 | 0.10947 | 0.10842 | 0.10737 | 0.10632 | 0.10526 | 0.10526 | 0.10421 | 0.098947 | 0.095789 | 0.089474 | 0.11579 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.11158 | 0.11053 | 0.10947 | 0.10947 | 0.10842 | 0.10316 | 0.1 | 0.093684
|  | GLENUIG | EE |  |  |  |  | 0.12211 | 0.12105 | 0.12105 | 0.12 | 0.11895 | 0.11789 | 0.11789 | 0.11684 | 0.11579 | 0.11579 | 0.11158 | 0.10842 | 0.10632 | 0.11263 | 0.11158 | 0.11158 | 0.11053 | 0.10947 | 0.10842 | 0.10842 | 0.10737 | 0.10632 | 0.10632 | 0.10421 | 0.1 | 0.098947 | 0.11684 | 0.11579 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.11263 | 0.11158 | 0.11053 | 0.11053 | 0.10842 | 0.10421 | 0.10316
|  | GLENUIG | HT |  |  |  |  | 0.12105 | 0.12105 | 0.12 | 0.11895 | 0.11789 | 0.11684 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.10737 | 0.10421 | 0.098947 | 0.11158 | 0.11158 | 0.11053 | 0.10947 | 0.10842 | 0.10737 | 0.10632 | 0.10526 | 0.10526 | 0.10421 | 0.098947 | 0.095789 | 0.089474 | 0.11579 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.11158 | 0.11053 | 0.10947 | 0.10947 | 0.10842 | 0.10316 | 0.1 | 0.093684
|  | GLENUIG | HE |  |  |  |  | 0.12211 | 0.12211 | 0.12105 | 0.12105 | 0.12 | 0.12 | 0.11895 | 0.11895 | 0.11789 | 0.11789 | 0.11684 | 0.11579 | 0.11579 | 0.11263 | 0.11263 | 0.11158 | 0.11158 | 0.11053 | 0.11053 | 0.10947 | 0.10947 | 0.10842 | 0.10842 | 0.10737 | 0.10632 | 0.10632 | 0.11579 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.11158 | 0.11053 | 0.10947 | 0.10947 | 0.10842 | 0.10316 | 0.1 | 0.093684
|  | GLENUIG | CF |  |  |  |  | 0.12316 | 0.12211 | 0.12211 | 0.12211 | 0.12211 | 0.12105 | 0.12105 | 0.12105 | 0.12105 | 0.12 | 0.11895 | 0.11895 | 0.11895 | 0.11368 | 0.11263 | 0.11263 | 0.11263 | 0.11263 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.10947 | 0.10947 | 0.10947 | 0.11789 | 0.11684 | 0.11684 | 0.11684 | 0.11684 | 0.11579 | 0.11579 | 0.11579 | 0.11579 | 0.11474 | 0.11368 | 0.11368 | 0.11368
| BRORA | GOLSPIE | MINIMUM HEADROOM | NC 82996 00240 | YES | YES | 0.044 | 3.4286 | 3.396 | 3.3571 | 3.3002 | 3.2413 | 3.0613 | 2.8728 | 2.6792 | 2.5339 | 2.3886 | 1.1349 | -0.51137 | -1.7851 | 3.1665 | 3.1013 | 3.0328 | 2.9655 | 2.9002 | 2.7107 | 2.5234 | 2.3318 | 2.2055 | 2.0802 | 0.75705 | -1.1093 | -2.4461 | 3.2402 | 3.2065 | 3.1434 | 3.076 | 3.0107 | 2.8086 | 2.6086 | 2.4034 | 2.2549 | 2.1065 | 0.71705 | -1.1661 | -2.5282
|  | GOLSPIE | EE |  |  |  |  | 3.4413 | 3.4139 | 3.3792 | 3.3434 | 3.2949 | 3.1602 | 3.0044 | 2.7971 | 2.6023 | 2.3992 | 1.1792 | -0.43453 | -1.7851 | 3.196 | 3.1434 | 3.0886 | 3.0307 | 2.9718 | 2.8539 | 2.7223 | 2.5192 | 2.3318 | 2.1381 | 0.94232 | -0.72505 | -2.2587 | 3.2528 | 3.2244 | 3.1897 | 3.1339 | 3.0739 | 2.9328 | 2.7718 | 2.5444 | 2.336 | 2.1223 | 0.80758 | -0.97979 | -2.5282
|  | GOLSPIE | HT |  |  |  |  | 3.4286 | 3.396 | 3.3571 | 3.3002 | 3.2413 | 3.0613 | 2.8728 | 2.6792 | 2.5339 | 2.3886 | 1.1349 | -0.51137 | -1.6851 | 3.1665 | 3.1013 | 3.0328 | 2.9655 | 2.9002 | 2.7107 | 2.5234 | 2.3318 | 2.2055 | 2.0802 | 0.75705 | -1.1093 | -2.4461 | 3.2402 | 3.2065 | 3.1434 | 3.076 | 3.0107 | 2.8086 | 2.6086 | 2.4034 | 2.2549 | 2.1065 | 0.71705 | -1.1661 | -2.524
|  | GOLSPIE | HE |  |  |  |  | 3.4602 | 3.4423 | 3.4213 | 3.4002 | 3.376 | 3.2676 | 3.1455 | 2.9855 | 2.8349 | 2.5949 | 1.5865 | 0.30547 | -1.0808 | 3.2371 | 3.2055 | 3.1707 | 3.1381 | 3.1023 | 2.9928 | 2.8644 | 2.7034 | 2.5528 | 2.3002 | 1.2749 | -0.099789 | -1.5893 | 3.2402 | 3.2065 | 3.1434 | 3.076 | 3.0107 | 2.8086 | 2.6086 | 2.4034 | 2.2549 | 2.1065 | 0.71705 | -1.1661 | -2.524
|  | GOLSPIE | CF |  |  |  |  | 3.4707 | 3.4613 | 3.4497 | 3.4381 | 3.4265 | 3.3844 | 3.3455 | 3.3076 | 3.2213 | 3.1065 | 2.5549 | 1.7381 | 0.80758 | 3.2549 | 3.2392 | 3.2181 | 3.1981 | 3.1771 | 3.1297 | 3.0855 | 3.0318 | 2.9128 | 2.7655 | 2.1792 | 1.3002 | 0.24863 | 3.2823 | 3.2728 | 3.2613 | 3.2486 | 3.2371 | 3.196 | 3.1571 | 3.1128 | 2.9918 | 2.8497 | 2.2476 | 1.3307 | 0.26442
| BURGHMUIR | GOODLYBURN | MINIMUM HEADROOM | NO 10084 24586 | NO | YES | 0.198 | 14.6828 | 14.5112 | 14.3207 | 14.1207 | 13.9091 | 13.6691 | 13.3344 | 12.9259 | 12.5523 | 12.2154 | 10.8386 | 9.8723 | 9.0291 | 13.3062 | 13.1125 | 12.8883 | 12.6378 | 12.2609 | 11.7862 | 11.3567 | 10.9073 | 10.4988 | 10.1336 | 8.6925 | 7.6178 | 6.6683 | 13.764 | 13.5924 | 13.4019 | 13.1661 | 12.6934 | 12.2229 | 11.7987 | 11.3534 | 10.9482 | 10.5871 | 9.1071 | 8.0313 | 7.0808
|  | GOODLYBURN | EE |  |  |  |  | 14.7512 | 14.6196 | 14.4828 | 14.3386 | 14.1881 | 14.0281 | 13.8744 | 13.6796 | 13.4102 | 13.1438 | 11.9186 | 11.2165 | 10.6228 | 13.382 | 13.2378 | 13.0831 | 12.9041 | 12.7125 | 12.4757 | 12.0388 | 11.722 | 11.4294 | 11.1388 | 9.8588 | 9.0736 | 8.402 | 13.8324 | 13.7008 | 13.564 | 13.4198 | 13.264 | 12.8998 | 12.4713 | 12.1577 | 11.8661 | 11.5777 | 10.265 | 9.4871 | 8.8134
|  | GOODLYBURN | HT |  |  |  |  | 14.6828 | 14.5112 | 14.3207 | 14.1207 | 13.9091 | 13.6691 | 13.3344 | 12.9259 | 12.5523 | 12.2154 | 10.8386 | 9.8723 | 9.0291 | 13.3062 | 13.1125 | 12.8883 | 12.6378 | 12.2609 | 11.7862 | 11.3567 | 10.9073 | 10.4988 | 10.1336 | 8.6925 | 7.6178 | 6.6683 | 13.764 | 13.5924 | 13.4019 | 13.1661 | 12.6934 | 12.2229 | 11.7987 | 11.3534 | 10.9482 | 10.5871 | 9.1071 | 8.0313 | 7.0808
|  | GOODLYBURN | HE |  |  |  |  | 14.8312 | 14.7375 | 14.6354 | 14.5238 | 14.4049 | 14.2744 | 14.1544 | 14.0365 | 13.9249 | 13.8238 | 13.2438 | 12.8607 | 12.5775 | 13.462 | 13.3683 | 13.2652 | 13.1357 | 12.9852 | 12.8146 | 12.6336 | 12.3588 | 12.1399 | 11.962 | 11.2841 | 10.8567 | 10.5336 | 13.764 | 13.5924 | 13.4019 | 13.1661 | 12.6934 | 12.2229 | 11.7987 | 11.3534 | 10.9482 | 10.5871 | 9.1071 | 8.0313 | 7.0808
|  | GOODLYBURN | CF |  |  |  |  | 14.8744 | 14.8144 | 14.7533 | 14.6902 | 14.6259 | 14.5586 | 14.4891 | 14.4217 | 14.3533 | 14.2859 | 13.9944 | 13.8396 | 13.5986 | 13.5052 | 13.4452 | 13.3841 | 13.3209 | 13.2494 | 13.1746 | 13.0946 | 12.9967 | 12.9104 | 12.822 | 12.322 | 11.9252 | 11.6231 | 13.9556 | 13.8956 | 13.8345 | 13.7713 | 13.7071 | 13.6398 | 13.5713 | 13.504 | 13.4356 | 13.3682 | 12.7492 | 12.3556 | 12.0566
| CHARLESTON | GOURDIE | MINIMUM HEADROOM | NO 34573 32203 | YES | YES | 0.086 | 6.7635 | 6.6635 | 6.4435 | 6.1793 | 5.8951 | 5.4561 | 5.1677 | 4.8729 | 4.3393 | 3.9698 | 2.9372 | 1.8677 | 0.31926 | 6.2235 | 6.0403 | 5.7814 | 5.4687 | 5.1487 | 4.6856 | 4.4014 | 4.1087 | 3.5435 | 3.1719 | 2.3635 | 1.2129 | -0.25758 | 6.3298 | 6.1803 | 5.9708 | 5.7056 | 5.3898 | 4.9056 | 4.5951 | 4.2761 | 3.6856 | 3.2814 | 2.2203 | 1.114 | -0.61442
|  | GOURDIE | EE |  |  |  |  | 6.7845 | 6.7361 | 6.5529 | 6.3329 | 6.0866 | 5.6782 | 5.2551 | 4.8772 | 4.5877 | 4.2603 | 2.9372 | 1.8677 | 0.31926 | 6.2666 | 6.1235 | 5.9087 | 5.6466 | 5.3666 | 4.9456 | 4.5203 | 4.1508 | 3.8729 | 3.554 | 2.3635 | 1.4835 | -0.21232 | 6.3666 | 6.2508 | 6.0761 | 5.8666 | 5.6003 | 5.1508 | 4.6877 | 4.2782 | 3.9645 | 3.6098 | 2.2203 | 1.114 | -0.61442
|  | GOURDIE | HT |  |  |  |  | 6.7635 | 6.6635 | 6.4435 | 6.1793 | 5.8951 | 5.4561 | 5.1677 | 4.8729 | 4.3393 | 3.9698 | 3.1193 | 1.9551 | 0.64558 | 6.2235 | 6.0403 | 5.7814 | 5.4687 | 5.1487 | 4.6856 | 4.4014 | 4.1087 | 3.5435 | 3.1719 | 2.4193 | 1.2129 | -0.25758 | 6.3298 | 6.1803 | 5.9708 | 5.7056 | 5.3898 | 4.9056 | 4.5951 | 4.2761 | 3.6856 | 3.2814 | 2.3982 | 1.1245 | -0.346
|  | GOURDIE | HE |  |  |  |  | 6.8151 | 6.7887 | 6.6529 | 6.4666 | 6.254 | 5.854 | 5.4519 | 5.1077 | 4.6919 | 4.4551 | 3.6677 | 2.8866 | 1.2182 | 6.2972 | 6.1793 | 6.0151 | 5.7887 | 5.5382 | 5.1319 | 4.7119 | 4.3593 | 3.9235 | 3.6972 | 3.0056 | 2.3161 | 0.59821 | 6.3298 | 6.1803 | 5.9708 | 5.7056 | 5.3898 | 4.9056 | 4.5951 | 4.2761 | 3.6856 | 3.2814 | 2.3982 | 1.1245 | -0.346
|  | GOURDIE | CF |  |  |  |  | 6.8298 | 6.8151 | 6.7982 | 6.7803 | 6.7519 | 6.6414 | 6.5066 | 6.3466 | 6.1772 | 5.9835 | 5.3551 | 4.7835 | 3.7108 | 6.3393 | 6.3119 | 6.2508 | 6.2098 | 6.1393 | 6.0308 | 5.8908 | 5.714 | 5.5256 | 5.3077 | 4.6698 | 4.1277 | 2.9561 | 6.4329 | 6.4087 | 6.3582 | 6.3235 | 6.2666 | 6.1614 | 6.0351 | 5.8835 | 5.7119 | 5.4898 | 4.8024 | 4.1824 | 2.9751
| BOAT OF GARTEN | GRANTOWN | MINIMUM HEADROOM | NJ 03670 26311 | NO | YES | 0.205 | 16.3713 | 16.1913 | 16.0282 | 15.8639 | 15.7039 | 15.5282 | 15.3576 | 15.1955 | 15.0418 | 14.8839 | 14.1913 | 13.6429 | 13.1892 | 14.2066 | 13.9918 | 13.8013 | 13.6108 | 13.4255 | 13.2255 | 13.0318 | 12.8476 | 12.6739 | 12.5055 | 11.7529 | 11.1487 | 10.6424 | 14.7689 | 14.5626 | 14.3784 | 14.1953 | 14.0153 | 13.8205 | 13.6311 | 13.4521 | 13.2816 | 13.1174 | 12.39 | 11.7837 | 11.2774
|  | GRANTOWN | EE |  |  |  |  | 16.4261 | 16.3008 | 16.1713 | 16.0408 | 15.9071 | 15.7703 | 15.6387 | 15.5061 | 15.3808 | 15.265 | 14.7039 | 14.2597 | 13.9166 | 14.2939 | 14.1213 | 13.9718 | 13.8213 | 13.6676 | 13.515 | 13.3655 | 13.215 | 13.0729 | 12.9424 | 12.3192 | 11.8361 | 11.4529 | 14.8521 | 14.6868 | 14.5426 | 14.3963 | 14.2479 | 14.0974 | 13.9511 | 13.8047 | 13.6658 | 13.5374 | 12.9268 | 12.4574 | 12.0774
|  | GRANTOWN | HT |  |  |  |  | 16.3713 | 16.1913 | 16.0282 | 15.8639 | 15.7039 | 15.5282 | 15.3576 | 15.1955 | 15.0418 | 14.8839 | 14.1913 | 13.6429 | 13.1892 | 14.2066 | 13.9918 | 13.8013 | 13.6108 | 13.4255 | 13.2255 | 13.0318 | 12.8476 | 12.6739 | 12.5055 | 11.7529 | 11.1487 | 10.6424 | 14.7689 | 14.5626 | 14.3784 | 14.1953 | 14.0153 | 13.8205 | 13.6311 | 13.4521 | 13.2816 | 13.1174 | 12.39 | 11.7837 | 11.2774
|  | GRANTOWN | HE |  |  |  |  | 16.4797 | 16.4292 | 16.3629 | 16.2766 | 16.1839 | 16.0839 | 15.9924 | 15.9008 | 15.8166 | 15.7376 | 15.4503 | 15.265 | 15.1103 | 14.4118 | 14.2961 | 14.2003 | 14.1013 | 13.9971 | 13.8887 | 13.7855 | 13.6855 | 13.5918 | 13.5045 | 13.1845 | 12.9718 | 12.7855 | 14.7689 | 14.5626 | 14.3784 | 14.1953 | 14.0153 | 13.8205 | 13.6311 | 13.4521 | 13.2816 | 13.1174 | 12.39 | 11.7837 | 11.2774
|  | GRANTOWN | CF |  |  |  |  | 16.5092 | 16.4797 | 16.4503 | 16.4197 | 16.3839 | 16.3282 | 16.2745 | 16.2218 | 16.1671 | 16.1145 | 15.8755 | 15.7176 | 15.6018 | 14.4613 | 14.4108 | 14.3445 | 14.2845 | 14.2245 | 14.1613 | 14.0982 | 14.0392 | 13.975 | 13.915 | 13.6371 | 13.4508 | 13.3066 | 15.0321 | 14.9647 | 14.9016 | 14.8437 | 14.7847 | 14.7237 | 14.6626 | 14.6047 | 14.5426 | 14.4826 | 14.2142 | 14.0311 | 13.8932
| SHETLAND | GREMISTA | MINIMUM HEADROOM | HU4646842756 | NO | YES | 2.3 | 30.2421 | 30.0326 | 29.8168 | 29.5979 | 28.96 | 27.7084 | 26.8726 | 26.0368 | 25.5232 | 25.0137 | 58.9916 | 57.9137 | 57.3389 | 26.4926 | 26.06 | 25.4789 | 24.5989 | 23.6326 | 22.3326 | 21.4968 | 20.6611 | 20.2179 | 19.7821 | 70.6021 | 69.2558 | 66.2221 | 29.9937 | 29.5758 | 29.0189 | 28.1811 | 27.2642 | 25.9568 | 25.0968 | 24.2358 | 23.7284 | 23.2274 | 67.6126 | 66.5779 | 64.1874
|  | GREMISTA | EE |  |  |  |  | 30.3158 | 30.1453 | 29.9674 | 29.7811 | 29.3242 | 28.0779 | 27.1916 | 26.3095 | 25.8337 | 25.36 | 61.6221 | 59.6537 | 58.9179 | 26.6716 | 26.3274 | 25.74 | 24.9221 | 24.0221 | 22.7547 | 21.8989 | 21.0526 | 20.6526 | 20.26 | 74.66 | 73.5232 | 71.0811 | 30.1663 | 29.8326 | 29.2726 | 28.4958 | 27.6411 | 26.3463 | 25.4389 | 24.5368 | 24.0695 | 23.6053 | 70.9242 | 69.0695 | 68.3684
|  | GREMISTA | HT |  |  |  |  | 30.2421 | 30.0326 | 29.8168 | 29.5979 | 28.96 | 27.7084 | 26.8726 | 26.0368 | 25.5232 | 25.0137 | 58.9916 | 57.9137 | 57.3389 | 26.4926 | 26.06 | 25.4789 | 24.5989 | 23.6326 | 22.3326 | 21.4968 | 20.6611 | 20.2179 | 19.7821 | 70.6021 | 69.2558 | 66.2221 | 29.9937 | 29.5758 | 29.0189 | 28.1811 | 27.2642 | 25.9568 | 25.0968 | 24.2358 | 23.7284 | 23.2274 | 67.6126 | 66.5779 | 64.1874
|  | GREMISTA | HE |  |  |  |  | 32.2589 | 30.3221 | 30.1979 | 30.0632 | 29.8284 | 28.6811 | 28.0726 | 27.2379 | 26.1789 | 25.2105 | 60.4042 | 59.2147 | 58.0432 | 28.3768 | 26.6179 | 26.0821 | 25.3716 | 24.5526 | 23.3811 | 22.8053 | 21.9653 | 20.8621 | 19.8642 | 71.9442 | 71.2747 | 68.9105 | 29.9937 | 29.5758 | 29.0189 | 28.1811 | 27.2642 | 25.9568 | 25.0968 | 24.2358 | 23.7284 | 23.2274 | 67.6126 | 66.5779 | 64.1874
|  | GREMISTA | CF |  |  |  |  | 32.3263 | 32.2611 | 30.3705 | 30.3021 | 30.2316 | 30.0505 | 29.8905 | 29.7305 | 29.5853 | 29.4611 | 62.3716 | 61.6232 | 61.1189 | 28.5126 | 28.3789 | 26.7937 | 26.6442 | 26.4084 | 26.04 | 25.64 | 25.2074 | 24.76 | 24.4326 | 73.2558 | 72.8179 | 72.5379 | 32.4747 | 32.3453 | 30.2842 | 30.1389 | 29.9147 | 29.5305 | 29.1242 | 28.6884 | 28.2411 | 27.9147 | 70.8958 | 70.1884 | 69.7147
| WILLOWDALE | GREYFRIARS | MINIMUM HEADROOM | NJ 94327 07070 | NO | YES | 0.281 | 24.4327 | 24.3116 | 24.1843 | 23.8906 | 23.3927 | 22.8285 | 22.5337 | 22.2264 | 21.8822 | 21.4706 | 20.5853 | 19.7369 | 18.9306 | 22.9632 | 22.819 | 22.6327 | 22.3779 | 21.8674 | 21.1979 | 20.8716 | 20.5369 | 20.159 | 19.7043 | 18.8527 | 17.9232 | 17.0243 | 23.5506 | 23.4032 | 23.2558 | 23.1053 | 22.9022 | 22.2422 | 21.9148 | 21.579 | 21.199 | 20.7411 | 19.9453 | 19.0106 | 18.1085
|  | GREYFRIARS | EE |  |  |  |  | 24.4958 | 24.4085 | 24.3148 | 24.2179 | 23.8422 | 23.3337 | 22.8232 | 22.599 | 22.3779 | 22.1348 | 21.1074 | 20.4337 | 19.8601 | 23.0285 | 22.9295 | 22.8201 | 22.6337 | 22.3843 | 21.7758 | 21.1685 | 20.9264 | 20.6885 | 20.4232 | 19.4043 | 18.6811 | 18.0443 | 23.6169 | 23.5148 | 23.4022 | 23.2832 | 23.1527 | 22.8137 | 22.2095 | 21.9653 | 21.7243 | 21.4569 | 20.4895 | 19.7506 | 19.1085
|  | GREYFRIARS | HT |  |  |  |  | 24.4327 | 24.3116 | 24.1843 | 23.8906 | 23.3927 | 22.8285 | 22.5337 | 22.2264 | 21.8822 | 21.4706 | 20.5853 | 19.7369 | 18.9306 | 22.9632 | 22.819 | 22.6327 | 22.3779 | 21.8674 | 21.1979 | 20.8716 | 20.5369 | 20.159 | 19.7043 | 18.8527 | 17.9232 | 17.0243 | 23.5506 | 23.4032 | 23.2558 | 23.1053 | 22.9022 | 22.2422 | 21.9148 | 21.579 | 21.199 | 20.7411 | 19.9453 | 19.0106 | 18.1085
|  | GREYFRIARS | HE |  |  |  |  | 24.5316 | 24.4579 | 24.3769 | 24.2906 | 24.1958 | 24.0885 | 23.9885 | 23.8779 | 23.5916 | 23.2948 | 21.6811 | 20.8611 | 20.4295 | 23.0674 | 22.9843 | 22.8979 | 22.8053 | 22.7032 | 22.5927 | 22.4485 | 22.2874 | 22.1222 | 21.8085 | 19.8274 | 18.9011 | 18.4253 | 23.5506 | 23.4032 | 23.2558 | 23.1053 | 22.9022 | 22.2422 | 21.9148 | 21.579 | 21.199 | 20.7411 | 19.9453 | 19.0106 | 18.1085
|  | GREYFRIARS | CF |  |  |  |  | 24.5495 | 24.4937 | 24.4369 | 24.3779 | 24.3179 | 24.2527 | 24.1874 | 24.1232 | 24.0579 | 23.9958 | 23.1958 | 22.6085 | 22.2179 | 23.0885 | 23.0264 | 22.9674 | 22.9053 | 22.8422 | 22.7748 | 22.7074 | 22.6401 | 22.5685 | 22.4937 | 21.6811 | 20.9853 | 20.5369 | 23.679 | 23.6148 | 23.5558 | 23.4927 | 23.4274 | 23.359 | 23.2885 | 23.2179 | 23.1464 | 23.0779 | 22.7095 | 22.019 | 21.5664
| SHETLAND | GUTCHER | MINIMUM HEADROOM | HU5453899599 | YES | YES | 0 | 0.97263 | 0.95684 | 0.94211 | 0.92737 | 0.91263 | 0.89789 | 0.88526 | 0.87158 | 0.85789 | 0.84632 | 0.79684 | 0.75579 | 0.72211 | 0.96842 | 0.95263 | 0.93684 | 0.92105 | 0.90526 | 0.88947 | 0.87579 | 0.86105 | 0.84737 | 0.83368 | 0.78105 | 0.73684 | 0.69789 | 0.96947 | 0.95263 | 0.93789 | 0.92211 | 0.90632 | 0.89053 | 0.87684 | 0.86211 | 0.84737 | 0.83474 | 0.78105 | 0.73684 | 0.69895
|  | GUTCHER | EE |  |  |  |  | 0.97895 | 0.96632 | 0.95474 | 0.94316 | 0.93158 | 0.92 | 0.90842 | 0.89789 | 0.88737 | 0.87895 | 0.83579 | 0.80526 | 0.78105 | 0.97579 | 0.96316 | 0.95053 | 0.93789 | 0.92526 | 0.91263 | 0.90105 | 0.88947 | 0.87789 | 0.86947 | 0.82316 | 0.79053 | 0.76316 | 0.97579 | 0.96316 | 0.95053 | 0.93789 | 0.92632 | 0.91368 | 0.90211 | 0.89053 | 0.87895 | 0.86947 | 0.82421 | 0.79158 | 0.76316
|  | GUTCHER | HT |  |  |  |  | 0.97263 | 0.95684 | 0.94211 | 0.92737 | 0.91263 | 0.89789 | 0.88526 | 0.87158 | 0.85789 | 0.84632 | 0.79684 | 0.75579 | 0.72211 | 0.96842 | 0.95263 | 0.93684 | 0.92105 | 0.90526 | 0.88947 | 0.87579 | 0.86105 | 0.84737 | 0.83368 | 0.78105 | 0.73684 | 0.69789 | 0.96947 | 0.95263 | 0.93789 | 0.92211 | 0.90632 | 0.89053 | 0.87684 | 0.86211 | 0.84737 | 0.83474 | 0.78105 | 0.73684 | 0.69895
|  | GUTCHER | HE |  |  |  |  | 0.98737 | 0.98105 | 0.97263 | 0.96526 | 0.95684 | 0.94947 | 0.94105 | 0.93474 | 0.92737 | 0.92 | 0.89684 | 0.88211 | 0.87053 | 0.98526 | 0.97895 | 0.96947 | 0.96105 | 0.95263 | 0.94421 | 0.93684 | 0.92947 | 0.92211 | 0.91474 | 0.89053 | 0.87368 | 0.86 | 0.96947 | 0.95263 | 0.93789 | 0.92211 | 0.90632 | 0.89053 | 0.87684 | 0.86211 | 0.84737 | 0.83474 | 0.78105 | 0.73684 | 0.69895
|  | GUTCHER | CF |  |  |  |  | 0.99158 | 0.98737 | 0.98316 | 0.97789 | 0.97368 | 0.96947 | 0.96421 | 0.96 | 0.95579 | 0.94947 | 0.92947 | 0.91684 | 0.90632 | 0.99053 | 0.98526 | 0.98 | 0.97579 | 0.97053 | 0.96526 | 0.96105 | 0.95579 | 0.95053 | 0.94526 | 0.92316 | 0.90947 | 0.89684 | 0.99053 | 0.98526 | 0.98105 | 0.97579 | 0.97053 | 0.96632 | 0.96105 | 0.95684 | 0.95158 | 0.94632 | 0.92421 | 0.91053 | 0.89789
| THURSO | HALKIRK | MINIMUM HEADROOM | ND 13246 58223 | YES | YES | 0 | 2.6871 | 2.6155 | 2.5113 | 2.4071 | 2.306 | 1.6576 | 0.83126 | -0.063474 | -0.85189 | -2.0803 | -9.2751 | -17.0045 | -23.4382 | 2.5839 | 2.506 | 2.4039 | 2.3018 | 2.2039 | 1.6892 | 0.99547 | 0.19863 | -0.55189 | -1.7719 | -8.4361 | -16.7214 | -23.1887 | 2.6007 | 2.5228 | 2.4134 | 2.3039 | 2.1976 | 1.566 | 0.77021 | -0.114 | -0.88347 | -2.0635 | -10.074 | -18.614 | -25.9498
|  | HALKIRK | EE |  |  |  |  | 2.7197 | 2.666 | 2.5576 | 2.4502 | 2.3439 | 1.6576 | 0.83126 | -0.063474 | -0.83821 | -1.7129 | -9.2751 | -17.0045 | -23.4382 | 2.6123 | 2.5607 | 2.4618 | 2.3618 | 2.2639 | 1.7365 | 1.0923 | 0.35021 | -0.29821 | -1.0561 | -8.4003 | -16.1824 | -23.1887 | 2.6376 | 2.5776 | 2.466 | 2.3544 | 2.2449 | 1.5734 | 0.77021 | -0.114 | -0.88347 | -1.7782 | -10.074 | -18.614 | -25.9498
|  | HALKIRK | HT |  |  |  |  | 2.6871 | 2.6155 | 2.5113 | 2.4071 | 2.306 | 1.6807 | 1.0523 | 0.41021 | -0.32768 | -1.7877 | -8.6193 | -16.1172 | -21.4003 | 2.5839 | 2.506 | 2.4039 | 2.3018 | 2.2039 | 1.6892 | 1.1765 | 0.64811 | 0.033368 | -1.4161 | -8.4361 | -16.7214 | -22.6761 | 2.6007 | 2.5228 | 2.4134 | 2.3039 | 2.1976 | 1.566 | 0.93547 | 0.29126 | -0.43716 | -2.0635 | -9.6708 | -18.2477 | -24.3403
|  | HALKIRK | HE |  |  |  |  | 2.7639 | 2.7313 | 2.6881 | 2.6418 | 2.5934 | 1.726 | 0.86811 | -0.011895 | -0.85189 | -2.0803 | -7.3077 | -13.3414 | -20.4603 | 2.6376 | 2.6165 | 2.5892 | 2.5439 | 2.4955 | 1.7681 | 0.99547 | 0.19863 | -0.55189 | -1.7719 | -6.8498 | -13.1445 | -20.4361 | 2.6007 | 2.5228 | 2.4134 | 2.3039 | 2.1976 | 1.566 | 0.93547 | 0.29126 | -0.43716 | -2.0635 | -9.6708 | -18.2477 | -24.3403
|  | HALKIRK | CF |  |  |  |  | 2.7871 | 2.7671 | 2.7386 | 2.7113 | 2.6828 | 2.4039 | 2.1586 | 1.6671 | 1.1418 | 0.54495 | -2.1572 | -5.9951 | -10.5645 | 2.6502 | 2.6386 | 2.6228 | 2.6081 | 2.5902 | 2.3765 | 2.1881 | 1.6881 | 1.1418 | 0.49337 | -2.2466 | -6.2719 | -11.2077 | 2.7071 | 2.6892 | 2.6607 | 2.6323 | 2.6018 | 2.3292 | 2.0892 | 1.5386 | 0.94916 | 0.27021 | -2.714 | -7.0151 | -12.1982
| ABERNETHY | HARBOUR | MINIMUM HEADROOM | NO 11948 22049 | NO | YES | 0.14 | 22.5874 | 22.4621 | 22.2084 | 21.8389 | 21.3789 | 20.9084 | 20.46 | 20.0589 | 19.6611 | 19.1926 | 17.9884 | 17.1421 | 16.4895 | 21.8253 | 21.6884 | 21.1874 | 20.7242 | 20.1347 | 19.62 | 19.1421 | 18.72 | 18.3063 | 17.8084 | 16.5863 | 15.7168 | 15.0168 | 21.7316 | 21.5926 | 21.4295 | 21.1253 | 20.5368 | 20.0063 | 19.5158 | 19.0789 | 18.6484 | 18.1326 | 16.8453 | 15.9337 | 15.2179
|  | HARBOUR | EE |  |  |  |  | 22.6411 | 22.5495 | 22.4505 | 22.1484 | 21.7674 | 21.3716 | 20.8947 | 20.5505 | 20.26 | 19.8768 | 18.5189 | 17.58 | 17.0295 | 21.8811 | 21.7821 | 21.5021 | 21.0926 | 20.5968 | 20.1305 | 19.6147 | 19.2653 | 18.9726 | 18.5695 | 17.2137 | 16.3326 | 15.7663 | 21.7884 | 21.6863 | 21.5705 | 21.4453 | 20.9979 | 20.5137 | 19.9758 | 19.6063 | 19.2947 | 18.8737 | 17.4168 | 16.4295 | 15.8305
|  | HARBOUR | HT |  |  |  |  | 22.5874 | 22.4621 | 22.2084 | 21.8389 | 21.3789 | 20.9084 | 20.46 | 20.0589 | 19.6611 | 19.1926 | 17.9884 | 17.1421 | 16.4895 | 21.8253 | 21.6884 | 21.1874 | 20.7242 | 20.1347 | 19.62 | 19.1421 | 18.72 | 18.3063 | 17.8084 | 16.5863 | 15.7168 | 15.0168 | 21.7316 | 21.5926 | 21.4295 | 21.1253 | 20.5368 | 20.0063 | 19.5158 | 19.0789 | 18.6484 | 18.1326 | 16.8453 | 15.9337 | 15.2179
|  | HARBOUR | HE |  |  |  |  | 22.6989 | 22.6347 | 22.5632 | 22.3979 | 22.0558 | 21.6821 | 21.2916 | 20.9758 | 20.6895 | 20.3684 | 19.5979 | 19.0537 | 18.5537 | 21.9421 | 21.8726 | 21.7368 | 21.3863 | 20.9337 | 20.4926 | 20.0347 | 19.7032 | 19.4063 | 19.0663 | 18.3232 | 17.8189 | 17.3642 | 21.7316 | 21.5926 | 21.4295 | 21.1253 | 20.5368 | 20.0063 | 19.5158 | 19.0789 | 18.6484 | 18.1326 | 16.8453 | 15.9337 | 15.2179
|  | HARBOUR | CF |  |  |  |  | 22.7295 | 22.6905 | 22.6484 | 22.6053 | 22.5621 | 22.4916 | 22.3579 | 22.1968 | 22.0779 | 21.9326 | 21.2116 | 20.8168 | 20.5189 | 21.9726 | 21.9337 | 21.8874 | 21.8379 | 21.7453 | 21.5705 | 21.3726 | 21.1811 | 21.0421 | 20.8663 | 20.0032 | 19.6137 | 19.3232 | 21.8811 | 21.8421 | 21.7926 | 21.7421 | 21.6895 | 21.6137 | 21.5411 | 21.4663 | 21.4011 | 21.2421 | 20.3516 | 19.9221 | 19.6021
| ARDMORE | HARRIS GRID | MINIMUM HEADROOM | NG 13500 94249 | YES | YES | 0 | 29.9842 | 29.9611 | 29.9421 | 29.9221 | 29.9032 | 29.8632 | 29.8379 | 29.8095 | 29.7789 | 29.7463 | 29.3874 | 27.6021 | 27.2579 | 29.9821 | 29.9558 | 29.9358 | 29.9137 | 29.8916 | 29.8547 | 29.8326 | 29.8105 | 29.7874 | 29.7589 | 29.3758 | 27.8253 | 27.4863 | 29.9821 | 29.9558 | 29.9358 | 29.9126 | 29.8916 | 29.8495 | 29.8232 | 29.7958 | 29.7674 | 29.7337 | 29.3274 | 27.4726 | 27.1042
|  | HARRIS GRID | EE |  |  |  |  | 29.9863 | 29.9811 | 29.9463 | 29.9295 | 29.9084 | 29.88 | 29.8453 | 29.8095 | 29.7789 | 29.7463 | 29.3989 | 27.6189 | 27.2579 | 29.9853 | 29.9789 | 29.9411 | 29.92 | 29.9 | 29.8758 | 29.8463 | 29.8179 | 29.7926 | 29.7642 | 29.4168 | 27.8968 | 27.5074 | 29.9853 | 29.9789 | 29.94 | 29.92 | 29.8979 | 29.8684 | 29.8326 | 29.7989 | 29.7674 | 29.7337 | 29.3537 | 27.5189 | 27.1042
|  | HARRIS GRID | HT |  |  |  |  | 29.9842 | 29.9611 | 29.9421 | 29.9221 | 29.9032 | 29.8632 | 29.8379 | 29.8105 | 29.7821 | 29.7526 | 29.3874 | 27.6021 | 27.2947 | 29.9821 | 29.9558 | 29.9358 | 29.9137 | 29.8916 | 29.8547 | 29.8326 | 29.8105 | 29.7874 | 29.7632 | 29.3758 | 27.8253 | 27.4863 | 29.9821 | 29.9558 | 29.9358 | 29.9126 | 29.8916 | 29.8495 | 29.8232 | 29.7958 | 29.7674 | 29.7368 | 29.3274 | 27.4726 | 27.1179
|  | HARRIS GRID | HE |  |  |  |  | 29.9926 | 29.9884 | 29.9568 | 29.9411 | 29.9263 | 29.8968 | 29.8716 | 29.8453 | 29.8147 | 29.7516 | 29.4842 | 28.4695 | 28.0958 | 29.9926 | 29.9874 | 29.9516 | 29.9337 | 29.9168 | 29.8937 | 29.8726 | 29.8516 | 29.8242 | 29.7589 | 29.4884 | 28.5968 | 28.2 | 29.9821 | 29.9558 | 29.9358 | 29.9126 | 29.8916 | 29.8495 | 29.8232 | 29.7958 | 29.7674 | 29.7368 | 29.3274 | 27.4726 | 27.1179
|  | HARRIS GRID | CF |  |  |  |  | 29.9947 | 29.9926 | 29.9895 | 29.9789 | 29.9747 | 29.9611 | 29.9463 | 29.9326 | 29.9074 | 29.8747 | 29.7274 | 29.5074 | 29.2505 | 29.9937 | 29.9926 | 29.9884 | 29.9768 | 29.9726 | 29.96 | 29.9463 | 29.9337 | 29.9084 | 29.8716 | 29.7168 | 29.4811 | 29.1968 | 29.9937 | 29.9926 | 29.9884 | 29.9768 | 29.9726 | 29.9579 | 29.9421 | 29.9274 | 29.9 | 29.8621 | 29.6979 | 29.4495 | 29.1558
| DYCE | HARVEST AVENUE | MINIMUM HEADROOM | NJ 86978 11769 | NO | YES | 0 | 23.9053 | 23.8979 | 23.8853 | 23.8726 | 23.86 | 23.8358 | 23.8126 | 23.7884 | 23.7632 | 23.7368 | 23.6179 | 23.4495 | 23.2832 | 22.5726 | 22.5653 | 22.5568 | 22.5453 | 22.5358 | 22.5211 | 22.5074 | 22.4895 | 22.4568 | 22.4263 | 22.2874 | 22.1179 | 21.9579 | 23.2589 | 23.2537 | 23.2474 | 23.2295 | 23.2063 | 23.1726 | 23.1389 | 23.1042 | 23.0695 | 23.0337 | 22.8811 | 22.7011 | 22.5105
|  | HARVEST AVENUE | EE |  |  |  |  | 23.9084 | 23.9032 | 23.8958 | 23.8853 | 23.8747 | 23.8495 | 23.8221 | 23.7958 | 23.7705 | 23.7453 | 23.6179 | 23.4495 | 23.2832 | 22.5747 | 22.5695 | 22.5642 | 22.5558 | 22.5484 | 22.5337 | 22.5179 | 22.5032 | 22.4884 | 22.4663 | 22.3232 | 22.1389 | 21.9589 | 23.2611 | 23.2568 | 23.2516 | 23.2453 | 23.2379 | 23.2032 | 23.1695 | 23.1347 | 23.1032 | 23.0695 | 22.9074 | 22.7011 | 22.5105
|  | HARVEST AVENUE | HT |  |  |  |  | 23.9053 | 23.8979 | 23.8853 | 23.8726 | 23.86 | 23.8358 | 23.8126 | 23.7884 | 23.7632 | 23.7368 | 23.6189 | 23.46 | 23.3189 | 22.5726 | 22.5653 | 22.5568 | 22.5453 | 22.5358 | 22.5211 | 22.5074 | 22.4895 | 22.4568 | 22.4263 | 22.2874 | 22.1179 | 21.9579 | 23.2589 | 23.2537 | 23.2474 | 23.2295 | 23.2063 | 23.1726 | 23.1389 | 23.1042 | 23.0695 | 23.0337 | 22.8811 | 22.7011 | 22.5379
|  | HARVEST AVENUE | HE |  |  |  |  | 23.9137 | 23.9105 | 23.9063 | 23.9021 | 23.8968 | 23.8747 | 23.8558 | 23.8358 | 23.8158 | 23.7947 | 23.6958 | 23.5621 | 23.3832 | 22.5789 | 22.5768 | 22.5726 | 22.5695 | 22.5642 | 22.5516 | 22.5411 | 22.5305 | 22.52 | 22.5084 | 22.4095 | 22.2389 | 22.0547 | 23.2589 | 23.2537 | 23.2474 | 23.2295 | 23.2063 | 23.1726 | 23.1389 | 23.1042 | 23.0695 | 23.0337 | 22.8811 | 22.7011 | 22.5379
|  | HARVEST AVENUE | CF |  |  |  |  | 23.9158 | 23.9137 | 23.9116 | 23.9084 | 23.9063 | 23.8979 | 23.8905 | 23.8821 | 23.8737 | 23.8642 | 23.8137 | 23.7474 | 23.6453 | 22.5811 | 22.5789 | 22.5779 | 22.5747 | 22.5737 | 22.5684 | 22.5632 | 22.5589 | 22.5547 | 22.5484 | 22.5179 | 22.4305 | 22.3032 | 23.2663 | 23.2642 | 23.2632 | 23.2611 | 23.2589 | 23.2516 | 23.2442 | 23.2368 | 23.2316 | 23.2263 | 23.1516 | 23.0337 | 22.9011
| THURSO | HASTIGROW | MINIMUM HEADROOM | ND 26576 60773 | YES | YES | 0 | 3.2038 | 3.1396 | 3.0154 | 2.8817 | 2.7469 | 2.1691 | -0.91832 | -4.0488 | -7.072 | -10.1088 | -17.6752 | -23.0667 | -26.2752 | 2.7775 | 2.6754 | 2.5512 | 2.4091 | 2.2648 | 1.7933 | -1.0752 | -4.0667 | -6.9731 | -9.8867 | -17.0815 | -22.8152 | -26.072 | 2.8027 | 2.6764 | 2.5227 | 2.3712 | 2.2217 | 1.6385 | -1.4267 | -4.5562 | -7.5794 | -10.6162 | -18.552 | -24.6741 | -28.0141
|  | HASTIGROW | EE |  |  |  |  | 3.2322 | 3.1817 | 3.0891 | 2.9638 | 2.8364 | 2.1891 | -0.91832 | -4.0488 | -7.072 | -10.1088 | -17.6752 | -22.0057 | -25.7509 | 2.8227 | 2.7459 | 2.6312 | 2.5133 | 2.3954 | 1.8806 | -1.0752 | -4.0667 | -6.9731 | -9.8867 | -17.0815 | -21.3646 | -25.3036 | 2.8617 | 2.7638 | 2.6217 | 2.4785 | 2.3375 | 1.6827 | -1.4267 | -4.5562 | -7.5794 | -10.6162 | -18.552 | -23.3562 | -27.5562
|  | HASTIGROW | HT |  |  |  |  | 3.2038 | 3.1396 | 3.0154 | 2.8817 | 2.7469 | 2.1691 | -0.74042 | -3.6541 | -6.0941 | -8.6488 | -15.4562 | -23.0667 | -26.0015 | 2.7775 | 2.6754 | 2.5512 | 2.4091 | 2.2648 | 1.7933 | -1.0067 | -3.8215 | -6.2678 | -8.8583 | -15.632 | -22.8152 | -26.072 | 2.8027 | 2.6764 | 2.5227 | 2.3712 | 2.2217 | 1.6385 | -1.2762 | -4.1952 | -6.6436 | -9.2383 | -16.5057 | -24.6741 | -28.0141
|  | HASTIGROW | HE |  |  |  |  | 3.2701 | 3.2375 | 3.1954 | 3.1491 | 3.1006 | 2.448 | 1.8175 | 1.1343 | -1.8709 | -5.0625 | -15.7794 | -21.6552 | -26.2752 | 2.8838 | 2.8364 | 2.7838 | 2.7238 | 2.6617 | 2.1333 | 1.6238 | 1.0143 | -1.9109 | -5.0594 | -15.5225 | -20.9657 | -25.4141 | 2.8027 | 2.6764 | 2.5227 | 2.3712 | 2.2217 | 1.6385 | -1.2762 | -4.1952 | -6.6436 | -9.2383 | -16.5057 | -24.6741 | -28.0141
|  | HASTIGROW | CF |  |  |  |  | 3.2912 | 3.2733 | 3.2491 | 3.2248 | 3.1996 | 2.9869 | 2.7659 | 2.5069 | 2.1859 | 1.8312 | 0.043789 | -4.3994 | -7.0973 | 2.9164 | 2.8891 | 2.8585 | 2.8269 | 2.7922 | 2.5869 | 2.4038 | 2.1922 | 1.8838 | 1.5006 | -0.252 | -4.2499 | -7.0678 | 2.9838 | 2.9491 | 2.9048 | 2.8638 | 2.8206 | 2.5564 | 2.3217 | 2.0417 | 1.6585 | 1.2522 | -0.71305 | -5.4267 | -8.4478
| STRICHEN | HATTON | MINIMUM HEADROOM | NK 06441 37348 | NO | YES | 0.16 | 6.1 | 5.9874 | 5.8053 | 5.5926 | 5.3737 | 4.6337 | 3.6379 | 2.5705 | 1.6905 | 0.76421 | -7.4653 | -15.2295 | -20.7726 | 5.6621 | 5.54 | 5.3474 | 5.1147 | 4.8726 | 4.2379 | 3.4274 | 2.5168 | 1.7358 | 0.94737 | -6.4358 | -13.9147 | -19.9211 | 5.7874 | 5.6663 | 5.4674 | 5.2295 | 4.9832 | 4.2274 | 3.2305 | 2.1242 | 1.2221 | 0.26316 | -8.3989 | -16.8453 | -23.1358
|  | HATTON | EE |  |  |  |  | 6.1337 | 6.0558 | 5.9063 | 5.7053 | 5.4926 | 4.6558 | 3.6379 | 2.5705 | 1.6905 | 0.76421 | -7.4653 | -15.2295 | -20.7726 | 5.6979 | 5.6137 | 5.4695 | 5.2568 | 5.0305 | 4.3242 | 3.4474 | 2.5168 | 1.7663 | 0.96421 | -6.4358 | -13.9147 | -19.9211 | 5.8232 | 5.7389 | 5.5842 | 5.3632 | 5.1274 | 4.2811 | 3.2305 | 2.1242 | 1.2221 | 0.26316 | -8.3989 | -16.8453 | -23.1358
|  | HATTON | HT |  |  |  |  | 6.1 | 5.9874 | 5.8053 | 5.5926 | 5.3737 | 4.6337 | 3.7663 | 2.8663 | 1.92 | 1.0179 | -6.5989 | -13.3305 | -17.8905 | 5.6621 | 5.54 | 5.3474 | 5.1147 | 4.8726 | 4.2379 | 3.4274 | 2.5832 | 1.7358 | 0.94737 | -6.1726 | -13.4874 | -18.5621 | 5.7874 | 5.6663 | 5.4674 | 5.2295 | 4.9832 | 4.2274 | 3.3053 | 2.3453 | 1.3537 | 0.42 | -7.7326 | -15.4358 | -20.6916
|  | HATTON | HE |  |  |  |  | 6.1779 | 6.1305 | 6.0621 | 5.9705 | 5.8463 | 4.9916 | 4.2063 | 3.3842 | 2.6389 | 1.6411 | -4.2568 | -10.1316 | -16.5042 | 5.7421 | 5.6905 | 5.6211 | 5.5221 | 5.3832 | 4.6747 | 3.9884 | 3.2537 | 2.6137 | 1.6579 | -3.8305 | -9.7316 | -16.1884 | 5.7874 | 5.6663 | 5.4674 | 5.2295 | 4.9832 | 4.2274 | 3.3053 | 2.3453 | 1.3537 | 0.42 | -7.7326 | -15.4358 | -20.6916
|  | HATTON | CF |  |  |  |  | 6.2042 | 6.18 | 6.1484 | 6.1126 | 6.0768 | 5.7779 | 5.4737 | 5.1526 | 4.8232 | 4.3137 | 1.8684 | -1.8221 | -5.7779 | 5.7674 | 5.7442 | 5.7137 | 5.6789 | 5.6442 | 5.4053 | 5.1432 | 4.8558 | 4.5432 | 3.98 | 1.5053 | -2.2505 | -6.5232 | 5.8926 | 5.8695 | 5.8368 | 5.8011 | 5.7632 | 5.4768 | 5.1632 | 4.8263 | 4.4726 | 3.8747 | 1.1411 | -2.9642 | -7.4884
| PERSLEY | HAUDAGAIN | MINIMUM HEADROOM | NJ 91425 09066 | NO | NO | 0.073 | 21.3417 | 21.1996 | 21.0502 | 20.8996 | 20.7438 | 20.5628 | 20.3849 | 20.2112 | 20.0186 | 19.7586 | 18.7259 | 17.847 | 17.027 | 19.7586 | 19.6165 | 19.4702 | 19.3175 | 19.0481 | 18.7638 | 18.4817 | 18.2081 | 17.9375 | 17.6659 | 16.5681 | 15.6144 | 14.7007 | 20.2007 | 19.9996 | 19.7954 | 19.5881 | 19.3807 | 19.1512 | 18.9249 | 18.7038 | 18.4849 | 18.2691 | 17.4428 | 16.4891 | 15.5733
|  | HAUDAGAIN | EE |  |  |  |  | 21.4007 | 21.2975 | 21.1817 | 21.0596 | 20.9312 | 20.7859 | 20.6417 | 20.4986 | 20.3617 | 20.2302 | 19.4186 | 18.6881 | 18.1028 | 19.8207 | 19.7123 | 19.5996 | 19.4786 | 19.3533 | 19.1712 | 18.9449 | 18.7228 | 18.5091 | 18.3017 | 17.3375 | 16.5723 | 15.927 | 20.2912 | 20.1386 | 19.9796 | 19.8154 | 19.6438 | 19.4586 | 19.2754 | 19.0933 | 18.9186 | 18.7502 | 17.9891 | 17.4144 | 16.7596
|  | HAUDAGAIN | HT |  |  |  |  | 21.3417 | 21.1996 | 21.0502 | 20.8996 | 20.7438 | 20.5628 | 20.3849 | 20.2112 | 20.0186 | 19.7586 | 18.7259 | 17.847 | 17.027 | 19.7586 | 19.6165 | 19.4702 | 19.3175 | 19.0481 | 18.7638 | 18.4817 | 18.2081 | 17.9375 | 17.6659 | 16.5681 | 15.6144 | 14.7007 | 20.2007 | 19.9996 | 19.7954 | 19.5881 | 19.3807 | 19.1512 | 18.9249 | 18.7038 | 18.4849 | 18.2691 | 17.4428 | 16.4891 | 15.5733
|  | HAUDAGAIN | HE |  |  |  |  | 21.4554 | 21.3765 | 21.2902 | 21.1954 | 21.0912 | 20.9659 | 20.8491 | 20.7375 | 20.6291 | 20.5312 | 20.1659 | 19.9396 | 19.6859 | 19.8807 | 19.7986 | 19.7091 | 19.6112 | 19.5081 | 19.3923 | 19.2849 | 19.1807 | 19.0817 | 18.9912 | 18.4123 | 17.9933 | 17.6565 | 20.2007 | 19.9996 | 19.7954 | 19.5881 | 19.3807 | 19.1512 | 18.9249 | 18.7038 | 18.4849 | 18.2691 | 17.4428 | 16.4891 | 15.5733
|  | HAUDAGAIN | CF |  |  |  |  | 21.4849 | 21.4312 | 21.3754 | 21.3186 | 21.2596 | 21.1933 | 21.1259 | 21.0575 | 20.9902 | 20.9238 | 20.6259 | 20.447 | 20.3417 | 19.9133 | 19.8575 | 19.7996 | 19.7396 | 19.6796 | 19.6133 | 19.5491 | 19.4828 | 19.4196 | 19.3554 | 19.0165 | 18.6481 | 18.3638 | 20.427 | 20.3723 | 20.2944 | 20.2154 | 20.1333 | 20.0449 | 19.9575 | 19.8691 | 19.7817 | 19.6944 | 19.2965 | 19.027 | 18.8386
| WILLOWDALE | HAYTON | MINIMUM HEADROOM | NJ 92753 08909 | NO | YES | 0 | 22.21 | 22.1142 | 22.1037 | 22.1026 | 22.0311 | 21.9479 | 21.5511 | 21.4616 | 21.3732 | 20.9689 | 19.9458 | 19.3037 | 18.6963 | 21.5821 | 21.4821 | 21.4747 | 21.4747 | 21.4011 | 21.3211 | 20.9137 | 20.8011 | 20.5821 | 20.3137 | 19.3263 | 18.6326 | 17.9642 | 21.5382 | 21.4371 | 21.4245 | 21.5161 | 21.4718 | 21.3687 | 21.2413 | 21.1129 | 20.9687 | 20.5045 | 19.3845 | 18.6866 | 18.0192
|  | HAYTON | EE |  |  |  |  | 22.2542 | 22.1816 | 22.1037 | 22.2932 | 22.2079 | 22.1111 | 22.0153 | 21.9205 | 21.8311 | 21.7426 | 20.4205 | 19.89 | 19.4458 | 21.6284 | 21.5537 | 21.4747 | 21.7263 | 21.6389 | 21.5453 | 21.4537 | 21.36 | 21.2695 | 21.1789 | 19.8695 | 19.3147 | 18.8358 | 21.5845 | 21.5076 | 21.4245 | 21.7129 | 21.6224 | 21.5203 | 21.4213 | 21.3182 | 21.2192 | 21.1192 | 19.8908 | 19.3161 | 18.8266
|  | HAYTON | HT |  |  |  |  | 22.21 | 22.1142 | 22.2847 | 22.1858 | 22.0826 | 21.9626 | 21.8447 | 21.7289 | 21.3868 | 20.9689 | 19.9458 | 19.3037 | 18.6963 | 21.5821 | 21.4821 | 21.7137 | 21.6116 | 21.5021 | 21.3832 | 21.2621 | 21.1389 | 20.9095 | 20.4442 | 19.3263 | 18.6326 | 17.9642 | 21.5382 | 21.4371 | 21.7076 | 21.6024 | 21.4929 | 21.3687 | 21.2413 | 21.1129 | 20.9687 | 20.5045 | 19.3845 | 18.6866 | 18.0192
|  | HAYTON | HE |  |  |  |  | 22.2879 | 22.2311 | 22.1689 | 22.1026 | 22.0311 | 21.9479 | 21.5511 | 21.4616 | 21.3732 | 21.2258 | 20.3826 | 19.9584 | 19.7226 | 21.6642 | 21.6063 | 21.5421 | 21.4747 | 21.4011 | 21.3211 | 20.9137 | 20.8011 | 20.5821 | 20.3137 | 19.3811 | 18.9211 | 18.6779 | 21.5382 | 21.4371 | 21.7076 | 21.6024 | 21.4929 | 21.3687 | 21.2413 | 21.1129 | 20.9687 | 20.5045 | 19.3845 | 18.6866 | 18.0192
|  | HAYTON | CF |  |  |  |  | 22.3068 | 22.2679 | 22.2279 | 22.1858 | 22.1437 | 22.0974 | 22.0511 | 22.0047 | 21.9574 | 21.9142 | 21.6553 | 21.1942 | 21.0047 | 21.6832 | 21.6442 | 21.6021 | 21.56 | 21.5168 | 21.4695 | 21.4242 | 21.3779 | 21.3305 | 21.2842 | 21.0189 | 20.5053 | 20.2979 | 21.6403 | 21.6003 | 21.5582 | 21.5161 | 21.4718 | 21.4234 | 21.375 | 21.3287 | 21.2782 | 21.2297 | 20.9992 | 20.4866 | 20.2761
| BRORA | HELMSDALE | MINIMUM HEADROOM | ND 02372 15376 | YES | YES | 0 | 1.6089 | 1.5795 | 1.5363 | 1.4847 | 1.43 | 1.0984 | 0.67947 | 0.21842 | -0.22263 | -0.89632 | -4.8121 | -9.4216 | -13.0574 | 1.4068 | 1.3647 | 1.3153 | 1.2616 | 1.2121 | 0.97421 | 0.58789 | 0.15421 | -0.25421 | -0.92579 | -4.61 | -9.4311 | -13.1321 | 1.4342 | 1.3963 | 1.3405 | 1.2847 | 1.2216 | 0.85947 | 0.42789 | -0.037368 | -0.44474 | -0.96684 | -5.3753 | -10.4616 | -14.6616
|  | HELMSDALE | EE |  |  |  |  | 1.6205 | 1.5911 | 1.5395 | 1.4847 | 1.43 | 1.0984 | 0.67947 | 0.21842 | -0.18474 | -0.64895 | -4.8121 | -9.4216 | -13.0574 | 1.4237 | 1.3868 | 1.3332 | 1.2784 | 1.2226 | 0.98789 | 0.65 | 0.27316 | -0.059474 | -0.45947 | -4.5584 | -9.1426 | -13.1321 | 1.45 | 1.4142 | 1.35 | 1.2858 | 1.2216 | 0.85947 | 0.42789 | -0.037368 | -0.44474 | -0.90053 | -5.3753 | -10.4616 | -14.6616
|  | HELMSDALE | HT |  |  |  |  | 1.6089 | 1.5795 | 1.5363 | 1.49 | 1.4447 | 1.1289 | 0.80263 | 0.46368 | 0.09 | -0.72053 | -4.4816 | -8.8563 | -11.89 | 1.4068 | 1.3647 | 1.3153 | 1.2616 | 1.2121 | 0.97421 | 0.69737 | 0.40684 | 0.098421 | -0.71526 | -4.61 | -9.4311 | -12.8668 | 1.4342 | 1.3963 | 1.3405 | 1.2847 | 1.2311 | 0.90684 | 0.58053 | 0.24368 | -0.13316 | -0.96684 | -5.1921 | -10.2237 | -13.7289
|  | HELMSDALE | HE |  |  |  |  | 1.6332 | 1.6195 | 1.5984 | 1.5763 | 1.5542 | 1.15 | 0.69421 | 0.22368 | -0.22263 | -0.89632 | -3.7395 | -7.3195 | -11.2563 | 1.45 | 1.4279 | 1.4026 | 1.3763 | 1.3511 | 1.0089 | 0.58789 | 0.15421 | -0.25421 | -0.92579 | -3.7216 | -7.4184 | -11.4995 | 1.4342 | 1.3963 | 1.3405 | 1.2847 | 1.2311 | 0.90684 | 0.58053 | 0.24368 | -0.13316 | -0.96684 | -5.1921 | -10.2237 | -13.7289
|  | HELMSDALE | CF |  |  |  |  | 1.6405 | 1.6342 | 1.6226 | 1.6121 | 1.6005 | 1.4795 | 1.3721 | 1.1216 | 0.83 | 0.49842 | -0.97947 | -3.2342 | -5.7953 | 1.4626 | 1.45 | 1.4353 | 1.4205 | 1.4058 | 1.3174 | 1.2353 | 0.96684 | 0.66263 | 0.30263 | -1.2132 | -3.5595 | -6.37 | 1.4847 | 1.4732 | 1.4574 | 1.4426 | 1.4279 | 1.2837 | 1.1553 | 0.90895 | 0.65 | 0.26684 | -1.3889 | -3.9374 | -6.87
| INVERNESS | HILTON | MINIMUM HEADROOM | NH 67326 43262 | NO | YES | 0.055 | 25.5218 | 24.9629 | 24.4134 | 23.8692 | 23.3071 | 22.6797 | 22.0776 | 21.5176 | 20.9903 | 20.4913 | 18.1345 | 16.2587 | 14.6661 | 23.9903 | 23.4313 | 22.845 | 22.2661 | 21.6661 | 20.9997 | 20.3597 | 19.7682 | 19.2124 | 18.6871 | 16.1397 | 14.0776 | 12.3039 | 24.7239 | 24.4261 | 23.9829 | 23.4061 | 22.8082 | 22.1418 | 21.5018 | 20.9092 | 20.3513 | 19.8239 | 17.2745 | 15.2208 | 13.4376
|  | HILTON | EE |  |  |  |  | 25.6818 | 25.3071 | 24.8945 | 24.4566 | 23.9903 | 23.5071 | 23.0408 | 22.5903 | 22.1587 | 21.7513 | 19.8397 | 18.3492 | 17.165 | 24.1092 | 23.8008 | 23.3629 | 22.8987 | 22.4018 | 21.8913 | 21.4018 | 20.9271 | 20.4724 | 20.0439 | 18.0124 | 16.405 | 15.0924 | 24.8397 | 24.6039 | 24.3555 | 24.0324 | 23.5408 | 23.0292 | 22.5355 | 22.0587 | 21.6018 | 21.1692 | 19.1239 | 17.5008 | 16.1966
|  | HILTON | HT |  |  |  |  | 25.5218 | 24.9629 | 24.4134 | 23.8692 | 23.3071 | 22.6797 | 22.0776 | 21.5176 | 20.9903 | 20.4913 | 18.1345 | 16.2587 | 14.6661 | 23.9903 | 23.4313 | 22.845 | 22.2661 | 21.6661 | 20.9997 | 20.3597 | 19.7682 | 19.2124 | 18.6871 | 16.1397 | 14.0776 | 12.3039 | 24.7239 | 24.4261 | 23.9829 | 23.4061 | 22.8082 | 22.1418 | 21.5018 | 20.9092 | 20.3513 | 19.8239 | 17.2745 | 15.2208 | 13.4376
|  | HILTON | HE |  |  |  |  | 25.8429 | 25.5618 | 25.265 | 24.9429 | 24.5913 | 24.2187 | 24.0029 | 23.7903 | 23.5892 | 23.3471 | 22.3597 | 21.705 | 21.1471 | 24.2703 | 24.0587 | 23.7439 | 23.4008 | 23.0271 | 22.6355 | 22.4218 | 22.2113 | 22.0134 | 21.7639 | 20.7334 | 20.0429 | 19.445 | 24.7239 | 24.4261 | 23.9829 | 23.4061 | 22.8082 | 22.1418 | 21.5018 | 20.9092 | 20.3513 | 19.8239 | 17.2745 | 15.2208 | 13.4376
|  | HILTON | CF |  |  |  |  | 26.0155 | 25.8892 | 25.7587 | 25.6229 | 25.4861 | 25.3145 | 25.1103 | 24.9208 | 24.7197 | 24.5271 | 23.6661 | 23.0829 | 22.6524 | 24.3608 | 24.2629 | 24.1618 | 24.0566 | 23.9503 | 23.8155 | 23.5997 | 23.3987 | 23.185 | 22.9808 | 22.0671 | 21.4429 | 20.9713 | 25.085 | 24.9892 | 24.8903 | 24.7871 | 24.6818 | 24.5734 | 24.4618 | 24.3503 | 24.2408 | 24.1029 | 23.1945 | 22.565 | 22.0903
| ARBROATH | HUME STREET | MINIMUM HEADROOM | NO 64067 41180 | NO | YES | 0.285 | 24.455 | 24.3255 | 24.1855 | 24.0445 | 23.8992 | 23.6687 | 23.4424 | 23.2192 | 22.9845 | 22.7518 | 21.2518 | 20.2961 | 19.6708 | 23.5329 | 23.2329 | 22.9739 | 22.7139 | 22.455 | 22.1318 | 21.8171 | 21.5076 | 21.1876 | 20.8687 | 19.0613 | 18.0687 | 17.3939 | 24.3413 | 24.1918 | 23.9297 | 23.6676 | 23.4066 | 23.0645 | 22.7308 | 22.4003 | 22.0592 | 21.7171 | 19.8097 | 18.7592 | 18.0582
|  | HUME STREET | EE |  |  |  |  | 24.5108 | 24.4097 | 24.2961 | 24.1782 | 24.0539 | 23.8403 | 23.6118 | 23.3813 | 23.1729 | 22.9655 | 21.975 | 20.7403 | 20.0139 | 23.6529 | 23.4129 | 23.2066 | 22.9992 | 22.7866 | 22.5055 | 22.215 | 21.9255 | 21.655 | 21.3908 | 20.0718 | 18.9003 | 18.1318 | 24.3971 | 24.2961 | 24.1634 | 23.9539 | 23.7382 | 23.435 | 23.1171 | 22.7982 | 22.5045 | 22.215 | 20.7592 | 19.4424 | 18.6255
|  | HUME STREET | HT |  |  |  |  | 24.455 | 24.3255 | 24.1855 | 24.0445 | 23.8992 | 23.6687 | 23.4424 | 23.2192 | 22.9845 | 22.7518 | 21.2518 | 20.2961 | 19.6708 | 23.5329 | 23.2329 | 22.9739 | 22.7139 | 22.455 | 22.1318 | 21.8171 | 21.5076 | 21.1876 | 20.8687 | 19.0613 | 18.0687 | 17.3939 | 24.3413 | 24.1918 | 23.9297 | 23.6676 | 23.4066 | 23.0645 | 22.7308 | 22.4003 | 22.0592 | 21.7171 | 19.8097 | 18.7592 | 18.0582
|  | HUME STREET | HE |  |  |  |  | 24.5655 | 24.4897 | 24.4034 | 24.3129 | 24.2139 | 24.0118 | 23.8339 | 23.6582 | 23.4887 | 23.3266 | 22.6645 | 22.1592 | 21.3739 | 23.7403 | 23.6182 | 23.4782 | 23.335 | 23.1834 | 22.9508 | 22.7403 | 22.5339 | 22.3361 | 22.1466 | 21.3361 | 20.2718 | 19.5224 | 24.3413 | 24.1918 | 23.9297 | 23.6676 | 23.4066 | 23.0645 | 22.7308 | 22.4003 | 22.0592 | 21.7171 | 19.8097 | 18.7592 | 18.0582
|  | HUME STREET | CF |  |  |  |  | 24.5961 | 24.5455 | 24.4918 | 24.4361 | 24.3803 | 24.2866 | 24.1971 | 24.1087 | 24.0234 | 23.9466 | 23.5518 | 23.2129 | 22.9961 | 23.7708 | 23.7203 | 23.6676 | 23.6118 | 23.555 | 23.4297 | 23.3066 | 23.1834 | 23.0634 | 22.9508 | 22.3866 | 21.8939 | 21.5224 | 24.4824 | 24.4318 | 24.3782 | 24.3224 | 24.2666 | 24.1771 | 24.0908 | 24.0055 | 23.9245 | 23.8487 | 23.2718 | 22.7234 | 22.315
| KEITH 2 | HUNTLY | MINIMUM HEADROOM | NJ 52762 39217 | NO | YES | 0.05 | 15.1421 | 15.0453 | 14.8937 | 14.7442 | 14.3568 | 13.9137 | 12.8642 | 11.6305 | 10.8274 | 9.8947 | -0.10842 | -13.6863 | -21.2105 | 13.3889 | 13.1921 | 12.9068 | 12.4595 | 11.9258 | 11.4195 | 10.6489 | 10.2405 | 9.3774 | 8.0289 | -1.8153 | -15.9732 | -24.3037 | 14.1755 | 13.9934 | 13.7145 | 13.2955 | 12.8018 | 12.3324 | 11.2903 | 10.1124 | 9.2692 | 8.2997 | -2.4887 | -17.7845 | -26.3687
|  | HUNTLY | EE |  |  |  |  | 15.18 | 15.1021 | 14.9421 | 14.7779 | 14.5726 | 14.1463 | 12.8642 | 12.6989 | 11.2842 | 9.8947 | -0.10842 | -11.8642 | -21.2105 | 13.4753 | 13.3247 | 13.0953 | 12.6963 | 12.2247 | 11.7511 | 10.7216 | 10.5332 | 9.4311 | 8.3784 | -1.3121 | -12.8858 | -22.8847 | 14.2461 | 14.1155 | 13.8734 | 13.4871 | 13.0376 | 12.5861 | 11.2903 | 11.1176 | 9.6934 | 8.2997 | -2.4887 | -15.3308 | -25.8224
|  | HUNTLY | HT |  |  |  |  | 15.1421 | 15.0453 | 14.8937 | 14.7442 | 14.3568 | 13.9137 | 12.9779 | 12.7958 | 11.4326 | 9.9337 | 0.29684 | -13.6863 | -21.1779 | 13.3889 | 13.1921 | 12.9068 | 12.4595 | 11.9258 | 11.4195 | 10.6489 | 10.4458 | 9.3774 | 8.1479 | -1.8153 | -15.9732 | -24.3037 | 14.1755 | 13.9934 | 13.7145 | 13.2955 | 12.8018 | 12.3324 | 11.3839 | 11.1945 | 9.8218 | 8.3029 | -2.3634 | -17.7845 | -26.3687
|  | HUNTLY | HE |  |  |  |  | 15.2326 | 15.18 | 15.1084 | 15.0305 | 14.9474 | 14.7453 | 13.5853 | 13.3937 | 11.9484 | 10.0168 | 2.6063 | -8.8 | -19.7274 | 13.5942 | 13.4995 | 13.3458 | 13.0679 | 12.6963 | 12.3184 | 11.3953 | 11.1668 | 9.9121 | 8.0289 | 0.78158 | -10.2963 | -21.1489 | 14.1755 | 13.9934 | 13.7145 | 13.2955 | 12.8018 | 12.3324 | 11.3839 | 11.1945 | 9.8218 | 8.3029 | -2.3634 | -17.7845 | -26.3687
|  | HUNTLY | CF |  |  |  |  | 15.2611 | 15.2305 | 15.1853 | 15.1421 | 15.0958 | 15.0516 | 14.6947 | 11.6305 | 10.8274 | 9.9821 | 6.4421 | 0.29368 | -6.4074 | 13.6511 | 13.5921 | 13.5184 | 13.4416 | 13.3605 | 13.2795 | 12.9142 | 10.2405 | 9.4132 | 8.4732 | 4.7342 | -1.57 | -8.6426 | 14.3766 | 14.3324 | 14.2703 | 14.205 | 14.1355 | 14.0555 | 13.6029 | 10.1124 | 9.2692 | 8.3661 | 4.4882 | -2.4003 | -9.8824
| BRIDGE OF DUN | INCHBARE | MINIMUM HEADROOM | NO 60684 65379 | YES | YES | 0 | 2.7726 | 2.7621 | 2.7253 | 2.6832 | 2.6442 | 2.2347 | 1.7305 | 1.2179 | 0.72737 | 0.025263 | -4.1863 | -9.0537 | -12.6095 | 2.6811 | 2.6621 | 2.6284 | 2.5958 | 2.5589 | 2.1832 | 1.7284 | 1.2621 | 0.81789 | 0.14 | -3.7011 | -8.3758 | -12.1653 | 2.7084 | 2.6905 | 2.6516 | 2.6032 | 2.5568 | 2.1358 | 1.6305 | 1.1116 | 0.66526 | 0.035789 | -4.6674 | -9.9432 | -13.9863
|  | INCHBARE | EE |  |  |  |  | 2.7768 | 2.7653 | 2.7253 | 2.6832 | 2.6442 | 2.24 | 1.7379 | 1.2221 | 0.77895 | 0.15789 | -4.1863 | -9.0537 | -12.6095 | 2.6895 | 2.6726 | 2.6358 | 2.5979 | 2.5589 | 2.2232 | 1.8232 | 1.4095 | 1.0547 | 0.48 | -3.7011 | -8.3758 | -12.1653 | 2.7168 | 2.7 | 2.6516 | 2.6032 | 2.5568 | 2.1358 | 1.6305 | 1.1116 | 0.66526 | 0.035789 | -4.6674 | -9.9432 | -13.9863
|  | INCHBARE | HT |  |  |  |  | 2.7726 | 2.7621 | 2.7316 | 2.7032 | 2.6716 | 2.3347 | 1.9916 | 1.5832 | 1.0642 | 0.24316 | -3.6105 | -7.8874 | -10.7579 | 2.6811 | 2.6621 | 2.6284 | 2.5958 | 2.56 | 2.2863 | 2.0095 | 1.6516 | 1.1926 | 0.38 | -3.4611 | -8.0537 | -11.2789 | 2.7084 | 2.6905 | 2.6516 | 2.6137 | 2.5737 | 2.2284 | 1.8832 | 1.4705 | 0.94947 | 0.064211 | -4.1968 | -9.0516 | -12.3589
|  | INCHBARE | HE |  |  |  |  | 2.7832 | 2.7768 | 2.7653 | 2.7537 | 2.7389 | 2.2347 | 1.7305 | 1.2179 | 0.72737 | 0.025263 | -3.0021 | -6.7126 | -10.7568 | 2.7021 | 2.6926 | 2.68 | 2.6663 | 2.6516 | 2.1832 | 1.7284 | 1.2621 | 0.81789 | 0.14 | -2.7295 | -6.4368 | -10.5 | 2.7084 | 2.6905 | 2.6516 | 2.6137 | 2.5737 | 2.2284 | 1.8832 | 1.4705 | 0.94947 | 0.064211 | -4.1968 | -9.0516 | -12.3589
|  | INCHBARE | CF |  |  |  |  | 2.7863 | 2.7842 | 2.7768 | 2.7684 | 2.76 | 2.6095 | 2.4779 | 2.1947 | 1.8968 | 1.5663 | 0.04 | -2.2884 | -4.8263 | 2.7074 | 2.7032 | 2.6947 | 2.6853 | 2.6768 | 2.5484 | 2.4305 | 2.1337 | 1.8389 | 1.5 | -0.014737 | -2.3568 | -5.0716 | 2.7337 | 2.7295 | 2.72 | 2.7084 | 2.6979 | 2.5295 | 2.3821 | 2.0884 | 1.7716 | 1.3968 | -0.28 | -2.8568 | -5.7232
| DUNOON | INNELLAN | MINIMUM HEADROOM | NS 15129 70875 | YES | YES | 0 | 2.7558 | 2.7021 | 2.6389 | 2.5758 | 2.4958 | 2.3316 | 2.1505 | 1.9516 | 1.7558 | 1.5716 | 0.70526 | -0.11895 | -0.43579 | 2.6547 | 2.5989 | 2.5305 | 2.4632 | 2.3768 | 2.2284 | 2.06 | 1.8811 | 1.6853 | 1.5211 | 0.82316 | 0.12947 | -0.14842 | 2.5968 | 2.54 | 2.4737 | 2.4063 | 2.32 | 2.1547 | 1.9705 | 1.7779 | 1.5632 | 1.3705 | 0.49474 | -0.34526 | -0.67474
|  | INNELLAN | EE |  |  |  |  | 2.7779 | 2.7347 | 2.6853 | 2.6284 | 2.5589 | 2.3853 | 2.1505 | 1.9516 | 1.7684 | 1.5832 | 0.70526 | -0.11895 | -0.43579 | 2.6789 | 2.6347 | 2.5842 | 2.5253 | 2.4537 | 2.2989 | 2.0821 | 1.9116 | 1.7484 | 1.5821 | 0.82316 | 0.12947 | -0.14842 | 2.62 | 2.5747 | 2.5242 | 2.4621 | 2.3895 | 2.2147 | 1.9747 | 1.7789 | 1.5895 | 1.3947 | 0.49474 | -0.34526 | -0.67474
|  | INNELLAN | HT |  |  |  |  | 2.7558 | 2.7021 | 2.6389 | 2.5758 | 2.4958 | 2.3316 | 2.1516 | 1.9642 | 1.7558 | 1.5716 | 0.95368 | 0.53895 | 0.30842 | 2.6547 | 2.5989 | 2.5305 | 2.4632 | 2.3768 | 2.2284 | 2.06 | 1.8811 | 1.6853 | 1.5211 | 0.98632 | 0.61368 | 0.39579 | 2.5968 | 2.54 | 2.4737 | 2.4063 | 2.32 | 2.1547 | 1.9705 | 1.7779 | 1.5632 | 1.3705 | 0.73474 | 0.30316 | 0.06
|  | INNELLAN | HE |  |  |  |  | 2.8105 | 2.7842 | 2.7495 | 2.7137 | 2.6621 | 2.4821 | 2.28 | 2.1084 | 1.9611 | 1.8221 | 1.2632 | 0.76737 | 0.25158 | 2.7158 | 2.6874 | 2.6505 | 2.6126 | 2.5558 | 2.3979 | 2.2063 | 2.0463 | 1.9147 | 1.7958 | 1.3242 | 0.90842 | 0.48211 | 2.5968 | 2.54 | 2.4737 | 2.4063 | 2.32 | 2.1547 | 1.9705 | 1.7779 | 1.5632 | 1.3705 | 0.73474 | 0.30316 | 0.06
|  | INNELLAN | CF |  |  |  |  | 2.8263 | 2.8084 | 2.7916 | 2.7716 | 2.7537 | 2.6884 | 2.6211 | 2.5474 | 2.4789 | 2.4126 | 2.1021 | 1.7884 | 1.5632 | 2.7316 | 2.7137 | 2.6947 | 2.6758 | 2.6558 | 2.6 | 2.5379 | 2.4674 | 2.4021 | 2.3347 | 2.0526 | 1.7874 | 1.5947 | 2.6716 | 2.6537 | 2.6347 | 2.6158 | 2.5947 | 2.5305 | 2.4621 | 2.3863 | 2.3147 | 2.2453 | 1.9337 | 1.6147 | 1.3842
| KEITH 2 | INSCH | MINIMUM HEADROOM | NJ 63100 28651 | NO | YES | 0 | 8.6961 | 8.4297 | 15.3753 | 15.0195 | 14.7353 | 13.6468 | 12.5489 | 11.2689 | 10.17 | 9.1089 | 0.56368 | -8.8658 | -15.1037 | 6.4179 | 6.1137 | 12.6537 | 12.2716 | 11.9758 | 10.9916 | 10.1716 | 9.0916 | 8.1621 | 7.2853 | -0.61053 | -10.8526 | -16.9284 | 6.7443 | 6.4412 | 13.1582 | 12.7676 | 12.4613 | 11.3097 | 10.2255 | 8.9445 | 7.8287 | 6.7613 | -2.3103 | -13.0808 | -19.6755
|  | INSCH | EE |  |  |  |  | 8.7939 | 8.6013 | 15.5805 | 15.2658 | 14.9521 | 13.8195 | 12.5489 | 11.2689 | 10.17 | 9.1089 | 0.56368 | -8.3226 | -15.1037 | 6.5284 | 6.3105 | 12.8937 | 12.5589 | 12.2337 | 11.2484 | 10.1716 | 9.0916 | 8.1621 | 7.2853 | -0.61053 | -9.1695 | -16.4705 | 6.8549 | 6.637 | 13.3929 | 13.0424 | 12.7013 | 11.5171 | 10.2255 | 8.9445 | 7.8287 | 6.7613 | -2.3103 | -11.9576 | -19.6755
|  | INSCH | HT |  |  |  |  | 8.6961 | 8.4297 | 15.3753 | 15.0195 | 14.7353 | 13.6468 | 12.7416 | 11.8237 | 10.7489 | 9.7416 | 1.8974 | -8.8658 | -14.3879 | 6.4179 | 6.1137 | 12.6537 | 12.2716 | 11.9758 | 10.9916 | 10.2074 | 9.4347 | 8.5263 | 7.6979 | -0.041053 | -10.8526 | -16.9284 | 6.7443 | 6.4412 | 13.1582 | 12.7676 | 12.4613 | 11.3097 | 10.3718 | 9.4466 | 8.3771 | 7.3824 | -1.205 | -13.0808 | -19.3934
|  | INSCH | HE |  |  |  |  | 8.9266 | 8.7982 | 15.8963 | 15.7047 | 15.4847 | 14.2405 | 13.2868 | 12.3511 | 11.4026 | 9.9216 | 3.5479 | -5.4321 | -13.4689 | 6.6789 | 6.5316 | 13.2316 | 13.0147 | 12.7653 | 11.6716 | 10.8537 | 10.0621 | 9.2537 | 7.8463 | 1.8726 | -6.6726 | -14.6758 | 6.7443 | 6.4412 | 13.1582 | 12.7676 | 12.4613 | 11.3097 | 10.3718 | 9.4466 | 8.3771 | 7.3824 | -1.205 | -13.0808 | -19.3934
|  | INSCH | CF |  |  |  |  | 8.9961 | 8.9255 | 16.1142 | 16.0132 | 15.9237 | 15.4921 | 15.0858 | 14.7079 | 14.1942 | 13.5384 | 10.3784 | 4.1711 | -0.70895 | 6.7568 | 6.6758 | 13.4811 | 13.3674 | 13.2684 | 12.9011 | 12.5389 | 12.2063 | 11.6947 | 11.0011 | 7.8768 | 2.0211 | -3.1389 | 7.0822 | 7.0022 | 13.9929 | 13.8771 | 13.775 | 13.3266 | 12.8992 | 12.5055 | 11.9318 | 11.1887 | 7.7318 | 1.0718 | -4.4503
| BURGHMUIR | INVERALMOND | MINIMUM HEADROOM | NO 08721 25807 | NO | YES | 0.11 | 24.4332 | 24.4332 | 24.1953 | 23.8668 | 23.4563 | 22.9689 | 22.4816 | 21.9921 | 21.5058 | 21.0174 | 18.53 | 15.9889 | 13.9879 | 22.8774 | 22.6353 | 22.3068 | 21.8911 | 21.3932 | 20.8058 | 20.2195 | 19.63 | 19.0437 | 18.4563 | 15.5216 | 12.5016 | 10.1542 | 23.8753 | 23.6679 | 23.3763 | 22.9921 | 22.5258 | 21.9468 | 21.3689 | 20.7889 | 20.2089 | 19.6311 | 16.7153 | 13.8837 | 11.5437
|  | INVERALMOND | EE |  |  |  |  | 24.4332 | 24.4332 | 24.1953 | 23.8668 | 23.4563 | 22.97 | 22.4816 | 21.9921 | 21.5058 | 21.0174 | 18.53 | 16.0868 | 14.0932 | 22.8784 | 22.6353 | 22.3068 | 21.8911 | 21.3932 | 20.8068 | 20.2195 | 19.63 | 19.0437 | 18.4563 | 15.5216 | 12.6847 | 10.3426 | 23.8763 | 23.6679 | 23.3763 | 22.9921 | 22.5258 | 21.9479 | 21.37 | 20.7889 | 20.2089 | 19.6311 | 16.7153 | 13.8837 | 11.5437
|  | INVERALMOND | HT |  |  |  |  | 24.4332 | 24.4332 | 24.1953 | 23.8679 | 23.4574 | 22.9689 | 22.4826 | 21.9953 | 21.5089 | 21.0216 | 18.5995 | 16.1111 | 14.1205 | 22.8774 | 22.6353 | 22.3068 | 21.8921 | 21.3942 | 20.8058 | 20.2195 | 19.6332 | 19.0458 | 18.4595 | 15.6279 | 12.7026 | 10.3616 | 23.8753 | 23.6679 | 23.3763 | 22.9932 | 22.5268 | 21.9468 | 21.3689 | 20.7921 | 20.2132 | 19.6353 | 16.83 | 13.9079 | 11.5711
|  | INVERALMOND | HE |  |  |  |  | 24.4332 | 24.4332 | 24.1953 | 23.8679 | 23.4574 | 22.9711 | 22.4826 | 21.9974 | 21.51 | 21.0237 | 18.5405 | 15.9889 | 13.9879 | 22.8784 | 22.6353 | 22.3068 | 21.8921 | 21.3942 | 20.8079 | 20.2205 | 19.6342 | 19.0479 | 18.4616 | 15.53 | 12.5016 | 10.1542 | 23.8753 | 23.6679 | 23.3763 | 22.9932 | 22.5268 | 21.9468 | 21.3689 | 20.7921 | 20.2132 | 19.6353 | 16.83 | 13.9079 | 11.5711
|  | INVERALMOND | CF |  |  |  |  | 24.4332 | 24.4332 | 24.4332 | 24.3311 | 24.1689 | 23.9826 | 23.7753 | 23.5395 | 23.2805 | 22.9984 | 21.4816 | 19.9489 | 18.7016 | 22.9374 | 22.8111 | 22.6574 | 22.4795 | 22.2732 | 22.0395 | 21.7795 | 21.4953 | 21.1816 | 20.8416 | 19.0132 | 17.1826 | 15.7163 | 23.91 | 23.8184 | 23.6879 | 23.5353 | 23.3458 | 23.1289 | 22.8879 | 22.6247 | 22.3174 | 21.9826 | 20.1795 | 18.3763 | 16.9132
| CLACHAN | INVERARAY | MINIMUM HEADROOM | NN 09172 09746 | YES | YES | 0.19 | 2.4732 | 2.4384 | 2.3984 | 2.3511 | 2.7963 | 2.7079 | 2.6195 | 2.5184 | 2.4205 | 2.2689 | 1.7226 | 0.77 | -0.011053 | 2.21 | 2.1774 | 2.1342 | 2.0837 | 2.5226 | 2.4447 | 2.3732 | 2.2974 | 2.1911 | 2.0447 | 1.53 | 0.49 | -0.26158 | 2.3532 | 2.3479 | 2.3353 | 2.2816 | 2.7195 | 2.6258 | 2.5374 | 2.4321 | 2.3184 | 2.1489 | 1.5584 | 0.46789 | -0.39737
|  | INVERARAY | EE |  |  |  |  | 2.4921 | 2.4679 | 2.4426 | 2.4058 | 2.8637 | 2.7563 | 2.6195 | 2.5184 | 2.4205 | 2.3058 | 1.7226 | 0.77 | -0.011053 | 2.2226 | 2.2068 | 2.1837 | 2.1447 | 2.5995 | 2.5058 | 2.3826 | 2.3005 | 2.2163 | 2.1142 | 1.5942 | 0.64053 | -0.23632 | 2.3553 | 2.3511 | 2.3426 | 2.3342 | 2.7974 | 2.6837 | 2.5374 | 2.4321 | 2.3258 | 2.2005 | 1.57 | 0.50579 | -0.39737
|  | INVERARAY | HT |  |  |  |  | 2.4732 | 2.4384 | 2.3984 | 2.3511 | 2.7963 | 2.7079 | 2.6258 | 2.5384 | 2.4216 | 2.2689 | 1.7353 | 0.79 | 0.13421 | 2.21 | 2.1774 | 2.1342 | 2.0837 | 2.5226 | 2.4447 | 2.3732 | 2.2974 | 2.1911 | 2.0447 | 1.53 | 0.49 | -0.26158 | 2.3532 | 2.3479 | 2.3353 | 2.2816 | 2.7195 | 2.6258 | 2.5395 | 2.4468 | 2.3184 | 2.1489 | 1.5584 | 0.46789 | -0.29632
|  | INVERARAY | HE |  |  |  |  | 2.4984 | 2.4763 | 2.4511 | 2.4163 | 2.8763 | 2.7679 | 2.6553 | 2.5626 | 2.4605 | 2.3405 | 1.9089 | 1.1542 | 0.33 | 2.2268 | 2.2132 | 2.1911 | 2.1542 | 2.6089 | 2.5142 | 2.4111 | 2.33 | 2.2374 | 2.1247 | 1.7353 | 0.95842 | 0.09 | 2.3532 | 2.3479 | 2.3353 | 2.2816 | 2.7195 | 2.6258 | 2.5395 | 2.4468 | 2.3184 | 2.1489 | 1.5584 | 0.46789 | -0.29632
|  | INVERARAY | CF |  |  |  |  | 2.5921 | 2.59 | 2.5868 | 2.5847 | 3.0826 | 3.0511 | 3.0142 | 2.9711 | 2.9342 | 2.8721 | 2.5584 | 2.0805 | 1.5311 | 2.3311 | 2.3279 | 2.3174 | 2.3079 | 2.7995 | 2.7721 | 2.7384 | 2.6995 | 2.6658 | 2.6005 | 2.2889 | 1.7963 | 1.1953 | 2.4742 | 2.4721 | 2.4689 | 2.4668 | 2.9647 | 2.9405 | 2.9205 | 2.9005 | 2.8837 | 2.8153 | 2.4658 | 1.9237 | 1.2911
| LUNANHEAD | INVERARITY | MINIMUM HEADROOM | NO 44549 44200 | YES | YES | 0 | 1.0116 | 1.0021 | 0.97789 | 0.94737 | 0.90947 | 0.56105 | 0.15263 | -0.26737 | -0.66632 | -1.2505 | -7.5516 | -11.5674 | -14.5589 | 0.97053 | 0.95368 | 0.92632 | 0.89684 | 0.86842 | 0.56737 | 0.19684 | -0.18526 | -0.54421 | -1.1189 | -6.5474 | -10.4568 | -13.7116 | 0.99368 | 0.97684 | 0.94632 | 0.91579 | 0.88 | 0.57895 | 0.18842 | -0.21579 | -0.56421 | -1.0979 | -7.9263 | -12.3074 | -15.7116
|  | INVERARITY | EE |  |  |  |  | 1.0147 | 1.0074 | 0.97789 | 0.94737 | 0.90947 | 0.58421 | 0.19474 | -0.20947 | -0.55368 | -1.0642 | -7.5516 | -11.5674 | -14.5589 | 0.97789 | 0.96526 | 0.93474 | 0.90211 | 0.86842 | 0.61474 | 0.31053 | -0.0042105 | -0.27263 | -0.74316 | -6.5474 | -10.4568 | -13.7116 | 1.0011 | 0.98842 | 0.95368 | 0.91684 | 0.88 | 0.57895 | 0.18842 | -0.21579 | -0.56421 | -1.0979 | -7.9263 | -12.3074 | -15.7116
|  | INVERARITY | HT |  |  |  |  | 1.0116 | 1.0021 | 0.97895 | 0.94737 | 0.91684 | 0.65158 | 0.63579 | 0.30526 | -0.11158 | -0.80737 | -6.3263 | -9.9653 | -12.4453 | 0.97053 | 0.95368 | 0.92632 | 0.89684 | 0.86947 | 0.65895 | 0.64211 | 0.35579 | -0.011579 | -0.70316 | -5.7884 | -9.7158 | -12.4863 | 0.99368 | 0.97684 | 0.94632 | 0.91579 | 0.88526 | 0.63895 | 0.62316 | 0.28526 | -0.15158 | -0.91579 | -6.7926 | -10.9316 | -13.7937
|  | INVERARITY | HE |  |  |  |  | 1.0189 | 1.0147 | 1.0053 | 0.99579 | 0.98526 | 0.56105 | 0.15263 | -0.26737 | -0.66632 | -1.2505 | -5.1832 | -8.2674 | -11.6621 | 0.98842 | 0.98105 | 0.96842 | 0.95684 | 0.94526 | 0.56737 | 0.19684 | -0.18526 | -0.54421 | -1.1189 | -4.6568 | -7.7947 | -11.2337 | 0.99368 | 0.97684 | 0.94632 | 0.91579 | 0.88526 | 0.63895 | 0.62316 | 0.28526 | -0.15158 | -0.91579 | -6.7926 | -10.9316 | -13.7937
|  | INVERARITY | CF |  |  |  |  | 1.0221 | 1.02 | 1.0137 | 1.0084 | 1.0021 | 0.88421 | 0.77263 | 0.52105 | 0.27263 | -0.0073684 | -2.7147 | -4.6589 | -6.8232 | 0.99368 | 0.98947 | 0.98211 | 0.97579 | 0.96737 | 0.86421 | 0.77368 | 0.51895 | 0.26526 | -0.032632 | -2.4442 | -4.4295 | -6.7284 | 1.0168 | 1.0126 | 1.0042 | 0.99684 | 0.98737 | 0.86737 | 0.76105 | 0.49053 | 0.21579 | -0.10105 | -2.9463 | -5.1032 | -7.5568
| INVERNESS | INVERARNIE | MINIMUM HEADROOM | NH 68830 34971 | YES | YES | 0 | 2.4453 | 2.4158 | 2.3684 | 2.3211 | 2.2653 | 1.9168 | 1.4611 | 0.98421 | 0.53474 | -0.15895 | -4.1305 | -8.9137 | -12.7547 | 2.44 | 2.4095 | 2.3653 | 2.3232 | 2.28 | 1.9821 | 1.5537 | 1.1126 | 0.69789 | 0.0042105 | -3.8168 | -8.8884 | -12.6832 | 2.44 | 2.4084 | 2.3579 | 2.3084 | 2.2516 | 1.9011 | 1.48 | 1.0474 | 0.67263 | -0.082105 | -4.6084 | -9.8747 | -14.2716
|  | INVERARNIE | EE |  |  |  |  | 2.46 | 2.4295 | 2.3768 | 2.3211 | 2.2653 | 1.9168 | 1.4968 | 1.0663 | 0.69474 | 0.12947 | -4.1305 | -8.9137 | -12.7547 | 2.4547 | 2.4263 | 2.3821 | 2.3347 | 2.2884 | 2.0074 | 1.6674 | 1.3179 | 1.0168 | 0.49895 | -3.7 | -8.4832 | -12.6832 | 2.4547 | 2.4221 | 2.3674 | 2.3084 | 2.2516 | 1.9011 | 1.48 | 1.0474 | 0.67263 | 0.071579 | -4.6084 | -9.8747 | -14.2716
|  | INVERARNIE | HT |  |  |  |  | 2.4453 | 2.4158 | 2.3684 | 2.3242 | 2.2779 | 1.9937 | 1.7011 | 1.3537 | 0.88737 | 0.06 | -3.8632 | -8.4632 | -11.6411 | 2.44 | 2.4095 | 2.3653 | 2.3232 | 2.28 | 2.0484 | 1.8105 | 1.5063 | 1.0842 | 0.25895 | -3.8168 | -8.8884 | -12.4968 | 2.44 | 2.4084 | 2.3579 | 2.3116 | 2.2632 | 1.9779 | 1.6853 | 1.3263 | 0.83474 | -0.082105 | -4.4663 | -9.7316 | -13.4084
|  | INVERARNIE | HE |  |  |  |  | 2.4768 | 2.4621 | 2.4421 | 2.4211 | 2.3979 | 1.9242 | 1.4611 | 0.98421 | 0.53474 | -0.15895 | -3.0947 | -6.8495 | -10.9505 | 2.4737 | 2.4589 | 2.44 | 2.42 | 2.3979 | 1.9821 | 1.5537 | 1.1126 | 0.69789 | 0.0042105 | -2.8968 | -6.7863 | -11.0421 | 2.44 | 2.4084 | 2.3579 | 2.3116 | 2.2632 | 1.9779 | 1.6853 | 1.3263 | 0.83474 | -0.082105 | -4.4663 | -9.7316 | -13.4084
|  | INVERARNIE | CF |  |  |  |  | 2.4853 | 2.4768 | 2.4663 | 2.4516 | 2.4411 | 2.3 | 2.1789 | 1.8863 | 1.5811 | 1.2316 | -0.30737 | -2.6758 | -5.3684 | 2.4832 | 2.4747 | 2.4632 | 2.4505 | 2.4411 | 2.3284 | 2.2284 | 1.9316 | 1.6147 | 1.2347 | -0.35263 | -2.8295 | -5.7768 | 2.4832 | 2.4737 | 2.4621 | 2.4474 | 2.4368 | 2.2958 | 2.1737 | 1.8474 | 1.5074 | 1.1074 | -0.60526 | -3.2568 | -6.3263
| FIDDES | INVERBERVIE | MINIMUM HEADROOM | NO 82850 72935 | NO | YES | 0.05 | 4.7363 | 4.5574 | 4.4005 | 4.2216 | 3.9742 | 3.5184 | 3.1616 | 2.6974 | 2.0416 | 1.3247 | -1.2447 | -4.9732 | -6.3711 | 3.9563 | 3.7553 | 3.59 | 3.3984 | 3.1268 | 2.7026 | 2.3911 | 1.9679 | 1.3121 | 0.59316 | -1.5911 | -4.9016 | -6.4721 | 4.2311 | 4.0321 | 3.8637 | 3.6679 | 3.3932 | 2.9068 | 2.5363 | 2.0511 | 1.3237 | 0.53526 | -2.1258 | -6.0142 | -7.6058
|  | INVERBERVIE | EE |  |  |  |  | 4.7932 | 4.6521 | 4.5174 | 4.3605 | 4.1458 | 3.6237 | 3.1616 | 2.6974 | 2.2879 | 1.7521 | -1.2447 | -4.2279 | -5.5626 | 4.0247 | 3.8584 | 3.7216 | 3.5563 | 3.3237 | 2.8563 | 2.4679 | 2.0763 | 1.7332 | 1.2363 | -1.5911 | -3.9711 | -5.5395 | 4.2963 | 4.1342 | 3.9921 | 3.8216 | 3.5837 | 3.03 | 2.55 | 2.0763 | 1.6605 | 1.0911 | -2.1258 | -5.1268 | -6.6963
|  | INVERBERVIE | HT |  |  |  |  | 4.7363 | 4.5574 | 4.4005 | 4.2216 | 3.9742 | 3.5184 | 3.1616 | 2.7068 | 2.0416 | 1.3247 | -0.63737 | -4.9732 | -6.3711 | 3.9563 | 3.7553 | 3.59 | 3.3984 | 3.1268 | 2.7026 | 2.3911 | 1.9679 | 1.3121 | 0.59316 | -1.2489 | -4.9016 | -6.4721 | 4.2311 | 4.0321 | 3.8637 | 3.6679 | 3.3932 | 2.9068 | 2.5363 | 2.0511 | 1.3237 | 0.53526 | -1.5574 | -6.0142 | -7.6058
|  | INVERBERVIE | HE |  |  |  |  | 4.8521 | 4.7763 | 4.6932 | 4.5584 | 4.39 | 3.9153 | 3.5679 | 3.2342 | 2.9174 | 2.4753 | 0.49737 | -3.03 | -5.3311 | 4.0911 | 3.9995 | 3.9058 | 3.7563 | 3.5668 | 3.1468 | 2.8511 | 2.5711 | 2.3184 | 1.9047 | 0.068947 | -2.9163 | -5.1637 | 4.2311 | 4.0321 | 3.8637 | 3.6679 | 3.3932 | 2.9068 | 2.5363 | 2.0511 | 1.3237 | 0.53526 | -1.5574 | -6.0142 | -7.6058
|  | INVERBERVIE | CF |  |  |  |  | 4.8826 | 4.8563 | 4.8226 | 4.7795 | 4.7332 | 4.5711 | 4.4247 | 4.2711 | 4.1332 | 3.9995 | 2.9753 | 0.022632 | -1.2984 | 4.1247 | 4.0963 | 4.0616 | 4.0132 | 3.9595 | 3.8247 | 3.7005 | 3.5637 | 3.4395 | 3.3047 | 2.3016 | -0.20158 | -1.6005 | 4.3932 | 4.3658 | 4.33 | 4.2826 | 4.23 | 4.0637 | 3.91 | 3.7468 | 3.6016 | 3.4532 | 2.3374 | -0.71316 | -2.2111
| GRUDIE BRIDGE | INVERBROOM | MINIMUM HEADROOM | NH 17885 84667 | YES | NO | 0 | 0.20947 | 0.20316 | 0.19579 | 0.18947 | 0.18421 | 0.17789 | 0.17053 | 0.16421 | 0.16 | 0.15474 | 0.13368 | 0.11684 | 0.10211 | 0.19474 | 0.18842 | 0.18 | 0.17368 | 0.16737 | 0.16 | 0.15368 | 0.14632 | 0.14211 | 0.13579 | 0.11368 | 0.094737 | 0.078947 | 0.2 | 0.19368 | 0.18632 | 0.17895 | 0.17263 | 0.16632 | 0.15895 | 0.15263 | 0.14737 | 0.14211 | 0.12 | 0.10105 | 0.085263
|  | INVERBROOM | EE |  |  |  |  | 0.21158 | 0.20737 | 0.20211 | 0.19684 | 0.19263 | 0.18737 | 0.18211 | 0.17684 | 0.17368 | 0.16842 | 0.15158 | 0.13895 | 0.12947 | 0.19895 | 0.19263 | 0.18737 | 0.18105 | 0.17579 | 0.17158 | 0.16526 | 0.16 | 0.15684 | 0.15158 | 0.13263 | 0.11895 | 0.10842 | 0.20421 | 0.19789 | 0.19263 | 0.18632 | 0.18211 | 0.17684 | 0.17053 | 0.16632 | 0.16211 | 0.15684 | 0.13895 | 0.12526 | 0.11474
|  | INVERBROOM | HT |  |  |  |  | 0.20947 | 0.20316 | 0.19579 | 0.18947 | 0.18421 | 0.17789 | 0.17053 | 0.16421 | 0.16 | 0.15474 | 0.13368 | 0.11684 | 0.10211 | 0.19474 | 0.18842 | 0.18 | 0.17368 | 0.16737 | 0.16 | 0.15368 | 0.14632 | 0.14211 | 0.13579 | 0.11368 | 0.094737 | 0.078947 | 0.2 | 0.19368 | 0.18632 | 0.17895 | 0.17263 | 0.16632 | 0.15895 | 0.15263 | 0.14737 | 0.14211 | 0.12 | 0.10105 | 0.085263
|  | INVERBROOM | HE |  |  |  |  | 0.21368 | 0.21158 | 0.20947 | 0.20737 | 0.20421 | 0.2 | 0.19684 | 0.19368 | 0.19053 | 0.18842 | 0.17895 | 0.17263 | 0.16737 | 0.20316 | 0.2 | 0.19579 | 0.19263 | 0.18842 | 0.18526 | 0.18211 | 0.17895 | 0.17474 | 0.17263 | 0.16316 | 0.15474 | 0.15053 | 0.2 | 0.19368 | 0.18632 | 0.17895 | 0.17263 | 0.16632 | 0.15895 | 0.15263 | 0.14737 | 0.14211 | 0.12 | 0.10105 | 0.085263
|  | INVERBROOM | CF |  |  |  |  | 0.21474 | 0.21368 | 0.21263 | 0.21158 | 0.21053 | 0.20947 | 0.20737 | 0.20632 | 0.20421 | 0.20211 | 0.19368 | 0.18842 | 0.18421 | 0.20421 | 0.20316 | 0.20105 | 0.19895 | 0.19684 | 0.19474 | 0.19263 | 0.19053 | 0.18947 | 0.18737 | 0.17684 | 0.17158 | 0.16737 | 0.20947 | 0.20842 | 0.20632 | 0.20421 | 0.20211 | 0.2 | 0.19789 | 0.19684 | 0.19474 | 0.19263 | 0.18316 | 0.17684 | 0.17368
| FORT AUGUSTUS | INVERGARRY | MINIMUM HEADROOM | NH 29862 01000 | YES | YES | 0 | 0.98526 | 0.97579 | 0.96 | 0.94316 | 0.92632 | 0.87895 | 0.82526 | 0.76737 | 0.71789 | 0.63579 | 0.011579 | -0.71263 | -1.3421 | 1.0095 | 0.99789 | 0.98632 | 0.97368 | 0.96105 | 0.91684 | 0.87053 | 0.81684 | 0.75579 | 0.64842 | 0.032632 | -0.79158 | -1.3853 | 1.02 | 1.0063 | 0.99053 | 0.97053 | 0.95474 | 0.9 | 0.84211 | 0.78 | 0.72526 | 0.63895 | -0.074737 | -0.89895 | -1.6084
|  | INVERGARRY | EE |  |  |  |  | 0.98842 | 0.97579 | 0.96 | 0.94316 | 0.92632 | 0.87895 | 0.82526 | 0.76737 | 0.71789 | 0.65263 | 0.011579 | -0.71263 | -1.3421 | 1.0137 | 1.0032 | 0.98842 | 0.97579 | 0.96105 | 0.91684 | 0.87053 | 0.82 | 0.77474 | 0.71789 | 0.073684 | -0.66105 | -1.3547 | 1.0232 | 1.0084 | 0.99053 | 0.97053 | 0.95474 | 0.9 | 0.84211 | 0.78 | 0.72526 | 0.65158 | -0.074737 | -0.88211 | -1.6084
|  | INVERGARRY | HT |  |  |  |  | 0.98526 | 0.97684 | 0.96526 | 0.95368 | 0.94421 | 0.90632 | 0.86947 | 0.82947 | 0.77789 | 0.65789 | 0.052632 | -0.68632 | -1.2105 | 1.0095 | 0.99789 | 0.98632 | 0.97368 | 0.96105 | 0.92842 | 0.89474 | 0.86105 | 0.81053 | 0.67895 | 0.032632 | -0.79158 | -1.3853 | 1.02 | 1.0063 | 0.99263 | 0.97895 | 0.96632 | 0.92316 | 0.88316 | 0.84 | 0.78 | 0.63895 | -0.048421 | -0.89895 | -1.5063
|  | INVERGARRY | HE |  |  |  |  | 0.99263 | 0.98842 | 0.98105 | 0.97368 | 0.96842 | 0.91895 | 0.86526 | 0.8 | 0.73684 | 0.63579 | 0.20211 | -0.37263 | -0.99789 | 1.0211 | 1.0158 | 1.0084 | 1.0021 | 0.99684 | 0.94316 | 0.88105 | 0.81684 | 0.75579 | 0.64842 | 0.20737 | -0.4 | -1.0632 | 1.02 | 1.0063 | 0.99263 | 0.97895 | 0.96632 | 0.92316 | 0.88316 | 0.84 | 0.78 | 0.63895 | -0.048421 | -0.89895 | -1.5063
|  | INVERGARRY | CF |  |  |  |  | 0.99579 | 0.99158 | 0.98947 | 0.98526 | 0.98316 | 0.96737 | 0.95263 | 0.92632 | 0.88842 | 0.83684 | 0.60316 | 0.24526 | -0.17684 | 1.0242 | 1.0211 | 1.0168 | 1.0126 | 1.0105 | 0.99579 | 0.98211 | 0.94 | 0.89053 | 0.82842 | 0.58 | 0.19158 | -0.27789 | 1.0295 | 1.0263 | 1.0242 | 1.0211 | 1.0179 | 1.0011 | 0.98316 | 0.94 | 0.88737 | 0.82316 | 0.55789 | 0.15053 | -0.33474
| ALNESS | INVERGORDON | MINIMUM HEADROOM | NH 70756 69177 | NO | YES | 0.05 | 14.4526 | 14.3284 | 14.1958 | 13.9337 | 13.6568 | 12.6611 | 11.6347 | 10.6 | 9.4484 | 8.4137 | 7.1232 | 5.7853 | 5.1916 | 13.7174 | 13.6089 | 13.4647 | 13.1721 | 12.8626 | 11.7532 | 10.6047 | 9.4458 | 8.1637 | 7.0258 | 5.9511 | 4.8742 | 4.3258 | 14.0029 | 13.8766 | 13.7345 | 13.4471 | 13.1429 | 12.0429 | 10.8839 | 9.6966 | 8.3776 | 7.2039 | 5.8966 | 4.5187 | 3.8903
|  | INVERGORDON | EE |  |  |  |  | 14.5074 | 14.4084 | 14.2968 | 14.0779 | 13.8326 | 13.4442 | 13.1305 | 12.2232 | 11.04 | 9.9874 | 7.1232 | 5.7853 | 5.1916 | 13.7616 | 13.6763 | 13.5805 | 13.3374 | 13.0658 | 12.6847 | 12.4079 | 11.4184 | 10.0974 | 8.9395 | 6.0058 | 4.8742 | 4.3258 | 14.0313 | 13.9639 | 13.8439 | 13.6029 | 13.3345 | 12.9261 | 12.6103 | 11.6124 | 10.2566 | 9.0597 | 5.8966 | 4.5187 | 3.8903
|  | INVERGORDON | HT |  |  |  |  | 14.4526 | 14.3284 | 14.1958 | 13.9337 | 13.6568 | 12.6611 | 11.6347 | 10.6 | 9.4484 | 8.4137 | 7.2432 | 6.4126 | 5.8768 | 13.7174 | 13.6089 | 13.4647 | 13.1721 | 12.8626 | 11.7532 | 10.6047 | 9.4458 | 8.1637 | 7.0258 | 5.9511 | 5.1616 | 4.6142 | 14.0029 | 13.8766 | 13.7345 | 13.4471 | 13.1429 | 12.0429 | 10.8839 | 9.6966 | 8.3776 | 7.2039 | 5.9755 | 5.0945 | 4.5124
|  | INVERGORDON | HE |  |  |  |  | 14.58 | 14.5168 | 14.4221 | 14.2421 | 14.0347 | 13.6579 | 13.4158 | 13.0316 | 12.3053 | 11.7253 | 9.2589 | 7.4663 | 6.6316 | 13.8237 | 13.7679 | 13.6911 | 13.5047 | 13.27 | 12.9047 | 12.6921 | 12.3026 | 11.5016 | 10.8795 | 8.2742 | 6.4342 | 5.7374 | 14.0029 | 13.8766 | 13.7345 | 13.4471 | 13.1429 | 12.0429 | 10.8839 | 9.6966 | 8.3776 | 7.2039 | 5.9755 | 5.0945 | 4.5124
|  | INVERGORDON | CF |  |  |  |  | 14.6147 | 14.5758 | 14.5326 | 14.4884 | 14.4032 | 14.2495 | 14.1484 | 14.0495 | 13.6811 | 13.3853 | 11.8716 | 10.6547 | 10.1811 | 13.8532 | 13.8195 | 13.7826 | 13.7447 | 13.6805 | 13.5405 | 13.4521 | 13.3637 | 12.9468 | 12.6121 | 10.9447 | 9.6679 | 9.2268 | 14.0913 | 14.0682 | 14.0418 | 14.0124 | 13.9566 | 13.7945 | 13.6934 | 13.5945 | 13.1808 | 12.8503 | 11.1661 | 9.8018 | 9.2955
| FORT WILLIAM | INVERLOCHY | MINIMUM HEADROOM | NN 11653 74987 | NO | NO | 0 | 16.0647 | 15.9489 | 30.3705 | 30.24 | 30.1074 | 29.8242 | 29.1526 | 28.0958 | 27.2042 | 26.3011 | 24.5779 | 22.7453 | 20.3147 | 13.9695 | 13.8547 | 27.5316 | 27.4063 | 27.28 | 26.9137 | 25.7926 | 24.6589 | 23.7232 | 22.7747 | 21.1821 | 19.5611 | 16.7316 | 14.9424 | 14.8266 | 28.8732 | 28.7426 | 28.61 | 28.2247 | 27.0353 | 25.8384 | 24.8384 | 23.8268 | 22.0426 | 20.1174 | 17.3353
|  | INVERLOCHY | EE |  |  |  |  | 16.1079 | 16.0153 | 30.4505 | 30.3316 | 30.2105 | 29.9158 | 29.5832 | 29.2495 | 28.5558 | 27.5032 | 24.5779 | 22.7453 | 20.3147 | 14.0126 | 13.9211 | 27.6168 | 27.5063 | 27.3947 | 27.2 | 26.9895 | 26.4021 | 25.3263 | 24.2116 | 21.3263 | 19.6916 | 17.0716 | 14.9855 | 14.8918 | 28.9521 | 28.8321 | 28.7111 | 28.4237 | 28.0868 | 27.5995 | 26.4311 | 25.2395 | 22.0426 | 20.1174 | 17.3353
|  | INVERLOCHY | HT |  |  |  |  | 16.0647 | 15.9489 | 30.3705 | 30.24 | 30.1074 | 29.8242 | 29.1526 | 28.0958 | 27.2042 | 26.3011 | 24.6274 | 23.0337 | 20.5084 | 13.9695 | 13.8547 | 27.5316 | 27.4063 | 27.28 | 26.9137 | 25.7926 | 24.6589 | 23.7232 | 22.7747 | 21.1821 | 19.5611 | 16.7316 | 14.9424 | 14.8266 | 28.8732 | 28.7426 | 28.61 | 28.2247 | 27.0353 | 25.8384 | 24.8384 | 23.8268 | 22.0437 | 20.2868 | 17.3721
|  | INVERLOCHY | HE |  |  |  |  | 16.1711 | 16.1089 | 30.5884 | 30.5116 | 30.4295 | 30.1421 | 29.8958 | 29.6537 | 29.4126 | 29.18 | 26.6211 | 25.0716 | 22.0747 | 14.0758 | 14.0147 | 27.7453 | 27.6695 | 27.5905 | 27.4105 | 27.2547 | 27.1 | 26.6895 | 25.9853 | 23.3842 | 21.8916 | 18.7547 | 14.9424 | 14.8266 | 28.8732 | 28.7426 | 28.61 | 28.2247 | 27.0353 | 25.8384 | 24.8384 | 23.8268 | 22.0437 | 20.2868 | 17.3721
|  | INVERLOCHY | CF |  |  |  |  | 16.2058 | 16.1689 | 30.68 | 30.6368 | 30.5958 | 30.4811 | 30.3747 | 30.2684 | 30.1716 | 30.0916 | 29.4084 | 28.3221 | 26.3158 | 14.1105 | 14.0737 | 27.8358 | 27.7958 | 27.7558 | 27.68 | 27.6074 | 27.5368 | 27.4695 | 27.4105 | 26.1358 | 25.0621 | 22.8863 | 15.0834 | 15.0455 | 29.1816 | 29.1405 | 29.0995 | 28.9879 | 28.8837 | 28.7816 | 28.6868 | 28.6068 | 27.3237 | 26.1321 | 23.8258
| PORT ANN | INVERNEIL | MINIMUM HEADROOM | NR 84790 80580 | YES | YES | 0 | 2.6195 | 2.5984 | 2.5711 | 2.5437 | 2.5111 | 2.3837 | 2.2132 | 2.0647 | 1.9205 | 1.7826 | 0.80789 | -0.42368 | -1.3521 | 2.8942 | 2.8658 | 2.8332 | 2.8005 | 2.77 | 2.6479 | 2.4963 | 2.3658 | 2.2363 | 2.1132 | 1.21 | 0.032105 | -0.95737 | 2.6595 | 2.6311 | 2.5984 | 2.5658 | 2.5321 | 2.3837 | 2.1932 | 2.0342 | 1.8795 | 1.7311 | 0.68158 | -0.65526 | -1.7111
|  | INVERNEIL | EE |  |  |  |  | 2.6268 | 2.6037 | 2.5742 | 2.5437 | 2.5111 | 2.3837 | 2.2132 | 2.0647 | 1.9205 | 1.7826 | 0.80789 | -0.42368 | -1.3521 | 2.9068 | 2.8816 | 2.8511 | 2.8195 | 2.7889 | 2.6584 | 2.4963 | 2.3658 | 2.2363 | 2.1132 | 1.21 | 0.032105 | -0.95737 | 2.6711 | 2.6426 | 2.6079 | 2.5711 | 2.5363 | 2.3837 | 2.1932 | 2.0342 | 1.8795 | 1.7311 | 0.68158 | -0.65526 | -1.7111
|  | INVERNEIL | HT |  |  |  |  | 2.6195 | 2.5984 | 2.5711 | 2.5447 | 2.5184 | 2.4026 | 2.2847 | 2.1595 | 1.9889 | 1.8447 | 0.96158 | -0.14263 | -0.89316 | 2.8942 | 2.8658 | 2.8332 | 2.8005 | 2.77 | 2.6479 | 2.5363 | 2.4195 | 2.2553 | 2.1226 | 1.2468 | 0.05 | -0.78789 | 2.6595 | 2.6311 | 2.5984 | 2.5658 | 2.5321 | 2.3974 | 2.2668 | 2.1311 | 1.9416 | 1.7879 | 0.81947 | -0.43421 | -1.2974
|  | INVERNEIL | HE |  |  |  |  | 2.6374 | 2.6258 | 2.6111 | 2.5974 | 2.5816 | 2.4584 | 2.3237 | 2.2016 | 2.0679 | 1.9532 | 1.19 | 0.25947 | -0.75 | 2.9258 | 2.91 | 2.8932 | 2.8763 | 2.8595 | 2.7216 | 2.5868 | 2.4732 | 2.3437 | 2.2395 | 1.5111 | 0.57526 | -0.44579 | 2.6595 | 2.6311 | 2.5984 | 2.5658 | 2.5321 | 2.3974 | 2.2668 | 2.1311 | 1.9416 | 1.7879 | 0.81947 | -0.43421 | -1.2974
|  | INVERNEIL | CF |  |  |  |  | 2.6426 | 2.6353 | 2.6289 | 2.6216 | 2.6142 | 2.5721 | 2.5321 | 2.4921 | 2.4363 | 2.3563 | 1.9721 | 1.3921 | 0.75526 | 2.9332 | 2.9247 | 2.9132 | 2.9047 | 2.8942 | 2.8532 | 2.8079 | 2.7584 | 2.6921 | 2.5995 | 2.2037 | 1.6079 | 0.92263 | 2.6953 | 2.6858 | 2.6774 | 2.6668 | 2.6563 | 2.61 | 2.5605 | 2.5068 | 2.4342 | 2.3363 | 1.9037 | 1.2574 | 0.53632
| INVERNESS | INVERNESS | MINIMUM HEADROOM | NH 65302 42625 | NO | YES | 0 | 16.7163 | 16.0921 | 15.4174 | 14.5605 | 13.6489 | 12.4416 | 11.2984 | 10.3489 | 9.4353 | 9.0026 | 7.1174 | 5.73 | 4.73 | 14.2621 | 13.5568 | 12.8337 | 11.86 | 10.8242 | 9.4968 | 8.2442 | 7.22 | 6.2505 | 5.8463 | 4.0126 | 2.6221 | 1.5642 | 15.5624 | 14.875 | 14.1624 | 13.2034 | 12.1824 | 10.8371 | 9.5466 | 8.4782 | 7.4571 | 7.0024 | 4.975 | 3.4634 | 2.3561
|  | INVERNESS | EE |  |  |  |  | 16.8532 | 16.2942 | 15.6058 | 14.8721 | 14.0068 | 12.8847 | 11.9953 | 11.0458 | 10.1374 | 9.6953 | 7.7205 | 5.9111 | 4.9532 | 14.4105 | 13.7768 | 13 | 12.2063 | 11.2232 | 10.0042 | 8.9842 | 7.9863 | 7.0179 | 6.6032 | 4.8105 | 3.1979 | 2.2558 | 15.6992 | 15.0918 | 14.3224 | 13.5371 | 12.5676 | 11.3171 | 10.3066 | 9.2424 | 8.2203 | 7.7487 | 5.6613 | 3.7392 | 2.6908
|  | INVERNESS | HT |  |  |  |  | 16.7163 | 16.0921 | 15.4174 | 14.5605 | 13.6489 | 12.4416 | 11.2984 | 10.3489 | 9.4353 | 9.0026 | 7.1174 | 5.73 | 4.73 | 14.2621 | 13.5568 | 12.8337 | 11.86 | 10.8242 | 9.4968 | 8.2442 | 7.22 | 6.2505 | 5.8463 | 4.0126 | 2.6221 | 1.5642 | 15.5624 | 14.875 | 14.1624 | 13.2034 | 12.1824 | 10.8371 | 9.5466 | 8.4782 | 7.4571 | 7.0024 | 4.975 | 3.4634 | 2.3561
|  | INVERNESS | HE |  |  |  |  | 17.0321 | 16.5605 | 15.9679 | 15.2542 | 14.4795 | 13.4121 | 12.4437 | 11.63 | 10.8226 | 10.5037 | 9.2816 | 8.3205 | 7.2847 | 14.6053 | 14.0663 | 13.3884 | 12.5695 | 11.6789 | 10.5242 | 9.4705 | 8.5989 | 7.7347 | 7.4421 | 6.3642 | 5.5463 | 4.6168 | 15.5624 | 14.875 | 14.1624 | 13.2034 | 12.1824 | 10.8371 | 9.5466 | 8.4782 | 7.4571 | 7.0024 | 4.975 | 3.4634 | 2.3561
|  | INVERNESS | CF |  |  |  |  | 17.2626 | 17.0542 | 16.7321 | 16.37 | 15.9889 | 15.5047 | 15.0079 | 14.6005 | 14.1563 | 13.9532 | 13.1995 | 12.5289 | 12.0342 | 14.8674 | 14.6326 | 14.2653 | 13.8495 | 13.4116 | 12.8811 | 12.3326 | 11.8905 | 11.4 | 11.1863 | 10.4653 | 9.8674 | 9.42 | 16.1118 | 15.9024 | 15.5718 | 15.1645 | 14.7339 | 14.1939 | 13.6361 | 13.1824 | 12.6855 | 12.4645 | 11.6613 | 10.9476 | 10.4161
| KINTORE | INVERURIE | MINIMUM HEADROOM | NJ 75665 21688 | NO | YES | 0.11 | 30.4668 | 30.1932 | 29.8616 | 28.6784 | 27.2995 | 25.6511 | 24.0542 | 22.3932 | 20.6332 | 19.3226 | 13.1626 | 9.0616 | 7.0816 | 28.9142 | 28.0858 | 26.8595 | 25.4163 | 23.7837 | 21.9984 | 20.29 | 18.55 | 16.7268 | 15.4311 | 10.3405 | 6.8963 | 4.9974 | 29.9816 | 29.5163 | 28.3237 | 26.9268 | 25.3468 | 23.5216 | 21.7721 | 19.99 | 18.0668 | 16.6595 | 10.4068 | 6.2079 | 4.0942
|  | INVERURIE | EE |  |  |  |  | 30.5774 | 30.3626 | 30.1068 | 29.3047 | 28.0363 | 26.2468 | 24.4679 | 22.8332 | 21.3247 | 20.1595 | 13.1626 | 9.0616 | 7.0816 | 29.1574 | 28.4932 | 27.4342 | 26.1416 | 24.6395 | 22.7079 | 20.8342 | 19.1795 | 17.6511 | 16.5268 | 10.4268 | 6.8963 | 4.9974 | 30.0921 | 29.8437 | 28.8805 | 27.6258 | 26.1689 | 24.1816 | 22.2258 | 20.4742 | 18.8679 | 17.6289 | 10.4068 | 6.2079 | 4.0942
|  | INVERURIE | HT |  |  |  |  | 30.4668 | 30.1932 | 29.8616 | 28.6784 | 27.2995 | 25.6511 | 24.0542 | 22.3932 | 20.6332 | 19.3226 | 13.4879 | 10.8637 | 8.9816 | 28.9142 | 28.0858 | 26.8595 | 25.4163 | 23.7837 | 21.9984 | 20.29 | 18.55 | 16.7268 | 15.4311 | 10.3405 | 7.8216 | 5.8711 | 29.9816 | 29.5163 | 28.3237 | 26.9268 | 25.3468 | 23.5216 | 21.7721 | 19.99 | 18.0668 | 16.6595 | 10.6732 | 7.8932 | 5.8363
|  | INVERURIE | HE |  |  |  |  | 30.7268 | 30.5837 | 30.4205 | 30.0121 | 28.8963 | 27.1932 | 25.6753 | 24.2889 | 22.9016 | 21.9089 | 17.6595 | 15.1868 | 12.6911 | 29.4826 | 28.9763 | 28.0742 | 26.93 | 25.5668 | 23.7479 | 22.1111 | 20.6426 | 19.2163 | 18.2447 | 14.5574 | 12.4142 | 10.2953 | 29.9816 | 29.5163 | 28.3237 | 26.9268 | 25.3468 | 23.5216 | 21.7721 | 19.99 | 18.0668 | 16.6595 | 10.6732 | 7.8932 | 5.8363
|  | INVERURIE | CF |  |  |  |  | 30.8068 | 30.7226 | 30.6311 | 30.5363 | 30.4416 | 30.1226 | 29.4774 | 28.7437 | 28.1132 | 27.6879 | 25.7216 | 24.1016 | 22.8826 | 29.5921 | 29.3837 | 28.9711 | 28.4616 | 27.8889 | 27.1616 | 26.4153 | 25.6058 | 24.9132 | 24.4553 | 22.4932 | 21.0679 | 19.9637 | 30.3216 | 30.2374 | 30.1458 | 29.8889 | 29.3342 | 28.5847 | 27.8205 | 26.9974 | 26.2942 | 25.8258 | 23.7195 | 22.0489 | 20.7753
| BROADFORD | KALNAKIL | MINIMUM HEADROOM | NG 69146 53941 | YES | YES | 0 | 1.0926 | 1.0779 | 1.0632 | 1.0484 | 1.0337 | 1.0179 | 1.0042 | 0.98947 | 0.97684 | 0.96316 | 0.90737 | 0.85895 | 0.81474 | 1.1063 | 1.0979 | 1.0832 | 1.0674 | 1.0516 | 1.0358 | 1.0211 | 1.0053 | 0.99263 | 0.97789 | 0.91684 | 0.86211 | 0.81368 | 1.1284 | 1.1179 | 1.1021 | 1.0874 | 1.0716 | 1.0547 | 1.04 | 1.0242 | 1.0116 | 0.99789 | 0.93579 | 0.88105 | 0.83158
|  | KALNAKIL | EE |  |  |  |  | 1.0979 | 1.0884 | 1.0768 | 1.0653 | 1.0537 | 1.0411 | 1.0305 | 1.0189 | 1.0074 | 0.99789 | 0.95263 | 0.91368 | 0.88211 | 1.1095 | 1.1032 | 1.0968 | 1.0853 | 1.0726 | 1.06 | 1.0484 | 1.0379 | 1.0263 | 1.0158 | 0.96737 | 0.92421 | 0.88842 | 1.1316 | 1.1253 | 1.1168 | 1.1053 | 1.0926 | 1.08 | 1.0684 | 1.0568 | 1.0453 | 1.0358 | 0.98526 | 0.94211 | 0.90632
|  | KALNAKIL | HT |  |  |  |  | 1.0926 | 1.0779 | 1.0632 | 1.0484 | 1.0337 | 1.0179 | 1.0042 | 0.98947 | 0.97684 | 0.96316 | 0.90737 | 0.85895 | 0.81474 | 1.1063 | 1.0979 | 1.0832 | 1.0674 | 1.0516 | 1.0358 | 1.0211 | 1.0053 | 0.99263 | 0.97789 | 0.91684 | 0.86211 | 0.81368 | 1.1284 | 1.1179 | 1.1021 | 1.0874 | 1.0716 | 1.0547 | 1.04 | 1.0242 | 1.0116 | 0.99789 | 0.93579 | 0.88105 | 0.83158
|  | KALNAKIL | HE |  |  |  |  | 1.1074 | 1.1011 | 1.0937 | 1.0874 | 1.08 | 1.0705 | 1.0642 | 1.0547 | 1.0474 | 1.0411 | 1.0179 | 0.99789 | 0.97895 | 1.1147 | 1.1105 | 1.1053 | 1.1011 | 1.0958 | 1.0895 | 1.0842 | 1.0768 | 1.0684 | 1.0621 | 1.0379 | 1.0168 | 0.99684 | 1.1284 | 1.1179 | 1.1021 | 1.0874 | 1.0716 | 1.0547 | 1.04 | 1.0242 | 1.0116 | 0.99789 | 0.93579 | 0.88105 | 0.83158
|  | KALNAKIL | CF |  |  |  |  | 1.1116 | 1.1084 | 1.1042 | 1.1011 | 1.0958 | 1.0916 | 1.0874 | 1.0821 | 1.0789 | 1.0737 | 1.0537 | 1.0411 | 1.0326 | 1.1168 | 1.1147 | 1.1126 | 1.1105 | 1.1074 | 1.1053 | 1.1021 | 1.1 | 1.0979 | 1.0947 | 1.0747 | 1.0611 | 1.0505 | 1.1389 | 1.1368 | 1.1347 | 1.1326 | 1.1295 | 1.1274 | 1.1242 | 1.1211 | 1.1189 | 1.1137 | 1.0937 | 1.08 | 1.0695
| DUNOON | KAMES | MINIMUM HEADROOM | NR 96305 71237 | YES | YES | 0 | 2.4874 | 2.4505 | 2.4095 | 2.3632 | 2.3179 | 2.2432 | 2.1716 | 2.1011 | 2.04 | 1.9916 | 1.8579 | 1.7463 | 1.6505 | 2.4811 | 2.4368 | 2.3916 | 2.34 | 2.2905 | 2.2084 | 2.1284 | 2.0484 | 1.9821 | 1.9284 | 1.7832 | 1.6621 | 1.5568 | 2.4463 | 2.4011 | 2.3558 | 2.3063 | 2.2568 | 2.1726 | 2.0937 | 2.0137 | 1.9463 | 1.8926 | 1.7463 | 1.6253 | 1.5179
|  | KAMES | EE |  |  |  |  | 2.4968 | 2.4726 | 2.4432 | 2.4074 | 2.3705 | 2.3042 | 2.2179 | 2.1674 | 2.1253 | 2.0811 | 1.9432 | 1.8547 | 1.7821 | 2.4989 | 2.4621 | 2.4295 | 2.3905 | 2.3516 | 2.2768 | 2.18 | 2.1242 | 2.0779 | 2.0316 | 1.8821 | 1.7895 | 1.7105 | 2.4621 | 2.4274 | 2.3937 | 2.3547 | 2.3137 | 2.2389 | 2.1421 | 2.0863 | 2.0379 | 1.9916 | 1.84 | 1.7442 | 1.6632
|  | KAMES | HT |  |  |  |  | 2.4874 | 2.4505 | 2.4095 | 2.3632 | 2.3179 | 2.2432 | 2.1716 | 2.1011 | 2.04 | 1.9916 | 1.8579 | 1.7463 | 1.6505 | 2.4811 | 2.4368 | 2.3916 | 2.34 | 2.2905 | 2.2084 | 2.1284 | 2.0484 | 1.9821 | 1.9284 | 1.7832 | 1.6621 | 1.5568 | 2.4463 | 2.4011 | 2.3558 | 2.3063 | 2.2568 | 2.1726 | 2.0937 | 2.0137 | 1.9463 | 1.8926 | 1.7463 | 1.6253 | 1.5179
|  | KAMES | HE |  |  |  |  | 2.5137 | 2.4968 | 2.4811 | 2.4621 | 2.4337 | 2.3663 | 2.2811 | 2.2358 | 2.2063 | 2.1842 | 2.1189 | 2.0737 | 2.0411 | 2.5253 | 2.5021 | 2.4779 | 2.4505 | 2.4168 | 2.3421 | 2.2442 | 2.1937 | 2.1621 | 2.1389 | 2.0695 | 2.0211 | 1.9853 | 2.4463 | 2.4011 | 2.3558 | 2.3063 | 2.2568 | 2.1726 | 2.0937 | 2.0137 | 1.9463 | 1.8926 | 1.7463 | 1.6253 | 1.5179
|  | KAMES | CF |  |  |  |  | 2.5232 | 2.5137 | 2.5042 | 2.4947 | 2.4842 | 2.4737 | 2.4558 | 2.4179 | 2.3926 | 2.3663 | 2.2821 | 2.2442 | 2.2147 | 2.5389 | 2.5253 | 2.5116 | 2.4979 | 2.4842 | 2.4663 | 2.4421 | 2.3989 | 2.3705 | 2.3411 | 2.2453 | 2.2042 | 2.1726 | 2.5 | 2.4874 | 2.4747 | 2.4621 | 2.4474 | 2.4305 | 2.4063 | 2.3632 | 2.3358 | 2.3053 | 2.2116 | 2.1705 | 2.1368
| KEITH 2 | KEITH | MINIMUM HEADROOM | NJ 43925 50405 | NO | YES | 0.2 | 15.8005 | 15.6889 | 15.5458 | 15.4047 | 15.1584 | 14.4237 | 13.5321 | 12.6037 | 11.7774 | 10.9058 | 3.7426 | -3.9942 | -10.3784 | 15.1084 | 14.9126 | 14.6347 | 14.4074 | 14.0568 | 13.3758 | 12.6463 | 11.8337 | 11.1084 | 10.3684 | 3.5 | -4.2642 | -11.2505 | 15.6382 | 15.4561 | 15.1666 | 14.9297 | 14.5676 | 13.7761 | 12.8487 | 11.8624 | 10.9992 | 10.1161 | 2.3497 | -6.1755 | -13.5629
|  | KEITH | EE |  |  |  |  | 15.8405 | 15.7542 | 15.6174 | 15.4805 | 15.3342 | 14.5247 | 13.5321 | 12.6037 | 11.7774 | 10.9058 | 3.7426 | -3.9942 | -10.3784 | 15.1695 | 15.0411 | 14.7979 | 14.6011 | 14.2968 | 13.5568 | 12.6463 | 11.8337 | 11.1084 | 10.3684 | 3.5 | -4.2642 | -11.2505 | 15.6761 | 15.5929 | 15.3297 | 15.1203 | 14.8013 | 13.9287 | 12.8487 | 11.8624 | 10.9992 | 10.1161 | 2.3497 | -6.1755 | -13.5629
|  | KEITH | HT |  |  |  |  | 15.8005 | 15.6889 | 15.5458 | 15.4047 | 15.1584 | 14.4237 | 13.6805 | 12.9363 | 12.71 | 11.8426 | 5.2479 | -2.2005 | -7.5216 | 15.1084 | 14.9126 | 14.6347 | 14.4074 | 14.0568 | 13.3758 | 12.68 | 12.0021 | 11.7484 | 10.9747 | 4.2453 | -4.0095 | -10.0032 | 15.6382 | 15.4561 | 15.1666 | 14.9297 | 14.5676 | 13.7761 | 12.9729 | 12.1824 | 11.9266 | 11.0076 | 3.6445 | -5.0103 | -11.1797
|  | KEITH | HE |  |  |  |  | 15.8974 | 15.8426 | 15.7711 | 15.6942 | 15.6047 | 14.8963 | 14.1058 | 13.4195 | 12.5742 | 11.35 | 5.9858 | -0.072105 | -7.1721 | 15.2263 | 15.1632 | 15.0632 | 14.9484 | 14.7137 | 13.9611 | 13.2158 | 12.6053 | 11.8042 | 10.5505 | 5.3411 | -0.94947 | -8.2368 | 15.6382 | 15.4561 | 15.1666 | 14.9297 | 14.5676 | 13.7761 | 12.9729 | 12.1824 | 11.9266 | 11.0076 | 3.6445 | -5.0103 | -11.1797
|  | KEITH | CF |  |  |  |  | 15.9289 | 15.8984 | 15.8584 | 15.8163 | 15.7742 | 15.51 | 15.2742 | 15.0321 | 14.6637 | 14.1089 | 11.4205 | 4.1079 | -0.40789 | 15.2579 | 15.2263 | 15.1842 | 15.1411 | 15.0716 | 14.7884 | 14.5158 | 14.2242 | 13.7211 | 13.0632 | 10.2463 | 3.5158 | -1.34 | 15.7645 | 15.7339 | 15.6939 | 15.6529 | 15.6139 | 15.2897 | 14.9708 | 14.6276 | 14.0666 | 13.3666 | 10.2792 | 2.5255 | -2.6713
| KINTORE | KEMNAY | MINIMUM HEADROOM | NJ 73180 16804 | NO | YES | 0 | 15.0226 | 14.8826 | 14.6879 | 14.5174 | 14.3742 | 14.1111 | 13.8542 | 13.5974 | 13.3195 | 13.0447 | 11.6532 | 9.4826 | 7.8447 | 13.7032 | 13.5168 | 13.2484 | 13.0274 | 12.8779 | 12.6379 | 12.4011 | 12.1642 | 11.9116 | 11.6632 | 10.3137 | 8.1189 | 6.5611 | 14.1666 | 14.0034 | 13.7382 | 13.5192 | 13.3687 | 13.095 | 12.8266 | 12.5603 | 12.2729 | 11.9866 | 10.5024 | 8.1845 | 6.3603
|  | KEMNAY | EE |  |  |  |  | 15.0732 | 14.9668 | 14.83 | 14.6668 | 14.5289 | 14.2489 | 13.9468 | 13.6553 | 13.3953 | 13.1353 | 11.6553 | 9.4826 | 7.8447 | 13.7695 | 13.6305 | 13.4505 | 13.2326 | 13.0547 | 12.7989 | 12.5295 | 12.2716 | 12.0411 | 11.8116 | 10.4705 | 8.3337 | 6.5611 | 14.2234 | 14.1034 | 13.9361 | 13.7182 | 13.5392 | 13.2424 | 12.9287 | 12.6266 | 12.3571 | 12.0887 | 10.5361 | 8.1845 | 6.3603
|  | KEMNAY | HT |  |  |  |  | 15.0226 | 14.8826 | 14.6879 | 14.5174 | 14.3742 | 14.1111 | 13.8542 | 13.5974 | 13.3195 | 13.0447 | 11.6532 | 9.6205 | 8.2321 | 13.7032 | 13.5168 | 13.2484 | 13.0274 | 12.8779 | 12.6379 | 12.4011 | 12.1642 | 11.9116 | 11.6632 | 10.3137 | 8.1189 | 6.5705 | 14.1666 | 14.0034 | 13.7382 | 13.5192 | 13.3687 | 13.095 | 12.8266 | 12.5603 | 12.2729 | 11.9866 | 10.5024 | 8.2445 | 6.6908
|  | KEMNAY | HE |  |  |  |  | 15.1458 | 15.0732 | 14.9647 | 14.8405 | 14.75 | 14.5005 | 14.2921 | 14.0858 | 13.8816 | 13.6837 | 12.3805 | 10.7258 | 8.9574 | 13.8621 | 13.7663 | 13.6147 | 13.4379 | 13.3211 | 13.1021 | 12.9179 | 12.7337 | 12.5558 | 12.3821 | 11.1021 | 9.4179 | 7.6105 | 14.1666 | 14.0034 | 13.7382 | 13.5192 | 13.3687 | 13.095 | 12.8266 | 12.5603 | 12.2729 | 11.9866 | 10.5024 | 8.2445 | 6.6908
|  | KEMNAY | CF |  |  |  |  | 15.1826 | 15.1468 | 15.1047 | 15.0553 | 15.0037 | 14.8921 | 14.7837 | 14.6774 | 14.5858 | 14.5068 | 13.8605 | 12.8089 | 11.6742 | 13.9084 | 13.8642 | 13.8105 | 13.7442 | 13.6737 | 13.5653 | 13.4526 | 13.3411 | 13.2495 | 13.1632 | 12.4579 | 11.3789 | 10.1632 | 14.3455 | 14.3066 | 14.2582 | 14.2003 | 14.1424 | 14.0234 | 13.9066 | 13.7824 | 13.6803 | 13.5876 | 12.8276 | 11.675 | 10.4108
| TAYNUILT | KENMORE | MINIMUM HEADROOM | NN 00325 34042 | YES | YES | 0 | 1.06 | 1.0547 | 1.0474 | 1.04 | 1.0347 | 1.0053 | 0.97263 | 0.93895 | 0.91158 | 0.88105 | 0.68526 | 0.46737 | 0.33789 | 1.0305 | 1.0284 | 1.0253 | 1.02 | 1.0168 | 1.0032 | 0.97684 | 0.94947 | 0.92632 | 0.90105 | 0.72947 | 0.53368 | 0.40632 | 1.0389 | 1.0337 | 1.0274 | 1.0189 | 1.0126 | 0.98421 | 0.95053 | 0.91789 | 0.88947 | 0.85789 | 0.65368 | 0.42316 | 0.27895
|  | KENMORE | EE |  |  |  |  | 1.0621 | 1.0558 | 1.0495 | 1.0421 | 1.0358 | 1.0053 | 0.97263 | 0.93895 | 0.91158 | 0.88105 | 0.68526 | 0.46737 | 0.33789 | 1.0326 | 1.0284 | 1.0253 | 1.0221 | 1.0179 | 1.0032 | 0.97684 | 0.94947 | 0.92632 | 0.90105 | 0.72947 | 0.53368 | 0.40632 | 1.0411 | 1.0358 | 1.0274 | 1.0211 | 1.0137 | 0.98421 | 0.95053 | 0.91789 | 0.88947 | 0.85789 | 0.65368 | 0.42316 | 0.27895
|  | KENMORE | HT |  |  |  |  | 1.06 | 1.0547 | 1.0474 | 1.04 | 1.0347 | 1.0105 | 0.98632 | 0.96421 | 0.93579 | 0.90737 | 0.74842 | 0.59368 | 0.49895 | 1.0305 | 1.0284 | 1.0253 | 1.02 | 1.0168 | 1.0032 | 0.98421 | 0.96421 | 0.94 | 0.91789 | 0.76842 | 0.61263 | 0.51158 | 1.0389 | 1.0337 | 1.0274 | 1.0189 | 1.0126 | 0.98947 | 0.96526 | 0.94105 | 0.91368 | 0.88526 | 0.71579 | 0.54316 | 0.43474
|  | KENMORE | HE |  |  |  |  | 1.0663 | 1.0621 | 1.0589 | 1.0558 | 1.0526 | 1.0253 | 1 | 0.97368 | 0.94842 | 0.91579 | 0.77789 | 0.62526 | 0.46211 | 1.0337 | 1.0326 | 1.0305 | 1.0284 | 1.0263 | 1.0137 | 1 | 0.97579 | 0.95474 | 0.92526 | 0.80211 | 0.65895 | 0.50632 | 1.0389 | 1.0337 | 1.0274 | 1.0189 | 1.0126 | 0.98947 | 0.96526 | 0.94105 | 0.91368 | 0.88526 | 0.71579 | 0.54316 | 0.43474
|  | KENMORE | CF |  |  |  |  | 1.0674 | 1.0663 | 1.0642 | 1.0611 | 1.0589 | 1.0495 | 1.0389 | 1.0295 | 1.0179 | 1.0053 | 0.94105 | 0.84737 | 0.75684 | 1.0347 | 1.0337 | 1.0326 | 1.0326 | 1.0316 | 1.0263 | 1.0221 | 1.0179 | 1.0126 | 1 | 0.94105 | 0.85158 | 0.76105 | 1.0432 | 1.0421 | 1.0411 | 1.0389 | 1.0379 | 1.0295 | 1.0189 | 1.0095 | 0.99789 | 0.98421 | 0.91474 | 0.81368 | 0.71368
| STRATHLEVEN | KEPCULLOCH | MINIMUM HEADROOM | NS 53864 91598 | NO | YES | 0 | 6.2282 | 6.1176 | 5.9576 | 5.765 | 13.7921 | 13.3932 | 12.9963 | 12.5795 | 12.1321 | 11.6816 | 9.6016 | 7.4142 | 6.2089 | 5.82 | 5.6768 | 5.5011 | 5.2863 | 12.8611 | 12.4726 | 12.0863 | 11.6779 | 11.2474 | 10.8168 | 8.9232 | 6.9737 | 5.7263 | 5.9783 | 5.8351 | 5.6572 | 5.4393 | 13.2316 | 12.8021 | 12.3747 | 11.9253 | 11.4453 | 10.9632 | 8.82 | 6.4979 | 5.1568
|  | KEPCULLOCH | EE |  |  |  |  | 6.2703 | 6.1808 | 6.0534 | 5.8871 | 13.9405 | 13.5363 | 13.1005 | 12.6353 | 12.2174 | 11.7953 | 9.6016 | 7.4142 | 6.2089 | 5.8747 | 5.7589 | 5.6105 | 5.4263 | 13.0337 | 12.6568 | 12.2579 | 11.8295 | 11.4337 | 11.0379 | 8.9979 | 6.9737 | 5.7263 | 6.032 | 5.9162 | 5.7657 | 5.5772 | 13.3989 | 12.9716 | 12.5116 | 12.0221 | 11.5779 | 11.1295 | 8.82 | 6.4979 | 5.1568
|  | KEPCULLOCH | HT |  |  |  |  | 6.2282 | 6.1176 | 5.9576 | 5.765 | 13.7921 | 13.3932 | 12.9963 | 12.5795 | 12.1321 | 11.6816 | 9.7584 | 8.2174 | 7.0647 | 5.82 | 5.6768 | 5.5011 | 5.2863 | 12.8611 | 12.4726 | 12.0863 | 11.6779 | 11.2474 | 10.8168 | 8.9232 | 7.3295 | 6.0547 | 5.9783 | 5.8351 | 5.6572 | 5.4393 | 13.2316 | 12.8021 | 12.3747 | 11.9253 | 11.4453 | 10.9632 | 8.8853 | 7.1705 | 5.8484
|  | KEPCULLOCH | HE |  |  |  |  | 6.3261 | 6.2671 | 6.1882 | 6.0692 | 14.1637 | 13.7753 | 13.4289 | 13.0626 | 12.7037 | 12.3437 | 10.6058 | 9.0374 | 7.4721 | 5.9463 | 5.8684 | 5.7611 | 5.6179 | 13.2663 | 12.9116 | 12.5905 | 12.2432 | 11.9032 | 11.5589 | 9.8716 | 8.3589 | 6.8716 | 5.9783 | 5.8351 | 5.6572 | 5.4393 | 13.2316 | 12.8021 | 12.3747 | 11.9253 | 11.4453 | 10.9632 | 8.8853 | 7.1705 | 5.8484
|  | KEPCULLOCH | CF |  |  |  |  | 6.3545 | 6.3155 | 6.2724 | 6.2218 | 14.4089 | 14.2511 | 14.1016 | 13.9416 | 13.79 | 13.6489 | 12.7847 | 11.8321 | 11.0637 | 5.9821 | 5.9337 | 5.8768 | 5.8063 | 13.5463 | 13.3989 | 13.2579 | 13.1042 | 12.9547 | 12.8095 | 11.9474 | 11.0326 | 10.2716 | 6.1404 | 6.0909 | 6.033 | 5.9625 | 13.9189 | 13.7526 | 13.5937 | 13.4221 | 13.2579 | 13.1021 | 12.1589 | 11.1316 | 10.2916
| TAYNUILT | KERRERA | MINIMUM HEADROOM | NM 82340 27997 | YES | YES | 0 | 0.32105 | 0.31895 | 0.31684 | 0.31579 | 0.31263 | 0.31053 | 0.30947 | 0.30632 | 0.30421 | 0.30211 | 0.29474 | 0.28947 | 0.28421 | 0.31053 | 0.30947 | 0.30842 | 0.30737 | 0.30526 | 0.30421 | 0.30316 | 0.30105 | 0.29895 | 0.29684 | 0.28842 | 0.28211 | 0.27684 | 0.31368 | 0.31263 | 0.31053 | 0.30842 | 0.30526 | 0.30316 | 0.30105 | 0.29789 | 0.29579 | 0.29474 | 0.28526 | 0.28 | 0.27368
|  | KERRERA | EE |  |  |  |  | 0.32316 | 0.32105 | 0.31895 | 0.31684 | 0.31579 | 0.31474 | 0.31263 | 0.31053 | 0.30947 | 0.30842 | 0.30211 | 0.29789 | 0.29474 | 0.31158 | 0.31053 | 0.30947 | 0.30842 | 0.30737 | 0.30632 | 0.30526 | 0.30421 | 0.30316 | 0.30211 | 0.29579 | 0.29158 | 0.28842 | 0.31474 | 0.31368 | 0.31263 | 0.31053 | 0.30842 | 0.30737 | 0.30526 | 0.30316 | 0.30105 | 0.3 | 0.29368 | 0.28842 | 0.28526
|  | KERRERA | HT |  |  |  |  | 0.32105 | 0.31895 | 0.31684 | 0.31579 | 0.31263 | 0.31053 | 0.30947 | 0.30632 | 0.30421 | 0.30211 | 0.29474 | 0.28947 | 0.28421 | 0.31053 | 0.30947 | 0.30842 | 0.30737 | 0.30526 | 0.30421 | 0.30316 | 0.30105 | 0.29895 | 0.29684 | 0.28842 | 0.28211 | 0.27684 | 0.31368 | 0.31263 | 0.31053 | 0.30842 | 0.30526 | 0.30316 | 0.30105 | 0.29789 | 0.29579 | 0.29474 | 0.28526 | 0.28 | 0.27368
|  | KERRERA | HE |  |  |  |  | 0.32421 | 0.32316 | 0.32211 | 0.32105 | 0.32 | 0.31895 | 0.31684 | 0.31684 | 0.31474 | 0.31368 | 0.31053 | 0.30842 | 0.30737 | 0.31263 | 0.31158 | 0.31053 | 0.31053 | 0.30947 | 0.30842 | 0.30737 | 0.30737 | 0.30632 | 0.30526 | 0.30316 | 0.30211 | 0.30211 | 0.31368 | 0.31263 | 0.31053 | 0.30842 | 0.30526 | 0.30316 | 0.30105 | 0.29789 | 0.29579 | 0.29474 | 0.28526 | 0.28 | 0.27368
|  | KERRERA | CF |  |  |  |  | 0.32526 | 0.32421 | 0.32316 | 0.32316 | 0.32316 | 0.32211 | 0.32105 | 0.32 | 0.32 | 0.31895 | 0.31579 | 0.31368 | 0.31263 | 0.31263 | 0.31263 | 0.31158 | 0.31158 | 0.31158 | 0.31053 | 0.31053 | 0.30947 | 0.30947 | 0.30947 | 0.30737 | 0.30632 | 0.30632 | 0.31579 | 0.31579 | 0.31474 | 0.31474 | 0.31474 | 0.31368 | 0.31368 | 0.31263 | 0.31263 | 0.31263 | 0.30947 | 0.30632 | 0.30526
| GRUDIE BRIDGE | KERRY FALLS | MINIMUM HEADROOM | NG 82909 71978 | YES | NO | 0 | 0.57789 | 0.52105 | 0.46632 | 0.41053 | 0.35158 | 0.26947 | 0.18526 | 0.10105 | 0.049474 | -0.021053 | -0.26947 | -0.46105 | -0.63263 | 1.0168 | 0.97895 | 0.94 | 0.87684 | 0.81684 | 0.70947 | 0.60211 | 0.49474 | 0.43895 | 0.38526 | 0.15474 | -0.037895 | -0.20842 | 0.35474 | 0.29789 | 0.24316 | 0.18632 | 0.12 | 0.046316 | -0.036842 | -0.12211 | -0.17684 | -0.26211 | -0.51895 | -0.71895 | -0.90105
|  | KERRY FALLS | EE |  |  |  |  | 0.59789 | 0.53895 | 0.47789 | 0.41579 | 0.35158 | 0.28842 | 0.22947 | 0.14632 | 0.062105 | -0.021053 | -0.26947 | -0.46105 | -0.63263 | 1.0295 | 0.99158 | 0.95158 | 0.91053 | 0.85368 | 0.79474 | 0.73895 | 0.64421 | 0.54842 | 0.45158 | 0.21789 | 0.031579 | -0.13368 | 0.37579 | 0.31474 | 0.25158 | 0.18632 | 0.12 | 0.054737 | -0.0063158 | -0.091579 | -0.17684 | -0.26211 | -0.51895 | -0.71895 | -0.90105
|  | KERRY FALLS | HT |  |  |  |  | 0.57789 | 0.52105 | 0.46632 | 0.41053 | 0.35474 | 0.26947 | 0.18526 | 0.10105 | 0.049474 | 4.4409e-16 | -0.20316 | -0.37158 | -0.51895 | 1.0168 | 0.97895 | 0.94 | 0.87684 | 0.81684 | 0.70947 | 0.60211 | 0.49474 | 0.43895 | 0.38526 | 0.15474 | -0.037895 | -0.20842 | 0.35474 | 0.29789 | 0.24316 | 0.18632 | 0.13158 | 0.046316 | -0.036842 | -0.12211 | -0.17474 | -0.22421 | -0.44526 | -0.67579 | -0.88211
|  | KERRY FALLS | HE |  |  |  |  | 0.62947 | 0.6 | 0.56737 | 0.53474 | 0.5 | 0.46632 | 0.43474 | 0.38211 | 0.33158 | 0.28316 | 0.15263 | 0.070526 | 0.0052632 | 1.0495 | 1.0284 | 1.0063 | 0.98211 | 0.95789 | 0.93158 | 0.90842 | 0.86211 | 0.8 | 0.73789 | 0.59684 | 0.51895 | 0.45789 | 0.35474 | 0.29789 | 0.24316 | 0.18632 | 0.13158 | 0.046316 | -0.036842 | -0.12211 | -0.17474 | -0.22421 | -0.44526 | -0.67579 | -0.88211
|  | KERRY FALLS | CF |  |  |  |  | 1.8347 | 1.8242 | 1.8137 | 1.8032 | 1.7916 | 1.7811 | 1.7695 | 1.7589 | 1.7484 | 1.7368 | 1.6832 | 1.6379 | 1.6063 | 1.7926 | 1.7821 | 1.7716 | 1.7611 | 1.7505 | 1.7389 | 1.7284 | 1.7179 | 1.7063 | 1.6958 | 1.5884 | 1.5358 | 1.4979 | 1.8568 | 1.8411 | 1.8263 | 1.8105 | 1.7926 | 1.7768 | 1.7611 | 1.7453 | 1.7189 | 1.6916 | 1.5853 | 1.5242 | 1.4779
| TAYNUILT | KILCHRENAN | MINIMUM HEADROOM | NN 03495 23835 | YES | YES | 0 | 0.98421 | 0.96211 | 0.93684 | 0.91158 | 0.88632 | 0.76316 | 0.61579 | 0.46421 | 0.32947 | 0.16737 | -1.1137 | -2.5389 | -3.6211 | 0.97579 | 0.95368 | 0.92947 | 0.90526 | 0.88 | 0.79368 | 0.67474 | 0.55368 | 0.43579 | 0.23158 | -0.92421 | -2.3084 | -3.4695 | 0.96842 | 0.94842 | 0.92526 | 0.90316 | 0.87579 | 0.75895 | 0.60842 | 0.45579 | 0.31684 | 0.16737 | -1.2421 | -2.7937 | -4.0242
|  | KILCHRENAN | EE |  |  |  |  | 0.99368 | 0.97368 | 0.94421 | 0.91789 | 0.88947 | 0.76316 | 0.61579 | 0.46421 | 0.32947 | 0.18316 | -1.1137 | -2.5389 | -3.6211 | 0.98526 | 0.96632 | 0.94105 | 0.91579 | 0.89158 | 0.79368 | 0.67474 | 0.55368 | 0.44421 | 0.32105 | -0.92421 | -2.3084 | -3.4695 | 0.97579 | 0.95684 | 0.92947 | 0.90316 | 0.87579 | 0.75895 | 0.60842 | 0.45579 | 0.31684 | 0.16737 | -1.2421 | -2.7937 | -4.0242
|  | KILCHRENAN | HT |  |  |  |  | 0.98421 | 0.96211 | 0.93684 | 0.91158 | 0.88632 | 0.78 | 0.67158 | 0.56105 | 0.53895 | 0.29789 | -0.85579 | -2.1442 | -3.0221 | 0.97579 | 0.95368 | 0.92947 | 0.90526 | 0.88 | 0.79368 | 0.70211 | 0.60842 | 0.58526 | 0.34947 | -0.81474 | -2.2168 | -3.2011 | 0.96842 | 0.94842 | 0.92526 | 0.90316 | 0.87895 | 0.77684 | 0.66526 | 0.55263 | 0.52842 | 0.26632 | -1.0084 | -2.4758 | -3.4853
|  | KILCHRENAN | HE |  |  |  |  | 1.0063 | 0.99579 | 0.98316 | 0.97053 | 0.95789 | 0.81579 | 0.66947 | 0.52 | 0.37474 | 0.16737 | -0.71789 | -1.8084 | -2.9937 | 0.99895 | 0.98842 | 0.97579 | 0.96421 | 0.95263 | 0.83579 | 0.70316 | 0.56632 | 0.43579 | 0.23158 | -0.61579 | -1.72 | -2.9242 | 0.96842 | 0.94842 | 0.92526 | 0.90316 | 0.87895 | 0.77684 | 0.66526 | 0.55263 | 0.52842 | 0.26632 | -1.0084 | -2.4758 | -3.4853
|  | KILCHRENAN | CF |  |  |  |  | 1.0126 | 1.0053 | 1 | 0.99263 | 0.98526 | 0.93684 | 0.89474 | 0.81579 | 0.72842 | 0.62842 | 0.17474 | -0.50947 | -1.2611 | 1.0053 | 1 | 0.99368 | 0.98632 | 0.97895 | 0.94316 | 0.90737 | 0.83263 | 0.74316 | 0.63684 | 0.18211 | -0.51684 | -1.3295 | 0.99263 | 0.98632 | 0.98211 | 0.97579 | 0.96842 | 0.92421 | 0.88526 | 0.81368 | 0.71579 | 0.60211 | 0.10316 | -0.65579 | -1.5084
| STRATHLEVEN | KILLEARN | MINIMUM HEADROOM | NS 51313 86758 | YES | YES | 0.066 | 1.3656 | 1.3045 | 1.1593 | 0.96663 | 0.73716 | 0.31505 | -0.106 | -0.56284 | -1.0039 | -1.4765 | -3.8144 | -7.3523 | -10.4249 | 1.1361 | 1.0203 | 0.86137 | 0.63611 | 0.374 | -0.046 | -0.46495 | -0.89653 | -1.3523 | -1.806 | -3.9555 | -8.0723 | -11.0249 | 1.0361 | 0.91505 | 0.75084 | 0.52453 | 0.25926 | -0.19337 | -0.64811 | -1.1144 | -1.6123 | -2.1092 | -4.5165 | -8.6534 | -11.9197
|  | KILLEARN | EE |  |  |  |  | 1.3814 | 1.3508 | 1.2414 | 1.0772 | 0.88032 | 0.44242 | -0.080737 | -0.56284 | -1.0039 | -1.4534 | -3.8144 | -7.3502 | -10.4249 | 1.1772 | 1.0866 | 0.95611 | 0.77084 | 0.54137 | 0.11926 | -0.38811 | -0.84495 | -1.2607 | -1.6849 | -3.8997 | -7.4586 | -10.8492 | 1.0793 | 0.98347 | 0.84663 | 0.65505 | 0.42137 | -0.043895 | -0.60389 | -1.1144 | -1.5765 | -2.046 | -4.5165 | -8.3934 | -11.9197
|  | KILLEARN | HT |  |  |  |  | 1.3656 | 1.3045 | 1.1593 | 0.96663 | 0.73716 | 0.31505 | -0.106 | -0.53758 | -1.0039 | -1.4765 | -3.6313 | -7.3523 | -9.9449 | 1.1361 | 1.0203 | 0.86137 | 0.63611 | 0.374 | -0.046 | -0.46495 | -0.89653 | -1.3523 | -1.806 | -3.9555 | -8.0723 | -11.0249 | 1.0361 | 0.91505 | 0.75084 | 0.52453 | 0.25926 | -0.19337 | -0.64811 | -1.1134 | -1.6123 | -2.1092 | -4.4239 | -8.6534 | -11.6513
|  | KILLEARN | HE |  |  |  |  | 1.4045 | 1.3845 | 1.3382 | 1.1972 | 1.0287 | 0.58768 | 0.15716 | -0.22495 | -0.60284 | -0.98811 | -2.8565 | -5.7734 | -8.986 | 1.2224 | 1.1529 | 1.0529 | 0.89295 | 0.69084 | 0.26347 | -0.16074 | -0.53126 | -0.89653 | -1.2628 | -3.0671 | -6.1176 | -9.4881 | 1.0361 | 0.91505 | 0.75084 | 0.52453 | 0.25926 | -0.19337 | -0.64811 | -1.1134 | -1.6123 | -2.1092 | -4.4239 | -8.6534 | -11.6513
|  | KILLEARN | CF |  |  |  |  | 1.4161 | 1.4056 | 1.3919 | 1.3782 | 1.3277 | 1.1687 | 1.0119 | 0.82874 | 0.66663 | 0.50979 | -0.66074 | -2.5334 | -4.6828 | 1.2498 | 1.2182 | 1.1729 | 1.1129 | 1.0424 | 0.89189 | 0.73611 | 0.54663 | 0.37821 | 0.21084 | -1.0144 | -2.9871 | -5.3513 | 1.154 | 1.1214 | 1.074 | 1.0098 | 0.93716 | 0.76768 | 0.59505 | 0.38979 | 0.20874 | 0.034 | -1.2597 | -3.3292 | -5.7471
| KILLIN | KILLIN TOWN | MINIMUM HEADROOM | NN 56931 32662 | YES | YES | 0 | 2.7253 | 2.6863 | 2.6421 | 2.5916 | 2.5305 | 2.3958 | 2.2621 | 2.1 | 1.9526 | 1.8021 | 0.88632 | 1.4326 | 0.79263 | 2.4684 | 2.4263 | 2.3768 | 2.32 | 2.2547 | 2.1337 | 2.0116 | 1.8832 | 1.7442 | 1.6042 | 0.77579 | 1.1663 | 0.46842 | 2.5347 | 2.5158 | 2.4832 | 2.4305 | 2.3684 | 2.2274 | 2.0863 | 1.9242 | 1.7705 | 1.6137 | 0.64105 | 1.1589 | 0.42211
|  | KILLIN TOWN | EE |  |  |  |  | 2.7379 | 2.7084 | 2.6674 | 2.6232 | 2.5705 | 2.4274 | 2.2674 | 2.1 | 1.9526 | 1.8021 | 0.88632 | 4.3758 | 3.46 | 2.4842 | 2.4516 | 2.4095 | 2.3611 | 2.3032 | 2.1821 | 2.0432 | 1.8958 | 1.7663 | 1.6326 | 0.78737 | 4.2968 | 3.2916 | 2.5411 | 2.5253 | 2.5032 | 2.4642 | 2.4084 | 2.2653 | 2.0979 | 1.9242 | 1.7705 | 1.6137 | 0.64105 | 4.0189 | 2.9653
|  | KILLIN TOWN | HT |  |  |  |  | 2.7253 | 2.6863 | 2.6421 | 2.5916 | 2.5305 | 2.3958 | 2.2621 | 2.1232 | 1.9726 | 1.8179 | 0.98421 | 4.5905 | 3.8411 | 2.4684 | 2.4263 | 2.3768 | 2.32 | 2.2547 | 2.1337 | 2.0116 | 1.8832 | 1.7442 | 1.6042 | 0.77579 | 4.2726 | 3.4211 | 2.5347 | 2.5158 | 2.4832 | 2.4305 | 2.3684 | 2.2274 | 2.0863 | 1.94 | 1.78 | 1.6189 | 0.70947 | 4.1453 | 3.2663
|  | KILLIN TOWN | HE |  |  |  |  | 2.7568 | 2.7368 | 2.7126 | 2.6821 | 2.6432 | 2.5042 | 2.38 | 2.2526 | 2.1253 | 2.0011 | 1.2326 | 5.0137 | 4.0021 | 2.5053 | 2.4842 | 2.4558 | 2.4211 | 2.3779 | 2.26 | 2.1516 | 2.0358 | 1.9211 | 1.8095 | 1.0663 | 4.8232 | 3.7832 | 2.5347 | 2.5158 | 2.4832 | 2.4305 | 2.3684 | 2.2274 | 2.0863 | 1.94 | 1.78 | 1.6189 | 0.70947 | 4.1453 | 3.2663
|  | KILLIN TOWN | CF |  |  |  |  | 2.7663 | 2.7558 | 2.7411 | 2.7232 | 2.7084 | 2.6537 | 2.6032 | 2.5526 | 2.5021 | 2.4232 | 2.0232 | 1.4326 | 0.79263 | 2.5158 | 2.5032 | 2.4874 | 2.4695 | 2.4505 | 2.4032 | 2.36 | 2.3137 | 2.2684 | 2.1821 | 1.7747 | 1.1663 | 0.46842 | 2.5558 | 2.5505 | 2.5442 | 2.5368 | 2.5305 | 2.4926 | 2.4495 | 2.3979 | 2.3474 | 2.2589 | 1.82 | 1.1589 | 0.42211
| TAYNUILT | KILMELFORD | MINIMUM HEADROOM | NM 84056 14437 | YES | YES | 0 | 1.4042 | 1.3611 | 1.3137 | 1.2663 | 1.2116 | 1.1537 | 5.1979 | 5.1432 | 5.0905 | 5.0368 | 4.8284 | 4.7232 | 4.6179 | 0.94105 | 0.89579 | 0.84421 | 0.79158 | 0.73158 | 0.66842 | 4.7053 | 4.6453 | 4.5863 | 4.5284 | 4.2937 | 4.1821 | 4.0663 | 0.94 | 0.89368 | 0.84211 | 0.78947 | 0.72947 | 0.66632 | 4.7042 | 4.6442 | 4.5853 | 4.5274 | 4.2937 | 4.1811 | 4.0642
|  | KILMELFORD | EE |  |  |  |  | 1.4211 | 1.3842 | 1.3432 | 1.2989 | 1.2495 | 1.1968 | 5.2453 | 5.1968 | 5.1484 | 5.1011 | 4.8979 | 4.8116 | 4.7379 | 0.96 | 0.92211 | 0.87895 | 0.83263 | 0.77789 | 0.72211 | 4.7663 | 4.7126 | 4.66 | 4.6095 | 4.3874 | 4.3 | 4.2253 | 0.95895 | 0.91895 | 0.87368 | 0.82632 | 0.77053 | 0.71263 | 4.7558 | 4.7011 | 4.6474 | 4.5947 | 4.3674 | 4.2726 | 4.1916
|  | KILMELFORD | HT |  |  |  |  | 1.4042 | 1.3611 | 1.3137 | 1.2663 | 1.2116 | 1.1537 | 5.1979 | 5.1432 | 5.0905 | 5.0368 | 4.8284 | 4.7232 | 4.6179 | 0.94105 | 0.89579 | 0.84421 | 0.79158 | 0.73158 | 0.66842 | 4.7053 | 4.6453 | 4.5863 | 4.5284 | 4.2937 | 4.1821 | 4.0663 | 0.94 | 0.89368 | 0.84211 | 0.78947 | 0.72947 | 0.66632 | 4.7042 | 4.6442 | 4.5853 | 4.5274 | 4.2937 | 4.1811 | 4.0642
|  | KILMELFORD | HE |  |  |  |  | 1.4442 | 1.4211 | 1.3947 | 1.3632 | 1.3263 | 1.2853 | 5.3463 | 5.3084 | 5.2705 | 5.2337 | 5.0884 | 5.0453 | 5.0126 | 0.98421 | 0.96 | 0.93053 | 0.89789 | 0.85579 | 0.81158 | 4.8684 | 4.8263 | 4.7832 | 4.7432 | 4.5789 | 4.5337 | 4.5 | 0.94 | 0.89368 | 0.84211 | 0.78947 | 0.72947 | 0.66632 | 4.7042 | 4.6442 | 4.5853 | 4.5274 | 4.2937 | 4.1811 | 4.0642
|  | KILMELFORD | CF |  |  |  |  | 1.4568 | 1.4432 | 1.4284 | 1.4137 | 1.3947 | 1.3758 | 5.4547 | 5.4337 | 5.4137 | 5.3905 | 5.2884 | 5.2537 | 5.2295 | 0.99789 | 0.98526 | 0.96947 | 0.95158 | 0.93053 | 0.90947 | 4.9874 | 4.9632 | 4.94 | 4.9137 | 4.7968 | 4.7589 | 4.7326 | 0.99789 | 0.98316 | 0.96737 | 0.95053 | 0.92947 | 0.90842 | 4.9853 | 4.9621 | 4.9389 | 4.9126 | 4.7968 | 4.7589 | 4.7337
| TAYNUILT | KILNINVER | MINIMUM HEADROOM | NM 83049 22251 | YES | YES | 0.075 | 0.76184 | 0.71237 | 0.66289 | 0.61447 | 0.56711 | 0.51763 | 0.47026 | 0.425 | 0.38184 | 0.33974 | 0.15868 | -0.0034211 | -0.24763 | 0.78711 | 0.73342 | 0.67974 | 0.62711 | 0.57658 | 0.525 | 0.47447 | 0.42605 | 0.37974 | 0.33447 | 0.13553 | -0.046579 | -0.28553 | 0.78395 | 0.72921 | 0.67658 | 0.62395 | 0.57237 | 0.51974 | 0.46816 | 0.41974 | 0.37237 | 0.32816 | 0.12711 | -0.055 | -0.31921
|  | KILNINVER | EE |  |  |  |  | 0.78395 | 0.74395 | 0.70395 | 0.66395 | 0.62184 | 0.58289 | 0.545 | 0.50816 | 0.47132 | 0.43974 | 0.29132 | 0.165 | -0.045526 | 0.81132 | 0.76921 | 0.72711 | 0.68395 | 0.64079 | 0.59868 | 0.55974 | 0.52079 | 0.48289 | 0.44921 | 0.29237 | 0.15237 | -0.045526 | 0.80816 | 0.765 | 0.72184 | 0.67763 | 0.63237 | 0.59132 | 0.54921 | 0.51026 | 0.47132 | 0.43658 | 0.27553 | 0.13237 | -0.093947
|  | KILNINVER | HT |  |  |  |  | 0.76184 | 0.71237 | 0.66289 | 0.61447 | 0.56711 | 0.51763 | 0.47026 | 0.425 | 0.38184 | 0.33974 | 0.15868 | -0.0034211 | -0.24763 | 0.78711 | 0.73342 | 0.67974 | 0.62711 | 0.57658 | 0.525 | 0.47447 | 0.42605 | 0.37974 | 0.33447 | 0.13553 | -0.046579 | -0.28553 | 0.78395 | 0.72921 | 0.67658 | 0.62395 | 0.57237 | 0.51974 | 0.46816 | 0.41974 | 0.37237 | 0.32816 | 0.12711 | -0.055 | -0.31921
|  | KILNINVER | HE |  |  |  |  | 0.81447 | 0.79132 | 0.76605 | 0.73974 | 0.71237 | 0.685 | 0.66079 | 0.63553 | 0.61342 | 0.59132 | 0.51237 | 0.45553 | 0.34816 | 0.845 | 0.82079 | 0.79237 | 0.765 | 0.73658 | 0.70816 | 0.68289 | 0.65553 | 0.63237 | 0.60921 | 0.52711 | 0.465 | 0.36184 | 0.78395 | 0.72921 | 0.67658 | 0.62395 | 0.57237 | 0.51974 | 0.46816 | 0.41974 | 0.37237 | 0.32816 | 0.12711 | -0.055 | -0.31921
|  | KILNINVER | CF |  |  |  |  | 0.83026 | 0.81447 | 0.80184 | 0.785 | 0.76921 | 0.75553 | 0.73868 | 0.72289 | 0.70921 | 0.69342 | 0.62711 | 0.58079 | 0.54816 | 0.86079 | 0.845 | 0.83026 | 0.81342 | 0.79658 | 0.78184 | 0.76395 | 0.74711 | 0.73132 | 0.71342 | 0.64184 | 0.59237 | 0.55447 | 0.85658 | 0.84079 | 0.82711 | 0.80921 | 0.79342 | 0.77763 | 0.75974 | 0.74289 | 0.72711 | 0.71026 | 0.63868 | 0.58711 | 0.54921
| BEAULY | KILTARLITY | MINIMUM HEADROOM | NH 50271 41265 | YES | YES | 0 | 5.9463 | 5.8968 | 5.8421 | 5.7863 | 5.7295 | 5.5526 | 5.3768 | 5.1926 | 5.0484 | 4.9095 | 4.1979 | 3.3516 | 2.78 | 5.7642 | 5.7063 | 5.6453 | 5.5842 | 5.5253 | 5.3537 | 5.1842 | 5.0053 | 4.8789 | 4.7589 | 4.1895 | 3.4295 | 2.8379 | 5.7979 | 5.7421 | 5.6821 | 5.6211 | 5.5632 | 5.3779 | 5.1937 | 4.9968 | 4.8474 | 4.7042 | 3.9821 | 3.0968 | 2.4537
|  | KILTARLITY | EE |  |  |  |  | 5.9695 | 5.9316 | 5.8832 | 5.8368 | 5.7905 | 5.6568 | 5.5042 | 5.3021 | 5.12 | 4.9274 | 4.1979 | 3.3516 | 2.78 | 5.7926 | 5.7474 | 5.6958 | 5.6453 | 5.5947 | 5.4821 | 5.3547 | 5.1674 | 4.9937 | 4.8095 | 4.1895 | 3.4295 | 2.8379 | 5.8253 | 5.7811 | 5.7295 | 5.6779 | 5.6274 | 5.4916 | 5.3347 | 5.1242 | 4.9316 | 4.7263 | 3.9821 | 3.0968 | 2.4537
|  | KILTARLITY | HT |  |  |  |  | 5.9463 | 5.8968 | 5.8421 | 5.7863 | 5.7295 | 5.5526 | 5.3768 | 5.1926 | 5.0484 | 4.9095 | 4.3284 | 3.7105 | 3.2453 | 5.7642 | 5.7063 | 5.6453 | 5.5842 | 5.5253 | 5.3537 | 5.1842 | 5.0053 | 4.8789 | 4.7589 | 4.2358 | 3.6116 | 3.1105 | 5.7979 | 5.7421 | 5.6821 | 5.6211 | 5.5632 | 5.3779 | 5.1937 | 4.9968 | 4.8474 | 4.7042 | 4.0968 | 3.4263 | 2.9063
|  | KILTARLITY | HE |  |  |  |  | 6 | 5.9768 | 5.9516 | 5.9232 | 5.8958 | 5.7674 | 5.6568 | 5.5105 | 5.3653 | 5.2274 | 4.6853 | 4.0179 | 3.2947 | 5.8284 | 5.8011 | 5.7726 | 5.7421 | 5.7116 | 5.6063 | 5.5147 | 5.3758 | 5.24 | 5.1126 | 4.64 | 3.9937 | 3.3021 | 5.7979 | 5.7421 | 5.6821 | 5.6211 | 5.5632 | 5.3779 | 5.1937 | 4.9968 | 4.8474 | 4.7042 | 4.0968 | 3.4263 | 2.9063
|  | KILTARLITY | CF |  |  |  |  | 6.0158 | 6.0021 | 5.9863 | 5.9695 | 5.9558 | 5.9011 | 5.8537 | 5.8063 | 5.7463 | 5.6937 | 5.42 | 4.9958 | 4.5779 | 5.8463 | 5.8305 | 5.8126 | 5.7937 | 5.7768 | 5.7305 | 5.6895 | 5.6484 | 5.5853 | 5.5295 | 5.2747 | 4.8653 | 4.4389 | 5.8779 | 5.8611 | 5.8442 | 5.8253 | 5.8095 | 5.7537 | 5.7042 | 5.6547 | 5.5863 | 5.5284 | 5.2411 | 4.7884 | 4.3305
| REDMOSS | KINCORTH | MINIMUM HEADROOM | NJ 94445 03252 | NO | YES | 0.125 | 15.5842 | 15.4495 | 14.8611 | 14.6905 | 14.52 | 14.3284 | 14.1432 | 13.9611 | 13.78 | 13.6063 | 12.9316 | 12.3516 | 11.8379 | 14.5687 | 14.1961 | 13.5213 | 13.3403 | 13.1561 | 12.9571 | 12.7645 | 12.575 | 12.3887 | 12.2076 | 11.5192 | 10.8982 | 10.3318 | 14.1938 | 13.8612 | 13.2022 | 13.0212 | 12.8401 | 12.6391 | 12.4433 | 12.2517 | 12.0622 | 11.878 | 11.1854 | 10.5612 | 9.9896
|  | KINCORTH | EE |  |  |  |  | 15.6179 | 15.5463 | 15.2537 | 14.8737 | 14.6011 | 14.3716 | 14.1726 | 14.0158 | 13.8663 | 13.7232 | 13.0474 | 12.5737 | 12.1905 | 14.6276 | 14.4466 | 13.9718 | 13.5392 | 13.235 | 12.9876 | 12.7792 | 12.6192 | 12.4666 | 12.3213 | 11.6297 | 11.1697 | 10.7571 | 14.2928 | 14.0991 | 13.6412 | 13.218 | 12.9191 | 12.6696 | 12.458 | 12.2928 | 12.137 | 11.9864 | 11.2717 | 10.7928 | 10.3749
|  | KINCORTH | HT |  |  |  |  | 15.5842 | 15.4495 | 14.8611 | 14.6905 | 14.52 | 14.3284 | 14.1432 | 13.9611 | 13.78 | 13.6063 | 12.9316 | 12.3516 | 11.8379 | 14.5687 | 14.1961 | 13.5213 | 13.3403 | 13.1561 | 12.9571 | 12.7645 | 12.575 | 12.3887 | 12.2076 | 11.5192 | 10.8982 | 10.3318 | 14.1938 | 13.8612 | 13.2022 | 13.0212 | 12.8401 | 12.6391 | 12.4433 | 12.2517 | 12.0622 | 11.878 | 11.1854 | 10.5612 | 9.9896
|  | KINCORTH | HE |  |  |  |  | 15.6611 | 15.6095 | 15.3326 | 15.0242 | 14.8516 | 14.7084 | 14.5863 | 14.4747 | 14.3684 | 14.2663 | 13.8611 | 13.5347 | 13.2937 | 14.6708 | 14.5887 | 14.0497 | 13.6982 | 13.5076 | 13.3603 | 13.2371 | 13.1234 | 13.0161 | 12.9139 | 12.5045 | 12.155 | 11.9161 | 14.1938 | 13.8612 | 13.2022 | 13.0212 | 12.8401 | 12.6391 | 12.4433 | 12.2517 | 12.0622 | 11.878 | 11.1854 | 10.5612 | 9.9896
|  | KINCORTH | CF |  |  |  |  | 15.6853 | 15.6505 | 15.6147 | 15.5779 | 15.5411 | 15.4958 | 15.3537 | 15.1874 | 15.0789 | 14.9579 | 14.5358 | 14.2842 | 14.1021 | 14.695 | 14.6603 | 14.6224 | 14.5718 | 14.4245 | 14.2803 | 14.0939 | 13.9108 | 13.7918 | 13.6582 | 13.2045 | 12.9413 | 12.7497 | 14.3601 | 14.3243 | 14.2833 | 14.2043 | 14.0833 | 13.9401 | 13.758 | 13.5749 | 13.4559 | 13.3233 | 12.8686 | 12.597 | 12.3991
| FORT WILLIAM | KINGAIRLOCH | MINIMUM HEADROOM | NM 76917 56652 | YES | NO | 0 | 0.12316 | 0.12211 | 0.12105 | 0.12 | 0.11684 | 0.11263 | 0.11053 | 0.10737 | 0.10316 | 0.10105 | -0.21474 | -0.22526 | -0.23789 | 0.11263 | 0.11158 | 0.11158 | 0.11158 | 0.10947 | 0.10737 | 0.10421 | 0.10211 | 0.098947 | 0.095789 | -0.15368 | -0.16526 | -0.17474 | 0.11684 | 0.11474 | 0.11368 | 0.11158 | 0.10842 | 0.10737 | 0.10526 | 0.10316 | 0.098947 | 0.095789 | -0.22211 | -0.23368 | -0.24737
|  | KINGAIRLOCH | EE |  |  |  |  | 0.12421 | 0.12211 | 0.12105 | 0.12 | 0.11684 | 0.11263 | 0.11053 | 0.10737 | 0.10316 | 0.10105 | -0.21474 | -0.22526 | -0.23789 | 0.11368 | 0.11158 | 0.11158 | 0.11158 | 0.10947 | 0.10737 | 0.10526 | 0.10316 | 0.098947 | 0.095789 | -0.15368 | -0.16316 | -0.17368 | 0.11789 | 0.11474 | 0.11368 | 0.11158 | 0.10842 | 0.10737 | 0.10526 | 0.10316 | 0.098947 | 0.095789 | -0.22211 | -0.23368 | -0.24737
|  | KINGAIRLOCH | HT |  |  |  |  | 0.12316 | 0.12316 | 0.12211 | 0.12105 | 0.11789 | 0.11579 | 0.11263 | 0.11053 | 0.10947 | 0.10526 | -0.20737 | -0.21789 | -0.22737 | 0.11263 | 0.11263 | 0.11263 | 0.11158 | 0.10947 | 0.10842 | 0.10421 | 0.10211 | 0.1 | 0.096842 | -0.15368 | -0.16526 | -0.17474 | 0.11684 | 0.11579 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.10842 | 0.10632 | 0.10316 | 0.1 | -0.21158 | -0.22421 | -0.23579
|  | KINGAIRLOCH | HE |  |  |  |  | 0.12421 | 0.12421 | 0.12211 | 0.12211 | 0.12211 | 0.12105 | 0.12 | 0.11895 | 0.11895 | 0.11895 | -0.038947 | -0.044211 | -0.049474 | 0.11368 | 0.11368 | 0.11263 | 0.11263 | 0.11158 | 0.11158 | 0.11053 | 0.11053 | 0.11053 | 0.11053 | -0.013684 | -0.017895 | -0.023158 | 0.11684 | 0.11579 | 0.11579 | 0.11474 | 0.11368 | 0.11263 | 0.10842 | 0.10632 | 0.10316 | 0.1 | -0.21158 | -0.22421 | -0.23579
|  | KINGAIRLOCH | CF |  |  |  |  | 0.12421 | 0.12421 | 0.12421 | 0.12421 | 0.12316 | 0.12316 | 0.12316 | 0.12316 | 0.12316 | 0.12211 | 0.12105 | 0.11684 | 0.11474 | 0.11368 | 0.11368 | 0.11368 | 0.11368 | 0.11263 | 0.11263 | 0.11263 | 0.11263 | 0.11263 | 0.11263 | 0.11158 | 0.10842 | 0.10632 | 0.11789 | 0.11789 | 0.11789 | 0.11684 | 0.11579 | 0.11579 | 0.11579 | 0.11579 | 0.11579 | 0.11579 | 0.11474 | 0.11263 | 0.11053
| DYCE | KINGSEAT | MINIMUM HEADROOM | NJ 89545 19709 | NO | YES | 1.108 | 12.4483 | 12.3367 | 12.2062 | 11.9578 | 11.5041 | 10.8631 | 10.2736 | 9.5883 | 8.9683 | 8.3588 | 6.0557 | 2.5567 | -0.58537 | 11.5183 | 11.4025 | 11.272 | 11.0015 | 10.4888 | 9.8583 | 9.2952 | 8.7162 | 8.1299 | 7.5383 | 5.6278 | 2.1278 | -1.0764 | 11.8965 | 11.7807 | 11.647 | 11.3723 | 10.8586 | 10.167 | 9.5428 | 8.8207 | 8.1617 | 7.5154 | 5.1733 | 1.427 | -2.1393
|  | KINGSEAT | EE |  |  |  |  | 12.4852 | 12.4094 | 12.2957 | 12.1799 | 11.7473 | 11.0009 | 10.2736 | 9.5883 | 8.9683 | 8.3588 | 6.0557 | 2.5567 | -0.58537 | 11.5552 | 11.4794 | 11.3688 | 11.2552 | 10.7678 | 10.0331 | 9.3478 | 8.7162 | 8.1352 | 7.5667 | 5.6278 | 2.3257 | -1.0764 | 11.9333 | 11.8575 | 11.7407 | 11.6217 | 11.1302 | 10.3217 | 9.5449 | 8.8207 | 8.1617 | 7.5154 | 5.1733 | 1.427 | -2.1393
|  | KINGSEAT | HT |  |  |  |  | 12.4483 | 12.3367 | 12.2062 | 11.9578 | 11.5041 | 10.8631 | 10.2799 | 9.6988 | 9.0609 | 8.4336 | 6.6852 | 3.0736 | 0.45568 | 11.5183 | 11.4025 | 11.272 | 11.0015 | 10.4888 | 9.8583 | 9.2952 | 8.7341 | 8.1299 | 7.5383 | 6.0173 | 2.1278 | -0.80379 | 11.8965 | 11.7807 | 11.647 | 11.3723 | 10.8586 | 10.167 | 9.5428 | 8.9207 | 8.2417 | 7.5744 | 5.7796 | 1.6996 | -1.3004
|  | KINGSEAT | HE |  |  |  |  | 12.5357 | 12.4915 | 12.4399 | 12.3778 | 12.0252 | 11.3325 | 10.7778 | 10.2399 | 9.7083 | 9.1925 | 7.6336 | 4.7799 | 1.3146 | 11.6057 | 11.5615 | 11.5109 | 11.4499 | 11.0457 | 10.3825 | 9.8562 | 9.3499 | 8.8488 | 8.3636 | 7.0678 | 4.2215 | 0.69411 | 11.8965 | 11.7807 | 11.647 | 11.3723 | 10.8586 | 10.167 | 9.5428 | 8.9207 | 8.2417 | 7.5744 | 5.7796 | 1.6996 | -1.3004
|  | KINGSEAT | CF |  |  |  |  | 12.562 | 12.5378 | 12.5094 | 12.4788 | 12.4494 | 12.2873 | 12.1294 | 11.9609 | 11.7273 | 11.4883 | 10.7041 | 8.7062 | 6.4957 | 11.632 | 11.6078 | 11.5794 | 11.5509 | 11.5215 | 11.3899 | 11.2552 | 11.1067 | 10.8752 | 10.6257 | 9.9341 | 7.8952 | 5.5183 | 12.0102 | 11.9859 | 11.9575 | 11.927 | 11.8975 | 11.7344 | 11.5733 | 11.3986 | 11.1449 | 10.8807 | 10.0691 | 7.8575 | 5.3575
| BOAT OF GARTEN | KINGUSSIE | MINIMUM HEADROOM | NH 75429 00426 | NO | YES | 0.05 | 7.4463 | 7.2884 | 7.1232 | 6.9242 | 6.7074 | 6.4674 | 6.2295 | 6.0495 | 5.8747 | 5.7495 | 5.2453 | 4.2221 | 3.8611 | 6.51 | 6.3016 | 6.0805 | 5.8437 | 5.5932 | 5.3132 | 5.0374 | 4.8332 | 4.6311 | 4.4953 | 3.9332 | 2.9889 | 2.5668 | 6.8303 | 6.6492 | 6.4313 | 6.1966 | 5.9482 | 5.6703 | 5.3966 | 5.1934 | 4.9934 | 4.8576 | 4.3039 | 3.225 | 2.8061
|  | KINGUSSIE | EE |  |  |  |  | 7.5032 | 7.3726 | 7.2326 | 7.0758 | 6.8842 | 6.6779 | 6.48 | 6.3274 | 6.1789 | 6.0811 | 5.6621 | 4.7368 | 4.4621 | 6.5837 | 6.4111 | 6.2226 | 6.0174 | 5.7953 | 5.5532 | 5.3226 | 5.1479 | 4.9774 | 4.8711 | 4.4142 | 3.5847 | 3.2647 | 6.8934 | 6.745 | 6.5703 | 6.3661 | 6.145 | 5.905 | 5.6745 | 5.5018 | 5.3313 | 5.225 | 4.7734 | 3.8039 | 3.4829
|  | KINGUSSIE | HT |  |  |  |  | 7.4463 | 7.2884 | 7.1232 | 6.9242 | 6.7074 | 6.4674 | 6.2295 | 6.0495 | 5.8747 | 5.7495 | 5.2453 | 4.2221 | 3.8611 | 6.51 | 6.3016 | 6.0805 | 5.8437 | 5.5932 | 5.3132 | 5.0374 | 4.8332 | 4.6311 | 4.4953 | 3.9332 | 2.9889 | 2.5668 | 6.8303 | 6.6492 | 6.4313 | 6.1966 | 5.9482 | 5.6703 | 5.3966 | 5.1934 | 4.9934 | 4.8576 | 4.3039 | 3.225 | 2.8061
|  | KINGUSSIE | HE |  |  |  |  | 7.5811 | 7.4884 | 7.3853 | 7.2695 | 7.1337 | 6.9611 | 6.7979 | 6.6779 | 6.5621 | 6.4968 | 6.2684 | 5.8 | 5.6874 | 6.6837 | 6.5574 | 6.4153 | 6.2542 | 6.0742 | 5.87 | 5.6784 | 5.5384 | 5.4047 | 5.3342 | 5.0847 | 4.6574 | 4.5258 | 6.8303 | 6.6492 | 6.4313 | 6.1966 | 5.9482 | 5.6703 | 5.3966 | 5.1934 | 4.9934 | 4.8576 | 4.3039 | 3.225 | 2.8061
|  | KINGUSSIE | CF |  |  |  |  | 7.6326 | 7.5853 | 7.5263 | 7.4621 | 7.3937 | 7.3211 | 7.2505 | 7.1916 | 7.1168 | 7.0705 | 6.8737 | 6.7463 | 6.6558 | 6.73 | 6.69 | 6.6068 | 6.5195 | 6.4216 | 6.3174 | 6.2163 | 6.1374 | 6.0489 | 5.9974 | 5.7774 | 5.6321 | 5.5247 | 6.9639 | 6.9408 | 6.9166 | 6.8429 | 6.7618 | 6.6661 | 6.565 | 6.4871 | 6.3997 | 6.3492 | 6.1313 | 5.9861 | 5.8797
| TAYNUILT | KINLOCH | MINIMUM HEADROOM | NM 52465 27215 | YES | YES | 0 | 1.2821 | 1.2474 | 1.2116 | 1.1768 | 1.1337 | 1.0884 | 1.0358 | 0.98211 | 0.93158 | 0.88105 | 0.66737 | 0.48105 | 0.31053 | 0.85368 | 0.80842 | 0.76105 | 0.71579 | 0.65474 | 0.59263 | 0.53263 | 0.47368 | 0.41789 | 0.36316 | 0.12421 | -0.086316 | -0.28211 | 0.62105 | 0.58 | 0.53895 | 0.49789 | 0.44526 | 0.39158 | 0.34 | 0.28842 | 0.24 | 0.19263 | -0.0073684 | -0.21684 | -0.41158
|  | KINLOCH | EE |  |  |  |  | 1.2979 | 1.2716 | 1.2432 | 1.2137 | 1.1863 | 1.1537 | 1.12 | 1.0884 | 1.0526 | 1.0158 | 0.84105 | 0.70105 | 0.57474 | 0.87474 | 0.84 | 0.80316 | 0.76737 | 0.73158 | 0.68842 | 0.64105 | 0.59684 | 0.55263 | 0.51053 | 0.31789 | 0.15895 | 0.013684 | 0.64 | 0.60842 | 0.57579 | 0.54316 | 0.51053 | 0.47263 | 0.43158 | 0.39368 | 0.35474 | 0.31895 | 0.15474 | 0.025263 | -0.11579
|  | KINLOCH | HT |  |  |  |  | 1.2821 | 1.2474 | 1.2116 | 1.1768 | 1.1337 | 1.0884 | 1.0358 | 0.98211 | 0.93158 | 0.88105 | 0.66737 | 0.48105 | 0.31053 | 0.85368 | 0.80842 | 0.76105 | 0.71579 | 0.65474 | 0.59263 | 0.53263 | 0.47368 | 0.41789 | 0.36316 | 0.12421 | -0.086316 | -0.28211 | 0.62105 | 0.58 | 0.53895 | 0.49789 | 0.44526 | 0.39158 | 0.34 | 0.28842 | 0.24 | 0.19263 | -0.0073684 | -0.21684 | -0.41158
|  | KINLOCH | HE |  |  |  |  | 1.32 | 1.3032 | 1.2842 | 1.2663 | 1.2463 | 1.2263 | 1.2074 | 1.1905 | 1.1726 | 1.1537 | 1.0768 | 1.0074 | 0.94105 | 0.90526 | 0.88316 | 0.86105 | 0.83789 | 0.81368 | 0.79053 | 0.76737 | 0.74632 | 0.72526 | 0.70105 | 0.58842 | 0.50105 | 0.42421 | 0.62105 | 0.58 | 0.53895 | 0.49789 | 0.44526 | 0.39158 | 0.34 | 0.28842 | 0.24 | 0.19263 | -0.0073684 | -0.21684 | -0.41158
|  | KINLOCH | CF |  |  |  |  | 1.3316 | 1.3211 | 1.3116 | 1.3011 | 1.2905 | 1.28 | 1.2695 | 1.2589 | 1.2484 | 1.2379 | 1.1874 | 1.1442 | 1.1032 | 0.91789 | 0.90737 | 0.89474 | 0.88105 | 0.86737 | 0.85368 | 0.84 | 0.82632 | 0.81263 | 0.79895 | 0.72947 | 0.65895 | 0.6 | 0.68 | 0.66737 | 0.65579 | 0.64421 | 0.63158 | 0.62 | 0.60737 | 0.59474 | 0.58316 | 0.57158 | 0.51053 | 0.45263 | 0.40632
| TUMMEL BRIDGE | KINLOCH RANNOCH | MINIMUM HEADROOM | NN 65927 58500 | YES | YES | 0 | 0.98 | 0.96105 | 0.93158 | 0.90105 | 0.86211 | 0.78316 | 0.68316 | 0.58 | 0.49053 | 0.39684 | -0.23789 | -1.0263 | -1.6253 | 0.97263 | 0.94842 | 0.91053 | 0.87158 | 0.83263 | 0.76105 | 0.69053 | 0.61895 | 0.54105 | 0.46105 | -0.10632 | -0.86 | -1.4842 | 0.98842 | 0.97263 | 0.93158 | 0.89158 | 0.84947 | 0.76632 | 0.66316 | 0.55474 | 0.45895 | 0.36105 | -0.31895 | -1.1758 | -1.8558
|  | KINLOCH RANNOCH | EE |  |  |  |  | 0.98421 | 0.96632 | 0.94211 | 0.90632 | 0.87579 | 0.78526 | 0.68316 | 0.58 | 0.49053 | 0.39684 | -0.23789 | -1.0263 | -1.6253 | 0.97895 | 0.96105 | 0.93263 | 0.89474 | 0.85895 | 0.78632 | 0.70737 | 0.62105 | 0.54632 | 0.46842 | -0.10632 | -0.86 | -1.4842 | 0.99053 | 0.97368 | 0.94947 | 0.90632 | 0.86526 | 0.76947 | 0.66316 | 0.55474 | 0.45895 | 0.36105 | -0.31895 | -1.1758 | -1.8558
|  | KINLOCH RANNOCH | HT |  |  |  |  | 0.98 | 0.96105 | 0.93158 | 0.90105 | 0.86211 | 0.78316 | 0.70316 | 0.62211 | 0.53368 | 0.44421 | -0.098947 | -0.79474 | -1.2705 | 0.97263 | 0.94842 | 0.91053 | 0.87158 | 0.83263 | 0.76105 | 0.69053 | 0.61895 | 0.54105 | 0.46105 | -0.071579 | -0.81579 | -1.34 | 0.98842 | 0.97263 | 0.93158 | 0.89158 | 0.84947 | 0.76632 | 0.68105 | 0.59684 | 0.50421 | 0.40947 | -0.18316 | -0.97158 | -1.5179
|  | KINLOCH RANNOCH | HE |  |  |  |  | 0.99263 | 0.98316 | 0.97474 | 0.96316 | 0.95368 | 0.87474 | 0.8 | 0.72421 | 0.64737 | 0.53474 | 0.049474 | -0.54 | -1.18 | 0.98947 | 0.97895 | 0.96947 | 0.96 | 0.94737 | 0.88526 | 0.81684 | 0.74105 | 0.67053 | 0.56 | 0.098947 | -0.49053 | -1.1326 | 0.98842 | 0.97263 | 0.93158 | 0.89158 | 0.84947 | 0.76632 | 0.68105 | 0.59684 | 0.50421 | 0.40947 | -0.18316 | -0.97158 | -1.5179
|  | KINLOCH RANNOCH | CF |  |  |  |  | 0.99579 | 0.99158 | 0.98632 | 0.98211 | 0.97684 | 0.94842 | 0.92211 | 0.88947 | 0.84947 | 0.8 | 0.55579 | 0.19053 | -0.20737 | 0.99368 | 0.98947 | 0.98316 | 0.97684 | 0.97263 | 0.94842 | 0.92842 | 0.89474 | 0.84316 | 0.78632 | 0.54211 | 0.17053 | -0.25579 | 0.99789 | 0.99474 | 0.99053 | 0.98632 | 0.98316 | 0.95789 | 0.93579 | 0.90105 | 0.84737 | 0.78632 | 0.51789 | 0.11368 | -0.33684
| GRUDIE BRIDGE | KINLOCHEWE | MINIMUM HEADROOM | NH 03723 62321 | YES | NO | 0 | 1.0411 | 1.0179 | 0.99368 | 0.97053 | 0.94526 | 0.92105 | 0.89789 | 0.87579 | 0.85474 | 0.83368 | 0.73579 | 0.65053 | 0.57263 | 0.98842 | 0.96316 | 0.93684 | 0.91368 | 0.88842 | 0.86526 | 0.84 | 0.81789 | 0.79579 | 0.77579 | 0.67263 | 0.58526 | 0.50316 | 1.0063 | 0.98 | 0.95368 | 0.92947 | 0.90316 | 0.87789 | 0.85368 | 0.83053 | 0.80737 | 0.78526 | 0.67684 | 0.58316 | 0.49684
|  | KINLOCHEWE | EE |  |  |  |  | 1.0453 | 1.0274 | 1.0032 | 0.97789 | 0.95368 | 0.92842 | 0.90526 | 0.88105 | 0.86 | 0.83895 | 0.73579 | 0.65053 | 0.57263 | 0.99895 | 0.97579 | 0.95368 | 0.93053 | 0.90842 | 0.88526 | 0.86421 | 0.84211 | 0.82211 | 0.80316 | 0.71053 | 0.63158 | 0.55789 | 1.0168 | 0.99053 | 0.96421 | 0.93789 | 0.91158 | 0.88421 | 0.86 | 0.83368 | 0.80947 | 0.78737 | 0.67684 | 0.58316 | 0.49684
|  | KINLOCHEWE | HT |  |  |  |  | 1.0411 | 1.0179 | 0.99368 | 0.97053 | 0.94526 | 0.92105 | 0.89789 | 0.87579 | 0.85474 | 0.83368 | 0.73579 | 0.65158 | 0.57368 | 0.98842 | 0.96316 | 0.93684 | 0.91368 | 0.88842 | 0.86526 | 0.84 | 0.81789 | 0.79579 | 0.77579 | 0.67263 | 0.58526 | 0.50316 | 1.0063 | 0.98 | 0.95368 | 0.92947 | 0.90316 | 0.87789 | 0.85368 | 0.83053 | 0.80737 | 0.78526 | 0.67895 | 0.58632 | 0.49895
|  | KINLOCHEWE | HE |  |  |  |  | 1.0526 | 1.0442 | 1.0368 | 1.0274 | 1.0137 | 1 | 0.98842 | 0.97474 | 0.96316 | 0.95158 | 0.90632 | 0.86632 | 0.82947 | 1.0126 | 1.0011 | 0.98842 | 0.97579 | 0.96211 | 0.94947 | 0.93789 | 0.92421 | 0.91368 | 0.90211 | 0.85895 | 0.82211 | 0.78526 | 1.0063 | 0.98 | 0.95368 | 0.92947 | 0.90316 | 0.87789 | 0.85368 | 0.83053 | 0.80737 | 0.78526 | 0.67895 | 0.58632 | 0.49895
|  | KINLOCHEWE | CF |  |  |  |  | 1.0568 | 1.0537 | 1.0495 | 1.0453 | 1.0411 | 1.0368 | 1.0326 | 1.0253 | 1.0189 | 1.0126 | 0.98316 | 0.96211 | 0.94632 | 1.0168 | 1.0137 | 1.0084 | 1 | 0.99474 | 0.98526 | 0.98 | 0.97158 | 0.96632 | 0.95789 | 0.92737 | 0.90526 | 0.88842 | 1.0337 | 1.0295 | 1.0263 | 1.0179 | 1.0116 | 1.0032 | 0.99579 | 0.98842 | 0.98316 | 0.97474 | 0.94316 | 0.92105 | 0.90316
| KINLOCHLEVEN | KINLOCHLEVEN | MINIMUM HEADROOM | NN 19285 62002 | NO | YES | 0 | 0.85368 | 0.78211 | 0.69158 | 0.60105 | 0.50526 | 0.36421 | 0.22421 | 0.047368 | -0.13053 | -0.30842 | -1.0389 | -1.9853 | -2.8274 | 0.76526 | 0.70211 | 0.6 | 0.49684 | 0.39263 | 0.26316 | 0.13895 | -0.029474 | -0.19474 | -0.36 | -1.0095 | -1.8505 | -2.6368 | 1.1263 | 1.0474 | 0.94316 | 0.83579 | 0.72842 | 0.57368 | 0.42 | 0.22842 | 0.027368 | -0.17158 | -0.95789 | -2.0284 | -2.9895
|  | KINLOCHLEVEN | EE |  |  |  |  | 0.86421 | 0.78211 | 0.69158 | 0.60105 | 0.50526 | 0.36421 | 0.22421 | 0.047368 | -0.13053 | -0.30842 | -1.0389 | -1.9853 | -2.8274 | 0.77474 | 0.70211 | 0.6 | 0.49684 | 0.39263 | 0.26316 | 0.13895 | -0.029474 | -0.19474 | -0.36 | -1.0095 | -1.8505 | -2.6368 | 1.1453 | 1.0474 | 0.94316 | 0.83579 | 0.72842 | 0.57368 | 0.42 | 0.22842 | 0.027368 | -0.17158 | -0.95789 | -2.0284 | -2.9895
|  | KINLOCHLEVEN | HT |  |  |  |  | 0.85368 | 0.80947 | 0.76421 | 0.71474 | 0.65684 | 0.51579 | 0.37789 | 0.24105 | 0.14737 | 0.052632 | -0.48316 | -1.3137 | -1.9242 | 0.76526 | 0.72316 | 0.66526 | 0.60632 | 0.54842 | 0.42632 | 0.30421 | 0.17474 | 0.094737 | 0.015789 | -0.47158 | -1.3421 | -1.9821 | 1.1263 | 1.0632 | 1 | 0.93579 | 0.87263 | 0.71684 | 0.56526 | 0.41474 | 0.31368 | 0.21474 | -0.37158 | -1.3221 | -2.0232
|  | KINLOCHLEVEN | HE |  |  |  |  | 0.87789 | 0.84632 | 0.81263 | 0.77789 | 0.74211 | 0.66737 | 0.59789 | 0.51263 | 0.41368 | 0.30737 | -0.24 | -0.90316 | -1.6116 | 0.78737 | 0.76737 | 0.73579 | 0.70105 | 0.66 | 0.59474 | 0.53158 | 0.44316 | 0.35684 | 0.26842 | -0.21579 | -0.85474 | -1.5568 | 1.1263 | 1.0632 | 1 | 0.93579 | 0.87263 | 0.71684 | 0.56526 | 0.41474 | 0.31368 | 0.21474 | -0.37158 | -1.3221 | -2.0232
|  | KINLOCHLEVEN | CF |  |  |  |  | 0.88526 | 0.87263 | 0.86 | 0.84737 | 0.83368 | 0.80526 | 0.78 | 0.75474 | 0.72842 | 0.67684 | 0.40526 | 0.027368 | -0.39789 | 0.79368 | 0.78632 | 0.77789 | 0.76632 | 0.75368 | 0.73368 | 0.71368 | 0.68842 | 0.65263 | 0.59789 | 0.32526 | -0.067368 | -0.53053 | 1.1853 | 1.1674 | 1.1484 | 1.1305 | 1.1105 | 1.0758 | 1.0432 | 1.0116 | 0.96421 | 0.89368 | 0.59053 | 0.16421 | -0.32421
| FORT WILLIAM | KINLOCHMOIDART | MINIMUM HEADROOM | NM 71407 72091 | YES | NO | 0 | 1.02 | 1.0084 | 0.98842 | 0.96842 | 0.94737 | 0.92526 | 0.90632 | 0.88632 | 0.86632 | 0.84421 | 0.75053 | 0.66947 | 0.58737 | 1.0116 | 1.0032 | 0.98316 | 0.96421 | 0.94211 | 0.92211 | 0.90316 | 0.88421 | 0.86526 | 0.84316 | 0.75368 | 0.67474 | 0.59579 | 1.0147 | 0.99895 | 0.98105 | 0.96316 | 0.94 | 0.91895 | 0.89895 | 0.87895 | 0.85895 | 0.83684 | 0.74211 | 0.66 | 0.57789
|  | KINLOCHMOIDART | EE |  |  |  |  | 1.02 | 1.0084 | 0.98842 | 0.96842 | 0.94737 | 0.92526 | 0.90632 | 0.88632 | 0.86632 | 0.84421 | 0.75053 | 0.66947 | 0.58737 | 1.0116 | 1.0032 | 0.98316 | 0.96421 | 0.94211 | 0.92211 | 0.90316 | 0.88421 | 0.86526 | 0.84316 | 0.75368 | 0.67474 | 0.59579 | 1.0147 | 0.99895 | 0.98105 | 0.96316 | 0.94 | 0.91895 | 0.89895 | 0.87895 | 0.85895 | 0.83684 | 0.74211 | 0.66 | 0.57789
|  | KINLOCHMOIDART | HT |  |  |  |  | 1.02 | 1.0158 | 1.0116 | 1.0074 | 1.0011 | 0.99579 | 0.98947 | 0.98316 | 0.97579 | 0.97053 | 0.93895 | 0.90842 | 0.87579 | 1.0116 | 1.0084 | 1.0074 | 1.0011 | 0.99579 | 0.98947 | 0.98421 | 0.97789 | 0.96947 | 0.96421 | 0.93263 | 0.90211 | 0.86947 | 1.0147 | 1.0095 | 1.0042 | 0.99895 | 0.99368 | 0.98737 | 0.98211 | 0.97579 | 0.96842 | 0.96316 | 0.93053 | 0.89789 | 0.86526
|  | KINLOCHMOIDART | HE |  |  |  |  | 1.0211 | 1.0168 | 1.0126 | 1.0095 | 1.0042 | 0.99895 | 0.99263 | 0.98632 | 0.98 | 0.97474 | 0.94421 | 0.91263 | 0.88105 | 1.0126 | 1.0095 | 1.0084 | 1.0042 | 0.99789 | 0.99263 | 0.98737 | 0.98105 | 0.97474 | 0.96947 | 0.94 | 0.90842 | 0.87789 | 1.0147 | 1.0095 | 1.0042 | 0.99895 | 0.99368 | 0.98737 | 0.98211 | 0.97579 | 0.96842 | 0.96316 | 0.93053 | 0.89789 | 0.86526
|  | KINLOCHMOIDART | CF |  |  |  |  | 1.0211 | 1.02 | 1.0179 | 1.0168 | 1.0168 | 1.0158 | 1.0147 | 1.0137 | 1.0137 | 1.0116 | 1.0074 | 1.0021 | 0.99684 | 1.0126 | 1.0126 | 1.0105 | 1.0105 | 1.0095 | 1.0095 | 1.0095 | 1.0084 | 1.0084 | 1.0063 | 1.0021 | 0.99579 | 0.99158 | 1.0158 | 1.0147 | 1.0126 | 1.0105 | 1.0095 | 1.0095 | 1.0074 | 1.0063 | 1.0063 | 1.0032 | 0.99895 | 0.99474 | 0.99053
| ELGIN | KINLOSS | MINIMUM HEADROOM | NJ 06695 61740 | NO | YES | 0.15 | 14.2442 | 14.1558 | 14.0589 | 13.9621 | 13.8632 | 13.6726 | 13.4884 | 13.3105 | 13.1253 | 12.94 | 11.9137 | 10.46 | 9.3947 | 13.4763 | 13.3805 | 13.2763 | 13.1721 | 13.0647 | 12.8889 | 12.7174 | 12.5532 | 12.3868 | 12.2205 | 11.2753 | 9.8532 | 8.7668 | 13.8513 | 13.7555 | 13.6513 | 13.5461 | 13.4376 | 13.2397 | 13.0471 | 12.8618 | 12.6713 | 12.4808 | 11.4155 | 9.8408 | 8.6366
|  | KINLOSS | EE |  |  |  |  | 14.28 | 14.2095 | 14.1274 | 14.0421 | 13.9526 | 13.7611 | 13.5495 | 13.34 | 13.1642 | 12.9863 | 11.9137 | 10.46 | 9.3947 | 13.5163 | 13.4395 | 13.3521 | 13.2616 | 13.1679 | 12.9942 | 12.8058 | 12.6205 | 12.4658 | 12.3111 | 11.33 | 9.9174 | 8.7668 | 13.8913 | 13.8145 | 13.7261 | 13.6334 | 13.5376 | 13.3376 | 13.1187 | 12.9029 | 12.7229 | 12.5397 | 11.4155 | 9.8408 | 8.6366
|  | KINLOSS | HT |  |  |  |  | 14.2442 | 14.1558 | 14.0589 | 13.9621 | 13.8632 | 13.6726 | 13.4884 | 13.3105 | 13.1253 | 12.94 | 11.9674 | 10.6432 | 9.7484 | 13.4763 | 13.3805 | 13.2763 | 13.1721 | 13.0647 | 12.8889 | 12.7174 | 12.5532 | 12.3868 | 12.2205 | 11.2753 | 9.8532 | 8.8563 | 13.8513 | 13.7555 | 13.6513 | 13.5461 | 13.4376 | 13.2397 | 13.0471 | 12.8618 | 12.6713 | 12.4808 | 11.4366 | 9.945 | 8.9239
|  | KINLOSS | HE |  |  |  |  | 14.3305 | 14.2842 | 14.2305 | 14.1737 | 14.1126 | 13.9316 | 13.7716 | 13.6189 | 13.4789 | 13.3379 | 12.4032 | 11.3021 | 10.1232 | 13.57 | 13.5195 | 13.4637 | 13.4016 | 13.3353 | 13.1753 | 13.0332 | 12.8963 | 12.7763 | 12.6542 | 11.7532 | 10.6405 | 9.4479 | 13.8513 | 13.7555 | 13.6513 | 13.5461 | 13.4376 | 13.2397 | 13.0471 | 12.8618 | 12.6713 | 12.4808 | 11.4366 | 9.945 | 8.9239
|  | KINLOSS | CF |  |  |  |  | 14.3547 | 14.3274 | 14.2958 | 14.2632 | 14.2305 | 14.1526 | 14.08 | 14.0095 | 13.9484 | 13.8937 | 13.3968 | 12.7 | 11.9537 | 13.5974 | 13.5668 | 13.5332 | 13.4984 | 13.4616 | 13.3911 | 13.3237 | 13.2605 | 13.2037 | 13.1511 | 12.6521 | 11.9437 | 11.1458 | 13.9724 | 13.9418 | 13.9082 | 13.8724 | 13.8366 | 13.7555 | 13.6787 | 13.6061 | 13.5429 | 13.485 | 12.9439 | 12.1734 | 11.3313
| BRACO | KIPPEN | MINIMUM HEADROOM | NS 66376 95628 | NO | YES | 0.03 | 9.0005 | 8.85 | 8.6753 | 8.4626 | 8.2258 | 7.9068 | 7.5932 | 7.2605 | 6.9247 | 6.5879 | 5.0563 | 1.5268 | 0.41 | 7.2668 | 7.1005 | 6.9068 | 6.6689 | 6.4037 | 6.0658 | 5.7311 | 5.3763 | 5.0216 | 4.6658 | 3.0016 | -0.15632 | -1.4374 | 7.6763 | 7.5163 | 7.33 | 7.1016 | 6.8447 | 6.5058 | 6.17 | 5.8132 | 5.4542 | 5.0942 | 3.4068 | -0.30684 | -1.5868
|  | KIPPEN | EE |  |  |  |  | 9.0605 | 8.9416 | 8.7984 | 8.6174 | 8.4184 | 8.1332 | 7.8426 | 7.5247 | 7.23 | 6.9353 | 5.4332 | 1.87 | 0.87526 | 7.3332 | 7.2016 | 7.0426 | 6.8416 | 6.6195 | 6.3237 | 6.0289 | 5.6995 | 5.3921 | 5.0868 | 3.5247 | 0.41105 | -0.69737 | 7.7405 | 7.6142 | 7.4605 | 7.2668 | 7.0511 | 6.7479 | 6.4416 | 6.1016 | 5.7868 | 5.4721 | 3.8574 | 0.13842 | -0.99211
|  | KIPPEN | HT |  |  |  |  | 9.0005 | 8.85 | 8.6753 | 8.4626 | 8.2258 | 7.9068 | 7.5932 | 7.2605 | 6.9247 | 6.5879 | 5.0563 | 1.5268 | 0.41 | 7.2668 | 7.1005 | 6.9068 | 6.6689 | 6.4037 | 6.0658 | 5.7311 | 5.3763 | 5.0216 | 4.6658 | 3.0016 | -0.15632 | -1.4374 | 7.6763 | 7.5163 | 7.33 | 7.1016 | 6.8447 | 6.5058 | 6.17 | 5.8132 | 5.4542 | 5.0942 | 3.4068 | -0.30684 | -1.5868
|  | KIPPEN | HE |  |  |  |  | 9.1163 | 9.0595 | 8.9553 | 8.8153 | 8.6532 | 8.3932 | 8.1511 | 7.8879 | 7.6321 | 7.3774 | 6.1595 | 3.9795 | 2.9237 | 7.3911 | 7.33 | 7.2132 | 7.0563 | 6.8721 | 6.6058 | 6.3553 | 6.0774 | 5.8089 | 5.5405 | 4.2458 | 2.2353 | 1.1174 | 7.6763 | 7.5163 | 7.33 | 7.1016 | 6.8447 | 6.5058 | 6.17 | 5.8132 | 5.4542 | 5.0942 | 3.4068 | -0.30684 | -1.5868
|  | KIPPEN | CF |  |  |  |  | 9.1384 | 9.1184 | 9.0837 | 9.0163 | 8.9437 | 8.8342 | 8.7247 | 8.6079 | 8.4879 | 8.37 | 7.6963 | 7.07 | 6.5016 | 7.4132 | 7.3932 | 7.3553 | 7.2816 | 7.1984 | 7.0858 | 6.97 | 6.8447 | 6.7163 | 6.5868 | 5.8542 | 5.1763 | 4.5563 | 7.8195 | 7.7995 | 7.7637 | 7.6911 | 7.6121 | 7.4963 | 7.3795 | 7.2521 | 7.1237 | 6.9963 | 6.2668 | 5.5868 | 4.9689
| THURSO | KIRKWALL | MINIMUM HEADROOM | HY 44669 10987 | NO | YES | 7.5 | 18.6874 | 18.5684 | 18.4442 | 18.1958 | 17.1684 | 16.0684 | 15.4547 | 14.8484 | 14.0547 | 12.6147 | 9.8158 | 8.3684 | 7.0358 | 15.4358 | 15.2853 | 15.0021 | 14.1642 | 13.0095 | 11.8011 | 11.1579 | 10.5232 | 9.6726 | 8.0663 | 5.1632 | 3.5632 | 2.0874 | 16.0316 | 15.9147 | 15.7947 | 15.4432 | 14.3442 | 13.1695 | 12.5253 | 11.8905 | 11.0484 | 9.5 | 6.5505 | 4.9516 | 3.4589
|  | KIRKWALL | EE |  |  |  |  | 19.9863 | 19.6716 | 19.3284 | 18.6947 | 17.8474 | 16.8705 | 16.2642 | 15.7063 | 15.1684 | 14.6295 | 21.1442 | 19.4811 | 18.3411 | 16.2274 | 15.8316 | 15.4126 | 14.7126 | 13.7632 | 12.6968 | 12.0674 | 11.4926 | 10.9358 | 10.3768 | 19.0463 | 17.4032 | 16.1842 | 17.2326 | 16.9926 | 16.6358 | 15.9695 | 15.0621 | 14.0211 | 13.3811 | 12.7937 | 12.2284 | 11.66 | 19.1726 | 17.4116 | 16.1579
|  | KIRKWALL | HT |  |  |  |  | 19.8253 | 19.4295 | 18.9505 | 18.1958 | 17.1684 | 16.0684 | 15.4547 | 14.8484 | 14.0547 | 12.6147 | 9.8158 | 8.3684 | 7.0358 | 16.0158 | 15.5168 | 15.0021 | 14.1642 | 13.0095 | 11.8011 | 11.1579 | 10.5232 | 9.6726 | 8.0663 | 5.1632 | 3.5632 | 2.0874 | 17.1432 | 16.7379 | 16.2463 | 15.4432 | 14.3442 | 13.1695 | 12.5253 | 11.8905 | 11.0484 | 9.5 | 6.5505 | 4.9516 | 3.4589
|  | KIRKWALL | HE |  |  |  |  | 20.2242 | 20.0242 | 19.72 | 19.2337 | 18.4863 | 17.5905 | 17.1042 | 16.6653 | 16.2263 | 15.9105 | 13.12 | 12.0221 | 11.0663 | 16.5337 | 16.2863 | 15.8705 | 15.2821 | 14.4379 | 13.46 | 12.9505 | 12.4947 | 12.04 | 11.7232 | 8.6863 | 7.5653 | 6.6168 | 17.1432 | 16.7379 | 16.2463 | 15.4432 | 14.3442 | 13.1695 | 12.5253 | 11.8905 | 11.0484 | 9.5 | 6.5505 | 4.9516 | 3.4589
|  | KIRKWALL | CF |  |  |  |  | 18.6874 | 18.5684 | 18.4442 | 18.3126 | 18.1895 | 18.0168 | 17.8389 | 17.6663 | 17.4505 | 17.2084 | 14.64 | 13.7979 | 13.2147 | 15.4358 | 15.2853 | 15.1295 | 14.9611 | 14.8095 | 14.6147 | 14.4042 | 14.2042 | 13.9242 | 13.6074 | 10.6989 | 9.8274 | 9.2189 | 16.0316 | 15.9147 | 15.7947 | 15.6663 | 15.5463 | 15.3779 | 15.1832 | 14.9874 | 14.7232 | 14.4211 | 11.6232 | 10.7263 | 10.1032
| BROADFORD | KISHORNHILL | MINIMUM HEADROOM | NG 88304 40591 | YES | YES | 0 | 0.42421 | 0.42 | 0.41474 | -0.053684 | -0.057895 | -0.062105 | -0.065263 | -0.069474 | -0.072632 | -0.075789 | -0.089474 | -0.096842 | -0.10105 | 0.46105 | 0.45579 | 0.44947 | 0.0042105 | -0.0010526 | -0.0052632 | -0.0094737 | -0.014737 | -0.017895 | -0.022105 | -0.038947 | -0.049474 | -0.057895 | 0.29684 | 0.29158 | 0.28421 | -0.16421 | -0.16947 | -0.17368 | -0.17684 | -0.18211 | -0.18526 | -0.18947 | -0.20421 | -0.21789 | -0.22842
|  | KISHORNHILL | EE |  |  |  |  | 0.42632 | 0.42211 | 0.41895 | -0.053684 | -0.057895 | -0.062105 | -0.065263 | -0.069474 | -0.072632 | -0.075789 | -0.089474 | -0.096842 | -0.10105 | 0.46316 | 0.45895 | 0.45474 | 0.0042105 | -0.0010526 | -0.0052632 | -0.0094737 | -0.014737 | -0.017895 | -0.022105 | -0.038947 | -0.049474 | -0.057895 | 0.3 | 0.29474 | 0.29053 | -0.16421 | -0.16947 | -0.17368 | -0.17684 | -0.18211 | -0.18526 | -0.18947 | -0.20421 | -0.21789 | -0.22842
|  | KISHORNHILL | HT |  |  |  |  | 0.42421 | 0.42 | 0.41474 | 0.41053 | 0.40526 | 0.4 | 0.39474 | 0.39053 | 0.38526 | 0.38105 | 0.36632 | 0.35684 | 0.35053 | 0.46105 | 0.45579 | 0.44947 | 0.44421 | 0.43789 | 0.43158 | 0.42526 | 0.42 | 0.41474 | 0.40947 | 0.39053 | 0.37579 | 0.36421 | 0.29684 | 0.29158 | 0.28421 | 0.27789 | 0.27158 | 0.26421 | 0.25789 | 0.25158 | 0.24526 | 0.24 | 0.21789 | 0.2 | 0.18421
|  | KISHORNHILL | HE |  |  |  |  | 0.42842 | 0.42632 | 0.42421 | 0.42105 | 0.41789 | 0.41474 | 0.41263 | 0.40947 | 0.40737 | 0.40421 | 0.39684 | 0.39263 | 0.39053 | 0.46632 | 0.46421 | 0.46105 | 0.45789 | 0.45474 | 0.45053 | 0.44842 | 0.44421 | 0.44211 | 0.43895 | 0.42947 | 0.42421 | 0.42 | 0.29684 | 0.29158 | 0.28421 | 0.27789 | 0.27158 | 0.26421 | 0.25789 | 0.25158 | 0.24526 | 0.24 | 0.21789 | 0.2 | 0.18421
|  | KISHORNHILL | CF |  |  |  |  | 0.43053 | 0.42947 | 0.42737 | 0.42632 | 0.42526 | 0.42316 | 0.42211 | 0.42105 | 0.41895 | 0.41789 | 0.41158 | 0.40842 | 0.40737 | 0.46947 | 0.46737 | 0.46526 | 0.46421 | 0.46211 | 0.46 | 0.45895 | 0.45684 | 0.45474 | 0.45368 | 0.44632 | 0.44105 | 0.43895 | 0.30632 | 0.30421 | 0.30211 | 0.30105 | 0.29895 | 0.29684 | 0.29474 | 0.29263 | 0.29053 | 0.28947 | 0.28 | 0.27474 | 0.27158
| BROADFORD | KYLE | MINIMUM HEADROOM | NG 76499 27247 | NO | YES | 0 | 5.9463 | 7.2074 | 7.1526 | 7.0968 | 7.0421 | 6.9126 | 6.7874 | 6.6632 | 6.5905 | 6.5211 | 6.22 | 5.9884 | 5.8137 | 5.5137 | 6.7832 | 6.7526 | 6.72 | 6.6874 | 6.6032 | 6.4695 | 6.3368 | 6.2684 | 6.2011 | 5.9053 | 5.6684 | 5.4811 | 5.6168 | 6.8842 | 6.8516 | 6.8168 | 6.7653 | 6.6232 | 6.4853 | 6.3484 | 6.2726 | 6.2 | 5.8789 | 5.6295 | 5.4358
|  | KYLE | EE |  |  |  |  | 5.9579 | 7.2337 | 7.2 | 7.1547 | 7.1074 | 7.0421 | 6.9726 | 6.8495 | 6.7305 | 6.62 | 6.3084 | 6.0232 | 5.86 | 5.5253 | 6.8011 | 6.7747 | 6.7484 | 6.7189 | 6.6821 | 6.6442 | 6.5568 | 6.4337 | 6.3168 | 6.0305 | 5.7684 | 5.6032 | 5.6295 | 6.9042 | 6.8768 | 6.8463 | 6.8158 | 6.7684 | 6.6958 | 6.5611 | 6.4305 | 6.3084 | 5.9842 | 5.6832 | 5.5053
|  | KYLE | HT |  |  |  |  | 5.9463 | 7.2074 | 7.1526 | 7.0968 | 7.0421 | 6.9126 | 6.7874 | 6.6632 | 6.5905 | 6.5211 | 6.22 | 5.9884 | 5.8137 | 5.5137 | 6.7832 | 6.7526 | 6.72 | 6.6874 | 6.6032 | 6.4695 | 6.3368 | 6.2684 | 6.2011 | 5.9053 | 5.6684 | 5.4811 | 5.6168 | 6.8842 | 6.8516 | 6.8168 | 6.7653 | 6.6232 | 6.4853 | 6.3484 | 6.2726 | 6.2 | 5.8789 | 5.6295 | 5.4358
|  | KYLE | HE |  |  |  |  | 5.9747 | 7.2579 | 7.2411 | 7.2211 | 7.2011 | 7.1526 | 7.1042 | 7.0253 | 6.9474 | 6.8747 | 6.6284 | 6.4779 | 6.2737 | 5.5421 | 6.8253 | 6.8084 | 6.7895 | 6.7695 | 6.7358 | 6.7084 | 6.68 | 6.6516 | 6.5926 | 6.3568 | 6.2253 | 6.0305 | 5.6168 | 6.8842 | 6.8516 | 6.8168 | 6.7653 | 6.6232 | 6.4853 | 6.3484 | 6.2726 | 6.2 | 5.8789 | 5.6295 | 5.4358
|  | KYLE | CF |  |  |  |  | 5.9832 | 7.2747 | 7.2653 | 7.2537 | 7.2442 | 7.2242 | 7.2074 | 7.1895 | 7.1526 | 7.1137 | 6.9421 | 6.8358 | 6.7358 | 5.5505 | 6.8421 | 6.8326 | 6.8221 | 6.8126 | 6.7979 | 6.7842 | 6.7705 | 6.7568 | 6.7453 | 6.6484 | 6.5516 | 6.4537 | 5.6568 | 6.9474 | 6.9379 | 6.9253 | 6.9158 | 6.8968 | 6.88 | 6.8621 | 6.8453 | 6.8295 | 6.6558 | 6.5442 | 6.4358
| LAIRG | LAIRG | MINIMUM HEADROOM | NC 58798 07111 | YES | YES | 0.17 | 1.0016 | 0.94789 | 0.87211 | 2.2953 | 2.2195 | 1.7763 | 1.2226 | 1.1868 | 0.63842 | -0.14579 | -6.5174 | -14.2416 | -18.3226 | 0.75632 | 0.69737 | 0.62158 | 2.0437 | 1.9679 | 1.6468 | 1.2037 | 1.0753 | 0.58158 | -0.21211 | -5.9016 | -13.0437 | -17.4784 | 0.80158 | 0.74579 | 0.66789 | 2.0879 | 2.0068 | 1.5668 | 1.0111 | 0.97421 | 0.42263 | -0.17105 | -7.2268 | -15.47 | -20.1111
|  | LAIRG | EE |  |  |  |  | 1.0153 | 0.98053 | 0.90158 | 2.3226 | 2.2426 | 1.7763 | 1.2226 | 1.1868 | 0.64368 | 0.061579 | -6.5174 | -14.2416 | -18.3226 | 0.77105 | 0.73316 | 0.65947 | 2.0826 | 2.0079 | 1.6468 | 1.2037 | 1.1647 | 0.70263 | 0.19842 | -5.9016 | -13.0437 | -17.4784 | 0.81526 | 0.77947 | 0.69947 | 2.1174 | 2.0353 | 1.5668 | 1.0111 | 0.97421 | 0.42263 | -0.17105 | -7.2268 | -15.47 | -20.1111
|  | LAIRG | HT |  |  |  |  | 1.0016 | 0.94789 | 0.87211 | 2.2953 | 2.2195 | 1.8216 | 1.3637 | 1.2332 | 0.75737 | 0.12158 | -5.8247 | -13.0395 | -16.4374 | 0.75632 | 0.69737 | 0.62158 | 2.0437 | 1.9679 | 1.6532 | 1.2626 | 1.1047 | 0.72684 | 0.14684 | -5.6016 | -12.7647 | -16.5563 | 0.80158 | 0.74579 | 0.66789 | 2.0879 | 2.0068 | 1.6079 | 1.1332 | 0.97842 | 0.50474 | -0.16789 | -6.65 | -14.5195 | -18.4353
|  | LAIRG | HE |  |  |  |  | 1.0332 | 1.0121 | 0.98263 | 2.4479 | 2.4068 | 1.9111 | 1.3805 | 1.19 | 0.63842 | -0.14579 | -2.8311 | -8.1753 | -12.7911 | 0.78895 | 0.76579 | 0.73632 | 2.2005 | 2.1584 | 1.7805 | 1.3121 | 1.0753 | 0.58158 | -0.21211 | -2.9774 | -8.1511 | -12.8574 | 0.80158 | 0.74579 | 0.66789 | 2.0879 | 2.0068 | 1.6079 | 1.1332 | 0.97842 | 0.50474 | -0.16789 | -6.65 | -14.5195 | -18.4353
|  | LAIRG | CF |  |  |  |  | 1.0479 | 1.0374 | 1.0226 | 2.5068 | 2.4911 | 2.3068 | 2.1405 | 2.0647 | 1.7321 | 1.3679 | -1.3879 | -4.0532 | -7.0005 | 0.80474 | 0.79421 | 0.78053 | 2.2647 | 2.2511 | 2.1111 | 1.9826 | 1.8889 | 1.5332 | 1.1163 | -1.4437 | -4.1795 | -7.3542 | 0.84789 | 0.83842 | 0.82263 | 2.3068 | 2.2911 | 2.1068 | 1.9395 | 1.8574 | 1.4784 | 1.0479 | -1.9216 | -4.8553 | -8.1911
| MYBSTER 1 | LATHERON | MINIMUM HEADROOM | ND 19924 33627 | YES | YES | 0 | 3.2495 | 3.1758 | 3.08 | 2.9874 | 2.8947 | 2.4632 | 1.9558 | 1.3705 | 0.85684 | 0.22421 | -4.3663 | -9.6 | -13.4726 | 3.1011 | 3.02 | 2.9242 | 2.8295 | 2.7379 | 2.3705 | 1.9853 | 1.4884 | 1.0505 | 0.32632 | -3.9063 | -9.0284 | -13.2937 | 3.12 | 3.0411 | 2.9389 | 2.84 | 2.7442 | 2.3011 | 1.8032 | 1.2053 | 0.68 | 0.061053 | -4.9453 | -10.6484 | -15.0537
|  | LATHERON | EE |  |  |  |  | 3.2832 | 3.2253 | 3.1347 | 3.0442 | 2.9537 | 2.4989 | 1.9558 | 1.3705 | 0.85684 | 0.32632 | -4.3663 | -9.6 | -13.4726 | 3.1379 | 3.0758 | 2.9895 | 2.9032 | 2.8158 | 2.4379 | 1.9853 | 1.4884 | 1.0505 | 0.59579 | -3.9063 | -9.0232 | -13.2937 | 3.1568 | 3.0947 | 3 | 2.9053 | 2.8105 | 2.3516 | 1.8032 | 1.2053 | 0.68 | 0.13684 | -4.9453 | -10.6484 | -15.0537
|  | LATHERON | HT |  |  |  |  | 3.2495 | 3.1758 | 3.08 | 2.9874 | 2.8947 | 2.4632 | 2.0347 | 1.5916 | 1.1179 | 0.31789 | -3.9158 | -8.6105 | -11.8421 | 3.1011 | 3.02 | 2.9242 | 2.8295 | 2.7379 | 2.3705 | 1.9958 | 1.6074 | 1.2074 | 0.44421 | -3.8663 | -9.0284 | -12.6295 | 3.12 | 3.0411 | 2.9389 | 2.84 | 2.7442 | 2.3011 | 1.8611 | 1.4042 | 0.92316 | 0.061053 | -4.6189 | -9.9779 | -13.6968
|  | LATHERON | HE |  |  |  |  | 3.3305 | 3.2958 | 3.2537 | 3.2084 | 3.1632 | 2.64 | 2.0895 | 1.5295 | 0.99263 | 0.22421 | -3.0474 | -7.0474 | -11.3958 | 3.1895 | 3.1526 | 3.1084 | 3.0632 | 3.0179 | 2.5737 | 2.0726 | 1.5589 | 1.0737 | 0.32632 | -2.8221 | -6.9211 | -11.3874 | 3.12 | 3.0411 | 2.9389 | 2.84 | 2.7442 | 2.3011 | 1.8611 | 1.4042 | 0.92316 | 0.061053 | -4.6189 | -9.9779 | -13.6968
|  | LATHERON | CF |  |  |  |  | 3.3558 | 3.3347 | 3.3084 | 3.2832 | 3.2558 | 3.0716 | 2.9084 | 2.6253 | 2.2958 | 1.9295 | 0.25579 | -2.2621 | -5.0147 | 3.2179 | 3.1958 | 3.1684 | 3.1421 | 3.1147 | 2.9621 | 2.8242 | 2.5516 | 2.2211 | 1.8358 | 0.13368 | -2.4642 | -5.4558 | 3.2358 | 3.2137 | 3.1853 | 3.1589 | 3.1284 | 2.9421 | 2.7768 | 2.4705 | 2.1063 | 1.6926 | -0.15053 | -2.9421 | -6.0705
| FIDDES | LAURENCEKIRK | MINIMUM HEADROOM | NO 70915 71028 | NO | YES | 0.17 | 14.6421 | 14.4168 | 14.0632 | 13.6674 | 13.2379 | 12.2189 | 11.1053 | 9.8716 | 8.7463 | 7.4505 | -2.2147 | -11.9379 | -19.2916 | 13.5868 | 13.3321 | 12.9405 | 12.51 | 12.0374 | 11.1142 | 10.1637 | 9.1395 | 7.9932 | 6.65 | -1.6416 | -11.3647 | -19.1521 | 13.7534 | 13.4945 | 13.0966 | 12.6576 | 12.1766 | 11.1018 | 9.9682 | 8.6945 | 7.5282 | 6.0397 | -3.8371 | -14.495 | -22.9108
|  | LAURENCEKIRK | EE |  |  |  |  | 14.6968 | 14.5768 | 14.2505 | 13.8726 | 13.4558 | 12.3379 | 11.1053 | 9.8716 | 8.7463 | 7.5632 | -2.2147 | -11.9379 | -19.2916 | 13.6458 | 13.5153 | 13.1574 | 12.75 | 12.2995 | 11.3121 | 10.2216 | 9.1395 | 8.1384 | 7.0753 | -1.5711 | -11.1279 | -19.1521 | 13.8124 | 13.6808 | 13.3082 | 12.8871 | 12.4229 | 11.2503 | 9.9682 | 8.6945 | 7.5282 | 6.2945 | -3.8371 | -14.495 | -22.9108
|  | LAURENCEKIRK | HT |  |  |  |  | 14.6421 | 14.4168 | 14.0632 | 13.6674 | 13.2379 | 12.2189 | 11.1884 | 10.1316 | 8.8642 | 7.4505 | -1.52 | -10.4853 | -16.5821 | 13.5868 | 13.3321 | 12.9405 | 12.51 | 12.0374 | 11.1142 | 10.1637 | 9.1753 | 7.9932 | 6.65 | -1.6416 | -11.3647 | -18.1932 | 13.7534 | 13.4945 | 13.0966 | 12.6576 | 12.1766 | 11.1018 | 10.0124 | 8.8913 | 7.5471 | 6.0397 | -3.4771 | -13.6708 | -20.6866
|  | LAURENCEKIRK | HE |  |  |  |  | 14.7537 | 14.6958 | 14.5158 | 14.2516 | 13.9368 | 12.8211 | 11.8642 | 10.8747 | 9.9442 | 9.0042 | 1.5684 | -5.9295 | -14.0968 | 13.7026 | 13.6426 | 13.4395 | 13.1321 | 12.7795 | 11.8142 | 10.9584 | 10.0616 | 9.2363 | 8.3995 | 1.4289 | -6.2258 | -14.5658 | 13.7534 | 13.4945 | 13.0966 | 12.6576 | 12.1766 | 11.1018 | 10.0124 | 8.8913 | 7.5471 | 6.0397 | -3.4771 | -13.6708 | -20.6866
|  | LAURENCEKIRK | CF |  |  |  |  | 14.7863 | 14.7568 | 14.7168 | 14.6021 | 14.4632 | 14.0232 | 13.6179 | 13.2084 | 12.8232 | 12.2074 | 9.0389 | 4.2979 | -0.93158 | 13.7353 | 13.7058 | 13.6679 | 13.5405 | 13.3753 | 12.99 | 12.6289 | 12.2511 | 11.8868 | 11.2353 | 8.0289 | 3.1626 | -2.4784 | 13.9018 | 13.8724 | 13.8324 | 13.6976 | 13.5324 | 13.0724 | 12.6461 | 12.2134 | 11.8008 | 11.1092 | 7.6187 | 2.3534 | -3.5739
| STORNOWAY | LAXAY | MINIMUM HEADROOM | NB 33424 21925 | YES | YES | 0 | 1.1968 | 6.4611 | 6.4179 | 6.3747 | 6.3316 | 6.2063 | 6.0663 | 5.9084 | 5.7695 | 5.5821 | 3.8189 | 1.74 | 0.14842 | 1.1032 | 6.3432 | 6.2674 | 6.1926 | 6.1189 | 5.9811 | 5.8463 | 5.7116 | 5.5642 | 5.3379 | 3.4821 | 1.1716 | -0.48737 | 1.0684 | 6.3032 | 6.2263 | 6.1516 | 6.0768 | 5.9126 | 5.7526 | 5.5905 | 5.4126 | 5.1558 | 3.2095 | 0.85789 | -0.84
|  | LAXAY | EE |  |  |  |  | 1.2095 | 6.48 | 6.4411 | 6.4 | 6.3589 | 6.2242 | 6.0663 | 5.9084 | 5.7695 | 5.6284 | 3.8842 | 1.8537 | 0.14842 | 1.1158 | 6.3863 | 6.3263 | 6.2632 | 6.1989 | 6.0589 | 5.9032 | 5.7484 | 5.6095 | 5.4695 | 3.7074 | 1.6432 | -0.25368 | 1.0979 | 6.3453 | 6.2821 | 6.2179 | 6.1516 | 5.9811 | 5.7863 | 5.5905 | 5.4168 | 5.2421 | 3.3158 | 1.0895 | -0.84
|  | LAXAY | HT |  |  |  |  | 1.1968 | 6.4611 | 6.4179 | 6.3747 | 6.3316 | 6.2063 | 6.0842 | 5.9611 | 5.82 | 5.5821 | 3.8189 | 1.74 | 0.28211 | 1.1032 | 6.3432 | 6.2674 | 6.1926 | 6.1189 | 5.9811 | 5.8463 | 5.7116 | 5.5642 | 5.3379 | 3.4821 | 1.1716 | -0.48737 | 1.0684 | 6.3032 | 6.2263 | 6.1516 | 6.0768 | 5.9126 | 5.7526 | 5.5916 | 5.4126 | 5.1558 | 3.2095 | 0.85789 | -0.82632
|  | LAXAY | HE |  |  |  |  | 1.2305 | 6.5105 | 6.4874 | 6.4632 | 6.4368 | 6.3 | 6.1821 | 6.0663 | 5.9242 | 5.6179 | 4.3526 | 2.7358 | 0.98421 | 1.1368 | 6.4168 | 6.3947 | 6.3705 | 6.3432 | 6.2137 | 6.0453 | 5.8484 | 5.6663 | 5.3558 | 4.0895 | 2.3874 | 0.54105 | 1.0684 | 6.3032 | 6.2263 | 6.1516 | 6.0768 | 5.9126 | 5.7526 | 5.5916 | 5.4126 | 5.1558 | 3.2095 | 0.85789 | -0.82632
|  | LAXAY | CF |  |  |  |  | 1.2411 | 6.5305 | 6.5168 | 6.5053 | 6.4905 | 6.4368 | 6.3895 | 6.3411 | 6.2968 | 6.24 | 5.5463 | 4.5158 | 3.3316 | 1.1474 | 6.4368 | 6.4242 | 6.4126 | 6.3989 | 6.3663 | 6.3147 | 6.2421 | 6.0937 | 5.9137 | 5.1905 | 4.0989 | 2.7916 | 1.1558 | 6.4411 | 6.4179 | 6.3968 | 6.3747 | 6.3042 | 6.2432 | 6.1621 | 6.0095 | 5.8274 | 5.0642 | 3.9211 | 2.5874
| COUPAR ANGUS | LEOCH | MINIMUM HEADROOM | NO 35945 36287 | YES | YES | 0.03 | -0.56789 | -0.68474 | -0.81947 | -0.95105 | -1.0784 | -1.4532 | -1.8447 | -2.3247 | -2.7479 | -3.1732 | -6.9679 | -11.31 | -14.5626 | 0.011053 | -0.11421 | -0.25316 | -0.38789 | -0.52053 | -0.84579 | -1.1668 | -1.5447 | -1.91 | -2.3311 | -5.8732 | -10.1205 | -13.6437 | -0.60684 | -0.72895 | -0.87 | -1.0079 | -1.1426 | -1.5237 | -1.9268 | -2.4237 | -2.8605 | -3.2995 | -7.3089 | -12.0374 | -15.7321
|  | LEOCH | EE |  |  |  |  | -0.51526 | -0.60684 | -0.72474 | -0.84158 | -0.95737 | -1.3689 | -1.8447 | -2.3247 | -2.7479 | -3.1732 | -6.9679 | -11.31 | -14.5626 | 0.066842 | -0.03 | -0.14895 | -0.26579 | -0.38158 | -0.73316 | -1.1321 | -1.5447 | -1.91 | -2.2763 | -5.8732 | -10.1205 | -13.6437 | -0.55211 | -0.64684 | -0.76895 | -0.89105 | -1.0111 | -1.4353 | -1.9268 | -2.4237 | -2.8605 | -3.2995 | -7.3089 | -12.0374 | -15.7321
|  | LEOCH | HT |  |  |  |  | -0.56789 | -0.68474 | -0.81947 | -0.95105 | -1.0784 | -1.4532 | -1.8216 | -2.1921 | -2.6174 | -3.0732 | -6.6111 | -10.5732 | -13.2637 | 0.011053 | -0.11421 | -0.25316 | -0.38789 | -0.52053 | -0.84579 | -1.1668 | -1.4889 | -1.8532 | -2.2521 | -5.8163 | -10.1016 | -13.0995 | -0.60684 | -0.72895 | -0.87 | -1.0079 | -1.1426 | -1.5237 | -1.9047 | -2.2868 | -2.7268 | -3.1995 | -7.0426 | -11.5363 | -14.6268
|  | LEOCH | HE |  |  |  |  | -0.44263 | -0.49947 | -0.56368 | -0.62895 | -0.69316 | -1.1047 | -1.5395 | -2.0132 | -2.4647 | -3.1153 | -5.8963 | -9.2195 | -12.8163 | 0.14474 | 0.084737 | 0.018421 | -0.048947 | -0.11632 | -0.45842 | -0.84895 | -1.2847 | -1.6963 | -2.3311 | -5.0468 | -8.4226 | -12.0847 | -0.60684 | -0.72895 | -0.87 | -1.0079 | -1.1426 | -1.5237 | -1.9047 | -2.2868 | -2.7268 | -3.1995 | -7.0426 | -11.5363 | -14.6268
|  | LEOCH | CF |  |  |  |  | -0.40684 | -0.44158 | -0.47842 | -0.51947 | -0.55842 | -0.72579 | -0.87211 | -1.0553 | -1.3384 | -1.6521 | -3.0763 | -5.1774 | -7.4711 | 0.18158 | 0.14579 | 0.10684 | 0.065789 | 0.024737 | -0.11737 | -0.24474 | -0.41211 | -0.69737 | -1.03 | -2.4668 | -4.6153 | -7.0711 | -0.43947 | -0.47526 | -0.51421 | -0.55632 | -0.59632 | -0.76895 | -0.92053 | -1.1121 | -1.4132 | -1.7584 | -3.3226 | -5.65 | -8.2468
| NAIRN | LETHEN | MINIMUM HEADROOM | NH 92307 50795 | YES | YES | 0 | 4.2453 | 4.1968 | 4.1074 | 4.0168 | 3.9126 | 2.9926 | 1.8768 | 0.74 | -0.35158 | -1.9253 | -11.3 | -20.4168 | -28.9105 | 4.1347 | 4.0789 | 3.9958 | 3.9147 | 3.8305 | 3.0579 | 2.04 | 0.99368 | 0.0021053 | -1.6 | -10.2611 | -20.7568 | -28.9263 | 4.1821 | 4.1221 | 4.0232 | 3.9284 | 3.8305 | 2.9495 | 1.8874 | 0.78947 | -0.15684 | -1.8495 | -12.4568 | -22.6979 | -32.3
|  | LETHEN | EE |  |  |  |  | 4.2611 | 4.2295 | 4.1263 | 4.0211 | 3.9126 | 3.0263 | 1.9642 | 0.86737 | -0.074737 | -1.4442 | -11.3 | -20.4168 | -28.9105 | 4.1526 | 4.1168 | 4.0295 | 3.9432 | 3.8484 | 3.1663 | 2.3495 | 1.4737 | 0.71368 | -0.54737 | -10.2611 | -19.6874 | -28.9263 | 4.1989 | 4.1632 | 4.0516 | 3.9411 | 3.8305 | 2.9495 | 1.8874 | 0.78947 | -0.15684 | -1.6011 | -12.4568 | -22.6116 | -32.3
|  | LETHEN | HT |  |  |  |  | 4.2453 | 4.1968 | 4.1074 | 4.0168 | 3.9242 | 3.1832 | 2.4453 | 1.5758 | 0.43158 | -1.4505 | -10.3495 | -19.8168 | -26.7726 | 4.1347 | 4.0789 | 3.9958 | 3.9147 | 3.8305 | 3.2516 | 2.6747 | 1.9379 | 0.93158 | -1.0011 | -10.2137 | -20.7568 | -28.6011 | 4.1821 | 4.1221 | 4.0232 | 3.9284 | 3.8305 | 3.0979 | 2.36 | 1.4642 | 0.26632 | -1.8495 | -11.8021 | -22.6979 | -30.7274
|  | LETHEN | HE |  |  |  |  | 4.2789 | 4.2632 | 4.2347 | 4.2011 | 4.1621 | 2.9926 | 1.8768 | 0.74 | -0.35158 | -1.9253 | -8.7705 | -16.0916 | -25.4989 | 4.1705 | 4.1558 | 4.1305 | 4.0979 | 4.06 | 3.0579 | 2.04 | 0.99368 | 0.0021053 | -1.6 | -8.2958 | -16.0821 | -25.7063 | 4.1821 | 4.1221 | 4.0232 | 3.9284 | 3.8305 | 3.0979 | 2.36 | 1.4642 | 0.26632 | -1.8495 | -11.8021 | -22.6979 | -30.7274
|  | LETHEN | CF |  |  |  |  | 4.2884 | 4.28 | 4.2621 | 4.2432 | 4.2263 | 3.8811 | 3.5705 | 2.8937 | 2.48 | 1.7389 | -1.7895 | -6.4684 | -12.5042 | 4.18 | 4.1716 | 4.1568 | 4.1411 | 4.1274 | 3.8726 | 3.6316 | 2.9274 | 2.4042 | 1.5568 | -2.0337 | -7.0263 | -13.5484 | 4.2263 | 4.2179 | 4.2 | 4.18 | 4.1632 | 3.8179 | 3.5053 | 2.7411 | 2.2179 | 1.3263 | -2.5884 | -7.8789 | -14.7274
| GRUDIE BRIDGE | LETTEREWE | MINIMUM HEADROOM | NG 93546 70082 | YES | NO | 0 | 0.10105 | 0.098947 | 0.096842 | 0.094737 | 0.092632 | 0.089474 | 0.088421 | 0.086316 | 0.083158 | 0.082105 | 0.071579 | 0.064211 | 0.054737 | 0.1 | 0.097895 | 0.096842 | 0.094737 | 0.092632 | 0.090526 | 0.089474 | 0.086316 | 0.084211 | 0.082105 | 0.072632 | 0.064211 | 0.055789 | 0.1 | 0.097895 | 0.096842 | 0.094737 | 0.092632 | 0.089474 | 0.088421 | 0.086316 | 0.083158 | 0.081053 | 0.070526 | 0.063158 | 0.053684
|  | LETTEREWE | EE |  |  |  |  | 0.10105 | 0.098947 | 0.096842 | 0.094737 | 0.092632 | 0.089474 | 0.088421 | 0.086316 | 0.083158 | 0.082105 | 0.071579 | 0.064211 | 0.054737 | 0.1 | 0.097895 | 0.096842 | 0.094737 | 0.092632 | 0.090526 | 0.089474 | 0.086316 | 0.084211 | 0.082105 | 0.072632 | 0.064211 | 0.055789 | 0.1 | 0.097895 | 0.096842 | 0.094737 | 0.092632 | 0.089474 | 0.088421 | 0.086316 | 0.083158 | 0.081053 | 0.070526 | 0.063158 | 0.053684
|  | LETTEREWE | HT |  |  |  |  | 0.10105 | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.091579 | 0.088421 | 0.085263 | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.094737 | 0.091579 | 0.087368 | 0.084211 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.095789 | 0.094737 | 0.094737 | 0.090526 | 0.087368 | 0.083158
|  | LETTEREWE | HE |  |  |  |  | 0.10105 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.095789 | 0.095789 | 0.092632 | 0.089474 | 0.086316 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.095789 | 0.095789 | 0.094737 | 0.092632 | 0.089474 | 0.086316 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.095789 | 0.094737 | 0.094737 | 0.090526 | 0.087368 | 0.083158
|  | LETTEREWE | CF |  |  |  |  | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.096842 | 0.1 | 0.1 | 0.1 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.097895 | 0.096842
| ELGIN | LHANBRYDE | MINIMUM HEADROOM | NJ 27940 61640 | NO | YES | 0 | 4.88 | 4.7789 | 4.5968 | 4.4316 | 4.3442 | 4.1632 | 3.9842 | 3.8063 | 3.6126 | 3.4179 | 2.5284 | 1.4526 | 0.55895 | 4.8589 | 4.6484 | 4.3968 | 4.2137 | 4.1211 | 3.9589 | 3.8011 | 3.64 | 3.4663 | 3.2926 | 2.6189 | 1.6537 | 0.72737 | 4.8684 | 4.6632 | 4.4158 | 4.2347 | 4.1421 | 3.9526 | 3.7674 | 3.5842 | 3.3811 | 3.1789 | 2.3126 | 1.1842 | 0.19684
|  | LHANBRYDE | EE |  |  |  |  | 4.9042 | 4.82 | 4.6884 | 4.5463 | 4.4411 | 4.2368 | 4.0179 | 3.8063 | 3.6189 | 3.4316 | 2.5284 | 1.4526 | 0.55895 | 4.8979 | 4.7168 | 4.5 | 4.3442 | 4.2305 | 4.0516 | 3.8579 | 3.6758 | 3.5105 | 3.3484 | 2.6189 | 1.6537 | 0.72737 | 4.9063 | 4.7295 | 4.5158 | 4.36 | 4.2463 | 4.0326 | 3.8042 | 3.5874 | 3.3926 | 3.1979 | 2.3126 | 1.1842 | 0.19684
|  | LHANBRYDE | HT |  |  |  |  | 4.88 | 4.7789 | 4.5968 | 4.4316 | 4.3442 | 4.1632 | 3.9842 | 3.8074 | 3.6126 | 3.4179 | 2.7274 | 1.8284 | 1.0989 | 4.8589 | 4.6484 | 4.3968 | 4.2137 | 4.1211 | 3.9589 | 3.8011 | 3.64 | 3.4663 | 3.2926 | 2.7189 | 1.8 | 1.0084 | 4.8684 | 4.6632 | 4.4158 | 4.2347 | 4.1421 | 3.9526 | 3.7674 | 3.5842 | 3.3811 | 3.1789 | 2.5095 | 1.5295 | 0.71684
|  | LHANBRYDE | HE |  |  |  |  | 4.9389 | 4.8705 | 4.7811 | 4.6653 | 4.5874 | 4.3979 | 4.2442 | 4.0905 | 3.9421 | 3.7947 | 3.1389 | 2.1863 | 1.1316 | 4.9505 | 4.7968 | 4.5989 | 4.4674 | 4.3811 | 4.2211 | 4.0884 | 3.9568 | 3.8284 | 3.7021 | 3.1432 | 2.1947 | 1.1632 | 4.8684 | 4.6632 | 4.4158 | 4.2347 | 4.1421 | 3.9526 | 3.7674 | 3.5842 | 3.3811 | 3.1789 | 2.5095 | 1.5295 | 0.71684
|  | LHANBRYDE | CF |  |  |  |  | 4.96 | 4.9253 | 4.8842 | 4.8537 | 4.8305 | 4.7568 | 4.6895 | 4.6242 | 4.5663 | 4.5179 | 4.1842 | 3.6232 | 2.9926 | 4.9884 | 4.9126 | 4.8232 | 4.7642 | 4.7242 | 4.6505 | 4.5758 | 4.5021 | 4.4389 | 4.3821 | 4.0789 | 3.5389 | 2.8853 | 4.9968 | 4.9221 | 4.8337 | 4.7758 | 4.7368 | 4.6495 | 4.5642 | 4.4821 | 4.4095 | 4.3474 | 3.9979 | 3.3947 | 2.7
| FORT WILLIAM | LIDDESDALE | MINIMUM HEADROOM | NM 78116 59480 | YES | NO | 0 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211
|  | LIDDESDALE | EE |  |  |  |  | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211
|  | LIDDESDALE | HT |  |  |  |  | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211
|  | LIDDESDALE | HE |  |  |  |  | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211
|  | LIDDESDALE | CF |  |  |  |  | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316
| KEITH 1 | LIMEHILLOCKS | MINIMUM HEADROOM | NJ 52093 50703 | YES | YES | 0 | 1.0626 | 1.0121 | 0.93316 | 0.84053 | 0.74684 | 0.17526 | -0.54368 | -1.2637 | -1.8858 | -2.8816 | -9.1911 | -15.3195 | -20.5468 | 1.0532 | 1.0016 | 0.92684 | 0.83947 | 0.74789 | 0.27737 | -0.33211 | -0.93842 | -1.5563 | -2.4774 | -8.2111 | -14.4089 | -20.0332 | 1.15 | 1.0921 | 1.0079 | 0.90895 | 0.80579 | 0.24579 | -0.47316 | -1.2142 | -1.8668 | -2.7711 | -9.0047 | -16.73 | -22.6542
|  | LIMEHILLOCKS | EE |  |  |  |  | 1.0868 | 1.0468 | 0.96474 | 0.87526 | 0.78158 | 0.17526 | -0.54368 | -1.2637 | -1.8858 | -2.6395 | -8.2911 | -15.3195 | -20.5468 | 1.0774 | 1.0374 | 0.96158 | 0.87842 | 0.79316 | 0.27737 | -0.33211 | -0.93842 | -1.4616 | -2.1184 | -7.4911 | -14.4089 | -20.0332 | 1.1763 | 1.1321 | 1.0458 | 0.95105 | 0.85105 | 0.24579 | -0.47316 | -1.2142 | -1.8668 | -2.6553 | -9.0047 | -16.73 | -22.6542
|  | LIMEHILLOCKS | HT |  |  |  |  | 1.0626 | 1.0121 | 0.93316 | 0.84053 | 0.74684 | 0.23737 | -0.26789 | -0.77211 | -1.4489 | -2.6426 | -7.9395 | -14.2426 | -18.4995 | 1.0532 | 1.0016 | 0.92684 | 0.83947 | 0.74789 | 0.31211 | -0.11842 | -0.54895 | -1.1342 | -2.2437 | -7.5553 | -14.3489 | -19.1637 | 1.15 | 1.0921 | 1.0079 | 0.90895 | 0.80579 | 0.29421 | -0.21211 | -0.71632 | -1.4174 | -2.7711 | -8.7353 | -15.9237 | -20.8616
|  | LIMEHILLOCKS | HE |  |  |  |  | 1.1195 | 1.0963 | 1.0616 | 1.0142 | 0.96474 | 0.25737 | -0.45842 | -1.1868 | -1.8847 | -2.8816 | -9.1911 | -14.5774 | -20.4511 | 1.11 | 1.0858 | 1.0532 | 1.0079 | 0.95737 | 0.34789 | -0.28684 | -0.93632 | -1.5563 | -2.4774 | -8.2111 | -13.6826 | -19.6595 | 1.15 | 1.0921 | 1.0079 | 0.90895 | 0.80579 | 0.29421 | -0.21211 | -0.71632 | -1.4174 | -2.7711 | -8.7353 | -15.9237 | -20.8616
|  | LIMEHILLOCKS | CF |  |  |  |  | 1.1374 | 1.1226 | 1.1016 | 1.0784 | 1.0574 | 0.81842 | 0.60579 | 0.20895 | -0.21211 | -0.67842 | -2.8479 | -6.2342 | -9.9563 | 1.1268 | 1.1132 | 1.0932 | 1.0711 | 1.0489 | 0.85 | 0.66789 | 0.30053 | -0.097368 | -0.54895 | -2.6068 | -6.0689 | -10.0289 | 1.2321 | 1.2163 | 1.1932 | 1.1689 | 1.1447 | 0.90895 | 0.69421 | 0.25316 | -0.22789 | -0.77632 | -3.2121 | -6.9479 | -11.1889
| ARDMORE | LOCH CARNAN | MINIMUM HEADROOM | NF 83230 42735 | NO | YES | 0 | 10.0838 | 10.0785 | 10.0743 | 10.0691 | 10.0638 | 10.0575 | 10.0522 | 10.0469 | 10.0417 | 10.0375 | 10.0217 | 10.0101 | 10.0027 | 9.7322 | 9.7227 | 9.7133 | 9.7038 | 9.6943 | 9.6848 | 9.6743 | 9.6659 | 9.6575 | 9.6501 | 9.6164 | 9.5891 | 9.5648 | 10.0101 | 10.0006 | 9.9901 | 9.9817 | 9.9722 | 9.9627 | 9.9522 | 9.9438 | 9.9354 | 9.928 | 9.8943 | 9.8669 | 9.8427
|  | LOCH CARNAN | EE |  |  |  |  | 10.0859 | 10.0817 | 10.0775 | 10.0722 | 10.068 | 10.0638 | 10.0596 | 10.0543 | 10.0512 | 10.0469 | 16.1606 | 16.1522 | 16.1469 | 9.7375 | 9.7301 | 9.7217 | 9.7133 | 9.7048 | 9.6985 | 9.6912 | 9.6827 | 9.6775 | 9.6701 | 17.8069 | 17.7985 | 17.7933 | 10.0143 | 10.0069 | 9.9996 | 9.9901 | 9.9827 | 9.9754 | 9.9691 | 9.9606 | 9.9554 | 9.948 | 17.2543 | 17.2459 | 17.2406
|  | LOCH CARNAN | HT |  |  |  |  | 10.0838 | 10.0785 | 10.0743 | 10.0691 | 10.0638 | 10.0575 | 10.0522 | 10.0469 | 10.0417 | 10.0375 | 10.0217 | 10.0101 | 10.0027 | 9.7322 | 9.7227 | 9.7133 | 9.7038 | 9.6943 | 9.6848 | 9.6743 | 9.6659 | 9.6575 | 9.6501 | 9.6164 | 9.5891 | 9.5648 | 10.0101 | 10.0006 | 9.9901 | 9.9817 | 9.9722 | 9.9627 | 9.9522 | 9.9438 | 9.9354 | 9.928 | 9.8943 | 9.8669 | 9.8427
|  | LOCH CARNAN | HE |  |  |  |  | 10.088 | 10.0859 | 10.0827 | 10.0796 | 10.0754 | 10.0722 | 10.0691 | 10.0659 | 10.0627 | 10.0596 | 10.0501 | 10.0459 | 10.0438 | 9.7427 | 9.7385 | 9.7333 | 9.728 | 9.7227 | 9.7175 | 9.7122 | 9.708 | 9.7038 | 9.6985 | 9.6827 | 9.6722 | 9.6648 | 10.0101 | 10.0006 | 9.9901 | 9.9817 | 9.9722 | 9.9627 | 9.9522 | 9.9438 | 9.9354 | 9.928 | 9.8943 | 9.8669 | 9.8427
|  | LOCH CARNAN | CF |  |  |  |  | 10.0901 | 10.088 | 10.0869 | 10.0848 | 10.0838 | 10.0817 | 10.0796 | 10.0785 | 10.0764 | 10.0754 | 10.068 | 10.0638 | 10.0617 | 9.7459 | 9.7438 | 9.7406 | 9.7375 | 9.7343 | 9.7312 | 9.728 | 9.7259 | 9.7217 | 9.7196 | 9.7059 | 9.6964 | 9.6891 | 10.0227 | 10.0206 | 10.0175 | 10.0143 | 10.0112 | 10.0091 | 10.0048 | 10.0027 | 9.9985 | 9.9975 | 9.9838 | 9.9743 | 9.9669
| GRUDIE BRIDGE | LOCH GLASCARNOCH | MINIMUM HEADROOM | NH 31620 71996 | YES | NO | 0 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49895 | 0.49579 | 0.49158 | 0.48842 | 0.48526 | 0.47895 | 0.44947 | 0.41368 | 0.38842 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49895 | 0.49579 | 0.49158 | 0.49053 | 0.48737 | 0.48105 | 0.45474 | 0.42 | 0.39263 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49895 | 0.49579 | 0.49263 | 0.48842 | 0.48632 | 0.48 | 0.44632 | 0.40842 | 0.37895
|  | LOCH GLASCARNOCH | EE |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49895 | 0.49579 | 0.49263 | 0.48842 | 0.48632 | 0.48105 | 0.44947 | 0.41368 | 0.38842 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49895 | 0.49684 | 0.49368 | 0.49158 | 0.48947 | 0.48421 | 0.45474 | 0.42 | 0.39263 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49895 | 0.49579 | 0.49263 | 0.48842 | 0.48632 | 0.48 | 0.44632 | 0.40842 | 0.37895
|  | LOCH GLASCARNOCH | HT |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49684 | 0.49474 | 0.49158 | 0.48737 | 0.48211 | 0.45263 | 0.42421 | 0.40316 | 0.5 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49789 | 0.49579 | 0.49263 | 0.48947 | 0.48421 | 0.45579 | 0.42316 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49684 | 0.49474 | 0.49158 | 0.48737 | 0.48105 | 0.44947 | 0.41579 | 0.39158
|  | LOCH GLASCARNOCH | HE |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.49579 | 0.49158 | 0.48842 | 0.48526 | 0.47895 | 0.45789 | 0.43158 | 0.40211 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.49579 | 0.49158 | 0.49053 | 0.48737 | 0.48105 | 0.46105 | 0.43368 | 0.40421 | 0.5 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49684 | 0.49474 | 0.49158 | 0.48737 | 0.48105 | 0.44947 | 0.41579 | 0.39158
|  | LOCH GLASCARNOCH | CF |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49684 | 0.49474 | 0.49368 | 0.49158 | 0.48 | 0.46316 | 0.44421 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49789 | 0.49474 | 0.49368 | 0.49158 | 0.48 | 0.46316 | 0.44316 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.49895 | 0.49684 | 0.49474 | 0.49263 | 0.49053 | 0.47789 | 0.46 | 0.43895
| FORT WILLIAM | LOCHALINE | MINIMUM HEADROOM | NM 67939 45444 | YES | NO | 0 | 0.97474 | 0.95789 | 0.94105 | 0.92316 | 0.90421 | 0.88526 | 0.86737 | 0.84947 | 0.83158 | 0.81474 | 0.73789 | 0.67895 | 0.62421 | 1.0179 | 1.0032 | 0.98632 | 0.96737 | 0.94737 | 0.92947 | 0.91158 | 0.89474 | 0.87684 | 0.85895 | 0.78421 | 0.72632 | 0.67158 | 0.97263 | 0.95474 | 0.93684 | 0.91789 | 0.89579 | 0.87579 | 0.85684 | 0.83789 | 0.81789 | 0.8 | 0.71789 | 0.65263 | 0.59263
|  | LOCHALINE | EE |  |  |  |  | 0.98 | 0.96211 | 0.94316 | 0.92316 | 0.90421 | 0.88526 | 0.86737 | 0.84947 | 0.83158 | 0.81474 | 0.73789 | 0.67895 | 0.62421 | 1.0221 | 1.0053 | 0.98632 | 0.96737 | 0.94737 | 0.92947 | 0.91158 | 0.89474 | 0.87684 | 0.85895 | 0.78421 | 0.72632 | 0.67158 | 0.97895 | 0.95895 | 0.93789 | 0.91789 | 0.89579 | 0.87579 | 0.85684 | 0.83789 | 0.81789 | 0.8 | 0.71789 | 0.65263 | 0.59263
|  | LOCHALINE | HT |  |  |  |  | 0.97474 | 0.95789 | 0.94105 | 0.92526 | 0.90842 | 0.89158 | 0.87684 | 0.86105 | 0.84632 | 0.83158 | 0.77263 | 0.72316 | 0.67789 | 1.0179 | 1.0032 | 0.98842 | 0.97474 | 0.96105 | 0.94526 | 0.93263 | 0.91895 | 0.90421 | 0.89263 | 0.84105 | 0.79684 | 0.75789 | 0.97263 | 0.95474 | 0.93684 | 0.92 | 0.90211 | 0.88421 | 0.86842 | 0.85263 | 0.83579 | 0.82105 | 0.75789 | 0.70316 | 0.65263
|  | LOCHALINE | HE |  |  |  |  | 0.98947 | 0.98 | 0.97158 | 0.96211 | 0.95053 | 0.94 | 0.93263 | 0.92211 | 0.91368 | 0.90526 | 0.87053 | 0.84421 | 0.82105 | 1.0295 | 1.02 | 1.0126 | 1.0032 | 0.99368 | 0.98421 | 0.97579 | 0.96632 | 0.95789 | 0.95053 | 0.91684 | 0.89158 | 0.86947 | 0.97263 | 0.95474 | 0.93684 | 0.92 | 0.90211 | 0.88421 | 0.86842 | 0.85263 | 0.83579 | 0.82105 | 0.75789 | 0.70316 | 0.65263
|  | LOCHALINE | CF |  |  |  |  | 0.99368 | 0.98947 | 0.98421 | 0.97895 | 0.97474 | 0.96947 | 0.96421 | 0.95895 | 0.95368 | 0.95053 | 0.92842 | 0.91263 | 0.9 | 1.0337 | 1.0295 | 1.0253 | 1.0211 | 1.0158 | 1.0126 | 1.0074 | 1.0042 | 1 | 0.99579 | 0.97579 | 0.96316 | 0.95474 | 0.99368 | 0.98842 | 0.98316 | 0.97789 | 0.97263 | 0.96737 | 0.96105 | 0.95684 | 0.95158 | 0.94632 | 0.92316 | 0.90632 | 0.89263
| GRUDIE BRIDGE | LOCHCARRON | MINIMUM HEADROOM | NG 91944 41839 | YES | NO | 0 | 1.1842 | 1.1147 | 1.0274 | 0.93895 | 0.84737 | 0.75684 | 0.67263 | 0.52211 | 0.37263 | 0.21368 | -0.16632 | -0.47053 | -0.76 | 1.02 | 0.96421 | 0.88632 | 0.80316 | 0.72316 | 0.64 | 0.52211 | 0.36947 | 0.24526 | 0.075789 | -0.31474 | -0.63158 | -0.93368 | 1.0958 | 1.0232 | 0.93263 | 0.83684 | 0.74211 | 0.64526 | 0.55053 | 0.37474 | 0.19474 | 0.0021053 | -0.40105 | -0.72526 | -1.0316
|  | LOCHCARRON | EE |  |  |  |  | 1.2011 | 1.1147 | 1.0274 | 0.93895 | 0.84737 | 0.75684 | 0.67263 | 0.52211 | 0.37263 | 0.21368 | -0.16632 | -0.47053 | -0.76 | 1.04 | 0.96421 | 0.88632 | 0.80316 | 0.72316 | 0.64 | 0.55789 | 0.4 | 0.24526 | 0.075789 | -0.31474 | -0.63158 | -0.93368 | 1.1158 | 1.0232 | 0.93263 | 0.83684 | 0.74211 | 0.64526 | 0.55789 | 0.37474 | 0.19474 | 0.0021053 | -0.40105 | -0.72526 | -1.0316
|  | LOCHCARRON | HT |  |  |  |  | 1.1842 | 1.1295 | 1.0747 | 1.0211 | 0.96632 | 0.84421 | 0.71263 | 0.57368 | 0.52421 | 0.47579 | 0.24842 | 0.055789 | -0.11368 | 1.02 | 0.96632 | 0.91263 | 0.85895 | 0.80421 | 0.66421 | 0.52211 | 0.36947 | 0.32316 | 0.27684 | 0.057895 | -0.13263 | -0.29789 | 1.0958 | 1.0347 | 0.97368 | 0.91474 | 0.85368 | 0.70211 | 0.55053 | 0.38947 | 0.33474 | 0.28105 | 0.027368 | -0.18842 | -0.37789
|  | LOCHCARRON | HE |  |  |  |  | 1.2242 | 1.1884 | 1.1537 | 1.1179 | 1.08 | 1.0432 | 1.0074 | 0.92105 | 0.83684 | 0.74105 | 0.54421 | 0.42421 | 0.30842 | 1.0674 | 1.0358 | 1.0021 | 0.96737 | 0.93158 | 0.89579 | 0.86211 | 0.76526 | 0.66947 | 0.56421 | 0.36737 | 0.25368 | 0.14947 | 1.0958 | 1.0347 | 0.97368 | 0.91474 | 0.85368 | 0.70211 | 0.55053 | 0.38947 | 0.33474 | 0.28105 | 0.027368 | -0.18842 | -0.37789
|  | LOCHCARRON | CF |  |  |  |  | 1.2368 | 1.2221 | 1.2074 | 1.1926 | 1.1758 | 1.1621 | 1.1463 | 1.1326 | 1.0905 | 1.0474 | 0.90737 | 0.85895 | 0.82316 | 1.0821 | 1.0674 | 1.0526 | 1.0379 | 1.0221 | 1.0074 | 0.99053 | 0.97684 | 0.92632 | 0.87158 | 0.71368 | 0.66737 | 0.63263 | 1.1579 | 1.1411 | 1.1253 | 1.1074 | 1.0895 | 1.0747 | 1.0568 | 1.0411 | 0.98737 | 0.93053 | 0.76421 | 0.71053 | 0.67053
| TAYNUILT | LOCHDONHEAD | MINIMUM HEADROOM | NM 72902 34134 | YES | YES | 0 | 1.3442 | 1.3316 | 1.3137 | 1.2274 | 1.1832 | 1.1316 | 1.0842 | 1.0347 | 0.96 | 0.86526 | 0.80632 | 0.76 | 0.72105 | 1.1979 | 1.1874 | 1.1758 | 1.0874 | 1.0295 | 0.97053 | 0.91684 | 0.86105 | 0.77474 | 0.66632 | 0.60316 | 0.55158 | 0.50842 | 1.1979 | 1.1874 | 1.1768 | 1.0947 | 1.0368 | 0.97684 | 0.92316 | 0.86632 | 0.77895 | 0.66947 | 0.60632 | 0.55474 | 0.51158
|  | LOCHDONHEAD | EE |  |  |  |  | 1.3474 | 1.34 | 1.3295 | 1.2779 | 1.2442 | 1.1926 | 1.1189 | 1.0853 | 1.0442 | 0.97789 | 0.84 | 0.80526 | 0.77684 | 1.2011 | 1.1937 | 1.1853 | 1.1537 | 1.1095 | 1.0421 | 0.95368 | 0.91684 | 0.86947 | 0.79368 | 0.63789 | 0.6 | 0.56842 | 1.2011 | 1.1937 | 1.1853 | 1.1474 | 1.1116 | 1.0495 | 0.96 | 0.92211 | 0.87474 | 0.79895 | 0.64105 | 0.60316 | 0.57053
|  | LOCHDONHEAD | HT |  |  |  |  | 1.3442 | 1.3316 | 1.3137 | 1.2274 | 1.1832 | 1.1316 | 1.0842 | 1.0347 | 0.96 | 0.86526 | 0.80632 | 0.76 | 0.72105 | 1.1979 | 1.1874 | 1.1758 | 1.0874 | 1.0295 | 0.97053 | 0.91684 | 0.86105 | 0.77474 | 0.66632 | 0.60316 | 0.55158 | 0.50842 | 1.1979 | 1.1874 | 1.1768 | 1.0947 | 1.0368 | 0.97684 | 0.92316 | 0.86632 | 0.77895 | 0.66947 | 0.60632 | 0.55474 | 0.51158
|  | LOCHDONHEAD | HE |  |  |  |  | 1.3537 | 1.3484 | 1.3432 | 1.2884 | 1.2547 | 1.2032 | 1.1263 | 1.0726 | 1.0053 | 0.94842 | 0.92211 | 0.90316 | 0.89053 | 1.2074 | 1.2021 | 1.1968 | 1.1621 | 1.1179 | 1.0495 | 0.95895 | 0.89789 | 0.82105 | 0.75579 | 0.72632 | 0.70632 | 0.69263 | 1.1979 | 1.1874 | 1.1768 | 1.0947 | 1.0368 | 0.97684 | 0.92316 | 0.86632 | 0.77895 | 0.66947 | 0.60632 | 0.55474 | 0.51158
|  | LOCHDONHEAD | CF |  |  |  |  | 1.3568 | 1.3537 | 1.3505 | 1.3474 | 1.3432 | 1.3337 | 1.3168 | 1.2937 | 1.2726 | 1.2242 | 1.1095 | 1.0937 | 1.0821 | 1.2105 | 1.2074 | 1.2042 | 1.2011 | 1.1979 | 1.1937 | 1.1905 | 1.1705 | 1.1432 | 1.0768 | 0.94 | 0.92316 | 0.91053 | 1.2105 | 1.2074 | 1.2042 | 1.2011 | 1.1979 | 1.1947 | 1.1884 | 1.1632 | 1.1411 | 1.0842 | 0.94632 | 0.92947 | 0.91579
| KILLIN | LOCHEARNHEAD | MINIMUM HEADROOM | NN 58766 24177 | YES | YES | 0.1 | -0.011579 | -0.043158 | -0.094737 | -0.22842 | -0.28316 | -0.49158 | -0.72526 | -0.96421 | -1.1747 | -1.3884 | -3.0168 | -5.2526 | -7.0189 | -0.41158 | -0.43474 | -0.46421 | -0.50316 | -0.53474 | -0.63684 | -0.75053 | -0.86842 | -0.96947 | -1.0737 | -2.8516 | -5.1021 | -6.98 | -0.51368 | -0.56526 | -0.62737 | -0.75368 | -0.83053 | -1.0768 | -1.3505 | -1.6263 | -1.8726 | -2.1242 | -4.2695 | -6.7568 | -8.7337
|  | LOCHEARNHEAD | EE |  |  |  |  | -0.0031579 | -0.043158 | -0.094737 | -0.22842 | -0.28316 | -0.49158 | -0.72526 | -0.96421 | -1.1747 | -1.3884 | -3.0168 | -5.2526 | -7.0189 | -0.40316 | -0.42526 | -0.45474 | -0.50316 | -0.53474 | -0.63684 | -0.75053 | -0.86842 | -0.96947 | -1.0737 | -2.8516 | -5.1021 | -6.98 | -0.49579 | -0.54737 | -0.61579 | -0.75368 | -0.83053 | -1.0768 | -1.3505 | -1.6263 | -1.8726 | -2.1242 | -4.2695 | -6.7568 | -8.7337
|  | LOCHEARNHEAD | HT |  |  |  |  | -0.011579 | -0.04 | -0.078947 | -0.11684 | -0.15263 | -0.31789 | -0.47895 | -0.64 | -0.82947 | -1.0221 | -2.5905 | -4.6589 | -6.0853 | -0.41158 | -0.43474 | -0.46421 | -0.49368 | -0.52105 | -0.61158 | -0.69895 | -0.78526 | -0.88421 | -0.98421 | -2.7716 | -5.02 | -6.5979 | -0.51368 | -0.56526 | -0.62737 | -0.69368 | -0.75895 | -0.96526 | -1.1653 | -1.3737 | -1.6095 | -1.8968 | -3.8937 | -6.2147 | -7.8221
|  | LOCHEARNHEAD | HE |  |  |  |  | 0.0094737 | -0.0084211 | -0.029474 | -0.052632 | -0.073684 | -0.26737 | -0.43368 | -0.59789 | -0.76 | -0.93368 | -2.2189 | -3.9074 | -5.8189 | -0.39053 | -0.40316 | -0.41684 | -0.43474 | -0.44947 | -0.54737 | -0.63053 | -0.71263 | -0.79474 | -0.90421 | -2.2821 | -4.06 | -5.9968 | -0.51368 | -0.56526 | -0.62737 | -0.69368 | -0.75895 | -0.96526 | -1.1653 | -1.3737 | -1.6095 | -1.8968 | -3.8937 | -6.2147 | -7.8221
|  | LOCHEARNHEAD | CF |  |  |  |  | 0.015789 | 0.0084211 | -0.0021053 | -0.011579 | -0.021053 | -0.093684 | -0.15895 | -0.22105 | -0.27684 | -0.32 | -0.83684 | -1.8116 | -2.9874 | -0.38421 | -0.38947 | -0.39789 | -0.40632 | -0.41263 | -0.45053 | -0.48421 | -0.51684 | -0.54632 | -0.57053 | -0.98316 | -2.1042 | -3.3968 | -0.45895 | -0.46947 | -0.48842 | -0.50632 | -0.52737 | -0.61895 | -0.70105 | -0.79368 | -0.94842 | -1.1232 | -1.9032 | -3.0747 | -4.4147
| LYNDHURST | LOCHEE | MINIMUM HEADROOM | NO 38065 31416 | NO | YES | 0.1 | 23.8237 | 23.7279 | 23.63 | 23.5289 | 23.4268 | 23.3068 | 23.1805 | 23.0216 | 22.8616 | 22.6963 | 21.89 | 21.2605 | 20.7447 | 22.1842 | 22.0705 | 21.9611 | 21.7958 | 21.6305 | 21.4526 | 21.2747 | 21.0958 | 20.9316 | 20.76 | 19.8832 | 19.1611 | 18.5611 | 22.8013 | 22.7055 | 22.5729 | 22.4066 | 22.2445 | 22.0676 | 21.8929 | 21.715 | 21.5518 | 21.3803 | 20.4382 | 19.7129 | 19.1118
|  | LOCHEE | EE |  |  |  |  | 23.8679 | 23.7963 | 23.7216 | 23.6416 | 23.5595 | 23.4679 | 23.3763 | 23.2858 | 23.1763 | 23.0616 | 22.4311 | 21.9247 | 21.5416 | 22.2284 | 22.1474 | 22.0632 | 21.9737 | 21.8442 | 21.7011 | 21.5663 | 21.4126 | 21.2705 | 21.1421 | 20.4832 | 19.9326 | 19.4884 | 22.8455 | 22.7739 | 22.6992 | 22.5855 | 22.4529 | 22.3118 | 22.1771 | 22.0255 | 21.8834 | 21.755 | 21.0539 | 20.4687 | 20.0224
|  | LOCHEE | HT |  |  |  |  | 23.8237 | 23.7279 | 23.63 | 23.5289 | 23.4268 | 23.3068 | 23.1805 | 23.0216 | 22.8616 | 22.6963 | 21.89 | 21.2605 | 20.7447 | 22.1842 | 22.0705 | 21.9611 | 21.7958 | 21.6305 | 21.4526 | 21.2747 | 21.0958 | 20.9316 | 20.76 | 19.8832 | 19.1611 | 18.5611 | 22.8013 | 22.7055 | 22.5729 | 22.4066 | 22.2445 | 22.0676 | 21.8929 | 21.715 | 21.5518 | 21.3803 | 20.4382 | 19.7129 | 19.1118
|  | LOCHEE | HE |  |  |  |  | 23.9058 | 23.8511 | 23.7911 | 23.7268 | 23.6574 | 23.5774 | 23.5037 | 23.4321 | 23.3637 | 23.3016 | 23.0289 | 22.7426 | 22.5374 | 22.2663 | 22.2105 | 22.1474 | 22.0768 | 22.0021 | 21.9221 | 21.8474 | 21.7674 | 21.6674 | 21.5695 | 21.1168 | 20.8137 | 20.6 | 22.8013 | 22.7055 | 22.5729 | 22.4066 | 22.2445 | 22.0676 | 21.8929 | 21.715 | 21.5518 | 21.3803 | 20.4382 | 19.7129 | 19.1118
|  | LOCHEE | CF |  |  |  |  | 23.9268 | 23.89 | 23.8532 | 23.8142 | 23.7742 | 23.7311 | 23.6889 | 23.6447 | 23.6016 | 23.5605 | 23.3742 | 23.2711 | 23.1774 | 22.2874 | 22.2505 | 22.2137 | 22.1747 | 22.1347 | 22.0937 | 22.0516 | 22.0053 | 21.9589 | 21.9147 | 21.6821 | 21.4379 | 21.2663 | 22.9045 | 22.8676 | 22.8308 | 22.7918 | 22.7518 | 22.7087 | 22.6666 | 22.6234 | 22.5803 | 22.5392 | 22.2866 | 22.0445 | 21.8761
| PORT ANN | LOCHGILPHEAD | MINIMUM HEADROOM | NR 86092 88371 | NO | YES | 0.125 | 25.0876 | 24.8887 | 24.6455 | 24.3308 | 24.0255 | 23.7161 | 23.2739 | 22.8487 | 22.3876 | 21.9582 | 19.4634 | 18.5634 | 17.1897 | 22.4571 | 22.2445 | 21.9845 | 21.6403 | 21.3076 | 20.9739 | 20.5771 | 20.1434 | 19.6487 | 19.2371 | 17.475 | 16.6961 | 15.3971 | 23.3171 | 23.2055 | 23.0824 | 22.8476 | 22.5034 | 22.1613 | 21.7097 | 21.2666 | 20.7266 | 20.2739 | 18.7266 | 17.1529 | 16.4013
|  | LOCHGILPHEAD | EE |  |  |  |  | 25.1476 | 25.0171 | 24.8297 | 24.5855 | 24.2708 | 23.8139 | 23.2739 | 22.8487 | 22.4224 | 22.0055 | 20.4245 | 18.8897 | 18.1803 | 22.5561 | 22.3876 | 22.1929 | 21.9329 | 21.6392 | 21.1982 | 20.6666 | 20.275 | 19.8666 | 19.4739 | 18.0329 | 16.7139 | 16.0592 | 23.3613 | 23.2655 | 23.1571 | 23.0434 | 22.7866 | 22.2961 | 21.7097 | 21.2676 | 20.8118 | 20.3708 | 18.7266 | 17.1529 | 16.4013
|  | LOCHGILPHEAD | HT |  |  |  |  | 25.0876 | 24.8887 | 24.6455 | 24.3308 | 24.0255 | 23.7161 | 23.3213 | 22.8866 | 22.3876 | 21.9582 | 20.6845 | 19.7087 | 19.0666 | 22.4571 | 22.2445 | 21.9845 | 21.6403 | 21.3076 | 20.9739 | 20.5771 | 20.1434 | 19.6487 | 19.2371 | 18.0434 | 17.1171 | 16.4666 | 23.3171 | 23.2055 | 23.0824 | 22.8476 | 22.5034 | 22.1613 | 21.735 | 21.2666 | 20.7266 | 20.2739 | 18.9445 | 17.9139 | 17.215
|  | LOCHGILPHEAD | HE |  |  |  |  | 25.2066 | 25.1466 | 25.0771 | 24.8876 | 24.6897 | 24.2413 | 23.7824 | 23.3929 | 23.0424 | 22.7666 | 19.4634 | 18.5634 | 17.1897 | 22.6508 | 22.5834 | 22.4529 | 22.2445 | 22.0287 | 21.5929 | 21.1308 | 20.7508 | 20.4118 | 20.1634 | 17.475 | 16.6961 | 15.3971 | 23.3171 | 23.2055 | 23.0824 | 22.8476 | 22.5034 | 22.1613 | 21.735 | 21.2666 | 20.7266 | 20.2739 | 18.9445 | 17.9139 | 17.215
|  | LOCHGILPHEAD | CF |  |  |  |  | 25.2403 | 25.2055 | 25.1687 | 25.1297 | 25.0813 | 24.9297 | 24.7687 | 24.5582 | 24.3897 | 24.2087 | 21.2413 | 20.6445 | 19.9118 | 22.6845 | 22.6497 | 22.6139 | 22.5382 | 22.455 | 22.3129 | 22.1529 | 21.9392 | 21.7676 | 21.5771 | 19.1055 | 18.5739 | 17.8497 | 23.4539 | 23.4182 | 23.3824 | 23.3424 | 23.3045 | 23.2066 | 23.1171 | 23.0266 | 22.9297 | 22.7318 | 19.7087 | 19.0929 | 18.295
| CLACHAN | LOCHGOILHEAD | MINIMUM HEADROOM | NN 20159 01862 | YES | YES | 0 | -0.095789 | -0.11158 | -0.13789 | -0.16842 | -0.19789 | -0.22842 | -0.25579 | -0.28421 | -0.31263 | -0.34211 | -0.47579 | -0.58632 | -0.69474 | -0.27158 | -0.28 | -0.29368 | -0.31895 | -0.34947 | -0.38 | -0.40947 | -0.44211 | -0.47263 | -0.50421 | -0.64737 | -0.76421 | -0.88421 | 0.33263 | 0.30632 | 0.27368 | 0.23789 | 0.20316 | 0.16632 | 0.13263 | 0.096842 | 0.063158 | 0.029474 | -0.12842 | -0.25368 | -0.37895
|  | LOCHGOILHEAD | EE |  |  |  |  | -0.092632 | -0.11158 | -0.13789 | -0.16842 | -0.19789 | -0.22842 | -0.25579 | -0.28421 | -0.31263 | -0.34211 | -0.47579 | -0.58632 | -0.69474 | -0.26737 | -0.28 | -0.29368 | -0.31895 | -0.34947 | -0.38 | -0.40947 | -0.44211 | -0.47263 | -0.50421 | -0.64737 | -0.76421 | -0.88421 | 0.33789 | 0.30632 | 0.27368 | 0.23789 | 0.20316 | 0.16632 | 0.13263 | 0.096842 | 0.063158 | 0.029474 | -0.12842 | -0.25368 | -0.37895
|  | LOCHGOILHEAD | HT |  |  |  |  | -0.095789 | -0.10632 | -0.11789 | -0.12947 | -0.14526 | -0.16421 | -0.18421 | -0.2 | -0.21684 | -0.23368 | -0.30526 | -0.37053 | -0.43053 | -0.27158 | -0.28 | -0.28947 | -0.3 | -0.30947 | -0.32105 | -0.33579 | -0.34947 | -0.36421 | -0.38105 | -0.45474 | -0.52211 | -0.58526 | 0.33263 | 0.31474 | 0.29579 | 0.27579 | 0.25684 | 0.23789 | 0.21789 | 0.2 | 0.18211 | 0.16316 | 0.085263 | 0.014737 | -0.051579
|  | LOCHGOILHEAD | HE |  |  |  |  | -0.088421 | -0.096842 | -0.10526 | -0.11368 | -0.12211 | -0.13368 | -0.14316 | -0.15579 | -0.16632 | -0.17684 | -0.22316 | -0.26632 | -0.30842 | -0.26316 | -0.26947 | -0.27684 | -0.28316 | -0.28947 | -0.29684 | -0.30316 | -0.31053 | -0.32105 | -0.32947 | -0.37684 | -0.42105 | -0.46632 | 0.33263 | 0.31474 | 0.29579 | 0.27579 | 0.25684 | 0.23789 | 0.21789 | 0.2 | 0.18211 | 0.16316 | 0.085263 | 0.014737 | -0.051579
|  | LOCHGOILHEAD | CF |  |  |  |  | -0.086316 | -0.089474 | -0.092632 | -0.095789 | -0.098947 | -0.10211 | -0.10526 | -0.10947 | -0.11263 | -0.11474 | -0.12842 | -0.13895 | -0.15368 | -0.26105 | -0.26421 | -0.26632 | -0.26842 | -0.27158 | -0.27474 | -0.27789 | -0.28105 | -0.28421 | -0.28632 | -0.29789 | -0.30526 | -0.31053 | 0.34737 | 0.34316 | 0.33789 | 0.33368 | 0.32842 | 0.32421 | 0.31895 | 0.31368 | 0.30842 | 0.30316 | 0.28 | 0.26421 | 0.24947
| GRUDIE BRIDGE | LOCHINVER | MINIMUM HEADROOM | NC 09516 22243 | YES | NO | 0 | 1.2653 | 1.2274 | 1.1874 | 1.1158 | 1.0442 | 0.96947 | 0.91579 | 0.86211 | 0.81053 | 0.76211 | 0.58316 | 0.41895 | 0.27158 | 1.1116 | 1.0811 | 1.0484 | 0.97579 | 0.90316 | 0.82737 | 0.77263 | 0.71579 | 0.66105 | 0.60842 | 0.41579 | 0.23158 | 0.065263 | 1.2137 | 1.1547 | 1.0947 | 1.0179 | 0.94105 | 0.86 | 0.80316 | 0.74632 | 0.69158 | 0.64 | 0.44947 | 0.26842 | 0.10632
|  | LOCHINVER | EE |  |  |  |  | 1.2811 | 1.2516 | 1.2232 | 1.1779 | 1.1158 | 1.0558 | 1.0126 | 0.97158 | 0.93158 | 0.89474 | 0.74842 | 0.62421 | 0.51789 | 1.1242 | 1.1 | 1.0758 | 1.0389 | 0.97579 | 0.91474 | 0.87053 | 0.82947 | 0.78947 | 0.75158 | 0.59474 | 0.45789 | 0.33684 | 1.2358 | 1.1958 | 1.1516 | 1.0842 | 1.0179 | 0.95263 | 0.90632 | 0.86211 | 0.82105 | 0.78105 | 0.62632 | 0.49158 | 0.37263
|  | LOCHINVER | HT |  |  |  |  | 1.2653 | 1.2274 | 1.1874 | 1.1158 | 1.0442 | 0.96947 | 0.91579 | 0.86211 | 0.81053 | 0.76211 | 0.58316 | 0.41895 | 0.27158 | 1.1116 | 1.0811 | 1.0484 | 0.97579 | 0.90316 | 0.82737 | 0.77263 | 0.71579 | 0.66105 | 0.60842 | 0.41579 | 0.23158 | 0.065263 | 1.2137 | 1.1547 | 1.0947 | 1.0179 | 0.94105 | 0.86 | 0.80316 | 0.74632 | 0.69158 | 0.64 | 0.44947 | 0.26842 | 0.10632
|  | LOCHINVER | HE |  |  |  |  | 1.2989 | 1.2832 | 1.2621 | 1.2389 | 1.2095 | 1.1632 | 1.1337 | 1.1053 | 1.0789 | 1.0589 | 0.97684 | 0.90842 | 0.85263 | 1.1411 | 1.1253 | 1.1084 | 1.0905 | 1.0716 | 1.0232 | 0.99368 | 0.96526 | 0.93895 | 0.91895 | 0.83579 | 0.76632 | 0.70421 | 1.2137 | 1.1547 | 1.0947 | 1.0179 | 0.94105 | 0.86 | 0.80316 | 0.74632 | 0.69158 | 0.64 | 0.44947 | 0.26842 | 0.10632
|  | LOCHINVER | CF |  |  |  |  | 1.3084 | 1.3 | 1.2916 | 1.2821 | 1.2716 | 1.2611 | 1.2495 | 1.2379 | 1.2274 | 1.2158 | 1.1495 | 1.0926 | 1.0505 | 1.1505 | 1.1421 | 1.1337 | 1.1242 | 1.1158 | 1.1063 | 1.0968 | 1.0874 | 1.0779 | 1.0684 | 1.0095 | 0.95263 | 0.90947 | 1.2621 | 1.2537 | 1.2453 | 1.2358 | 1.2274 | 1.2137 | 1.1958 | 1.1779 | 1.1621 | 1.1453 | 1.0547 | 0.99263 | 0.94526
| LUNANHEAD | LOCHSIDE | MINIMUM HEADROOM | NO 45151 50548 | NO | YES | 3.153 | 22.9933 | 21.0249 | 20.8965 | 20.7628 | 20.6228 | 20.3933 | 20.1502 | 19.907 | 19.6849 | 19.3912 | 17.7512 | 16.1796 | 14.9923 | 20.7491 | 18.4733 | 18.3459 | 18.2144 | 18.0754 | 17.8649 | 17.6438 | 17.4238 | 17.2217 | 16.9354 | 15.3038 | 13.7312 | 12.4428 | 21.8838 | 19.5817 | 19.4523 | 19.3196 | 19.1786 | 18.947 | 18.7007 | 18.4554 | 18.2312 | 17.9207 | 16.1565 | 14.4428 | 13.1017
|  | LOCHSIDE | EE |  |  |  |  | 22.9933 | 21.0249 | 20.8965 | 20.7628 | 20.6228 | 20.3933 | 20.1502 | 19.907 | 19.6849 | 19.3912 | 17.7512 | 16.1796 | 14.9923 | 20.7491 | 18.4733 | 18.3459 | 18.2144 | 18.0754 | 17.8649 | 17.6438 | 17.4238 | 17.2217 | 16.9354 | 15.3038 | 13.7312 | 12.4428 | 21.8838 | 19.5817 | 19.4523 | 19.3196 | 19.1786 | 18.947 | 18.7007 | 18.4554 | 18.2312 | 17.9207 | 16.1565 | 14.4428 | 13.1017
|  | LOCHSIDE | HT |  |  |  |  | 24.0723 | 23.927 | 23.7554 | 23.5765 | 23.2207 | 22.7228 | 22.2312 | 21.8154 | 21.4302 | 21.1438 | 19.9691 | 18.9438 | 18.1512 | 22.4228 | 22.2354 | 21.9902 | 21.5786 | 21.1291 | 20.6038 | 20.0859 | 19.6575 | 19.267 | 18.9923 | 17.8407 | 16.7849 | 15.9365 | 23.2438 | 23.0986 | 22.9459 | 22.7407 | 22.2744 | 21.7281 | 21.1902 | 20.7407 | 20.327 | 20.0323 | 18.7923 | 17.6807 | 16.8059
|  | LOCHSIDE | HE |  |  |  |  | 23.0659 | 22.9838 | 21.0396 | 20.9417 | 20.8365 | 20.5859 | 20.3575 | 20.127 | 19.907 | 19.6344 | 18.5386 | 17.3712 | 16.1796 | 20.8217 | 20.7396 | 18.4881 | 18.3902 | 18.2859 | 18.0491 | 17.8291 | 17.6081 | 17.3986 | 17.1238 | 16.0386 | 14.8354 | 13.6007 | 23.2438 | 23.0986 | 22.9459 | 22.7407 | 22.2744 | 21.7281 | 21.1902 | 20.7407 | 20.327 | 20.0323 | 18.7923 | 17.6807 | 16.8059
|  | LOCHSIDE | CF |  |  |  |  | 24.2407 | 23.0544 | 21.1481 | 21.0923 | 21.0354 | 20.9417 | 20.8512 | 20.7059 | 20.5681 | 20.4175 | 19.7607 | 18.9965 | 18.2154 | 22.6017 | 20.8102 | 18.5965 | 18.5407 | 18.4838 | 18.3986 | 18.3144 | 18.1659 | 18.0238 | 17.8659 | 17.1975 | 16.4049 | 15.5628 | 23.4123 | 21.9449 | 19.7049 | 19.6481 | 19.5923 | 19.4975 | 19.407 | 19.2512 | 19.1017 | 18.9375 | 18.2302 | 17.3849 | 16.4986
| BRIDGE OF DUN | LOGIE PERT | MINIMUM HEADROOM | NO 67764 64427 | YES | YES | 0 | 5.0516 | 5.0347 | 5.0095 | 4.9853 | 4.9621 | 4.8284 | 4.6547 | 4.4937 | 4.3389 | 4.08 | 2.4937 | 0.78632 | -0.56526 | 4.9758 | 4.9568 | 4.9316 | 4.9074 | 4.8832 | 4.7789 | 4.6368 | 4.4895 | 4.3284 | 4.0747 | 2.5221 | 0.88421 | -0.54316 | 5.0221 | 5.0032 | 4.9758 | 4.9495 | 4.9242 | 4.7926 | 4.6179 | 4.4705 | 4.3168 | 4.0663 | 2.2684 | 0.44632 | -1.1021
|  | LOGIE PERT | EE |  |  |  |  | 5.06 | 5.0474 | 5.0221 | 4.9979 | 4.9726 | 4.8284 | 4.6547 | 4.4937 | 4.34 | 4.1453 | 2.5537 | 0.78632 | -0.56526 | 4.9853 | 4.9705 | 4.9474 | 4.9242 | 4.9 | 4.7789 | 4.6368 | 4.52 | 4.3937 | 4.2221 | 2.6758 | 0.93368 | -0.54316 | 5.0316 | 5.0168 | 4.9905 | 4.9653 | 4.9379 | 4.7926 | 4.6179 | 4.4705 | 4.3168 | 4.1158 | 2.3821 | 0.44632 | -1.1021
|  | LOGIE PERT | HT |  |  |  |  | 5.0516 | 5.0347 | 5.0095 | 4.9853 | 4.9621 | 4.8579 | 4.7337 | 4.6042 | 4.4337 | 4.1242 | 2.4937 | 1.0526 | -0.064211 | 4.9758 | 4.9568 | 4.9316 | 4.9074 | 4.8832 | 4.8105 | 4.7063 | 4.5968 | 4.4495 | 4.1432 | 2.5221 | 0.88421 | -0.37474 | 5.0221 | 5.0032 | 4.9758 | 4.9495 | 4.9242 | 4.8347 | 4.7095 | 4.5768 | 4.4021 | 4.0663 | 2.2684 | 0.59684 | -0.69158
|  | LOGIE PERT | HE |  |  |  |  | 5.0726 | 5.0632 | 5.0516 | 5.0411 | 5.0284 | 4.8779 | 4.72 | 4.5168 | 4.3389 | 4.08 | 2.9821 | 1.6158 | 0.11895 | 4.9989 | 4.9895 | 4.9779 | 4.9663 | 4.9537 | 4.8295 | 4.6905 | 4.4895 | 4.3284 | 4.0747 | 3.0084 | 1.6084 | 0.075789 | 5.0221 | 5.0032 | 4.9758 | 4.9495 | 4.9242 | 4.8347 | 4.7095 | 4.5768 | 4.4021 | 4.0663 | 2.2684 | 0.59684 | -0.69158
|  | LOGIE PERT | CF |  |  |  |  | 5.0779 | 5.0726 | 5.0653 | 5.06 | 5.0516 | 4.9947 | 4.9442 | 4.8905 | 4.8011 | 4.6768 | 4.1116 | 3.2495 | 2.2863 | 5.0053 | 4.9989 | 4.9926 | 4.9853 | 4.9779 | 4.9295 | 4.8863 | 4.8421 | 4.7526 | 4.6211 | 4.0474 | 3.1547 | 2.1137 | 5.0516 | 5.0453 | 5.0379 | 5.0305 | 5.0232 | 4.9632 | 4.9116 | 4.8589 | 4.76 | 4.6179 | 3.9884 | 3.0242 | 1.9316
| MILTON OF CRAIGIE | LONGHAUGH | MINIMUM HEADROOM | NO 42768 33789 | NO | YES | 5.106 | 18.7514 | 18.484 | 17.9977 | 17.6429 | 16.9998 | 16.0566 | 15.7072 | 15.3619 | 14.9966 | 14.6335 | 12.6608 | 11.0924 | 9.9977 | 18.6535 | 18.4082 | 18.1672 | 17.9451 | 17.2293 | 16.2166 | 15.8998 | 15.5882 | 15.2651 | 14.944 | 13.0145 | 11.4187 | 10.2545 | 18.6587 | 18.4356 | 18.2082 | 17.9914 | 17.744 | 17.0956 | 16.7461 | 16.3998 | 16.0335 | 15.6703 | 13.5829 | 11.8935 | 10.6956
|  | LONGHAUGH | EE |  |  |  |  | 18.8177 | 18.6661 | 18.3724 | 17.9893 | 17.4187 | 16.5766 | 16.1787 | 15.7808 | 15.4198 | 15.0619 | 13.1156 | 11.1935 | 10.1303 | 18.7229 | 18.5366 | 18.3387 | 18.1345 | 17.6935 | 16.8072 | 16.4556 | 16.104 | 15.7819 | 15.4651 | 13.7072 | 11.9556 | 10.884 | 18.7272 | 18.5545 | 18.364 | 18.1661 | 17.9451 | 17.5851 | 17.2472 | 16.8651 | 16.4987 | 16.1366 | 14.1314 | 12.1187 | 10.9714
|  | LONGHAUGH | HT |  |  |  |  | 18.7514 | 18.484 | 17.9977 | 17.6429 | 16.9998 | 16.0566 | 15.7072 | 15.3619 | 14.9966 | 14.6335 | 12.6608 | 11.0924 | 9.9977 | 18.6535 | 18.4082 | 18.1672 | 17.9451 | 17.2293 | 16.2166 | 15.8998 | 15.5882 | 15.2651 | 14.944 | 13.0145 | 11.4187 | 10.2545 | 18.6587 | 18.4356 | 18.2082 | 17.9914 | 17.744 | 17.0956 | 16.7461 | 16.3998 | 16.0335 | 15.6703 | 13.5829 | 11.8935 | 10.6956
|  | LONGHAUGH | HE |  |  |  |  | 18.9166 | 18.8124 | 18.6945 | 18.304 | 17.7682 | 16.9566 | 16.6545 | 16.3566 | 16.0651 | 15.7861 | 14.6135 | 13.744 | 11.8672 | 18.8219 | 18.6998 | 18.5566 | 18.3851 | 18.0429 | 17.1914 | 16.9229 | 16.6587 | 16.3998 | 16.1545 | 15.1398 | 14.4251 | 12.5345 | 18.6587 | 18.4356 | 18.2082 | 17.9914 | 17.744 | 17.0956 | 16.7461 | 16.3998 | 16.0335 | 15.6703 | 13.5829 | 11.8935 | 10.6956
|  | LONGHAUGH | CF |  |  |  |  | 18.9745 | 18.9114 | 18.8451 | 18.7766 | 18.7082 | 18.5787 | 18.4556 | 18.2703 | 18.0566 | 17.8493 | 16.9524 | 16.2335 | 15.1187 | 18.8861 | 18.8198 | 18.7503 | 18.6766 | 18.5998 | 18.4903 | 18.3819 | 18.2724 | 18.1672 | 18.0672 | 17.3808 | 16.7272 | 15.5493 | 18.8882 | 18.8229 | 18.7556 | 18.6829 | 18.6082 | 18.4777 | 18.3514 | 18.2251 | 18.1051 | 17.9977 | 17.4429 | 16.9587 | 16.1608
| INVERNESS | LONGMAN DRIVE | MINIMUM HEADROOM | NH 67139 46770 | NO | YES | 0.467 | 25.429 | 25.3115 | 25.1893 | 23.9422 | 23.8576 | 23.7022 | 23.623 | 23.374 | 23.1294 | 22.7998 | 22.1084 | 22.0165 | 21.7938 | 24.8224 | 24.7139 | 24.6026 | 23.5762 | 23.491 | 23.3233 | 23.2494 | 22.973 | 22.7013 | 22.3718 | 21.6522 | 21.6132 | 21.342 | 25.4419 | 25.3589 | 25.275 | 23.8961 | 23.8221 | 23.5996 | 23.5037 | 23.0457 | 22.5891 | 22.1035 | 21.3036 | 21.3031 | 21.0305
|  | LONGMAN DRIVE | EE |  |  |  |  | 25.4523 | 25.3596 | 25.2597 | 23.9422 | 23.8576 | 23.7022 | 23.623 | 23.374 | 23.1294 | 22.7998 | 22.1084 | 22.0165 | 21.7938 | 24.8414 | 24.7551 | 24.6641 | 23.5762 | 23.491 | 23.3233 | 23.2494 | 22.973 | 22.7013 | 22.3718 | 21.6522 | 21.6132 | 21.342 | 25.4585 | 25.3916 | 25.3235 | 23.8961 | 23.8221 | 23.5996 | 23.5037 | 23.0457 | 22.5891 | 22.1035 | 21.3036 | 21.3031 | 21.0305
|  | LONGMAN DRIVE | HT |  |  |  |  | 25.429 | 25.3115 | 25.1893 | 25.0509 | 24.9195 | 24.5744 | 24.2825 | 23.9139 | 23.6452 | 23.3843 | 23.1572 | 22.8005 | 22.488 | 24.8224 | 24.7139 | 24.6026 | 24.4721 | 24.35 | 23.9782 | 23.6604 | 23.3023 | 23.043 | 22.7876 | 22.6538 | 22.2311 | 21.8143 | 25.4419 | 25.3589 | 25.275 | 25.1816 | 25.0431 | 24.4216 | 23.8882 | 23.3633 | 23.0523 | 22.7553 | 22.6152 | 22.1628 | 21.7469
|  | LONGMAN DRIVE | HE |  |  |  |  | 25.4756 | 25.4171 | 25.3465 | 25.2677 | 25.1813 | 25.0222 | 24.9468 | 24.802 | 24.664 | 24.5314 | 24.1253 | 23.939 | 23.3537 | 24.8652 | 24.8043 | 24.7404 | 24.6692 | 24.5906 | 24.4339 | 24.3605 | 24.2059 | 24.0562 | 23.9114 | 23.4812 | 23.4728 | 22.6785 | 25.4419 | 25.3589 | 25.275 | 25.1816 | 25.0431 | 24.4216 | 23.8882 | 23.3633 | 23.0523 | 22.7553 | 22.6152 | 22.1628 | 21.7469
|  | LONGMAN DRIVE | CF |  |  |  |  | 25.4957 | 25.4713 | 25.4442 | 25.4084 | 25.3716 | 25.3054 | 25.2601 | 25.2233 | 25.1409 | 25.0552 | 24.7224 | 24.5426 | 24.3991 | 24.8902 | 24.8588 | 24.8252 | 24.7909 | 24.7558 | 24.6952 | 24.6542 | 24.6214 | 24.535 | 24.4442 | 24.0914 | 23.9082 | 23.7581 | 25.4955 | 25.4707 | 25.4447 | 25.4178 | 25.3892 | 25.3454 | 25.3136 | 25.2857 | 25.2073 | 25.0697 | 24.5368 | 24.2619 | 24.0233
| ELGIN | LOSSIEMOUTH | MINIMUM HEADROOM | NJ 23203 69923 | NO | YES | 0 | 15.27 | 15.1668 | 15.0584 | 14.9489 | 14.8384 | 14.6616 | 14.3963 | 14.1384 | 13.8774 | 13.6216 | 12.5647 | 11.9226 | 11.3921 | 15.7137 | 15.5189 | 15.2684 | 15.0105 | 14.7432 | 14.4505 | 14.1579 | 13.8726 | 13.5842 | 13.3021 | 12.1421 | 11.4484 | 10.8611 | 14.6792 | 14.5761 | 14.4676 | 14.3582 | 14.1287 | 13.8392 | 13.5508 | 13.2697 | 12.9845 | 12.7055 | 11.5203 | 10.8087 | 10.2108
|  | LOSSIEMOUTH | EE |  |  |  |  | 15.3068 | 15.2226 | 15.1342 | 15.0395 | 14.9416 | 14.8205 | 14.6647 | 14.4342 | 14.2111 | 13.9932 | 12.9521 | 12.3458 | 11.9342 | 15.7526 | 15.6526 | 15.4453 | 15.2232 | 14.9884 | 14.7274 | 14.4674 | 14.2179 | 13.9716 | 13.7337 | 12.5905 | 11.9821 | 11.5358 | 14.7161 | 14.6318 | 14.5434 | 14.4487 | 14.3508 | 14.1045 | 13.8445 | 13.595 | 13.3508 | 13.1129 | 11.9476 | 11.3045 | 10.8445
|  | LOSSIEMOUTH | HT |  |  |  |  | 15.27 | 15.1668 | 15.0584 | 14.9489 | 14.8384 | 14.6616 | 14.3963 | 14.1384 | 13.8774 | 13.6216 | 12.5647 | 11.9226 | 11.3921 | 15.7137 | 15.5189 | 15.2684 | 15.0105 | 14.7432 | 14.4505 | 14.1579 | 13.8726 | 13.5842 | 13.3021 | 12.1421 | 11.4484 | 10.8611 | 14.6792 | 14.5761 | 14.4676 | 14.3582 | 14.1287 | 13.8392 | 13.5508 | 13.2697 | 12.9845 | 12.7055 | 11.5203 | 10.8087 | 10.2108
|  | LOSSIEMOUTH | HE |  |  |  |  | 15.3637 | 15.3068 | 15.2437 | 15.1753 | 15.1026 | 15.0005 | 14.91 | 14.8195 | 14.7132 | 14.5426 | 13.8068 | 13.4353 | 13.1647 | 15.8126 | 15.7526 | 15.6853 | 15.5263 | 15.3463 | 15.1305 | 14.9274 | 14.7263 | 14.5305 | 14.3421 | 13.5232 | 13.1295 | 12.86 | 14.6792 | 14.5761 | 14.4676 | 14.3582 | 14.1287 | 13.8392 | 13.5508 | 13.2697 | 12.9845 | 12.7055 | 11.5203 | 10.8087 | 10.2108
|  | LOSSIEMOUTH | CF |  |  |  |  | 15.3942 | 15.3605 | 15.3247 | 15.2879 | 15.2511 | 15.2037 | 15.1574 | 15.1111 | 15.0658 | 15.0237 | 14.7458 | 14.4679 | 14.2784 | 15.8453 | 15.8095 | 15.7716 | 15.7326 | 15.6895 | 15.5832 | 15.4747 | 15.3632 | 15.2495 | 15.1305 | 14.5432 | 14.2474 | 14.04 | 14.8034 | 14.7697 | 14.7339 | 14.6971 | 14.6603 | 14.6139 | 14.5687 | 14.5224 | 14.4782 | 14.4361 | 13.9182 | 13.6161 | 13.4066
| BROADFORD | LOWER OLLACH | MINIMUM HEADROOM | NG 51241 37001 | YES | YES | 0 | 1.2011 | 1.1726 | 1.1368 | 1.1032 | 1.0684 | 0.93158 | 0.74947 | 0.56211 | 0.4 | 0.21263 | -1.3053 | -2.9895 | -4.2158 | 1.1768 | 1.1484 | 1.1116 | 1.0779 | 1.0432 | 0.93053 | 0.79579 | 0.64421 | 0.51158 | 0.27895 | -1.1011 | -2.7379 | -4.0611 | 1.1779 | 1.1621 | 1.1316 | 1.0989 | 1.0653 | 0.92211 | 0.73684 | 0.54526 | 0.38105 | 0.20316 | -1.4326 | -3.2653 | -4.6789
|  | LOWER OLLACH | EE |  |  |  |  | 1.2137 | 1.1905 | 1.1558 | 1.12 | 1.0874 | 0.93158 | 0.74947 | 0.56211 | 0.4 | 0.23579 | -1.3053 | -2.9895 | -4.2158 | 1.1916 | 1.1674 | 1.1347 | 1.1021 | 1.0705 | 0.94316 | 0.79579 | 0.64421 | 0.51158 | 0.37895 | -1.1011 | -2.7379 | -4.0611 | 1.1853 | 1.1705 | 1.1474 | 1.1147 | 1.0811 | 0.92211 | 0.73684 | 0.54526 | 0.38105 | 0.21263 | -1.4326 | -3.2653 | -4.6789
|  | LOWER OLLACH | HT |  |  |  |  | 1.2011 | 1.1726 | 1.1368 | 1.1032 | 1.0684 | 0.93368 | 0.8 | 0.66526 | 0.50526 | 0.22842 | -1.1263 | -2.6074 | -3.6032 | 1.1768 | 1.1484 | 1.1116 | 1.0779 | 1.0432 | 0.93053 | 0.81789 | 0.70526 | 0.57474 | 0.30526 | -1.0663 | -2.6779 | -3.8116 | 1.1779 | 1.1621 | 1.1316 | 1.0989 | 1.0653 | 0.92842 | 0.79158 | 0.65474 | 0.49368 | 0.20316 | -1.3011 | -3.0084 | -4.1737
|  | LOWER OLLACH | HE |  |  |  |  | 1.2316 | 1.2179 | 1.2011 | 1.1853 | 1.1674 | 0.99789 | 0.81895 | 0.63579 | 0.46105 | 0.21263 | -0.84316 | -2.1189 | -3.5042 | 1.2063 | 1.1968 | 1.18 | 1.1632 | 1.1453 | 1.0063 | 0.84421 | 0.67789 | 0.52211 | 0.27895 | -0.73158 | -2.0211 | -3.4221 | 1.1779 | 1.1621 | 1.1316 | 1.0989 | 1.0653 | 0.92842 | 0.79158 | 0.65474 | 0.49368 | 0.20316 | -1.3011 | -3.0084 | -4.1737
|  | LOWER OLLACH | CF |  |  |  |  | 1.2389 | 1.2316 | 1.22 | 1.2105 | 1.2011 | 1.1379 | 1.0842 | 0.99789 | 0.89158 | 0.77684 | 0.23895 | -0.56105 | -1.4295 | 1.2116 | 1.2063 | 1.2011 | 1.1895 | 1.1811 | 1.1284 | 1.0832 | 1.0011 | 0.89368 | 0.77053 | 0.23263 | -0.58211 | -1.5179 | 1.1979 | 1.1937 | 1.1874 | 1.18 | 1.1758 | 1.1263 | 1.0747 | 0.99053 | 0.88526 | 0.75368 | 0.15895 | -0.73474 | -1.7316
| KILLIN | LUBNAIG | MINIMUM HEADROOM | NN 57455 13800 | YES | YES | 0 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19579 | 0.19474 | 0.20105 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19684 | 0.19579 | 0.19579 | 0.19368 | 0.19158 | 0.20105 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19684 | 0.19579 | 0.19579 | 0.19368 | 0.19158
|  | LUBNAIG | EE |  |  |  |  | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19579 | 0.19579 | 0.19474 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19579 | 0.19579 | 0.19474
|  | LUBNAIG | HT |  |  |  |  | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19579 | 0.19474 | 0.20105 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19684 | 0.19579 | 0.19579 | 0.19368 | 0.19158 | 0.20105 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19684 | 0.19579 | 0.19579 | 0.19368 | 0.19158
|  | LUBNAIG | HE |  |  |  |  | 0.20316 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19789 | 0.20105 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19684 | 0.19579 | 0.19579 | 0.19368 | 0.19158
|  | LUBNAIG | CF |  |  |  |  | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.19895 | 0.19895 | 0.20211 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.20105 | 0.19895 | 0.19895
| LUNANHEAD | LUNANHEAD | MINIMUM HEADROOM | NO 47042 51733 | NO | YES | 1.018 | 13.2615 | 13.0815 | 12.8478 | 12.6131 | 12.3783 | 11.2888 | 10.3446 | 9.3309 | 7.992 | 6.0509 | -4.508 | -17.8375 | -28.8891 | 11.8967 | 11.7009 | 11.4662 | 11.2315 | 10.9967 | 10.2094 | 9.3894 | 8.5641 | 7.4125 | 5.4536 | -5.4159 | -17.7138 | -29.8927 | 12.1949 | 11.997 | 11.7465 | 11.4959 | 11.2454 | 10.197 | 9.2412 | 8.2349 | 7.0381 | 4.9896 | -7.2114 | -21.3967 | -34.1883
|  | LUNANHEAD | EE |  |  |  |  | 13.312 | 13.1846 | 12.9541 | 12.7173 | 12.4794 | 11.2888 | 11.1573 | 9.7415 | 8.5152 | 7.2678 | -4.3796 | -17.8375 | -28.8891 | 11.9483 | 11.8136 | 11.5936 | 11.3694 | 11.1441 | 10.2357 | 10.0978 | 8.9715 | 7.9925 | 6.9999 | -4.4727 | -17.7138 | -29.8927 | 12.2465 | 12.1096 | 11.8654 | 11.617 | 11.3665 | 10.197 | 10.0559 | 8.6644 | 7.4444 | 6.2023 | -6.6483 | -21.3967 | -34.1883
|  | LUNANHEAD | HT |  |  |  |  | 13.2615 | 13.0815 | 12.8478 | 12.6131 | 12.3783 | 11.3488 | 10.3446 | 9.3309 | 8.132 | 6.2467 | -4.508 | -15.3459 | -23.7691 | 11.8967 | 11.7009 | 11.4662 | 11.2315 | 10.9967 | 10.2094 | 9.3894 | 8.5641 | 7.5946 | 5.782 | -5.4159 | -17.2369 | -26.7306 | 12.1949 | 11.997 | 11.7465 | 11.4959 | 11.2454 | 10.2275 | 9.2412 | 8.2349 | 7.0381 | 4.9896 | -7.2114 | -19.6219 | -29.3198
|  | LUNANHEAD | HE |  |  |  |  | 13.3731 | 13.2899 | 13.1888 | 13.0678 | 12.9331 | 11.6878 | 10.6604 | 9.3625 | 7.992 | 6.0509 | -2.2101 | -12.5406 | -24.7469 | 12.0094 | 11.922 | 11.8178 | 11.6957 | 11.5557 | 10.6315 | 9.8146 | 8.6588 | 7.4125 | 5.4536 | -2.7106 | -13.2359 | -25.9117 | 12.1949 | 11.997 | 11.7465 | 11.4959 | 11.2454 | 10.2275 | 9.2412 | 8.2349 | 7.0381 | 4.9896 | -7.2114 | -19.6219 | -29.3198
|  | LUNANHEAD | CF |  |  |  |  | 13.4236 | 13.3825 | 13.3278 | 13.272 | 13.2162 | 12.7478 | 12.3236 | 11.9046 | 11.3299 | 10.4162 | 6.1941 | -0.27432 | -7.4427 | 12.0631 | 12.022 | 11.9704 | 11.9188 | 11.8652 | 11.5252 | 11.2115 | 10.8736 | 10.3157 | 9.2894 | 4.8809 | -1.8654 | -9.6854 | 12.3623 | 12.3212 | 12.2644 | 12.2086 | 12.1517 | 11.6949 | 11.277 | 10.8654 | 10.2381 | 9.1444 | 4.3244 | -2.9777 | -11.1872
| PORT ANN | LUSSAGIVEN | MINIMUM HEADROOM | NR 63461 86798 | YES | YES | 0 | 0.10526 | 0.10526 | 0.10421 | 0.10316 | 0.10211 | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.095789 | 0.092632 | 0.088421 | 0.084211 | 0.10316 | 0.10211 | 0.10105 | 0.1 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.092632 | 0.088421 | 0.084211 | 0.08 | 0.10316 | 0.10211 | 0.10105 | 0.10105 | 0.1 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.092632 | 0.089474 | 0.085263 | 0.081053
|  | LUSSAGIVEN | EE |  |  |  |  | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.098947 | 0.094737 | 0.092632 | 0.089474 | 0.10316 | 0.10316 | 0.10105 | 0.10105 | 0.10105 | 0.098947 | 0.098947 | 0.097895 | 0.097895 | 0.096842 | 0.091579 | 0.088421 | 0.086316 | 0.10316 | 0.10316 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.097895 | 0.097895 | 0.096842 | 0.092632 | 0.089474 | 0.087368
|  | LUSSAGIVEN | HT |  |  |  |  | 0.10526 | 0.10526 | 0.10421 | 0.10316 | 0.10211 | 0.1 | 0.098947 | 0.097895 | 0.097895 | 0.095789 | 0.092632 | 0.088421 | 0.084211 | 0.10316 | 0.10211 | 0.10105 | 0.1 | 0.098947 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.092632 | 0.088421 | 0.084211 | 0.08 | 0.10316 | 0.10211 | 0.10105 | 0.10105 | 0.1 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.092632 | 0.089474 | 0.085263 | 0.081053
|  | LUSSAGIVEN | HE |  |  |  |  | 0.10737 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.1 | 0.098947 | 0.096842 | 0.10526 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.097895 | 0.096842 | 0.093684 | 0.10316 | 0.10211 | 0.10105 | 0.10105 | 0.1 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.092632 | 0.089474 | 0.085263 | 0.081053
|  | LUSSAGIVEN | CF |  |  |  |  | 0.10737 | 0.10737 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10105 | 0.1 | 0.10526 | 0.10526 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.10105 | 0.098947 | 0.097895 | 0.10526 | 0.10526 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.10105 | 0.098947 | 0.097895
| LYNDHURST | LYNDHURST | MINIMUM HEADROOM | NO 37434 32575 | NO | YES | 0.197 | 15.7635 | 15.7119 | 15.6562 | 15.5993 | 15.5404 | 15.4688 | 15.4046 | 15.3414 | 15.2793 | 15.2193 | 14.9962 | 14.6698 | 14.3972 | 14.5535 | 14.5019 | 14.4483 | 14.3925 | 14.3346 | 14.2683 | 14.2072 | 14.1483 | 14.0914 | 14.0219 | 13.6083 | 13.2135 | 12.903 | 15.0801 | 15.0285 | 14.9748 | 14.918 | 14.8601 | 14.7906 | 14.7264 | 14.6643 | 14.6043 | 14.5443 | 14.2096 | 13.8148 | 13.5064
|  | LYNDHURST | EE |  |  |  |  | 15.7846 | 15.7425 | 15.6983 | 15.6509 | 15.6004 | 15.5393 | 15.4846 | 15.4298 | 15.3793 | 15.3298 | 15.1119 | 14.9593 | 14.7667 | 14.5735 | 14.5325 | 14.4904 | 14.4419 | 14.3935 | 14.3388 | 14.2893 | 14.2398 | 14.1935 | 14.1493 | 13.9072 | 13.5935 | 13.3525 | 15.1012 | 15.0591 | 15.0159 | 14.9685 | 14.9201 | 14.8612 | 14.8064 | 14.7538 | 14.7022 | 14.6538 | 14.4412 | 14.1738 | 13.9317
|  | LYNDHURST | HT |  |  |  |  | 15.7635 | 15.7119 | 15.6562 | 15.5993 | 15.5404 | 15.4688 | 15.4046 | 15.3414 | 15.2793 | 15.2193 | 14.9962 | 14.6698 | 14.3972 | 14.5535 | 14.5019 | 14.4483 | 14.3925 | 14.3346 | 14.2683 | 14.2072 | 14.1483 | 14.0914 | 14.0219 | 13.6083 | 13.2135 | 12.903 | 15.0801 | 15.0285 | 14.9748 | 14.918 | 14.8601 | 14.7906 | 14.7264 | 14.6643 | 14.6043 | 14.5443 | 14.2096 | 13.8148 | 13.5064
|  | LYNDHURST | HE |  |  |  |  | 15.8098 | 15.7793 | 15.7446 | 15.7067 | 15.6656 | 15.6141 | 15.5709 | 15.5277 | 15.4877 | 15.4519 | 15.3162 | 15.2246 | 15.1593 | 14.5988 | 14.5683 | 14.5346 | 14.4977 | 14.4577 | 14.4114 | 14.3725 | 14.3346 | 14.2977 | 14.2651 | 14.1472 | 14.0556 | 13.9556 | 15.0801 | 15.0285 | 14.9748 | 14.918 | 14.8601 | 14.7906 | 14.7264 | 14.6643 | 14.6043 | 14.5443 | 14.2096 | 13.8148 | 13.5064
|  | LYNDHURST | CF |  |  |  |  | 15.8235 | 15.8046 | 15.7846 | 15.7635 | 15.7435 | 15.7193 | 15.6941 | 15.6709 | 15.6467 | 15.6235 | 15.5183 | 15.4498 | 15.4109 | 14.6114 | 14.5935 | 14.5735 | 14.5525 | 14.5325 | 14.5114 | 14.4872 | 14.4651 | 14.4419 | 14.4209 | 14.3241 | 14.2662 | 14.2356 | 15.1391 | 15.1201 | 15.1012 | 15.0801 | 15.0601 | 15.0359 | 15.0106 | 14.9875 | 14.9633 | 14.9422 | 14.8391 | 14.7727 | 14.7348
| THURSO | LYNESS | MINIMUM HEADROOM | ND 30350 94625 | YES | YES | 0 | 0.99474 | 0.97895 | 0.96316 | 0.94947 | 0.93368 | 0.91789 | 0.90316 | 0.88842 | 0.87474 | 0.86105 | 0.80842 | 0.76421 | 0.72 | 0.98526 | 0.96947 | 0.95158 | 0.93579 | 0.91895 | 0.90105 | 0.88526 | 0.86947 | 0.85474 | 0.84 | 0.78211 | 0.73368 | 0.68421 | 0.98947 | 0.97263 | 0.95474 | 0.94 | 0.92316 | 0.90526 | 0.88947 | 0.87368 | 0.85895 | 0.84421 | 0.78737 | 0.73895 | 0.68947
|  | LYNESS | EE |  |  |  |  | 1.0021 | 0.98947 | 0.97684 | 0.96421 | 0.95158 | 0.94 | 0.92737 | 0.91684 | 0.90526 | 0.89579 | 0.84947 | 0.81789 | 0.78842 | 0.98947 | 0.98 | 0.96737 | 0.95368 | 0.94 | 0.92632 | 0.91263 | 0.90105 | 0.88842 | 0.87789 | 0.82737 | 0.79263 | 0.76 | 0.99684 | 0.98421 | 0.97053 | 0.95684 | 0.94316 | 0.93053 | 0.91684 | 0.90526 | 0.89263 | 0.88211 | 0.83263 | 0.79789 | 0.76421
|  | LYNESS | HT |  |  |  |  | 0.99474 | 0.97895 | 0.96316 | 0.94947 | 0.93368 | 0.91789 | 0.90316 | 0.88842 | 0.87474 | 0.86105 | 0.80842 | 0.76421 | 0.72 | 0.98526 | 0.96947 | 0.95158 | 0.93579 | 0.91895 | 0.90105 | 0.88526 | 0.86947 | 0.85474 | 0.84 | 0.78211 | 0.73368 | 0.68421 | 0.98947 | 0.97263 | 0.95474 | 0.94 | 0.92316 | 0.90526 | 0.88947 | 0.87368 | 0.85895 | 0.84421 | 0.78737 | 0.73895 | 0.68947
|  | LYNESS | HE |  |  |  |  | 1.0116 | 1.0032 | 0.99684 | 0.98737 | 0.98 | 0.97053 | 0.96211 | 0.95474 | 0.94737 | 0.94 | 0.91579 | 0.89895 | 0.88737 | 0.99579 | 0.98947 | 0.98421 | 0.97789 | 0.97053 | 0.96211 | 0.95263 | 0.94421 | 0.93684 | 0.92842 | 0.90211 | 0.88211 | 0.86947 | 0.98947 | 0.97263 | 0.95474 | 0.94 | 0.92316 | 0.90526 | 0.88947 | 0.87368 | 0.85895 | 0.84421 | 0.78737 | 0.73895 | 0.68947
|  | LYNESS | CF |  |  |  |  | 1.0179 | 1.0126 | 1.0074 | 1.0032 | 0.99789 | 0.99263 | 0.98947 | 0.98421 | 0.97895 | 0.97368 | 0.95263 | 0.93789 | 0.92842 | 1 | 0.99579 | 0.99368 | 0.98947 | 0.98526 | 0.98211 | 0.97895 | 0.97474 | 0.96947 | 0.96421 | 0.94 | 0.92421 | 0.91263 | 1.0137 | 1.0084 | 1.0042 | 0.99895 | 0.99368 | 0.98737 | 0.98316 | 0.97789 | 0.97263 | 0.96737 | 0.94421 | 0.92842 | 0.91684
| STORNOWAY | MAARUIG | MINIMUM HEADROOM | NB 19162 06332 | YES | YES | 0 | 0.20632 | 0.20526 | 0.20316 | 0.2 | 0.19789 | 0.18105 | 0.15684 | 0.13158 | 0.10842 | 0.068421 | -0.15368 | -0.43789 | -0.66632 | 0.19474 | 0.19368 | 0.19053 | 0.18842 | 0.18526 | 0.17053 | 0.14632 | 0.12105 | 0.097895 | 0.056842 | -0.17684 | -0.49579 | -0.72421 | 0.21053 | 0.20842 | 0.20526 | 0.20211 | 0.2 | 0.18316 | 0.16211 | 0.13895 | 0.12 | 0.070526 | -0.19053 | -0.51789 | -0.76105
|  | MAARUIG | EE |  |  |  |  | 0.20737 | 0.20632 | 0.20421 | 0.20105 | 0.19895 | 0.18105 | 0.16 | 0.13789 | 0.11895 | 0.090526 | -0.15158 | -0.43053 | -0.66632 | 0.19684 | 0.19474 | 0.19263 | 0.18947 | 0.18632 | 0.17263 | 0.15368 | 0.13684 | 0.12105 | 0.093684 | -0.15579 | -0.44211 | -0.70421 | 0.21158 | 0.21053 | 0.20737 | 0.20316 | 0.20105 | 0.18421 | 0.16211 | 0.13895 | 0.12 | 0.089474 | -0.18316 | -0.49053 | -0.76105
|  | MAARUIG | HT |  |  |  |  | 0.20632 | 0.20526 | 0.20316 | 0.2 | 0.19789 | 0.18211 | 0.16632 | 0.15053 | 0.12632 | 0.08 | -0.15368 | -0.43789 | -0.63789 | 0.19474 | 0.19368 | 0.19053 | 0.18842 | 0.18526 | 0.17158 | 0.15895 | 0.14526 | 0.12211 | 0.070526 | -0.17684 | -0.49579 | -0.72421 | 0.21053 | 0.20842 | 0.20526 | 0.20211 | 0.2 | 0.18316 | 0.16842 | 0.15158 | 0.12526 | 0.070526 | -0.19053 | -0.51789 | -0.74947
|  | MAARUIG | HE |  |  |  |  | 0.20842 | 0.20842 | 0.20632 | 0.20421 | 0.20421 | 0.18211 | 0.15684 | 0.13158 | 0.10842 | 0.068421 | -0.10105 | -0.32526 | -0.57053 | 0.19789 | 0.19789 | 0.19579 | 0.19263 | 0.19263 | 0.17053 | 0.14632 | 0.12105 | 0.097895 | 0.056842 | -0.11579 | -0.35263 | -0.61263 | 0.21053 | 0.20842 | 0.20526 | 0.20211 | 0.2 | 0.18316 | 0.16842 | 0.15158 | 0.12526 | 0.070526 | -0.19053 | -0.51789 | -0.74947
|  | MAARUIG | CF |  |  |  |  | 0.20947 | 0.20842 | 0.20842 | 0.20737 | 0.20526 | 0.19895 | 0.19368 | 0.17895 | 0.16211 | 0.14211 | 0.052632 | -0.089474 | -0.25579 | 0.19895 | 0.19789 | 0.19789 | 0.19684 | 0.19474 | 0.18947 | 0.18526 | 0.16632 | 0.14842 | 0.12421 | 0.028421 | -0.12316 | -0.30737 | 0.21263 | 0.21158 | 0.21158 | 0.21158 | 0.20947 | 0.20421 | 0.19789 | 0.18 | 0.15895 | 0.13474 | 0.033684 | -0.12526 | -0.31579
| LYNDHURST | MACALPINE ROAD | MINIMUM HEADROOM | NO 38034 33691 | NO | YES | 0.05 | 16.5521 | 16.3963 | 16.2353 | 16.0711 | 15.9068 | 15.6437 | 15.3174 | 14.9795 | 14.6332 | 14.2279 | 12.9174 | 11.9574 | 11.2153 | 16.0111 | 15.8468 | 15.6784 | 15.4058 | 15.1058 | 14.7953 | 14.4374 | 14.0721 | 13.6984 | 13.2532 | 11.8289 | 10.77 | 9.9416 | 16.0626 | 15.8984 | 15.7289 | 15.4321 | 15.1353 | 14.8237 | 14.4647 | 14.0984 | 13.7237 | 13.2784 | 11.8563 | 10.7963 | 9.9721
|  | MACALPINE ROAD | EE |  |  |  |  | 16.6121 | 16.4889 | 16.3595 | 16.2237 | 16.0816 | 15.9237 | 15.7668 | 15.53 | 15.2679 | 15.0047 | 13.7637 | 12.9511 | 12.3837 | 16.0753 | 15.9458 | 15.8111 | 15.6689 | 15.4921 | 15.2363 | 14.9889 | 14.69 | 14.4026 | 14.1205 | 12.7858 | 11.9153 | 11.2879 | 16.1268 | 15.9974 | 15.8616 | 15.7195 | 15.5174 | 15.2584 | 15.0079 | 14.7058 | 14.4174 | 14.1311 | 12.79 | 11.8995 | 11.27
|  | MACALPINE ROAD | HT |  |  |  |  | 16.5521 | 16.3963 | 16.2353 | 16.0711 | 15.9068 | 15.6437 | 15.3174 | 14.9795 | 14.6332 | 14.2279 | 12.9174 | 11.9574 | 11.2153 | 16.0111 | 15.8468 | 15.6784 | 15.4058 | 15.1058 | 14.7953 | 14.4374 | 14.0721 | 13.6984 | 13.2532 | 11.8289 | 10.77 | 9.9416 | 16.0626 | 15.8984 | 15.7289 | 15.4321 | 15.1353 | 14.8237 | 14.4647 | 14.0984 | 13.7237 | 13.2784 | 11.8563 | 10.7963 | 9.9721
|  | MACALPINE ROAD | HE |  |  |  |  | 16.6953 | 16.6111 | 16.5195 | 16.4195 | 16.3132 | 16.1847 | 16.0668 | 15.9532 | 15.8426 | 15.7416 | 14.8658 | 14.3805 | 14.0363 | 16.1647 | 16.0763 | 15.9816 | 15.8784 | 15.7689 | 15.6468 | 15.5332 | 15.4216 | 15.2016 | 14.9489 | 13.95 | 13.4289 | 13.0647 | 16.0626 | 15.8984 | 15.7289 | 15.4321 | 15.1353 | 14.8237 | 14.4647 | 14.0984 | 13.7237 | 13.2784 | 11.8563 | 10.7963 | 9.9721
|  | MACALPINE ROAD | CF |  |  |  |  | 16.7416 | 16.6921 | 16.6416 | 16.5889 | 16.5342 | 16.4742 | 16.4132 | 16.3532 | 16.2932 | 16.2353 | 15.95 | 15.5921 | 15.3332 | 16.2132 | 16.1616 | 16.1079 | 16.0532 | 15.9974 | 15.9374 | 15.8774 | 15.8174 | 15.7563 | 15.6974 | 15.1247 | 14.7258 | 14.4395 | 16.2647 | 16.2132 | 16.1595 | 16.1047 | 16.0479 | 15.9858 | 15.9226 | 15.8605 | 15.7974 | 15.7374 | 15.1416 | 14.7363 | 14.4468
| MACDUFF | MACDUFF | MINIMUM HEADROOM | NJ 70363 63908 | NO | YES | 0.05 | 21.0026 | 20.8089 | 20.4942 | 20.1005 | 19.6016 | 18.6374 | 17.8479 | 17.0437 | 16.0521 | 14.6732 | 10.6942 | 5.0058 | 3.6005 | 17.9226 | 17.4805 | 17.0468 | 16.6089 | 16.0363 | 15.0374 | 14.2605 | 13.4647 | 12.4658 | 10.9711 | 7.3595 | 2.9426 | 0.15421 | 19.41 | 19.0521 | 18.6879 | 18.3205 | 17.8279 | 16.8689 | 16.0826 | 15.2816 | 14.2595 | 12.7332 | 8.5753 | 2.8163 | 0.84474
|  | MACDUFF | EE |  |  |  |  | 21.0763 | 20.9216 | 20.7342 | 20.4574 | 20.0763 | 19.1553 | 18.2595 | 17.3774 | 16.5711 | 15.7395 | 10.6942 | 5.0058 | 16.5932 | 18.0942 | 17.7468 | 17.3984 | 17.0268 | 16.6026 | 15.6889 | 14.8489 | 14.0321 | 13.2711 | 12.4816 | 7.4595 | 2.9426 | 19.6079 | 19.5479 | 19.2668 | 18.9658 | 18.6479 | 18.2932 | 17.3805 | 16.4858 | 15.6037 | 14.7984 | 13.97 | 8.5753 | 2.8163 | 18.77
|  | MACDUFF | HT |  |  |  |  | 21.0026 | 20.8089 | 20.4942 | 20.1005 | 19.6016 | 18.6374 | 17.8479 | 17.0437 | 16.0521 | 14.6732 | 11.0584 | 6.5111 | 3.6005 | 17.9226 | 17.4805 | 17.0468 | 16.6089 | 16.0363 | 15.0374 | 14.2605 | 13.4647 | 12.4658 | 10.9711 | 7.3595 | 3.4932 | 0.15421 | 19.41 | 19.0521 | 18.6879 | 18.3205 | 17.8279 | 16.8689 | 16.0826 | 15.2816 | 14.2595 | 12.7332 | 8.8511 | 4.1732 | 0.84474
|  | MACDUFF | HE |  |  |  |  | 21.1816 | 21.0784 | 20.9605 | 20.8321 | 20.6953 | 19.8258 | 19.1332 | 18.4637 | 17.8016 | 17.1258 | 14.2942 | 10.01 | 6.1795 | 18.33 | 18.0963 | 17.8668 | 17.6121 | 17.2784 | 16.4311 | 15.7742 | 15.1447 | 14.5205 | 13.8784 | 11.25 | 7.3047 | 3.3205 | 19.41 | 19.0521 | 18.6879 | 18.3205 | 17.8279 | 16.8689 | 16.0826 | 15.2816 | 14.2595 | 12.7332 | 8.8511 | 4.1732 | 0.84474
|  | MACDUFF | CF |  |  |  |  | 21.2405 | 21.1805 | 21.1132 | 21.0458 | 20.9763 | 20.7742 | 20.5879 | 20.4026 | 20.1763 | 19.9332 | 18.2216 | 16.1016 | 13.7447 | 18.4542 | 18.3195 | 18.1889 | 18.0521 | 17.91 | 17.6563 | 17.4111 | 17.1647 | 16.9142 | 16.6584 | 14.9016 | 12.7258 | 10.0816 | 19.7647 | 19.7047 | 19.6226 | 19.5079 | 19.39 | 19.1163 | 18.8584 | 18.6016 | 18.3511 | 18.1163 | 16.4447 | 14.31 | 11.6468
| CARRADALE 1 | MACHRIE | MINIMUM HEADROOM | NR 90092 33864 | YES | YES | 0 | 2.8179 | 2.7726 | 2.7274 | 2.6758 | 2.6242 | 2.5695 | 2.5179 | 2.4674 | 2.4179 | 2.3716 | 2.1979 | 2.0821 | 1.98 | 2.6453 | 2.5937 | 2.5442 | 2.4863 | 2.4274 | 2.3663 | 2.3074 | 2.2505 | 2.1947 | 2.1421 | 1.9421 | 1.8084 | 1.6947 | 2.6789 | 2.6274 | 2.5779 | 2.52 | 2.4611 | 2.4 | 2.3411 | 2.2842 | 2.2284 | 2.1758 | 1.9758 | 1.8421 | 1.7284
|  | MACHRIE | EE |  |  |  |  | 2.8379 | 2.8032 | 2.7674 | 2.7253 | 2.6821 | 2.6379 | 2.5958 | 2.5537 | 2.5137 | 2.4758 | 2.3253 | 2.24 | 2.1705 | 2.6684 | 2.6295 | 2.5895 | 2.5421 | 2.4926 | 2.4432 | 2.3947 | 2.3474 | 2.3011 | 2.2579 | 2.0853 | 1.9874 | 1.9063 | 2.7011 | 2.6632 | 2.6232 | 2.5758 | 2.5263 | 2.4768 | 2.4284 | 2.3811 | 2.3347 | 2.2916 | 2.1189 | 2.0211 | 1.94
|  | MACHRIE | HT |  |  |  |  | 2.8179 | 2.7726 | 2.7274 | 2.6758 | 2.6242 | 2.5695 | 2.5179 | 2.4674 | 2.4179 | 2.3716 | 2.1979 | 2.0821 | 1.98 | 2.6453 | 2.5937 | 2.5442 | 2.4863 | 2.4274 | 2.3663 | 2.3074 | 2.2505 | 2.1947 | 2.1421 | 1.9421 | 1.8084 | 1.6947 | 2.6789 | 2.6274 | 2.5779 | 2.52 | 2.4611 | 2.4 | 2.3411 | 2.2842 | 2.2284 | 2.1758 | 1.9758 | 1.8421 | 1.7284
|  | MACHRIE | HE |  |  |  |  | 2.8663 | 2.8453 | 2.8221 | 2.7937 | 2.7621 | 2.7284 | 2.6968 | 2.6653 | 2.6358 | 2.6074 | 2.5105 | 2.4663 | 2.4347 | 2.7 | 2.6768 | 2.6516 | 2.6189 | 2.5832 | 2.5453 | 2.5095 | 2.4737 | 2.4389 | 2.4063 | 2.2958 | 2.2453 | 2.2074 | 2.6789 | 2.6274 | 2.5779 | 2.52 | 2.4611 | 2.4 | 2.3411 | 2.2842 | 2.2284 | 2.1758 | 1.9758 | 1.8421 | 1.7284
|  | MACHRIE | CF |  |  |  |  | 2.8811 | 2.8684 | 2.8558 | 2.84 | 2.8232 | 2.8063 | 2.7895 | 2.7716 | 2.7526 | 2.7347 | 2.6589 | 2.62 | 2.5926 | 2.7168 | 2.7032 | 2.6884 | 2.6705 | 2.6505 | 2.6316 | 2.6126 | 2.5916 | 2.5705 | 2.5495 | 2.4611 | 2.4168 | 2.3832 | 2.7242 | 2.7168 | 2.7095 | 2.7011 | 2.6842 | 2.6653 | 2.6463 | 2.6253 | 2.6042 | 2.5832 | 2.4947 | 2.4505 | 2.4168
| FORT WILLIAM | MALLAIG | MINIMUM HEADROOM | NM 67637 94811 | YES | NO | 0 | 2.1434 | 2.1066 | 2.0708 | 2.0361 | 2.0003 | 1.8887 | 1.7866 | 1.6834 | 1.6508 | 1.6203 | 1.4761 | 1.3561 | 1.2466 | 2.2497 | 2.2097 | 2.1697 | 2.1308 | 2.0918 | 1.9603 | 1.8371 | 1.7139 | 1.6782 | 1.6455 | 1.4824 | 1.3445 | 1.2224 | 2.1455 | 2.1097 | 2.075 | 2.0403 | 2.0034 | 1.8697 | 1.7455 | 1.6213 | 1.5855 | 1.5518 | 1.3887 | 1.2497 | 1.1255
|  | MALLAIG | EE |  |  |  |  | 2.1603 | 2.1318 | 2.1034 | 2.0739 | 2.0455 | 2.0171 | 1.9897 | 1.895 | 1.8003 | 1.7076 | 1.5918 | 1.5024 | 1.4213 | 2.2592 | 2.2371 | 2.2066 | 2.175 | 2.1434 | 2.1129 | 2.0834 | 1.9687 | 1.855 | 1.7434 | 1.6129 | 1.5097 | 1.4139 | 2.1613 | 2.1339 | 2.1066 | 2.0782 | 2.0497 | 2.0224 | 1.9939 | 1.8792 | 1.7645 | 1.6508 | 1.5203 | 1.4161 | 1.3192
|  | MALLAIG | HT |  |  |  |  | 2.1434 | 2.1066 | 2.0708 | 2.0361 | 2.0003 | 1.8887 | 1.7866 | 1.6834 | 1.6508 | 1.6203 | 1.4761 | 1.3561 | 1.2466 | 2.2497 | 2.2097 | 2.1697 | 2.1308 | 2.0918 | 1.9603 | 1.8371 | 1.7139 | 1.6782 | 1.6455 | 1.4824 | 1.3445 | 1.2224 | 2.1455 | 2.1097 | 2.075 | 2.0403 | 2.0034 | 1.8697 | 1.7455 | 1.6213 | 1.5855 | 1.5518 | 1.3887 | 1.2497 | 1.1255
|  | MALLAIG | HE |  |  |  |  | 2.1824 | 2.1645 | 2.1466 | 2.1276 | 2.1076 | 2.0887 | 2.0697 | 1.9971 | 1.9234 | 1.8529 | 1.7539 | 1.7171 | 1.6897 | 2.2718 | 2.2592 | 2.2466 | 2.2339 | 2.2129 | 2.1929 | 2.1718 | 2.0845 | 1.9961 | 1.9108 | 1.7971 | 1.7539 | 1.7234 | 2.1455 | 2.1097 | 2.075 | 2.0403 | 2.0034 | 1.8697 | 1.7455 | 1.6213 | 1.5855 | 1.5518 | 1.3887 | 1.2497 | 1.1255
|  | MALLAIG | CF |  |  |  |  | 2.1929 | 2.1824 | 2.1718 | 2.1592 | 2.1487 | 2.1361 | 2.1255 | 2.1139 | 2.0729 | 2.0297 | 1.9182 | 1.8845 | 1.8603 | 2.2782 | 2.2718 | 2.2645 | 2.2571 | 2.2497 | 2.2424 | 2.2308 | 2.2182 | 2.1687 | 2.1161 | 1.9855 | 1.9476 | 1.9182 | 2.1939 | 2.1834 | 2.1729 | 2.1603 | 2.1508 | 2.1382 | 2.1276 | 2.1161 | 2.0782 | 2.0276 | 1.895 | 1.8571 | 1.8276
| KEITH 1 | MARNOCH | MINIMUM HEADROOM | NJ 61955 53001 | NO | YES | 0 | 1.5011 | 1.4105 | 1.2916 | 1.1737 | 1.0568 | 0.44737 | -0.39053 | -1.2937 | -2.0789 | -2.8853 | -7.3547 | -13.0432 | -17.8526 | 3.4547 | 3.3053 | 3.1179 | 2.9147 | 2.7074 | 2.1411 | 1.4811 | 0.71474 | 0.037895 | -0.67053 | -5.6432 | -10.5716 | -15.3242 | 1.7263 | 1.6358 | 1.5189 | 1.4021 | 1.2874 | 0.71895 | 0.013684 | -0.70842 | -1.4305 | -2.1916 | -7.2379 | -14.5568 | -19.7632
|  | MARNOCH | EE |  |  |  |  | 1.5274 | 1.4516 | 1.3326 | 1.2105 | 1.0895 | 0.44737 | -0.39053 | -1.2937 | -2.0789 | -2.8853 | -6.7684 | -13.0432 | -17.8526 | 3.5105 | 3.3895 | 3.2263 | 3.0484 | 2.8663 | 2.2284 | 1.4811 | 0.71474 | 0.037895 | -0.67053 | -4.8768 | -10.5716 | -15.3242 | 1.7526 | 1.6768 | 1.5611 | 1.4411 | 1.3232 | 0.71895 | 0.013684 | -0.70842 | -1.4305 | -2.1916 | -6.8347 | -14.5568 | -19.7632
|  | MARNOCH | HT |  |  |  |  | 1.5011 | 1.4105 | 1.2916 | 1.1737 | 1.0568 | 0.50526 | -0.12526 | -0.79368 | -1.58 | -2.4032 | -5.9232 | -10.5926 | -14.5632 | 3.4547 | 3.3053 | 3.1179 | 2.9147 | 2.7074 | 2.1411 | 1.54 | 0.90316 | 0.17053 | -0.64421 | -5.6432 | -9.5358 | -13.5537 | 1.7263 | 1.6358 | 1.5189 | 1.4021 | 1.2874 | 0.76632 | 0.25158 | -0.32842 | -1.0884 | -1.9042 | -7.2379 | -12.3979 | -16.76
|  | MARNOCH | HE |  |  |  |  | 1.5747 | 1.5305 | 1.4747 | 1.4158 | 1.3547 | 0.69579 | 0.13158 | -0.53158 | -1.1947 | -1.9379 | -7.3547 | -9.3832 | -16.7874 | 3.5989 | 3.5274 | 3.4368 | 3.3274 | 3.2116 | 2.5789 | 2.02 | 1.4242 | 0.82 | -0.027368 | -5.2095 | -7.5642 | -14.1316 | 1.7263 | 1.6358 | 1.5189 | 1.4021 | 1.2874 | 0.76632 | 0.25158 | -0.32842 | -1.0884 | -1.9042 | -7.2379 | -12.3979 | -16.76
|  | MARNOCH | CF |  |  |  |  | 1.58 | 1.5347 | 1.4811 | 1.4274 | 1.3726 | 1.1011 | 0.85789 | 0.61579 | 0.40316 | 0.16 | -1.4379 | -4.9768 | -7.2211 | 3.6232 | 3.56 | 3.4884 | 3.4147 | 3.3389 | 3.0758 | 2.8316 | 2.5832 | 2.2042 | 1.7979 | -0.13684 | -3.9463 | -6.9021 | 1.8053 | 1.76 | 1.7063 | 1.6537 | 1.6 | 1.3432 | 1.1126 | 0.88421 | 0.68316 | 0.52632 | -1.16 | -5.5316 | -8.6789
| BEAULY | MARYBANK | MINIMUM HEADROOM | NH 46749 53948 | YES | YES | 0 | 4.2158 | 3.9368 | 3.6211 | 3.2442 | 2.8358 | 2.3547 | 1.9063 | 1.4358 | 0.96947 | 0.49263 | -1.6737 | -3.6716 | -5.6168 | 4.0095 | 3.7926 | 3.4737 | 3.08 | 2.6758 | 2.2147 | 1.7863 | 1.3189 | 0.85263 | 0.37263 | -1.7232 | -3.8221 | -5.7368 | 4.0242 | 3.7158 | 3.3716 | 2.9737 | 2.5589 | 2.0705 | 1.6084 | 1.1021 | 0.60105 | 0.089474 | -2.1684 | -4.4147 | -6.7611
|  | MARYBANK | EE |  |  |  |  | 4.2274 | 3.9368 | 3.6211 | 3.2442 | 2.8358 | 2.3547 | 1.9063 | 1.4358 | 0.96947 | 0.49263 | -1.6737 | -3.6716 | -5.6168 | 4.0337 | 3.7926 | 3.4737 | 3.08 | 2.6758 | 2.2147 | 1.7863 | 1.3189 | 0.85263 | 0.37263 | -1.7232 | -3.8221 | -5.7368 | 4.0463 | 3.7158 | 3.3716 | 2.9737 | 2.5589 | 2.0705 | 1.6084 | 1.1021 | 0.60105 | 0.089474 | -2.1684 | -4.4147 | -6.7611
|  | MARYBANK | HT |  |  |  |  | 4.2158 | 4.1074 | 3.9937 | 3.88 | 3.7589 | 3.5253 | 3.2674 | 3 | 2.8021 | 2.6042 | 1.4968 | -0.096842 | -1.3589 | 4.0095 | 3.9126 | 3.8084 | 3.6926 | 3.5621 | 3.3137 | 3.0642 | 2.8074 | 2.64 | 2.4716 | 1.4295 | -0.10947 | -1.3495 | 4.0242 | 3.8895 | 3.7484 | 3.6084 | 3.4663 | 3.1705 | 2.8726 | 2.5642 | 2.3589 | 2.1526 | 0.9 | -0.93474 | -2.3758
|  | MARYBANK | HE |  |  |  |  | 4.2442 | 4.1484 | 4.0505 | 3.9526 | 3.8526 | 3.6821 | 3.5147 | 3.3168 | 3.1158 | 2.8968 | 1.8274 | 0.52105 | -0.91895 | 4.0653 | 3.9926 | 3.9147 | 3.8126 | 3.7063 | 3.5547 | 3.3937 | 3.2084 | 3.0126 | 2.7958 | 1.7853 | 0.53789 | -0.78842 | 4.0242 | 3.8895 | 3.7484 | 3.6084 | 3.4663 | 3.1705 | 2.8726 | 2.5642 | 2.3589 | 2.1526 | 0.9 | -0.93474 | -2.3758
|  | MARYBANK | CF |  |  |  |  | 4.2537 | 4.2242 | 4.1937 | 4.1653 | 4.1368 | 4.0821 | 4.0337 | 3.9842 | 3.9347 | 3.8695 | 3.4368 | 2.78 | 2.0432 | 4.0811 | 4.0558 | 4.0284 | 4.0021 | 3.9737 | 3.9274 | 3.8821 | 3.8347 | 3.7421 | 3.6284 | 3.1758 | 2.5137 | 1.7326 | 4.0905 | 4.0547 | 4.0168 | 3.9811 | 3.9453 | 3.88 | 3.8211 | 3.76 | 3.6537 | 3.5284 | 3.0116 | 2.2653 | 1.42
| LUNANHEAD | MARYTON | MINIMUM HEADROOM | NO 39206 53075 | NO | YES | 0 | 15.6479 | 15.3395 | 14.9879 | 14.6184 | 14.2984 | 13.2595 | 11.9953 | 10.6153 | 9.41 | 8.2258 | -1.1237 | -11.93 | -19.7511 | 13.5526 | 13.1989 | 12.8147 | 12.4116 | 12.0674 | 11.1811 | 10.2789 | 9.1558 | 8.1674 | 7.1832 | -1.6758 | -12.1674 | -20.6811 | 14.1339 | 13.7845 | 13.3918 | 12.9792 | 12.6276 | 11.5687 | 10.3339 | 8.9403 | 7.7234 | 6.5382 | -3.5829 | -15.3397 | -24.2071
|  | MARYTON | EE |  |  |  |  | 15.7142 | 15.5026 | 15.1721 | 14.8226 | 14.5153 | 13.35 | 11.9953 | 10.6153 | 9.41 | 8.2258 | -1.1237 | -11.93 | -19.7511 | 13.6747 | 13.3853 | 13.0389 | 12.6653 | 12.3484 | 11.3853 | 10.2789 | 9.1558 | 8.1674 | 7.1832 | -1.6758 | -12.1674 | -20.6811 | 14.2487 | 13.9666 | 13.6024 | 13.2129 | 12.8803 | 11.7003 | 10.3339 | 8.9403 | 7.7234 | 6.5382 | -3.5829 | -15.3397 | -24.2071
|  | MARYTON | HT |  |  |  |  | 15.6479 | 15.3395 | 14.9879 | 14.6184 | 14.2984 | 13.2595 | 12.2311 | 11.1921 | 9.9984 | 8.8258 | 0.37421 | -9.1458 | -15.6068 | 13.5526 | 13.1989 | 12.8147 | 12.4116 | 12.0674 | 11.1811 | 10.3042 | 9.4232 | 8.4263 | 7.4663 | -1.2084 | -11.5505 | -18.6926 | 14.1339 | 13.7845 | 13.3918 | 12.9792 | 12.6276 | 11.5687 | 10.5171 | 9.4592 | 8.2476 | 7.0666 | -2.3492 | -13.2239 | -20.6261
|  | MARYTON | HE |  |  |  |  | 15.7879 | 15.7142 | 15.5205 | 15.2911 | 15.1047 | 13.9184 | 12.9111 | 11.8237 | 10.6311 | 9.0174 | 2.1111 | -6.2511 | -15.2605 | 13.84 | 13.6295 | 13.4053 | 13.1484 | 12.9453 | 11.9842 | 11.1621 | 10.24 | 9.1768 | 7.5789 | 0.89474 | -7.7105 | -16.8074 | 14.1339 | 13.7845 | 13.3918 | 12.9792 | 12.6276 | 11.5687 | 10.5171 | 9.4592 | 8.2476 | 7.0666 | -2.3492 | -13.2239 | -20.6261
|  | MARYTON | CF |  |  |  |  | 15.8289 | 15.7858 | 15.7332 | 15.6405 | 15.5374 | 15.07 | 14.6437 | 14.2205 | 13.6426 | 12.9132 | 9.4384 | 4.3279 | -1.2363 | 13.8821 | 13.8116 | 13.6842 | 13.5463 | 13.4337 | 13.0442 | 12.6874 | 12.3295 | 11.7505 | 10.9389 | 7.3821 | 2.0705 | -3.8989 | 14.4445 | 14.3771 | 14.2571 | 14.1224 | 14.0087 | 13.5339 | 13.0992 | 12.6676 | 12.0297 | 11.1813 | 7.2961 | 1.5108 | -4.8429
| STRICHEN | MAUD | MINIMUM HEADROOM | NJ 92528 47491 | NO | YES | 0 | 7.5358 | 7.4 | 7.2263 | 7.0421 | 6.8884 | 6.2779 | 5.4695 | 4.5747 | 3.7768 | 2.7989 | -2.8347 | -9.7432 | -14.6137 | 7.1147 | 6.9642 | 6.7811 | 6.5874 | 6.4284 | 5.9284 | 5.2547 | 4.5137 | 3.6432 | 2.7126 | -2.2916 | -8.8895 | -14.1337 | 7.3158 | 7.1653 | 6.9758 | 6.7758 | 6.6105 | 6 | 5.1789 | 4.2621 | 3.3747 | 2.3095 | -3.5916 | -11.0621 | -16.5653
|  | MAUD | EE |  |  |  |  | 7.5874 | 7.4958 | 7.3295 | 7.1526 | 6.9642 | 6.2779 | 5.4695 | 4.5747 | 3.7768 | 2.8705 | -2.8347 | -9.7432 | -14.6137 | 7.1705 | 7.0705 | 6.9011 | 6.7189 | 6.5263 | 5.96 | 5.2821 | 4.5137 | 3.8211 | 3.0053 | -2.2916 | -8.8895 | -14.1337 | 7.3716 | 7.2716 | 7.0916 | 6.9 | 6.6958 | 6 | 5.1789 | 4.2621 | 3.4421 | 2.4895 | -3.5916 | -11.0621 | -16.5653
|  | MAUD | HT |  |  |  |  | 7.5358 | 7.4 | 7.2263 | 7.0421 | 6.8884 | 6.2905 | 5.5505 | 4.7979 | 3.8 | 2.7989 | -2.0063 | -7.9547 | -11.9137 | 7.1147 | 6.9642 | 6.7811 | 6.5874 | 6.4284 | 5.9284 | 5.2547 | 4.5705 | 3.6432 | 2.7126 | -1.9905 | -8.3547 | -12.7611 | 7.3158 | 7.1653 | 6.9758 | 6.7758 | 6.6105 | 6.0011 | 5.2253 | 4.4347 | 3.3747 | 2.3095 | -2.9084 | -9.6316 | -14.1716
|  | MAUD | HE |  |  |  |  | 7.6568 | 7.5979 | 7.5063 | 7.4042 | 7.2916 | 6.5411 | 5.9368 | 5.1821 | 4.4432 | 3.4284 | -0.92105 | -6.1168 | -11.7768 | 7.2453 | 7.1811 | 7.0832 | 6.9726 | 6.8505 | 6.2253 | 5.7168 | 5.0389 | 4.3779 | 3.4053 | -0.70316 | -5.9011 | -11.5621 | 7.3158 | 7.1653 | 6.9758 | 6.7758 | 6.6105 | 6.0011 | 5.2253 | 4.4347 | 3.3747 | 2.3095 | -2.9084 | -9.6316 | -14.1716
|  | MAUD | CF |  |  |  |  | 7.6937 | 7.6579 | 7.6137 | 7.56 | 7.5011 | 7.2158 | 6.9484 | 6.6979 | 6.2695 | 5.8053 | 3.6116 | 0.33789 | -3.1674 | 7.2863 | 7.2474 | 7.2021 | 7.1421 | 7.08 | 6.8389 | 6.6095 | 6.3937 | 5.9674 | 5.4779 | 3.3032 | 0.011579 | -3.6968 | 7.4874 | 7.4484 | 7.4011 | 7.34 | 7.2758 | 6.9832 | 6.7084 | 6.4526 | 5.9821 | 5.46 | 3.0632 | -0.54211 | -4.4874
| DOUNREAY | MELVICH | MINIMUM HEADROOM | NC 88547 64274 | YES | YES | 0.06 | 0.98947 | 0.93579 | 0.87895 | 0.68737 | 0.63158 | 0.35368 | -0.21474 | -0.83789 | -1.4347 | -2.3221 | -7.4221 | -13.5189 | -18.1916 | 0.85895 | 0.81684 | 0.76842 | 0.61368 | 0.56421 | 0.33368 | -0.18421 | -0.75895 | -1.3011 | -2.1789 | -6.9179 | -12.9874 | -18.1789 | 0.88 | 0.82632 | 0.76737 | 0.57263 | 0.51579 | 0.23263 | -0.33053 | -0.90842 | -1.4074 | -2.1168 | -8.0842 | -14.7621 | -20.1684
|  | MELVICH | EE |  |  |  |  | 0.99684 | 0.93579 | 0.87895 | 0.68737 | 0.63158 | 0.35368 | -0.20105 | -0.77158 | -1.2621 | -1.9421 | -7.4221 | -13.5189 | -18.1916 | 0.86737 | 0.81684 | 0.76842 | 0.61368 | 0.56421 | 0.33368 | -0.12316 | -0.59158 | -0.99684 | -1.5979 | -6.9179 | -12.9874 | -18.1789 | 0.88842 | 0.82632 | 0.76737 | 0.57263 | 0.51579 | 0.23263 | -0.33053 | -0.90842 | -1.4074 | -2.1168 | -8.0842 | -14.7621 | -20.1684
|  | MELVICH | HT |  |  |  |  | 0.98947 | 0.96421 | 0.91579 | 0.86737 | 0.82 | 0.43789 | 0.41158 | 0.0084211 | -0.60947 | -1.6726 | -6.6021 | -12.2695 | -16.1821 | 0.85895 | 0.83263 | 0.78737 | 0.74421 | 0.7 | 0.39474 | 0.36842 | 0.031579 | -0.51368 | -1.5611 | -6.6821 | -12.9726 | -17.4074 | 0.88 | 0.85368 | 0.80421 | 0.75263 | 0.70421 | 0.31684 | 0.29053 | -0.12105 | -0.76421 | -1.9326 | -7.4232 | -13.9589 | -18.48
|  | MELVICH | HE |  |  |  |  | 1.0053 | 0.99789 | 0.98211 | 0.96316 | 0.94211 | 0.39474 | -0.21474 | -0.83789 | -1.4347 | -2.3221 | -6.0874 | -10.8105 | -15.9779 | 0.87579 | 0.86842 | 0.85474 | 0.83579 | 0.81684 | 0.36421 | -0.18421 | -0.75895 | -1.3011 | -2.1789 | -5.8716 | -10.7705 | -16.1316 | 0.88 | 0.85368 | 0.80421 | 0.75263 | 0.70421 | 0.31684 | 0.29053 | -0.12105 | -0.76421 | -1.9326 | -7.4232 | -13.9589 | -18.48
|  | MELVICH | CF |  |  |  |  | 1.0105 | 1.0063 | 0.99684 | 0.98632 | 0.97684 | 0.79263 | 0.62947 | 0.33368 | -0.048421 | -0.48 | -2.4221 | -5.3979 | -8.7263 | 0.88105 | 0.87684 | 0.86842 | 0.85895 | 0.85158 | 0.70947 | 0.57474 | 0.3 | -0.095789 | -0.57158 | -2.5726 | -5.6863 | -9.3516 | 0.90211 | 0.89789 | 0.88842 | 0.87789 | 0.86737 | 0.68 | 0.51474 | 0.19789 | -0.22842 | -0.71789 | -2.8695 | -6.2105 | -10.0432
| CHARLESTON | MENZIESHILL | MINIMUM HEADROOM | NO 35918 31022 | NO | YES | 0.22 | 21.9458 | 21.7868 | 21.6226 | 21.4553 | 21.2837 | 21.0826 | 20.8868 | 20.6953 | 20.5068 | 20.3258 | 19.4132 | 18.3311 | 17.4784 | 19.9084 | 19.7495 | 19.5863 | 19.4189 | 19.2484 | 19.0547 | 18.8663 | 18.6832 | 18.3316 | 17.9989 | 16.4379 | 15.2547 | 14.3116 | 21.5376 | 21.3787 | 21.2145 | 20.9229 | 20.6261 | 20.3082 | 19.9724 | 19.6324 | 19.2818 | 18.9534 | 17.4261 | 16.2492 | 15.3176
|  | MENZIESHILL | EE |  |  |  |  | 22.0142 | 21.8911 | 21.7616 | 21.6247 | 21.4837 | 21.3184 | 21.1574 | 20.9974 | 20.8458 | 20.7026 | 20.1005 | 19.3595 | 18.7247 | 19.9768 | 19.8537 | 19.7242 | 19.5895 | 19.4484 | 19.2937 | 19.1442 | 18.9968 | 18.8568 | 18.6747 | 17.4063 | 16.4358 | 15.7411 | 21.6061 | 21.4829 | 21.3534 | 21.2166 | 20.9892 | 20.7155 | 20.4534 | 20.1576 | 19.8787 | 19.605 | 18.3492 | 17.3682 | 16.6734
|  | MENZIESHILL | HT |  |  |  |  | 21.9458 | 21.7868 | 21.6226 | 21.4553 | 21.2837 | 21.0826 | 20.8868 | 20.6953 | 20.5068 | 20.3258 | 19.4132 | 18.3311 | 17.4784 | 19.9084 | 19.7495 | 19.5863 | 19.4189 | 19.2484 | 19.0547 | 18.8663 | 18.6832 | 18.3316 | 17.9989 | 16.4379 | 15.2547 | 14.3116 | 21.5376 | 21.3787 | 21.2145 | 20.9229 | 20.6261 | 20.3082 | 19.9724 | 19.6324 | 19.2818 | 18.9534 | 17.4261 | 16.2492 | 15.3176
|  | MENZIESHILL | HE |  |  |  |  | 22.09 | 22.0026 | 21.9058 | 21.8016 | 21.6911 | 21.5532 | 21.4279 | 21.3037 | 21.1868 | 21.0784 | 20.6732 | 20.4374 | 20.2711 | 20.0526 | 19.9653 | 19.8684 | 19.7653 | 19.6547 | 19.5263 | 19.4105 | 19.2958 | 19.1874 | 19.0884 | 18.5842 | 17.9979 | 17.5884 | 21.5376 | 21.3787 | 21.2145 | 20.9229 | 20.6261 | 20.3082 | 19.9724 | 19.6324 | 19.2818 | 18.9534 | 17.4261 | 16.2492 | 15.3176
|  | MENZIESHILL | CF |  |  |  |  | 22.13 | 22.0753 | 22.0184 | 21.9584 | 21.8984 | 21.83 | 21.7616 | 21.6932 | 21.6258 | 21.5595 | 21.2637 | 21.0868 | 20.9889 | 20.0926 | 20.0379 | 19.9811 | 19.9221 | 19.8621 | 19.7968 | 19.7326 | 19.6663 | 19.6021 | 19.5379 | 19.26 | 19.1053 | 18.9389 | 21.7218 | 21.6671 | 21.6103 | 21.5503 | 21.4903 | 21.4229 | 21.3545 | 21.2861 | 21.2197 | 21.1534 | 20.6282 | 20.1776 | 19.8618
| KINTORE | METHLICK | MINIMUM HEADROOM | NJ 85339 36835 | NO | YES | 0.11 | 3.1732 | 3.1321 | 3.0732 | 3.0142 | 2.9553 | 2.6026 | 2.1511 | 1.6447 | 1.1721 | -1.13 | -4.4311 | -7.5416 | -9.4374 | 2.9058 | 2.8237 | 2.7279 | 2.6332 | 2.5384 | 2.2153 | 1.8332 | 1.3826 | 0.99 | -0.87421 | -3.73 | -6.6216 | -8.5679 | 2.9774 | 2.9047 | 2.8132 | 2.7216 | 2.63 | 2.2374 | 1.7047 | 1.1574 | 0.68263 | -0.18579 | -4.5826 | -8.0489 | -9.9268
|  | METHLICK | EE |  |  |  |  | 3.19 | 3.1584 | 3.0995 | 3.0395 | 2.9784 | 2.6026 | 2.1511 | 1.6447 | 1.1721 | 1.0995 | -4.0732 | -7.5416 | -9.4342 | 2.9426 | 2.8816 | 2.7953 | 2.7079 | 2.6205 | 2.2574 | 1.8332 | 1.3826 | 0.99 | 0.90895 | -3.4763 | -6.6216 | -8.5679 | 3.0089 | 2.9553 | 2.8689 | 2.7805 | 2.6921 | 2.2374 | 1.7047 | 1.1574 | 0.68263 | 0.61211 | -4.5826 | -8.0489 | -9.9268
|  | METHLICK | HT |  |  |  |  | 3.1732 | 3.1321 | 3.0732 | 3.0142 | 2.9553 | 2.6342 | 2.3132 | 1.9111 | 1.4089 | 1.3237 | -3.21 | -5.5468 | -6.9995 | 2.9058 | 2.8237 | 2.7279 | 2.6332 | 2.5384 | 2.2153 | 1.8805 | 1.5437 | 1.11 | 1.0153 | -2.9205 | -5.2995 | -6.8311 | 2.9774 | 2.9047 | 2.8132 | 2.7216 | 2.63 | 2.2374 | 1.8342 | 1.4279 | 0.92474 | 0.83947 | -3.7047 | -6.0058 | -7.3858
|  | METHLICK | HE |  |  |  |  | 3.2142 | 3.1932 | 3.1658 | 3.1384 | 3.1068 | 2.7132 | 2.3784 | 2.0437 | 1.6489 | -1.13 | -4.4311 | -6.8405 | -9.4374 | 2.9921 | 2.9553 | 2.9111 | 2.8647 | 2.8142 | 2.4468 | 2.1342 | 1.7605 | 1.3953 | -0.87421 | -3.73 | -5.9942 | -8.4405 | 2.9774 | 2.9047 | 2.8132 | 2.7216 | 2.63 | 2.2374 | 1.8342 | 1.4279 | 0.92474 | 0.83947 | -3.7047 | -6.0058 | -7.3858
|  | METHLICK | CF |  |  |  |  | 3.2268 | 3.2153 | 3.1995 | 3.1837 | 3.1689 | 3.0195 | 2.8879 | 2.7584 | 2.6447 | 0.31105 | -0.73 | -2.2184 | -3.6226 | 3.0163 | 2.9942 | 2.9689 | 2.9426 | 2.9153 | 2.77 | 2.6395 | 2.5111 | 2.3374 | 0.34474 | -0.62789 | -2.0405 | -3.4532 | 3.0753 | 3.0553 | 3.0311 | 3.0058 | 2.9805 | 2.7984 | 2.6363 | 2.4763 | 2.2911 | -0.18579 | -1.2247 | -2.71 | -4.1047
| SHETLAND | MID YELL | MINIMUM HEADROOM | HU4817291442 | YES | YES | 0 | 1.2179 | 1.1905 | 1.1632 | 1.1358 | 1.1084 | 1.0821 | 1.0558 | 1.0305 | 1.0053 | 0.98211 | 0.89053 | 0.81684 | 0.75263 | 1.0726 | 1.0432 | 1.0126 | 0.98316 | 0.95474 | 0.92632 | 0.89895 | 0.87158 | 0.84526 | 0.82 | 0.72105 | 0.64 | 0.56842 | 1.1453 | 1.1168 | 1.0863 | 1.0579 | 1.0295 | 1.0011 | 0.97368 | 0.94737 | 0.92105 | 0.89579 | 0.79789 | 0.71789 | 0.64737
|  | MID YELL | EE |  |  |  |  | 1.2295 | 1.2084 | 1.1853 | 1.1642 | 1.1421 | 1.12 | 1.1 | 1.0789 | 1.06 | 1.0421 | 0.96316 | 0.90737 | 0.86211 | 1.0853 | 1.0621 | 1.0379 | 1.0147 | 0.99158 | 0.96737 | 0.94737 | 0.92421 | 0.90421 | 0.88526 | 0.8 | 0.73895 | 0.68842 | 1.1579 | 1.1358 | 1.1116 | 1.0895 | 1.0653 | 1.0421 | 1.0211 | 0.99895 | 0.97895 | 0.96105 | 0.87579 | 0.81579 | 0.76632
|  | MID YELL | HT |  |  |  |  | 1.2179 | 1.1905 | 1.1632 | 1.1358 | 1.1084 | 1.0821 | 1.0558 | 1.0305 | 1.0053 | 0.98211 | 0.89053 | 0.81684 | 0.75263 | 1.0726 | 1.0432 | 1.0126 | 0.98316 | 0.95474 | 0.92632 | 0.89895 | 0.87158 | 0.84526 | 0.82 | 0.72105 | 0.64 | 0.56842 | 1.1453 | 1.1168 | 1.0863 | 1.0579 | 1.0295 | 1.0011 | 0.97368 | 0.94737 | 0.92105 | 0.89579 | 0.79789 | 0.71789 | 0.64737
|  | MID YELL | HE |  |  |  |  | 1.2474 | 1.2347 | 1.2189 | 1.2053 | 1.1905 | 1.1747 | 1.1621 | 1.1463 | 1.1347 | 1.1232 | 1.0768 | 1.0495 | 1.0284 | 1.1042 | 1.0905 | 1.0747 | 1.06 | 1.0442 | 1.0274 | 1.0137 | 0.99789 | 0.98526 | 0.97263 | 0.92421 | 0.89368 | 0.87053 | 1.1453 | 1.1168 | 1.0863 | 1.0579 | 1.0295 | 1.0011 | 0.97368 | 0.94737 | 0.92105 | 0.89579 | 0.79789 | 0.71789 | 0.64737
|  | MID YELL | CF |  |  |  |  | 1.2558 | 1.2474 | 1.2389 | 1.2305 | 1.2211 | 1.2137 | 1.2053 | 1.1958 | 1.1874 | 1.1789 | 1.1389 | 1.1147 | 1.0947 | 1.1137 | 1.1042 | 1.0958 | 1.0863 | 1.0768 | 1.0684 | 1.0589 | 1.0495 | 1.04 | 1.0305 | 0.98842 | 0.96105 | 0.93895 | 1.1821 | 1.1768 | 1.1684 | 1.16 | 1.1495 | 1.1411 | 1.1326 | 1.1232 | 1.1126 | 1.1042 | 1.0621 | 1.0347 | 1.0137
| KINTORE | MIDMAR | MINIMUM HEADROOM | NJ 68253 06875 | YES | YES | 0 | 4.9505 | 4.3495 | 4.1832 | 4.0032 | 6.6084 | 6.4568 | 5.7537 | 5.0147 | 4.3789 | 3.7295 | -2.1221 | -9.0126 | -14.2305 | 4.8737 | 4.3579 | 4.1768 | 3.9789 | 6.1726 | 6.0105 | 5.4663 | 4.8537 | 4.3253 | 3.6463 | -1.9074 | -8.7905 | -14.3021 | 4.8474 | 4.2295 | 4.0474 | 3.8484 | 6.2411 | 6.0768 | 5.3737 | 4.6284 | 3.9874 | 3.3337 | -3.0316 | -10.5411 | -16.4842
|  | MIDMAR | EE |  |  |  |  | 4.9958 | 4.4337 | 4.2842 | 4.1221 | 6.7042 | 6.5189 | 5.7537 | 5.0147 | 4.3789 | 3.7295 | -2.1221 | -9.0126 | -14.2305 | 4.9242 | 4.4516 | 4.2989 | 4.1284 | 6.2958 | 6.1116 | 5.4663 | 4.8537 | 4.3253 | 3.7863 | -1.88 | -8.6326 | -14.3021 | 4.8958 | 4.3232 | 4.1621 | 3.9863 | 6.3495 | 6.1516 | 5.3737 | 4.6284 | 3.9874 | 3.3337 | -3.0316 | -10.5411 | -16.4842
|  | MIDMAR | HT |  |  |  |  | 4.9505 | 4.3495 | 4.1832 | 4.0032 | 6.6084 | 6.4568 | 5.9789 | 5.4421 | 4.8105 | 3.9337 | -1.6516 | -7.9684 | -12.2632 | 4.8737 | 4.3579 | 4.1768 | 3.9789 | 6.1726 | 6.0105 | 5.6074 | 5.1547 | 4.6221 | 3.7989 | -1.9074 | -8.7905 | -13.6253 | 4.8474 | 4.2295 | 4.0474 | 3.8484 | 6.2411 | 6.0768 | 5.5916 | 5.0463 | 4.4074 | 3.4779 | -2.7284 | -9.9147 | -14.8621
|  | MIDMAR | HE |  |  |  |  | 5.0547 | 4.9811 | 4.8926 | 4.7832 | 7.4095 | 6.7421 | 6.1768 | 5.5116 | 4.8189 | 3.8347 | -0.45053 | -5.76 | -11.5358 | 4.9916 | 4.9042 | 4.8021 | 4.6768 | 6.8789 | 6.3389 | 5.8632 | 5.2632 | 4.6295 | 3.6463 | -0.50316 | -5.9137 | -11.8137 | 4.8474 | 4.2295 | 4.0474 | 3.8484 | 6.2411 | 6.0768 | 5.5916 | 5.0463 | 4.4074 | 3.4779 | -2.7284 | -9.9147 | -14.8621
|  | MIDMAR | CF |  |  |  |  | 5.0874 | 5.0484 | 5.0116 | 4.9611 | 7.6663 | 7.3937 | 7.16 | 6.9242 | 6.5042 | 6.0316 | 3.8137 | 0.46526 | -3.2326 | 5.0305 | 4.9832 | 4.9432 | 4.8853 | 7.1832 | 6.9547 | 6.7547 | 6.5495 | 6.1074 | 5.5842 | 3.3379 | -0.10211 | -4.0916 | 4.9874 | 4.9474 | 4.9126 | 4.8558 | 7.3558 | 7.0758 | 6.8358 | 6.5926 | 6.1274 | 5.5789 | 3.1326 | -0.58632 | -4.7789
| BRIDGE OF DUN | MILL RD | MINIMUM HEADROOM | NO 71317 57683 | NO | YES | 0 | 14.4495 | 14.3495 | 14.24 | 14.0368 | 13.8189 | 13.5011 | 13.1853 | 12.8747 | 12.5453 | 12.2179 | 10.8853 | 9.7989 | 9.0568 | 12.96 | 12.8305 | 12.6358 | 12.3989 | 12.1632 | 11.8484 | 11.5379 | 11.2326 | 10.9116 | 10.5958 | 9.2842 | 8.2274 | 7.3811 | 13.442 | 13.3483 | 13.2451 | 13.1157 | 12.8767 | 12.5399 | 12.2051 | 11.8746 | 11.5272 | 11.1809 | 9.7536 | 8.6178 | 7.7304
|  | MILL RD | EE |  |  |  |  | 14.4926 | 14.4137 | 14.3232 | 14.2295 | 14.0895 | 13.7947 | 13.4789 | 13.1621 | 12.8726 | 12.5832 | 11.1421 | 9.7989 | 9.0568 | 13.0032 | 12.9242 | 12.8042 | 12.6505 | 12.4642 | 12.1832 | 11.8863 | 11.5895 | 11.3147 | 11.0411 | 9.6968 | 8.46 | 7.7084 | 13.4809 | 13.4072 | 13.322 | 13.2336 | 13.1409 | 12.8736 | 12.5451 | 12.2136 | 11.9093 | 11.6062 | 10.0999 | 8.6925 | 7.8778
|  | MILL RD | HT |  |  |  |  | 14.4495 | 14.3495 | 14.24 | 14.0368 | 13.8189 | 13.5011 | 13.1853 | 12.8747 | 12.5453 | 12.2179 | 10.8853 | 9.8484 | 9.0589 | 12.96 | 12.8305 | 12.6358 | 12.3989 | 12.1632 | 11.8484 | 11.5379 | 11.2326 | 10.9116 | 10.5958 | 9.2842 | 8.2274 | 7.3811 | 13.442 | 13.3483 | 13.2451 | 13.1157 | 12.8767 | 12.5399 | 12.2051 | 11.8746 | 11.5272 | 11.1809 | 9.7536 | 8.6178 | 7.7304
|  | MILL RD | HE |  |  |  |  | 14.5379 | 14.4811 | 14.4168 | 14.3484 | 14.2747 | 14.0832 | 13.9158 | 13.7389 | 13.5189 | 13.3074 | 12.3747 | 11.5779 | 10.7958 | 13.0495 | 12.9926 | 12.9284 | 12.8589 | 12.7874 | 12.5863 | 12.4011 | 12.2 | 11.9958 | 11.8021 | 10.9453 | 10.2179 | 9.5137 | 13.442 | 13.3483 | 13.2451 | 13.1157 | 12.8767 | 12.5399 | 12.2051 | 11.8746 | 11.5272 | 11.1809 | 9.7536 | 8.6178 | 7.7304
|  | MILL RD | CF |  |  |  |  | 14.56 | 14.5242 | 14.4842 | 14.4432 | 14.4011 | 14.3158 | 14.2347 | 14.1547 | 14.0811 | 14.0147 | 13.5253 | 12.98 | 12.5684 | 13.0716 | 13.0358 | 12.9958 | 12.9547 | 12.9126 | 12.8495 | 12.7758 | 12.6747 | 12.5768 | 12.4884 | 11.9758 | 11.4653 | 11.0716 | 13.5451 | 13.5093 | 13.4704 | 13.4314 | 13.3914 | 13.3104 | 13.2336 | 13.1578 | 13.0862 | 13.0241 | 12.6178 | 12.043 | 11.602
| ABERNETHY | MILNATHORT | MINIMUM HEADROOM | NO 11900 05074 | NO | YES | 0.08 | 17.3216 | 16.9016 | 39.9337 | 39.4442 | 38.9832 | 37.6253 | 36.3411 | 34.7705 | 33.3453 | 31.8884 | 20.5105 | 6.5516 | -3.6095 | 15.0989 | 14.5379 | 36.8705 | 36.2589 | 35.7474 | 34.5895 | 33.48 | 32.3589 | 31.0874 | 29.9432 | 19.0379 | 5.3621 | -5.2347 | 16.0024 | 15.4518 | 38.4084 | 37.7947 | 37.2768 | 35.8874 | 34.5737 | 33.0305 | 31.5726 | 30.0863 | 18.1 | 2.9337 | -8.5926
|  | MILNATHORT | EE |  |  |  |  | 17.4816 | 17.1574 | 40.2789 | 39.8579 | 39.4789 | 38.0326 | 36.4011 | 34.7705 | 33.3453 | 31.8884 | 20.5105 | 6.5516 | -3.6095 | 15.3032 | 14.8684 | 37.3316 | 36.8147 | 36.3705 | 35.1442 | 33.7579 | 32.4 | 31.1905 | 29.9432 | 19.3916 | 5.7916 | -5.2347 | 16.2055 | 15.7771 | 38.8537 | 38.3274 | 37.8705 | 36.3684 | 34.6895 | 33.0305 | 31.5726 | 30.0863 | 18.1 | 2.9337 | -8.5926
|  | MILNATHORT | HT |  |  |  |  | 17.3216 | 16.9016 | 39.9337 | 39.4442 | 38.9832 | 37.6253 | 36.3411 | 35.0505 | 33.5674 | 32.3474 | 21.2463 | 8.8011 | 0.42632 | 15.0989 | 14.5379 | 36.8705 | 36.2589 | 35.7474 | 34.5895 | 33.48 | 32.3589 | 31.0874 | 30.2379 | 19.0379 | 5.3621 | -4.1947 | 16.0024 | 15.4518 | 38.4084 | 37.7947 | 37.2768 | 35.8874 | 34.5737 | 33.2526 | 31.7368 | 30.7 | 18.5179 | 4.3284 | -5.4663
|  | MILNATHORT | HE |  |  |  |  | 17.6816 | 17.4542 | 40.7158 | 40.44 | 40.1979 | 38.7674 | 37.5621 | 36.3768 | 35.0221 | 32.9811 | 23.8789 | 13.2989 | 1.8453 | 15.5558 | 15.2495 | 37.8526 | 37.4884 | 37.1842 | 36.0084 | 34.9916 | 34.0021 | 32.7284 | 30.6905 | 21.7674 | 11.0674 | -0.63263 | 16.0024 | 15.4518 | 38.4084 | 37.7947 | 37.2768 | 35.8874 | 34.5737 | 33.2526 | 31.7368 | 30.7 | 18.5179 | 4.3284 | -5.4663
|  | MILNATHORT | CF |  |  |  |  | 17.7942 | 17.6742 | 41.0789 | 40.9368 | 40.8053 | 40.2358 | 39.72 | 39.2074 | 38.6442 | 37.8137 | 33.2737 | 26.6032 | 19.4021 | 15.7011 | 15.5411 | 38.3516 | 38.1705 | 38.0021 | 37.5116 | 37.0505 | 36.5895 | 35.9979 | 34.9474 | 30.3747 | 23.52 | 15.6874 | 16.6045 | 16.4445 | 39.8768 | 39.6926 | 39.5253 | 38.9326 | 38.3853 | 37.84 | 37.1747 | 36.0695 | 31.0958 | 23.7189 | 15.5095
| MILTON OF CRAIGIE | MILTON OF CRAIGIE | MINIMUM HEADROOM | NO 43137 31857 | NO | YES | 0.245 | 9.3997 | 9.3039 | 9.2039 | 9.1039 | 9.0008 | 9.3103 | 9.2661 | 9.2218 | 9.1776 | 9.1355 | 15.3534 | 14.8039 | 14.2492 | 7.8792 | 7.7834 | 7.6845 | 7.5645 | 7.3718 | 7.7918 | 7.7508 | 7.7076 | 7.6666 | 7.6255 | 13.4561 | 12.7676 | 12.1529 | 8.4942 | 8.3984 | 8.2984 | 8.1984 | 8.0953 | 8.4047 | 8.3605 | 8.3163 | 8.2732 | 8.23 | 13.6268 | 12.8942 | 12.2911
|  | MILTON OF CRAIGIE | EE |  |  |  |  | 9.4387 | 9.365 | 9.2861 | 9.2029 | 9.1166 | 16.3429 | 16.2429 | 16.1439 | 16.0513 | 15.9618 | 15.5745 | 15.3187 | 15.0155 | 7.9182 | 7.8445 | 7.7666 | 7.6834 | 7.5645 | 14.7476 | 14.6171 | 14.5003 | 14.3897 | 14.2866 | 13.8055 | 13.4613 | 13.0329 | 8.5332 | 8.4595 | 8.3805 | 8.2974 | 8.2111 | 15.4374 | 15.3384 | 15.2395 | 15.1205 | 14.9679 | 14.1805 | 13.5658 | 13.1279
|  | MILTON OF CRAIGIE | HT |  |  |  |  | 9.3997 | 9.3039 | 9.2039 | 9.1039 | 9.0008 | 16.2039 | 16.0839 | 15.9682 | 15.8524 | 15.7397 | 15.3534 | 14.8039 | 14.2492 | 7.8792 | 7.7834 | 7.6845 | 7.5645 | 7.3718 | 14.5561 | 14.4171 | 14.2792 | 14.1455 | 14.0139 | 13.4561 | 12.7676 | 12.1529 | 8.4942 | 8.3984 | 8.2984 | 8.1984 | 8.0953 | 15.2984 | 15.1795 | 14.9974 | 14.8068 | 14.6163 | 13.6268 | 12.8942 | 12.2911
|  | MILTON OF CRAIGIE | HE |  |  |  |  | 9.4818 | 9.4261 | 9.3661 | 9.3008 | 9.2303 | 16.4703 | 16.3913 | 16.3145 | 16.2408 | 16.1734 | 15.9271 | 15.7776 | 15.6724 | 7.9613 | 7.9055 | 7.8455 | 7.7803 | 7.7108 | 14.9276 | 14.8403 | 14.7539 | 14.6718 | 14.5939 | 14.2761 | 14.0803 | 13.9497 | 8.4942 | 8.3984 | 8.2984 | 8.1984 | 8.0953 | 15.2984 | 15.1795 | 14.9974 | 14.8068 | 14.6163 | 13.6268 | 12.8942 | 12.2911
|  | MILTON OF CRAIGIE | CF |  |  |  |  | 9.505 | 9.4692 | 9.4324 | 9.3945 | 9.3545 | 9.3103 | 9.2661 | 9.2218 | 9.1776 | 9.1355 | 16.2703 | 16.1566 | 16.0945 | 7.9845 | 7.9487 | 7.9118 | 7.8739 | 7.835 | 7.7918 | 7.7508 | 7.7076 | 7.6666 | 7.6255 | 14.7339 | 14.5792 | 14.4813 | 8.5995 | 8.5637 | 8.5268 | 8.4889 | 8.4489 | 8.4047 | 8.3605 | 8.3163 | 8.2732 | 8.23 | 15.3668 | 15.2532 | 15.1921
| STRICHEN | MINTLAW | MINIMUM HEADROOM | NK 00897 48662 | NO | YES | 0.336 | 12.4056 | 12.0614 | 11.7382 | 11.3687 | 10.9645 | 10.3435 | 9.6887 | 9.0277 | 8.2245 | 7.4856 | 1.7645 | -1.3386 | -2.3039 | 12.2851 | 11.8808 | 11.5103 | 11.0819 | 10.6103 | 9.9777 | 9.2977 | 8.6093 | 7.7682 | 7.0051 | 1.9619 | -0.94021 | -1.8307 | 11.7874 | 11.4043 | 11.0464 | 10.6348 | 10.159 | 9.4664 | 8.7264 | 7.9779 | 7.0632 | 6.2264 | 0.19795 | -3.1052 | -4.1189
|  | MINTLAW | EE |  |  |  |  | 12.494 | 12.1951 | 11.9056 | 11.5729 | 11.2045 | 10.574 | 9.8898 | 9.1929 | 8.5382 | 7.8087 | 1.7645 | -1.3386 | -2.3039 | 12.3851 | 12.0303 | 11.7019 | 11.3187 | 10.8914 | 10.2661 | 9.5977 | 8.9198 | 8.2661 | 7.5208 | 1.9619 | -0.94021 | -1.8307 | 11.8548 | 11.5485 | 11.2274 | 10.8579 | 10.4337 | 9.7327 | 8.9769 | 8.2064 | 7.4758 | 6.6506 | 0.19795 | -3.1052 | -4.1189
|  | MINTLAW | HT |  |  |  |  | 12.4056 | 12.0614 | 11.7382 | 11.3687 | 10.9645 | 10.3435 | 9.6887 | 9.0277 | 8.2245 | 7.4856 | 2.1329 | 0.0013684 | -1.4513 | 12.2851 | 11.8808 | 11.5103 | 11.0819 | 10.6103 | 9.9777 | 9.2977 | 8.6093 | 7.7682 | 7.0051 | 2.0629 | -0.14126 | -1.7118 | 11.7874 | 11.4043 | 11.0464 | 10.6348 | 10.159 | 9.4664 | 8.7264 | 7.9779 | 7.0632 | 6.2264 | 0.49584 | -1.8694 | -3.4999
|  | MINTLAW | HE |  |  |  |  | 12.5887 | 12.374 | 12.1561 | 11.8919 | 11.5845 | 10.974 | 10.4161 | 9.8266 | 9.2182 | 8.5708 | 4.4866 | 2.274 | 0.67189 | 12.4872 | 12.2314 | 11.9756 | 11.6619 | 11.2966 | 10.7029 | 10.1461 | 9.5461 | 8.9219 | 8.2472 | 4.3008 | 2.164 | 0.79137 | 11.7874 | 11.4043 | 11.0464 | 10.6348 | 10.159 | 9.4664 | 8.7264 | 7.9779 | 7.0632 | 6.2264 | 0.49584 | -1.8694 | -3.4999
|  | MINTLAW | CF |  |  |  |  | 12.6329 | 12.5793 | 12.4677 | 12.3435 | 12.2045 | 11.9614 | 11.7161 | 11.4603 | 11.2087 | 10.9508 | 9.1361 | 7.7898 | 6.6024 | 12.5345 | 12.4745 | 12.344 | 12.1977 | 12.0324 | 11.7945 | 11.5472 | 11.2861 | 11.0187 | 10.7314 | 8.7145 | 7.364 | 6.1008 | 11.9516 | 11.9211 | 11.8474 | 11.7074 | 11.5506 | 11.2853 | 11.0169 | 10.7358 | 10.4558 | 10.1674 | 8.0306 | 6.5106 | 5.1337
| BRIDGE OF DUN | MONTROSE NORTH | MINIMUM HEADROOM | NO 71226 59070 | NO | YES | 0.051 | 16.2201 | 15.9632 | 15.5622 | 15.1411 | 38.2669 | 37.8637 | 37.3522 | 36.9227 | 36.3774 | 35.7753 | 35.0132 | 34.3164 | 34.0216 | 15.2848 | 14.9385 | 14.3648 | 13.7501 | 35.9764 | 35.4079 | 34.8448 | 34.3764 | 33.6953 | 33.0153 | 32.3595 | 31.7122 | 31.4016 | 15.6503 | 15.4261 | 15.0935 | 14.4103 | 37.2606 | 36.6848 | 36.1122 | 35.6353 | 35.049 | 34.4048 | 33.5206 | 32.7943 | 32.4753
|  | MONTROSE NORTH | EE |  |  |  |  | 16.2906 | 16.099 | 15.7453 | 15.3706 | 38.5248 | 38.1395 | 37.5827 | 36.9985 | 36.4269 | 35.8585 | 35.0132 | 34.3164 | 34.0216 | 15.3711 | 15.1164 | 14.6079 | 14.0658 | 36.389 | 35.7427 | 35.0943 | 34.449 | 33.8122 | 33.1795 | 32.3595 | 31.7122 | 31.4016 | 15.7135 | 15.5472 | 15.2545 | 14.7787 | 37.6732 | 37.0164 | 36.3553 | 35.6964 | 35.049 | 34.4048 | 33.5206 | 32.7943 | 32.4753
|  | MONTROSE NORTH | HT |  |  |  |  | 16.2201 | 15.9632 | 15.5622 | 15.1411 | 38.2669 | 37.8637 | 37.3522 | 36.9227 | 36.489 | 36.1385 | 35.7943 | 34.7111 | 34.1332 | 15.2848 | 14.9385 | 14.3648 | 13.7501 | 35.9764 | 35.4079 | 34.8448 | 34.3764 | 33.9069 | 33.5322 | 33.2658 | 32.2301 | 31.5879 | 15.6503 | 15.4261 | 15.0935 | 14.4103 | 37.2606 | 36.6848 | 36.1122 | 35.6353 | 35.1543 | 34.7701 | 34.4627 | 33.3164 | 32.6732
|  | MONTROSE NORTH | HE |  |  |  |  | 16.3832 | 16.1906 | 15.8832 | 15.5474 | 38.7353 | 38.3322 | 37.7532 | 37.0637 | 36.3774 | 35.7753 | 35.2111 | 34.8164 | 34.5016 | 15.4858 | 15.2122 | 14.7606 | 14.2627 | 36.6479 | 35.9437 | 35.2522 | 34.4722 | 33.6953 | 33.0153 | 32.4679 | 32.0943 | 31.8101 | 15.6503 | 15.4261 | 15.0935 | 14.4103 | 37.2606 | 36.6848 | 36.1122 | 35.6353 | 35.1543 | 34.7701 | 34.4627 | 33.3164 | 32.6732
|  | MONTROSE NORTH | CF |  |  |  |  | 16.439 | 16.3653 | 16.2864 | 16.2137 | 39.7058 | 39.6311 | 39.5185 | 39.389 | 39.2616 | 39.1353 | 38.6901 | 38.3216 | 37.9606 | 15.5553 | 15.4595 | 15.3574 | 15.2658 | 38.1995 | 38.1216 | 37.9837 | 37.8174 | 37.6543 | 37.4848 | 36.9595 | 36.4995 | 35.8827 | 15.8482 | 15.7829 | 15.7135 | 15.6482 | 39.2206 | 39.1511 | 39.0532 | 38.9437 | 38.8343 | 38.7279 | 38.2911 | 37.7279 | 37.0922
| TARLAND | MOSSAT | MINIMUM HEADROOM | NJ 47470 19897 | NO | YES | 0 | 2.9632 | 2.8221 | 2.6284 | 2.4516 | 7.5232 | 6.8568 | 6.2442 | 5.6137 | 4.86 | 3.8179 | -1.2263 | -10.0916 | -15.0137 | 2.3105 | 2.1516 | 1.9442 | 1.7558 | 6.8147 | 6.24 | 5.7379 | 5.2158 | 4.5958 | 3.6189 | -1.22 | -9.22 | -14.4526 | 2.3126 | 2.1537 | 1.94 | 1.7432 | 6.7937 | 6.0979 | 5.4779 | 4.8463 | 4.0947 | 3.1432 | -2.4221 | -11.8505 | -17.3874
|  | MOSSAT | EE |  |  |  |  | 3.0021 | 2.9179 | 2.7253 | 2.5463 | 7.6158 | 7.4116 | 6.7011 | 5.8105 | 5.04 | 4.2495 | -1.2263 | -10.0916 | -15.0137 | 2.3516 | 2.2589 | 2.0589 | 1.8737 | 6.9347 | 6.72 | 6.1189 | 5.3979 | 4.7705 | 4.1263 | -1.0674 | -9.22 | -14.4526 | 2.3537 | 2.2621 | 2.0484 | 1.8516 | 6.9021 | 6.6758 | 5.94 | 5.0463 | 4.2811 | 3.4937 | -2.4221 | -11.8505 | -17.3874
|  | MOSSAT | HT |  |  |  |  | 2.9632 | 2.8221 | 2.6284 | 2.4516 | 7.5232 | 6.8568 | 6.2442 | 5.6137 | 4.86 | 3.9453 | -0.97263 | -8.5084 | -12.4621 | 2.3105 | 2.1516 | 1.9442 | 1.7558 | 6.8147 | 6.24 | 5.7379 | 5.2158 | 4.5958 | 3.7874 | -1.22 | -8.7958 | -13.1453 | 2.3126 | 2.1537 | 1.94 | 1.7432 | 6.7937 | 6.0979 | 5.4779 | 4.8463 | 4.0947 | 3.1432 | -2.3126 | -10.6116 | -15.1379
|  | MOSSAT | HE |  |  |  |  | 3.0568 | 3.0074 | 2.8926 | 2.7579 | 7.8632 | 7.0368 | 6.3074 | 5.6579 | 4.8716 | 3.8179 | -0.23263 | -6.4232 | -12.3411 | 2.4147 | 2.3589 | 2.2305 | 2.08 | 7.1674 | 6.4716 | 5.8526 | 5.3253 | 4.6316 | 3.6189 | -0.23053 | -6.1832 | -12.0305 | 2.3126 | 2.1537 | 1.94 | 1.7432 | 6.7937 | 6.0979 | 5.4779 | 4.8463 | 4.0947 | 3.1432 | -2.3126 | -10.6116 | -15.1379
|  | MOSSAT | CF |  |  |  |  | 3.0842 | 3.0558 | 3.0189 | 2.9505 | 8.1368 | 7.8189 | 7.5221 | 7.2242 | 6.8537 | 6.3916 | 4.2389 | 0.82632 | -2.7611 | 2.4453 | 2.4126 | 2.3726 | 2.2979 | 7.4768 | 7.2053 | 6.9516 | 6.6926 | 6.3326 | 5.8421 | 3.7105 | 0.32526 | -3.4263 | 2.4463 | 2.4147 | 2.3726 | 2.2968 | 7.4737 | 7.1421 | 6.8358 | 6.5284 | 6.1221 | 5.5989 | 3.2463 | -0.49158 | -4.5126
| THURSO | MOUNT PLEASANT | MINIMUM HEADROOM | ND 12706 67832 | YES | YES | 0 | 15.9479 | 15.8426 | 15.7058 | 15.5289 | 15.1963 | 14.9658 | 14.7637 | 14.4542 | 14.1289 | 13.8816 | 12.8532 | 11.9511 | 11.2921 | 14.4663 | 14.3442 | 13.9937 | 13.5874 | 13.1768 | 12.9474 | 12.7674 | 12.4474 | 12.1189 | 11.88 | 10.8705 | 10.0926 | 9.4453 | 14.9108 | 14.7866 | 14.4392 | 14.0361 | 13.6276 | 13.375 | 13.1676 | 12.8455 | 12.4961 | 12.2329 | 11.1371 | 10.2161 | 9.5024
|  | MOUNT PLEASANT | EE |  |  |  |  | 15.9826 | 15.8974 | 15.7753 | 15.6437 | 15.3889 | 14.9658 | 14.7637 | 14.5595 | 14.3774 | 14.1879 | 12.9826 | 11.9511 | 11.2921 | 14.4937 | 14.4189 | 14.1463 | 13.7863 | 13.4053 | 12.9474 | 12.7674 | 12.5874 | 12.4242 | 12.2526 | 11.1126 | 10.1758 | 9.5021 | 14.9382 | 14.8634 | 14.5887 | 14.2318 | 13.8529 | 13.375 | 13.1676 | 12.9571 | 12.7697 | 12.5729 | 11.2982 | 10.2161 | 9.5024
|  | MOUNT PLEASANT | HT |  |  |  |  | 15.9479 | 15.8426 | 15.7058 | 15.5289 | 15.1963 | 14.9953 | 14.7974 | 14.4542 | 14.1289 | 13.8816 | 12.8532 | 12.0784 | 11.4689 | 14.4663 | 14.3442 | 13.9937 | 13.5874 | 13.1768 | 12.9884 | 12.8021 | 12.4474 | 12.1189 | 11.88 | 10.8705 | 10.0926 | 9.4453 | 14.9108 | 14.7866 | 14.4392 | 14.0361 | 13.6276 | 13.4213 | 13.2161 | 12.8455 | 12.4961 | 12.2329 | 11.1371 | 10.3076 | 9.6445
|  | MOUNT PLEASANT | HE |  |  |  |  | 16.0437 | 15.9732 | 15.8826 | 15.7795 | 15.5763 | 15.3174 | 15.0016 | 14.6805 | 14.3637 | 14.0511 | 13.3774 | 12.8426 | 12.2353 | 14.5442 | 14.4926 | 14.2716 | 13.9516 | 13.6 | 13.3358 | 13.0021 | 12.6684 | 12.34 | 12.0158 | 11.4063 | 10.9463 | 10.4032 | 14.9108 | 14.7866 | 14.4392 | 14.0361 | 13.6276 | 13.4213 | 13.2161 | 12.8455 | 12.4961 | 12.2329 | 11.1371 | 10.3076 | 9.6445
|  | MOUNT PLEASANT | CF |  |  |  |  | 16.0742 | 16.0395 | 16.0005 | 15.9626 | 15.9226 | 15.8458 | 15.77 | 15.6942 | 15.6237 | 15.5584 | 15.1142 | 14.7226 | 14.0932 | 14.5705 | 14.54 | 14.5074 | 14.4737 | 14.4379 | 14.3853 | 14.2853 | 14.1537 | 14.0295 | 13.9042 | 13.2411 | 12.8716 | 12.1547 | 15.015 | 14.9845 | 14.9508 | 14.9171 | 14.8813 | 14.8139 | 14.7087 | 14.5708 | 14.4403 | 14.3108 | 13.6139 | 13.1908 | 12.4434
| BEAULY | MUIR OF ORD | MINIMUM HEADROOM | NH 53420 48534 | NO | YES | 0.05 | 27.8605 | 27.5742 | 27.2542 | 26.93 | 26.6026 | 25.2426 | 23.8921 | 22.5542 | 21.3279 | 20.1079 | 17.4289 | 14.61 | 13.1374 | 26.5584 | 26.23 | 25.8795 | 25.5247 | 25.1679 | 23.6521 | 22.1468 | 20.6595 | 19.3679 | 18.0889 | 15.8511 | 13.5353 | 12.1047 | 27.0837 | 26.7616 | 26.4163 | 26.0647 | 25.7111 | 24.1816 | 22.6142 | 21.0595 | 19.7037 | 18.3574 | 15.6416 | 12.7384 | 11.1521
|  | MUIR OF ORD | EE |  |  |  |  | 27.9247 | 27.7605 | 27.49 | 27.2079 | 26.9205 | 26.31 | 25.6353 | 24.2268 | 22.9058 | 21.5732 | 17.4289 | 14.61 | 13.1374 | 26.6984 | 26.4374 | 26.1479 | 25.8437 | 25.5342 | 24.9721 | 24.3668 | 22.8511 | 21.4132 | 19.9647 | 15.9563 | 13.5353 | 12.1047 | 27.2205 | 26.9647 | 26.6742 | 26.3689 | 26.0584 | 25.4258 | 24.7279 | 23.1605 | 21.6511 | 20.1121 | 15.6416 | 12.7384 | 11.1521
|  | MUIR OF ORD | HT |  |  |  |  | 27.8605 | 27.5742 | 27.2542 | 26.93 | 26.6026 | 25.2426 | 23.8921 | 22.5542 | 21.3279 | 20.1079 | 17.6532 | 15.9605 | 14.2342 | 26.5584 | 26.23 | 25.8795 | 25.5247 | 25.1679 | 23.6521 | 22.1468 | 20.6595 | 19.3679 | 18.0889 | 15.8511 | 14.2468 | 12.3742 | 27.0837 | 26.7616 | 26.4163 | 26.0647 | 25.7111 | 24.1816 | 22.6142 | 21.0595 | 19.7037 | 18.3574 | 15.7879 | 13.9974 | 12.0689
|  | MUIR OF ORD | HE |  |  |  |  | 28.0142 | 27.9332 | 27.8395 | 27.6626 | 27.4679 | 26.8911 | 26.3889 | 25.6437 | 24.9258 | 24.1995 | 21.4079 | 18.9963 | 15.4963 | 26.8889 | 26.7205 | 26.5342 | 26.3332 | 26.1195 | 25.6047 | 25.1542 | 24.3984 | 23.6742 | 22.9395 | 20.2237 | 17.8974 | 14.3037 | 27.0837 | 26.7616 | 26.4163 | 26.0647 | 25.7111 | 24.1816 | 22.6142 | 21.0595 | 19.7037 | 18.3574 | 15.7879 | 13.9974 | 12.0689
|  | MUIR OF ORD | CF |  |  |  |  | 28.0626 | 28.0174 | 27.9658 | 27.9142 | 27.8595 | 27.61 | 27.3774 | 27.1679 | 26.8321 | 26.5142 | 24.9089 | 23.3068 | 21.1658 | 26.9953 | 26.8984 | 26.7847 | 26.6689 | 26.55 | 26.3184 | 26.0995 | 25.9079 | 25.55 | 25.1995 | 23.5311 | 21.9458 | 19.57 | 27.4574 | 27.4121 | 27.3047 | 27.1889 | 27.0711 | 26.8121 | 26.5679 | 26.3511 | 25.9805 | 25.6258 | 23.87 | 22.1237 | 19.6121
| BEAULY | MUIREND | MINIMUM HEADROOM | NH 64508 54337 | YES | YES | 0 | 3.1662 | 3.0694 | 2.9578 | 2.8715 | 2.7873 | 2.5557 | 2.3262 | 2.0904 | 1.8809 | 1.6788 | 0.68305 | -0.32958 | -0.72958 | 2.9767 | 2.8578 | 2.7262 | 2.6283 | 2.5346 | 2.2999 | 2.0683 | 1.8273 | 1.642 | 1.4652 | 0.70095 | -0.15695 | -0.53274 | 3.0599 | 2.9515 | 2.8273 | 2.7346 | 2.6441 | 2.3925 | 2.1378 | 1.8725 | 1.6536 | 1.4431 | 0.44305 | -0.60642 | -1.0422
|  | MUIREND | EE |  |  |  |  | 3.202 | 3.1231 | 3.0273 | 2.9515 | 2.8788 | 2.6841 | 2.4652 | 2.1988 | 1.9578 | 1.7083 | 0.68305 | -0.32958 | -0.72958 | 3.0188 | 2.922 | 2.8094 | 2.7283 | 2.6483 | 2.4788 | 2.2915 | 2.0409 | 1.8104 | 1.5683 | 0.70095 | -0.15695 | -0.53274 | 3.0988 | 3.0104 | 2.9041 | 2.8231 | 2.7452 | 2.5462 | 2.3209 | 2.0378 | 1.7799 | 1.5041 | 0.44305 | -0.60642 | -1.0422
|  | MUIREND | HT |  |  |  |  | 3.1662 | 3.0694 | 2.9578 | 2.8715 | 2.7873 | 2.5557 | 2.3262 | 2.0904 | 1.8809 | 1.6788 | 0.85989 | 0.30937 | -0.0043158 | 2.9767 | 2.8578 | 2.7262 | 2.6283 | 2.5346 | 2.2999 | 2.0683 | 1.8273 | 1.642 | 1.4652 | 0.71463 | 0.19042 | -0.14011 | 3.0599 | 2.9515 | 2.8273 | 2.7346 | 2.6441 | 2.3925 | 2.1378 | 1.8725 | 1.6536 | 1.4431 | 0.56832 | -0.029579 | -0.38958
|  | MUIREND | HE |  |  |  |  | 3.2536 | 3.1978 | 3.1325 | 3.0883 | 3.0441 | 2.8578 | 2.6978 | 2.5062 | 2.3188 | 2.1378 | 1.4157 | 0.82621 | 0.21674 | 3.0809 | 3.0115 | 2.9325 | 2.8831 | 2.8346 | 2.6788 | 2.5452 | 2.3673 | 2.1915 | 2.0252 | 1.4083 | 0.92937 | 0.43463 | 3.0599 | 2.9515 | 2.8273 | 2.7346 | 2.6441 | 2.3925 | 2.1378 | 1.8725 | 1.6536 | 1.4431 | 0.56832 | -0.029579 | -0.38958
|  | MUIREND | CF |  |  |  |  | 3.2778 | 3.2567 | 3.2167 | 3.1873 | 3.1609 | 3.0831 | 3.0115 | 2.9399 | 2.8588 | 2.7915 | 2.4188 | 2.042 | 1.7736 | 3.1083 | 3.0841 | 3.0357 | 2.9988 | 2.9694 | 2.9009 | 2.8378 | 2.7736 | 2.6915 | 2.6199 | 2.2662 | 1.9536 | 1.7273 | 3.1809 | 3.1588 | 3.1136 | 3.0809 | 3.0525 | 2.9704 | 2.8967 | 2.8241 | 2.7357 | 2.6631 | 2.2694 | 1.8809 | 1.6031
| NAIRN | NAIRN CENTRAL | MINIMUM HEADROOM | NH 88496 56295 | NO | YES | 0.19 | 16.9053 | 16.7126 | 16.3484 | 15.9063 | 15.4053 | 14.4389 | 13.4653 | 12.4716 | 11.4758 | 10.5421 | 8.5326 | 7.0432 | 5.9421 | 15.1121 | 14.6395 | 14.1553 | 13.6532 | 13.0774 | 11.9711 | 10.8837 | 9.8089 | 8.7395 | 7.7416 | 5.7226 | 4.1942 | 3.0153 | 15.7008 | 15.245 | 14.7766 | 14.2913 | 13.7355 | 12.6503 | 11.5829 | 10.5008 | 9.3903 | 8.3534 | 6.2008 | 4.5861 | 3.3692
|  | NAIRN CENTRAL | EE |  |  |  |  | 16.9832 | 16.8316 | 16.6474 | 16.2674 | 15.8242 | 15.22 | 14.5979 | 13.6632 | 12.7337 | 11.8516 | 9.1916 | 7.4126 | 6.4221 | 15.2847 | 14.8984 | 14.4921 | 14.0637 | 13.5532 | 12.9111 | 12.2584 | 11.2121 | 10.1963 | 9.2542 | 6.5847 | 4.9132 | 3.9047 | 15.8682 | 15.4955 | 15.1018 | 14.685 | 14.1924 | 13.5355 | 12.8629 | 11.8176 | 10.8092 | 9.8408 | 6.9692 | 5.0924 | 4.0155
|  | NAIRN CENTRAL | HT |  |  |  |  | 16.9053 | 16.7126 | 16.3484 | 15.9063 | 15.4053 | 14.4389 | 13.4653 | 12.4716 | 11.4758 | 10.5421 | 8.5326 | 7.0432 | 5.9421 | 15.1121 | 14.6395 | 14.1553 | 13.6532 | 13.0774 | 11.9711 | 10.8837 | 9.8089 | 8.7395 | 7.7416 | 5.7226 | 4.1942 | 3.0153 | 15.7008 | 15.245 | 14.7766 | 14.2913 | 13.7355 | 12.6503 | 11.5829 | 10.5008 | 9.3903 | 8.3534 | 6.2008 | 4.5861 | 3.3692
|  | NAIRN CENTRAL | HE |  |  |  |  | 17.0905 | 16.9895 | 16.8747 | 16.7526 | 16.4295 | 15.8895 | 15.3958 | 14.8158 | 14.2442 | 13.7379 | 12.1242 | 10.74 | 9.3789 | 15.5205 | 15.2458 | 14.9542 | 14.6342 | 14.2268 | 13.6616 | 13.1374 | 12.5037 | 11.8784 | 11.3321 | 9.7142 | 8.3458 | 7.0079 | 15.7008 | 15.245 | 14.7766 | 14.2913 | 13.7355 | 12.6503 | 11.5829 | 10.5008 | 9.3903 | 8.3534 | 6.2008 | 4.5861 | 3.3692
|  | NAIRN CENTRAL | CF |  |  |  |  | 17.1484 | 17.0905 | 17.0274 | 16.9632 | 16.8989 | 16.7821 | 16.6295 | 16.3758 | 16.0716 | 15.7979 | 14.78 | 13.8568 | 13.1137 | 15.5953 | 15.5311 | 15.4184 | 15.2395 | 15.0342 | 14.7689 | 14.4984 | 14.2195 | 13.8753 | 13.5616 | 12.4732 | 11.5163 | 10.7205 | 16.1155 | 16.0576 | 15.9945 | 15.8239 | 15.6271 | 15.3555 | 15.0829 | 14.8029 | 14.4629 | 14.1555 | 13.0461 | 12.0397 | 11.2176
| STRICHEN | NEW PITSLIGO | MINIMUM HEADROOM | NJ 88529 54853 | NO | YES | 0.225 | 4.8792 | 4.8455 | 4.8076 | 4.7687 | 4.7287 | 4.6213 | 4.5097 | 4.375 | 4.2571 | 4.1392 | 1.8897 | 0.55079 | -1.0934 | 4.8729 | 4.8382 | 4.8013 | 4.7634 | 4.7245 | 4.6539 | 4.575 | 4.3971 | 4.1739 | 3.8992 | 1.815 | 0.56342 | -1.1103 | 4.7592 | 4.7024 | 4.6424 | 4.5792 | 4.5076 | 4.3666 | 4.1834 | 3.9908 | 3.7497 | 3.4603 | 2.6571 | -0.30079 | -2.7303
|  | NEW PITSLIGO | EE |  |  |  |  | 4.8918 | 4.8655 | 4.8318 | 4.7961 | 4.7592 | 4.6434 | 4.5097 | 4.375 | 4.2571 | 4.1392 | 3.6382 | 1.095 | -1.0934 | 4.8855 | 4.8592 | 4.8276 | 4.795 | 4.7613 | 4.6918 | 4.6139 | 4.5066 | 4.3466 | 4.1718 | 3.2297 | 0.85395 | -1.1103 | 4.7729 | 4.7392 | 4.6876 | 4.6339 | 4.5792 | 4.4297 | 4.2582 | 4.0624 | 3.8803 | 3.6845 | 2.6571 | -0.30079 | -2.7303
|  | NEW PITSLIGO | HT |  |  |  |  | 4.8792 | 4.8455 | 4.8076 | 4.7687 | 4.7287 | 4.6213 | 4.515 | 4.4087 | 4.2887 | 4.1676 | 3.8182 | 1.6108 | -0.55763 | 4.8729 | 4.8382 | 4.8013 | 4.7634 | 4.7245 | 4.6539 | 4.575 | 4.3971 | 4.1739 | 3.8992 | 3.2834 | 1.1961 | -0.72605 | 4.7592 | 4.7024 | 4.6424 | 4.5792 | 4.5076 | 4.3666 | 4.1834 | 3.9908 | 3.7497 | 3.4603 | 2.7961 | 0.18237 | -2.1829
|  | NEW PITSLIGO | HE |  |  |  |  | 4.9108 | 4.8939 | 4.8739 | 4.8529 | 4.8287 | 4.7118 | 4.6139 | 4.5161 | 4.4192 | 4.3245 | 1.8897 | 0.55079 | -0.75974 | 4.9045 | 4.8876 | 4.8687 | 4.8476 | 4.8234 | 4.7582 | 4.7013 | 4.6434 | 4.5066 | 4.2982 | 1.815 | 0.56342 | -0.67763 | 4.7592 | 4.7024 | 4.6424 | 4.5792 | 4.5076 | 4.3666 | 4.1834 | 3.9908 | 3.7497 | 3.4603 | 2.7961 | 0.18237 | -2.1829
|  | NEW PITSLIGO | CF |  |  |  |  | 4.9213 | 4.9118 | 4.9013 | 4.8897 | 4.8782 | 4.8329 | 4.7918 | 4.7508 | 4.715 | 4.6866 | 4.4971 | 4.2739 | 4.1192 | 4.915 | 4.9055 | 4.8961 | 4.8845 | 4.8739 | 4.8476 | 4.8224 | 4.7982 | 4.7761 | 4.7561 | 4.4097 | 4.1782 | 4.0076 | 4.8024 | 4.7929 | 4.7824 | 4.7697 | 4.7592 | 4.7045 | 4.6518 | 4.5992 | 4.5529 | 4.5013 | 3.9908 | 3.7024 | 3.495
| DUNOON | NEWTON | MINIMUM HEADROOM | NS 04939 98621 | YES | YES | 0 | 0.33158 | 0.32632 | 0.32105 | 0.31474 | 0.30947 | 0.29684 | 0.28105 | 0.26737 | 0.25368 | 0.23895 | 0.17263 | 0.11263 | 0.063158 | 0.31368 | 0.30842 | 0.30316 | 0.29895 | 0.29053 | 0.27895 | 0.26737 | 0.25789 | 0.24526 | 0.23368 | 0.17895 | 0.12632 | 0.082105 | 0.32316 | 0.31789 | 0.31053 | 0.30316 | 0.29474 | 0.27789 | 0.26316 | 0.24737 | 0.23263 | 0.21789 | 0.14737 | 0.084211 | 0.028421
|  | NEWTON | EE |  |  |  |  | 0.33263 | 0.32737 | 0.32105 | 0.31474 | 0.30947 | 0.29684 | 0.28105 | 0.26737 | 0.25368 | 0.23895 | 0.17263 | 0.11263 | 0.063158 | 0.31474 | 0.31053 | 0.30526 | 0.30105 | 0.29368 | 0.28105 | 0.26947 | 0.25789 | 0.24632 | 0.23368 | 0.17895 | 0.12632 | 0.082105 | 0.32421 | 0.31789 | 0.31053 | 0.30316 | 0.29474 | 0.27789 | 0.26316 | 0.24737 | 0.23263 | 0.21789 | 0.14737 | 0.084211 | 0.028421
|  | NEWTON | HT |  |  |  |  | 0.33158 | 0.32632 | 0.32105 | 0.31579 | 0.31053 | 0.29789 | 0.28737 | 0.27684 | 0.26316 | 0.25053 | 0.20105 | 0.16526 | 0.12842 | 0.31368 | 0.30842 | 0.30316 | 0.29895 | 0.29053 | 0.27895 | 0.26737 | 0.25789 | 0.24526 | 0.23474 | 0.19053 | 0.15789 | 0.12105 | 0.32316 | 0.31789 | 0.31263 | 0.30316 | 0.29474 | 0.28105 | 0.26842 | 0.25684 | 0.24421 | 0.22947 | 0.17789 | 0.14 | 0.1
|  | NEWTON | HE |  |  |  |  | 0.33579 | 0.33263 | 0.32947 | 0.32632 | 0.32316 | 0.31474 | 0.30737 | 0.3 | 0.29263 | 0.28526 | 0.24842 | 0.20421 | 0.15474 | 0.31789 | 0.31579 | 0.31263 | 0.30947 | 0.30632 | 0.3 | 0.29579 | 0.29158 | 0.28211 | 0.27474 | 0.24211 | 0.2 | 0.15579 | 0.32316 | 0.31789 | 0.31263 | 0.30316 | 0.29474 | 0.28105 | 0.26842 | 0.25684 | 0.24421 | 0.22947 | 0.17789 | 0.14 | 0.1
|  | NEWTON | CF |  |  |  |  | 0.33684 | 0.33579 | 0.33474 | 0.33368 | 0.33053 | 0.32737 | 0.32421 | 0.32211 | 0.32 | 0.31579 | 0.30316 | 0.28211 | 0.25684 | 0.31895 | 0.31789 | 0.31684 | 0.31579 | 0.31368 | 0.31158 | 0.30842 | 0.30632 | 0.30421 | 0.30316 | 0.29053 | 0.26526 | 0.24 | 0.32842 | 0.32737 | 0.32526 | 0.32421 | 0.32211 | 0.31895 | 0.31474 | 0.31263 | 0.31053 | 0.30842 | 0.29158 | 0.26421 | 0.23474
| REDMOSS | NEWTONHILL | MINIMUM HEADROOM | NO 90190 93653 | NO | YES | 0.3 | 15.6047 | 15.4353 | 15.2489 | 29.3526 | 28.5747 | 27.4768 | 26.3916 | 25.3137 | 24.2705 | 23.2316 | 12.7874 | 5.3884 | 4.2232 | 14.0874 | 13.5842 | 12.9642 | 26.0695 | 25.1958 | 24.0326 | 22.8842 | 21.7432 | 20.6611 | 19.5853 | 8.0358 | 0.38632 | -0.73579 | 14.5961 | 14.4066 | 13.8171 | 27.2921 | 26.4132 | 25.1963 | 23.9932 | 22.7984 | 21.6489 | 20.5079 | 8.5784 | 0.29211 | -0.95316
|  | NEWTONHILL | EE |  |  |  |  | 15.6742 | 15.5416 | 15.3847 | 29.6779 | 28.9495 | 27.8642 | 26.7316 | 25.6032 | 24.6074 | 23.6147 | 12.7874 | 5.3884 | 4.2232 | 14.1674 | 13.8126 | 13.2579 | 26.4274 | 25.6084 | 24.4737 | 23.3042 | 22.1432 | 21.1179 | 20.0958 | 8.2768 | 0.38632 | -0.73579 | 14.6655 | 14.5203 | 14.1087 | 27.6479 | 26.8205 | 25.6195 | 24.3732 | 23.1311 | 22.0363 | 20.9437 | 8.6321 | 0.29211 | -0.95316
|  | NEWTONHILL | HT |  |  |  |  | 15.6047 | 15.4353 | 15.2489 | 29.3526 | 28.5747 | 27.4768 | 26.3916 | 25.3137 | 24.2705 | 23.2316 | 12.8063 | 6.2621 | 5.1368 | 14.0874 | 13.5842 | 12.9642 | 26.0695 | 25.1958 | 24.0326 | 22.8842 | 21.7432 | 20.6611 | 19.5853 | 8.0358 | 0.74632 | -0.42105 | 14.5961 | 14.4066 | 13.8171 | 27.2921 | 26.4132 | 25.1963 | 23.9932 | 22.7984 | 21.6489 | 20.5079 | 8.5784 | 1.0711 | -0.16053
|  | NEWTONHILL | HE |  |  |  |  | 15.7721 | 15.6858 | 15.5879 | 30.0316 | 29.4695 | 28.4958 | 27.5221 | 26.5558 | 25.6695 | 24.8011 | 14.84 | 8.4232 | 6.9832 | 14.2653 | 14.0221 | 13.6474 | 26.8958 | 26.1505 | 25.1484 | 24.1263 | 23.1116 | 22.1884 | 21.2842 | 10.2568 | 3.2337 | 2.0074 | 14.5961 | 14.4066 | 13.8171 | 27.2921 | 26.4132 | 25.1963 | 23.9932 | 22.7984 | 21.6489 | 20.5079 | 8.5784 | 1.0711 | -0.16053
|  | NEWTONHILL | CF |  |  |  |  | 15.8237 | 15.7742 | 15.7205 | 30.2168 | 30.1611 | 30.0116 | 29.6863 | 29.2168 | 28.7779 | 28.3421 | 22.3126 | 18.2495 | 17.58 | 14.3495 | 14.2737 | 14.1642 | 27.7137 | 27.3884 | 26.9347 | 26.4621 | 25.96 | 25.4874 | 25.0105 | 18.2274 | 13.8084 | 13.2116 | 14.8171 | 14.7666 | 14.7097 | 28.8195 | 28.6184 | 28.1374 | 27.6416 | 27.1163 | 26.6247 | 26.1332 | 19.2068 | 14.5668 | 13.8689
| ALNESS | NIGG | MINIMUM HEADROOM | NH 79490 69773 | YES | YES | 0 | 1.2895 | 1.2884 | 1.2884 | 1.2884 | 1.2874 | 1.2863 | 1.2863 | 1.2863 | 1.2853 | 1.2842 | 1.2821 | 1.2789 | 1.2768 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1747 | 1.1747 | 1.1747 | 1.1747
|  | NIGG | EE |  |  |  |  | 1.2895 | 1.2895 | 1.2884 | 1.2884 | 1.2884 | 1.2874 | 1.2874 | 1.2863 | 1.2863 | 1.2863 | 1.2842 | 1.2821 | 1.28 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1747 | 1.1747 | 1.1747
|  | NIGG | HT |  |  |  |  | 1.2895 | 1.2884 | 1.2884 | 1.2884 | 1.2874 | 1.2863 | 1.2863 | 1.2863 | 1.2853 | 1.2842 | 1.2821 | 1.2789 | 1.2768 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1747 | 1.1747 | 1.1747 | 1.1747
|  | NIGG | HE |  |  |  |  | 1.2895 | 1.2895 | 1.2895 | 1.2895 | 1.2884 | 1.2884 | 1.2884 | 1.2884 | 1.2884 | 1.2884 | 1.2863 | 1.2863 | 1.2842 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1747 | 1.1747 | 1.1747 | 1.1747
|  | NIGG | CF |  |  |  |  | 1.2895 | 1.2895 | 1.2895 | 1.2895 | 1.2895 | 1.2895 | 1.2895 | 1.2884 | 1.2884 | 1.2884 | 1.2884 | 1.2863 | 1.2863 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1589 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758 | 1.1758
| CHARLESTON | NINEWELLS | MINIMUM HEADROOM | NO 35148 30641 | NO | YES | 0.908 | 15.9273 | 15.7094 | 15.4462 | 15.1262 | 14.5631 | 14.482 | 14.4062 | 14.3283 | 14.2567 | 14.1778 | 13.7978 | 13.3778 | 13.0294 | 14.5657 | 14.4962 | 14.3131 | 13.9867 | 13.4015 | 13.3267 | 13.2552 | 13.1836 | 13.1173 | 13.0425 | 12.6531 | 12.2141 | 11.8436 | 14.9817 | 14.9112 | 14.8028 | 14.4491 | 13.8102 | 13.7281 | 13.6512 | 13.5723 | 13.5007 | 13.4186 | 13.0312 | 12.5996 | 12.2207
|  | NINEWELLS | EE |  |  |  |  | 15.9862 | 15.7915 | 15.5504 | 15.2525 | 14.5631 | 14.482 | 14.4062 | 14.3283 | 14.2567 | 14.1778 | 13.802 | 13.5104 | 13.2883 | 14.5952 | 14.5404 | 14.4236 | 14.1246 | 13.4015 | 13.3267 | 13.2552 | 13.1836 | 13.1173 | 13.0425 | 12.6867 | 12.412 | 12.1941 | 15.0112 | 14.9512 | 14.8859 | 14.5838 | 13.8102 | 13.7281 | 13.6512 | 13.5723 | 13.5007 | 13.4186 | 13.0312 | 12.7281 | 12.4881
|  | NINEWELLS | HT |  |  |  |  | 15.9273 | 15.7094 | 15.4462 | 15.1262 | 14.9978 | 14.8588 | 14.7273 | 14.5946 | 14.4715 | 14.3441 | 13.7978 | 13.3778 | 13.0294 | 14.5657 | 14.4962 | 14.3131 | 13.9867 | 13.8583 | 13.7194 | 13.5888 | 13.4573 | 13.3362 | 13.212 | 12.6531 | 12.2141 | 11.8436 | 14.9817 | 14.9112 | 14.8028 | 14.4491 | 14.3144 | 14.1691 | 14.0323 | 13.8933 | 13.7649 | 13.6323 | 13.0491 | 12.5996 | 12.2207
|  | NINEWELLS | HE |  |  |  |  | 16.0599 | 15.9062 | 15.7062 | 15.4462 | 15.3767 | 15.2957 | 15.2231 | 15.1441 | 15.0715 | 15.002 | 14.7052 | 14.4967 | 14.3441 | 14.6309 | 14.5941 | 14.5541 | 14.3109 | 14.2415 | 14.1636 | 14.092 | 14.0152 | 13.9436 | 13.8752 | 13.5888 | 13.3888 | 13.2478 | 14.9817 | 14.9112 | 14.8028 | 14.4491 | 14.3144 | 14.1691 | 14.0323 | 13.8933 | 13.7649 | 13.6323 | 13.0491 | 12.5996 | 12.2207
|  | NINEWELLS | CF |  |  |  |  | 16.1167 | 16.0294 | 15.9283 | 15.8041 | 15.7652 | 15.7199 | 15.6746 | 15.6294 | 15.5862 | 15.5431 | 15.3452 | 15.1904 | 15.0841 | 14.6499 | 14.6278 | 14.6067 | 14.5825 | 14.5594 | 14.5341 | 14.5078 | 14.4815 | 14.4573 | 14.4152 | 14.2173 | 14.0646 | 13.9604 | 15.0659 | 15.0428 | 15.0217 | 14.9975 | 14.9744 | 14.947 | 14.9186 | 14.8902 | 14.8638 | 14.8375 | 14.7049 | 14.5396 | 14.4249
| THURSO | NORTH HOY | MINIMUM HEADROOM | HY 25681 02549 | YES | YES | 0 | 0.20947 | 0.20737 | 0.20526 | 0.20421 | 0.2 | 0.19895 | 0.19579 | 0.19368 | 0.19158 | 0.18842 | 0.17684 | 0.16842 | 0.15895 | 0.19684 | 0.19368 | 0.19158 | 0.18947 | 0.18526 | 0.18316 | 0.18 | 0.17789 | 0.17474 | 0.17158 | 0.15895 | 0.14947 | 0.13895 | 0.20105 | 0.19684 | 0.19474 | 0.19263 | 0.18947 | 0.18737 | 0.18316 | 0.18211 | 0.17895 | 0.17579 | 0.16316 | 0.15474 | 0.14421
|  | NORTH HOY | EE |  |  |  |  | 0.20947 | 0.20842 | 0.20737 | 0.20632 | 0.20421 | 0.20211 | 0.2 | 0.19789 | 0.19579 | 0.19474 | 0.18526 | 0.17895 | 0.17263 | 0.19789 | 0.19579 | 0.19474 | 0.19263 | 0.19053 | 0.18737 | 0.18526 | 0.18316 | 0.18105 | 0.17895 | 0.16842 | 0.16105 | 0.15368 | 0.20105 | 0.2 | 0.19789 | 0.19579 | 0.19368 | 0.19053 | 0.18947 | 0.18737 | 0.18421 | 0.18211 | 0.17263 | 0.16526 | 0.15789
|  | NORTH HOY | HT |  |  |  |  | 0.20947 | 0.20737 | 0.20526 | 0.20421 | 0.2 | 0.19895 | 0.19579 | 0.19368 | 0.19158 | 0.18842 | 0.17684 | 0.16842 | 0.15895 | 0.19684 | 0.19368 | 0.19158 | 0.18947 | 0.18526 | 0.18316 | 0.18 | 0.17789 | 0.17474 | 0.17158 | 0.15895 | 0.14947 | 0.13895 | 0.20105 | 0.19684 | 0.19474 | 0.19263 | 0.18947 | 0.18737 | 0.18316 | 0.18211 | 0.17895 | 0.17579 | 0.16316 | 0.15474 | 0.14421
|  | NORTH HOY | HE |  |  |  |  | 0.21053 | 0.20947 | 0.20842 | 0.20842 | 0.20737 | 0.20632 | 0.20526 | 0.20421 | 0.20211 | 0.20211 | 0.19684 | 0.19368 | 0.19053 | 0.2 | 0.19789 | 0.19579 | 0.19579 | 0.19474 | 0.19368 | 0.19158 | 0.19053 | 0.18842 | 0.18842 | 0.18211 | 0.17789 | 0.17368 | 0.20105 | 0.19684 | 0.19474 | 0.19263 | 0.18947 | 0.18737 | 0.18316 | 0.18211 | 0.17895 | 0.17579 | 0.16316 | 0.15474 | 0.14421
|  | NORTH HOY | CF |  |  |  |  | 0.21053 | 0.21053 | 0.20947 | 0.20947 | 0.20947 | 0.20842 | 0.20842 | 0.20737 | 0.20737 | 0.20632 | 0.20421 | 0.20105 | 0.19895 | 0.2 | 0.2 | 0.19789 | 0.19789 | 0.19789 | 0.19579 | 0.19579 | 0.19474 | 0.19474 | 0.19368 | 0.19053 | 0.18632 | 0.18421 | 0.20316 | 0.20316 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.19789 | 0.19789 | 0.19684 | 0.19368 | 0.19053 | 0.18737
| BEAULY | NORTH KESSOCK | MINIMUM HEADROOM | NH 65004 48461 | YES | YES | 0 | 4.18 | 4.1284 | 4.0632 | 3.9968 | 3.9326 | 3.8032 | 3.6726 | 3.5453 | 3.4042 | 3.2695 | 2.3853 | 1.2158 | 0.31684 | 3.9505 | 3.8789 | 3.8053 | 3.7316 | 3.6589 | 3.5358 | 3.4147 | 3.2947 | 3.1653 | 3.0453 | 2.1305 | 0.89368 | 0.018947 | 4.0495 | 3.9811 | 3.9084 | 3.8358 | 3.7653 | 3.6263 | 3.4905 | 3.3537 | 3.2053 | 3.0653 | 2.0979 | 0.81579 | -0.18632
|  | NORTH KESSOCK | EE |  |  |  |  | 4.1958 | 4.1653 | 4.1158 | 4.06 | 4.0053 | 3.8768 | 3.7316 | 3.5832 | 3.4495 | 3.3158 | 2.3937 | 1.2158 | 0.31684 | 3.9842 | 3.9284 | 3.8695 | 3.8084 | 3.7484 | 3.6347 | 3.5084 | 3.3789 | 3.26 | 3.1421 | 2.24 | 1.0663 | 0.063158 | 4.0811 | 4.0284 | 3.9695 | 3.9084 | 3.8484 | 3.7147 | 3.5642 | 3.4084 | 3.2695 | 3.1305 | 2.1316 | 0.84947 | -0.18632
|  | NORTH KESSOCK | HT |  |  |  |  | 4.18 | 4.1284 | 4.0632 | 3.9968 | 3.9326 | 3.8032 | 3.6726 | 3.5453 | 3.4042 | 3.2695 | 2.3853 | 1.2716 | 0.50211 | 3.9505 | 3.8789 | 3.8053 | 3.7316 | 3.6589 | 3.5358 | 3.4147 | 3.2947 | 3.1653 | 3.0453 | 2.1305 | 0.89368 | 0.018947 | 4.0495 | 3.9811 | 3.9084 | 3.8358 | 3.7653 | 3.6263 | 3.4905 | 3.3537 | 3.2053 | 3.0653 | 2.0979 | 0.81579 | -0.075789
|  | NORTH KESSOCK | HE |  |  |  |  | 4.2189 | 4.2 | 4.1779 | 4.1537 | 4.1284 | 4.0063 | 3.9021 | 3.7916 | 3.6674 | 3.4989 | 2.7695 | 1.8653 | 0.89684 | 4.0295 | 3.9968 | 3.9611 | 3.9242 | 3.8874 | 3.7842 | 3.6958 | 3.5979 | 3.48 | 3.2979 | 2.5579 | 1.6189 | 0.60947 | 4.0495 | 3.9811 | 3.9084 | 3.8358 | 3.7653 | 3.6263 | 3.4905 | 3.3537 | 3.2053 | 3.0653 | 2.0979 | 0.81579 | -0.075789
|  | NORTH KESSOCK | CF |  |  |  |  | 4.2316 | 4.2211 | 4.2084 | 4.1968 | 4.1842 | 4.1421 | 4.1053 | 4.0568 | 4.0053 | 3.9253 | 3.5547 | 2.9832 | 2.3568 | 4.0537 | 4.0337 | 4.0126 | 3.9905 | 3.9695 | 3.9221 | 3.8811 | 3.8389 | 3.7874 | 3.6884 | 3.2747 | 2.6737 | 1.9853 | 4.1484 | 4.1305 | 4.1095 | 4.0874 | 4.0663 | 4.0116 | 3.9632 | 3.9137 | 3.8579 | 3.76 | 3.3295 | 2.6968 | 1.9758
| BROADFORD | NOSTIE BRIDGE | MINIMUM HEADROOM | NG 85209 27252 | YES | YES | 0 | 0.87053 | 0.78632 | 0.69895 | 0.61368 | 0.52737 | 0.35895 | 0.19368 | 0.027368 | -0.14737 | -0.32211 | -1.6716 | -3.3063 | -4.6232 | 0.90211 | 0.81368 | 0.71895 | 0.62842 | 0.54 | 0.38421 | 0.23158 | 0.077895 | -0.077895 | -0.23263 | -1.6358 | -3.4505 | -4.74 | 0.89474 | 0.80526 | 0.71158 | 0.62105 | 0.52947 | 0.35684 | 0.18421 | 0.013684 | -0.16526 | -0.34211 | -1.8232 | -3.6926 | -5.1168
|  | NOSTIE BRIDGE | EE |  |  |  |  | 0.90842 | 0.84316 | 0.76947 | 0.69579 | 0.62105 | 0.45368 | 0.26737 | 0.075789 | -0.094737 | -0.26105 | -1.6326 | -3.2905 | -4.6232 | 0.94421 | 0.87474 | 0.79895 | 0.72211 | 0.64737 | 0.5 | 0.33789 | 0.17158 | 0.021053 | -0.12421 | -1.4674 | -3.1484 | -4.6263 | 0.93474 | 0.86526 | 0.78737 | 0.70947 | 0.63053 | 0.46105 | 0.27053 | 0.075789 | -0.098947 | -0.26842 | -1.7568 | -3.5863 | -5.1168
|  | NOSTIE BRIDGE | HT |  |  |  |  | 0.87053 | 0.78632 | 0.69895 | 0.61368 | 0.52737 | 0.35895 | 0.19368 | 0.027368 | -0.14737 | -0.32211 | -1.6716 | -3.3063 | -4.4411 | 0.90211 | 0.81368 | 0.71895 | 0.62842 | 0.54 | 0.38421 | 0.23158 | 0.077895 | -0.077895 | -0.23263 | -1.6358 | -3.4505 | -4.74 | 0.89474 | 0.80526 | 0.71158 | 0.62105 | 0.52947 | 0.35684 | 0.18421 | 0.013684 | -0.16526 | -0.34211 | -1.8232 | -3.6926 | -5.0042
|  | NOSTIE BRIDGE | HE |  |  |  |  | 0.96 | 0.92105 | 0.87789 | 0.83579 | 0.78947 | 0.63579 | 0.50105 | 0.32737 | 0.15474 | -0.097895 | -1.1463 | -2.44 | -3.8305 | 0.98842 | 0.95895 | 0.91368 | 0.86737 | 0.82211 | 0.69053 | 0.57579 | 0.41263 | 0.25053 | -0.0052632 | -1.0547 | -2.4116 | -3.8768 | 0.89474 | 0.80526 | 0.71158 | 0.62105 | 0.52947 | 0.35684 | 0.18421 | 0.013684 | -0.16526 | -0.34211 | -1.8232 | -3.6926 | -5.0042
|  | NOSTIE BRIDGE | CF |  |  |  |  | 0.98632 | 0.96421 | 0.93895 | 0.91474 | 0.88842 | 0.82316 | 0.76316 | 0.70316 | 0.60842 | 0.47684 | -0.091579 | -0.91158 | -1.8316 | 1.0032 | 0.99053 | 0.97684 | 0.95263 | 0.92526 | 0.86737 | 0.81368 | 0.76105 | 0.66211 | 0.51789 | -0.072632 | -0.93895 | -1.9547 | 0.97579 | 0.96316 | 0.94842 | 0.93368 | 0.91579 | 0.84842 | 0.78737 | 0.72526 | 0.62211 | 0.47579 | -0.14632 | -1.0568 | -2.1021
| TAYNUILT | OBAN | MINIMUM HEADROOM | NM 85643 29338 | NO | YES | 0.05 | 28.7247 | 28.5458 | 28.3605 | 28.1732 | 27.9511 | 27.3079 | 26.6953 | 26.0626 | 25.4405 | 24.9921 | 23.8311 | 22.8637 | 22.0237 | 25.3016 | 25.1226 | 24.9374 | 24.75 | 24.1089 | 23.3911 | 22.7079 | 21.9995 | 21.3016 | 20.8068 | 19.5553 | 18.4984 | 17.5658 | 23.6416 | 23.2511 | 22.7353 | 22.1205 | 21.3447 | 20.6258 | 19.9426 | 19.2342 | 18.5374 | 18.0416 | 16.7868 | 15.7279 | 14.7953
|  | OBAN | EE |  |  |  |  | 28.7995 | 28.6605 | 28.5142 | 28.3605 | 28.2016 | 28.0353 | 27.23 | 26.7868 | 26.3405 | 25.9237 | 24.6121 | 23.8784 | 23.2711 | 25.3763 | 25.2374 | 25.0911 | 24.9384 | 24.7795 | 24.2237 | 23.2816 | 22.79 | 22.2921 | 21.8289 | 20.3963 | 19.5984 | 18.9247 | 23.7258 | 23.5268 | 23.1921 | 22.7405 | 22.1637 | 21.4574 | 20.5153 | 20.0237 | 19.5247 | 19.0605 | 17.6226 | 16.8195 | 16.1437
|  | OBAN | HT |  |  |  |  | 28.7247 | 28.5458 | 28.3605 | 28.1732 | 27.9511 | 27.3079 | 26.6953 | 26.0626 | 25.4405 | 24.9921 | 23.8311 | 22.8637 | 22.0237 | 25.3016 | 25.1226 | 24.9374 | 24.75 | 24.1089 | 23.3911 | 22.7079 | 21.9995 | 21.3016 | 20.8068 | 19.5553 | 18.4984 | 17.5658 | 23.6416 | 23.2511 | 22.7353 | 22.1205 | 21.3447 | 20.6258 | 19.9426 | 19.2342 | 18.5374 | 18.0416 | 16.7868 | 15.7279 | 14.7953
|  | OBAN | HE |  |  |  |  | 28.8879 | 28.79 | 28.6826 | 28.5658 | 28.4416 | 28.3068 | 27.6711 | 27.1584 | 26.7542 | 26.5321 | 25.9668 | 25.5795 | 25.2847 | 25.4647 | 25.3668 | 25.2595 | 25.1426 | 25.0184 | 24.6342 | 23.7458 | 23.1658 | 22.7111 | 22.4689 | 21.8721 | 21.4563 | 21.1332 | 23.6416 | 23.2511 | 22.7353 | 22.1205 | 21.3447 | 20.6258 | 19.9426 | 19.2342 | 18.5374 | 18.0416 | 16.7868 | 15.7279 | 14.7953
|  | OBAN | CF |  |  |  |  | 28.9363 | 28.8753 | 28.8121 | 28.7479 | 28.6816 | 28.6132 | 28.5437 | 28.4742 | 28.4047 | 28.3363 | 27.6405 | 27.2921 | 27.0342 | 25.5132 | 25.4521 | 25.3889 | 25.3247 | 25.2584 | 25.19 | 25.1226 | 25.0532 | 24.9837 | 24.8089 | 23.7363 | 23.3574 | 23.0689 | 23.8626 | 23.8016 | 23.7384 | 23.6742 | 23.6079 | 23.4068 | 23.1374 | 22.7658 | 22.4416 | 22.0416 | 20.97 | 20.5879 | 20.2984
| MILTON OF CRAIGIE | OLD CRAIGIE ROAD | MINIMUM HEADROOM | NO 42156 32130 | NO | YES | 0 | 11.2505 | 10.8726 | 10.5505 | 10.3032 | 10.0937 | 9.8695 | 9.6432 | 9.4189 | 9.2084 | 9 | 7.9926 | 7.2432 | 6.6537 | 11.0726 | 10.9411 | 10.7926 | 10.5221 | 10.2958 | 10.0589 | 9.8189 | 9.58 | 9.3579 | 9.1379 | 8.0484 | 7.2158 | 6.5505 | 11.3947 | 11.1653 | 10.9579 | 10.7263 | 10.5021 | 10.2632 | 10.0232 | 9.7842 | 9.5611 | 9.3379 | 8.2611 | 7.4337 | 6.7779
|  | OLD CRAIGIE ROAD | EE |  |  |  |  | 11.3632 | 11.0305 | 10.7442 | 10.5284 | 10.3495 | 10.1642 | 9.9842 | 9.7853 | 9.5989 | 9.4326 | 8.5926 | 7.9989 | 7.5453 | 11.1242 | 11.0189 | 10.9126 | 10.7684 | 10.5747 | 10.38 | 10.1916 | 9.9842 | 9.7853 | 9.6095 | 8.7105 | 8.0968 | 7.5905 | 11.4705 | 11.2747 | 11.0979 | 10.9474 | 10.7779 | 10.5811 | 10.3884 | 10.1779 | 9.9779 | 9.8011 | 8.8916 | 8.2705 | 7.7684
|  | OLD CRAIGIE ROAD | HT |  |  |  |  | 11.2505 | 10.8726 | 10.5505 | 10.3032 | 10.0937 | 9.8695 | 9.6432 | 9.4189 | 9.2084 | 9 | 7.9926 | 7.2432 | 6.6537 | 11.0726 | 10.9411 | 10.7926 | 10.5221 | 10.2958 | 10.0589 | 9.8189 | 9.58 | 9.3579 | 9.1379 | 8.0484 | 7.2158 | 6.5505 | 11.3947 | 11.1653 | 10.9579 | 10.7263 | 10.5021 | 10.2632 | 10.0232 | 9.7842 | 9.5611 | 9.3379 | 8.2611 | 7.4337 | 6.7779
|  | OLD CRAIGIE ROAD | HE |  |  |  |  | 11.4863 | 11.2137 | 10.9779 | 10.8211 | 10.6958 | 10.5579 | 10.4295 | 10.3 | 10.1716 | 10.0453 | 9.46 | 9.0295 | 8.7474 | 11.1874 | 11.1126 | 11.0326 | 10.9537 | 10.8705 | 10.7768 | 10.6832 | 10.5495 | 10.4147 | 10.2842 | 9.6526 | 9.1611 | 8.86 | 11.3947 | 11.1653 | 10.9579 | 10.7263 | 10.5021 | 10.2632 | 10.0232 | 9.7842 | 9.5611 | 9.3379 | 8.2611 | 7.4337 | 6.7779
|  | OLD CRAIGIE ROAD | CF |  |  |  |  | 11.5905 | 11.4526 | 11.3295 | 11.2368 | 11.1568 | 11.0747 | 10.9884 | 10.9021 | 10.8179 | 10.7379 | 10.3632 | 10.0663 | 9.8558 | 11.2242 | 11.18 | 11.1358 | 11.0916 | 11.0474 | 11.0011 | 10.9537 | 10.9074 | 10.8589 | 10.8137 | 10.6105 | 10.3063 | 10.0716 | 11.5737 | 11.5284 | 11.4632 | 11.4 | 11.3411 | 11.28 | 11.2158 | 11.1526 | 11.0895 | 11.0305 | 10.7547 | 10.4874 | 10.2505
| KINTORE | OLDMELDRUM | MINIMUM HEADROOM | NJ 81659 27360 | NO | YES | 0.182 | 8.0822 | 7.7991 | 7.4675 | 28.3433 | 27.8369 | 27.318 | 26.8096 | 26.2706 | 25.6696 | 25.1633 | 23.2033 | 21.2591 | 20.4254 | 7.1233 | 6.8106 | 6.4464 | 26.1685 | 25.6022 | 25.0927 | 24.5959 | 24.0643 | 23.4759 | 23.0001 | 21.4012 | 19.7591 | 18.9917 | 7.5959 | 7.2959 | 6.9454 | 27.2238 | 26.6617 | 26.1069 | 25.5659 | 24.9891 | 24.3459 | 23.8101 | 21.788 | 19.7733 | 18.8922
|  | OLDMELDRUM | EE |  |  |  |  | 8.1654 | 7.9233 | 7.6748 | 28.6633 | 28.2654 | 27.6475 | 26.8601 | 26.3275 | 25.8369 | 25.3591 | 23.2033 | 21.2591 | 20.4254 | 7.2127 | 6.9443 | 6.6759 | 26.5296 | 26.0875 | 25.478 | 24.6896 | 24.2012 | 23.7433 | 23.3033 | 21.4012 | 19.7591 | 18.9917 | 7.6822 | 7.4254 | 7.1643 | 27.5764 | 27.1364 | 26.4712 | 25.6185 | 25.0585 | 24.5396 | 24.0364 | 21.788 | 19.7733 | 18.8922
|  | OLDMELDRUM | HT |  |  |  |  | 8.0822 | 7.7991 | 7.4675 | 28.3433 | 27.8369 | 27.318 | 26.8096 | 26.2706 | 25.6696 | 25.1633 | 23.5896 | 22.4885 | 21.7769 | 7.1233 | 6.8106 | 6.4464 | 26.1685 | 25.6022 | 25.0927 | 24.5959 | 24.0643 | 23.4759 | 23.0001 | 21.5896 | 20.5696 | 19.8548 | 7.5959 | 7.2959 | 6.9454 | 27.2238 | 26.6617 | 26.1069 | 25.5659 | 24.9891 | 24.3459 | 23.8101 | 22.1712 | 21.0133 | 20.2491
|  | OLDMELDRUM | HE |  |  |  |  | 8.278 | 8.0906 | 7.8917 | 28.9096 | 28.5264 | 27.9001 | 27.2622 | 26.8022 | 26.3612 | 26.0264 | 24.6969 | 23.5412 | 22.3422 | 7.3348 | 7.1243 | 6.9033 | 26.7812 | 26.3464 | 25.7327 | 25.0854 | 24.6464 | 24.2264 | 23.9306 | 22.8043 | 21.8391 | 20.8454 | 7.5959 | 7.2959 | 6.9454 | 27.2238 | 26.6617 | 26.1069 | 25.5659 | 24.9891 | 24.3459 | 23.8101 | 22.1712 | 21.0133 | 20.2491
|  | OLDMELDRUM | CF |  |  |  |  | 8.3622 | 8.2548 | 8.1706 | 29.4096 | 29.2969 | 29.0959 | 28.8664 | 28.5696 | 28.3591 | 28.1464 | 27.2748 | 26.5348 | 26.0064 | 7.4264 | 7.3064 | 7.2148 | 27.3433 | 27.2169 | 27.0264 | 26.7991 | 26.4917 | 26.2801 | 26.058 | 25.2222 | 24.5906 | 24.1391 | 7.8717 | 7.7727 | 7.6843 | 28.368 | 28.2469 | 28.0364 | 27.7954 | 27.4796 | 27.2533 | 27.0206 | 26.0922 | 25.3238 | 24.7733
| THURSO | ORMLIE | MINIMUM HEADROOM | ND 10757 67408 | YES | YES | 0 | 15.3111 | 15.1521 | 14.9774 | 14.8068 | 14.6374 | 13.9689 | 13.3037 | 12.6258 | 12.2795 | 11.7047 | 9.8563 | 7.1279 | 4.6363 | 14.4253 | 14.3284 | 14.1758 | 13.9958 | 13.8158 | 13.1189 | 12.4242 | 11.7158 | 11.3189 | 10.7558 | 9.2737 | 6.3842 | 3.9526 | 14.9887 | 14.8476 | 14.6708 | 14.4982 | 14.3255 | 13.6424 | 12.9308 | 12.1845 | 11.7961 | 11.1782 | 9.3045 | 6.3887 | 3.5771
|  | ORMLIE | EE |  |  |  |  | 15.3763 | 15.2489 | 15.1005 | 14.9489 | 14.7984 | 14.6489 | 14.3153 | 13.5837 | 12.8974 | 12.2005 | 9.8563 | 7.1279 | 4.6363 | 14.4579 | 14.3789 | 14.2874 | 14.1558 | 14.0021 | 13.8474 | 13.5568 | 12.8242 | 12.1274 | 11.4189 | 9.2737 | 6.6884 | 3.9526 | 15.0213 | 14.9424 | 14.7961 | 14.6413 | 14.4908 | 14.3392 | 13.9992 | 13.2497 | 12.5276 | 11.7655 | 9.3045 | 6.3887 | 3.5771
|  | ORMLIE | HT |  |  |  |  | 15.3111 | 15.1521 | 14.9774 | 14.8068 | 14.6374 | 13.9689 | 13.3037 | 12.6258 | 12.2795 | 11.7047 | 10.0732 | 7.4132 | 5.3026 | 14.4253 | 14.3284 | 14.1758 | 13.9958 | 13.8158 | 13.1189 | 12.4242 | 11.7158 | 11.3189 | 10.7558 | 9.2779 | 6.3842 | 3.9895 | 14.9887 | 14.8476 | 14.6708 | 14.4982 | 14.3255 | 13.6424 | 12.9308 | 12.1845 | 11.7961 | 11.1782 | 9.4792 | 6.4992 | 4.0571
|  | ORMLIE | HE |  |  |  |  | 15.47 | 15.3932 | 15.3089 | 15.2205 | 15.13 | 14.7879 | 14.4932 | 14.0216 | 13.5553 | 13.0816 | 11.2332 | 8.7689 | 6.1289 | 14.5095 | 14.46 | 14.4053 | 14.3463 | 14.2853 | 14.06 | 13.8095 | 13.3484 | 12.8916 | 12.4242 | 10.6684 | 8.1358 | 5.4158 | 14.9887 | 14.8476 | 14.6708 | 14.4982 | 14.3255 | 13.6424 | 12.9308 | 12.1845 | 11.7961 | 11.1782 | 9.4792 | 6.4992 | 4.0571
|  | ORMLIE | CF |  |  |  |  | 15.5058 | 15.4437 | 15.3795 | 15.3153 | 15.2458 | 15.0889 | 14.9426 | 14.7974 | 14.5668 | 14.3521 | 13.1837 | 11.5479 | 9.7837 | 14.5242 | 14.48 | 14.4368 | 14.3926 | 14.3442 | 14.26 | 14.1811 | 14.0758 | 13.8389 | 13.6116 | 12.4221 | 10.7305 | 8.8084 | 15.0876 | 15.0434 | 14.9992 | 14.9539 | 14.9045 | 14.7813 | 14.6361 | 14.4887 | 14.2529 | 14.0339 | 12.8318 | 11.0318 | 9.0487
| DUNOON | OTTER FERRY | MINIMUM HEADROOM | NR 93352 84713 | YES | YES | 0 | 1.0084 | 0.98842 | 0.96526 | 0.94211 | 0.91579 | 0.83474 | 0.75474 | 0.65263 | 0.56316 | 0.46947 | -0.010526 | -0.54842 | -0.82421 | 1.0063 | 0.98526 | 0.96316 | 0.93895 | 0.90947 | 0.83895 | 0.76842 | 0.69053 | 0.61368 | 0.53579 | 0.12947 | -0.33684 | -0.60632 | 0.97789 | 0.95789 | 0.93474 | 0.91053 | 0.88211 | 0.80526 | 0.72737 | 0.63158 | 0.54526 | 0.45789 | -0.026316 | -0.58211 | -0.88737
|  | OTTER FERRY | EE |  |  |  |  | 1.0158 | 1.0021 | 0.98 | 0.95895 | 0.93895 | 0.85368 | 0.75474 | 0.65263 | 0.56316 | 0.46947 | -0.010526 | -0.54842 | -0.82421 | 1.0158 | 0.99895 | 0.97895 | 0.95789 | 0.93789 | 0.86526 | 0.77789 | 0.69053 | 0.61368 | 0.53579 | 0.12947 | -0.33684 | -0.60632 | 0.98632 | 0.97053 | 0.94947 | 0.92737 | 0.90632 | 0.82526 | 0.72947 | 0.63158 | 0.54526 | 0.45789 | -0.026316 | -0.58211 | -0.88737
|  | OTTER FERRY | HT |  |  |  |  | 1.0084 | 0.98842 | 0.96526 | 0.94211 | 0.91579 | 0.83474 | 0.75684 | 0.67789 | 0.58842 | 0.49895 | 0.14105 | -0.16526 | -0.36737 | 1.0063 | 0.98526 | 0.96316 | 0.93895 | 0.90947 | 0.83895 | 0.76842 | 0.69895 | 0.62 | 0.54105 | 0.22421 | -0.067368 | -0.27053 | 0.97789 | 0.95789 | 0.93474 | 0.91053 | 0.88211 | 0.80526 | 0.72737 | 0.65158 | 0.56421 | 0.47684 | 0.11474 | -0.21684 | -0.43895
|  | OTTER FERRY | HE |  |  |  |  | 1.0253 | 1.0179 | 1.0074 | 0.99789 | 0.98737 | 0.90632 | 0.83579 | 0.76632 | 0.69684 | 0.62 | 0.25263 | -0.12105 | -0.51895 | 1.0284 | 1.0189 | 1.0084 | 0.99789 | 0.98526 | 0.91474 | 0.85579 | 0.79789 | 0.74105 | 0.67368 | 0.35474 | 0.016842 | -0.34632 | 0.97789 | 0.95789 | 0.93474 | 0.91053 | 0.88211 | 0.80526 | 0.72737 | 0.65158 | 0.56421 | 0.47684 | 0.11474 | -0.21684 | -0.43895
|  | OTTER FERRY | CF |  |  |  |  | 1.0316 | 1.0274 | 1.0211 | 1.0158 | 1.0105 | 0.97895 | 0.95053 | 0.92211 | 0.89684 | 0.87368 | 0.70947 | 0.47895 | 0.27368 | 1.0358 | 1.0305 | 1.0242 | 1.0179 | 1.0116 | 0.98211 | 0.95789 | 0.93368 | 0.91158 | 0.89053 | 0.74 | 0.52947 | 0.33368 | 0.99789 | 0.99474 | 0.99053 | 0.98632 | 0.98105 | 0.94947 | 0.92316 | 0.89579 | 0.87158 | 0.84947 | 0.68632 | 0.45895 | 0.24
| DUDHOPE | OVERGATE | MINIMUM HEADROOM | NO 40033 30155 | NO | YES | 0.34 | 41.2747 | 41.2274 | 41.1768 | 41.1042 | 41.0421 | 39.6284 | 39.5968 | 39.5642 | 39.4053 | 39.3147 | 39.1274 | 38.3832 | 38.1295 | 38.4168 | 38.2874 | 38.1547 | 37.8684 | 37.6526 | 35.9663 | 35.6768 | 35.4579 | 35.3337 | 35.2642 | 35.1053 | 34.3126 | 34.0316 | 38.6774 | 38.6026 | 38.5258 | 38.3826 | 38.2689 | 38.1616 | 38.0584 | 37.9163 | 37.8047 | 37.6742 | 37.3174 | 35.4111 | 35.13
|  | OVERGATE | EE |  |  |  |  | 41.2968 | 41.2653 | 41.2295 | 41.8253 | 41.7747 | 41.7137 | 41.6453 | 41.5926 | 41.4105 | 41.1832 | 40.6842 | 40.4568 | 40.2589 | 38.4432 | 38.3768 | 38.2716 | 39.1042 | 39.0611 | 39.0126 | 38.9495 | 38.7947 | 38.6611 | 38.4768 | 37.9221 | 37.6716 | 37.4537 | 38.7005 | 38.6574 | 38.5984 | 39.9658 | 39.9184 | 39.8637 | 39.7911 | 39.7037 | 39.6268 | 39.5132 | 39.09 | 38.8426 | 38.6289
|  | OVERGATE | HT |  |  |  |  | 41.2747 | 41.2274 | 41.1768 | 41.1042 | 41.0421 | 40.9758 | 40.8526 | 40.4989 | 40.2021 | 39.9621 | 39.5874 | 38.3832 | 38.1295 | 38.4168 | 38.2874 | 38.1547 | 37.8684 | 37.6526 | 37.4611 | 37.2821 | 37.0074 | 36.8053 | 36.5926 | 36.1789 | 34.3126 | 34.0316 | 38.6774 | 38.6026 | 38.5258 | 38.3826 | 38.2689 | 38.1616 | 38.0584 | 37.9163 | 37.8047 | 37.6742 | 37.3174 | 35.4111 | 35.13
|  | OVERGATE | HE |  |  |  |  | 41.3042 | 41.28 | 41.2432 | 41.1832 | 41.1326 | 39.6284 | 39.5968 | 39.5642 | 39.4053 | 39.3147 | 39.1274 | 38.9853 | 38.8705 | 38.4505 | 38.4116 | 38.2905 | 38.02 | 37.8189 | 35.9663 | 35.6768 | 35.4579 | 35.3337 | 35.2642 | 35.1053 | 34.9579 | 34.8337 | 38.6774 | 38.6026 | 38.5258 | 38.3826 | 38.2689 | 38.1616 | 38.0584 | 37.9163 | 37.8047 | 37.6742 | 37.3174 | 35.4111 | 35.13
|  | OVERGATE | CF |  |  |  |  | 41.3095 | 41.2916 | 41.2716 | 41.2442 | 41.22 | 41.1947 | 41.1642 | 41.1232 | 41.0937 | 41.0611 | 40.9484 | 41.5463 | 41.5137 | 38.4621 | 38.4421 | 38.4074 | 38.3179 | 38.2579 | 38.1979 | 38.1063 | 37.9326 | 37.8474 | 37.7389 | 37.46 | 38.86 | 38.8326 | 38.7153 | 38.6974 | 38.6721 | 38.6237 | 38.5879 | 38.5511 | 38.5005 | 38.4163 | 38.3668 | 38.31 | 38.1416 | 39.7005 | 39.6689
| CASSLEY | OVERSCAIG | MINIMUM HEADROOM | NC 39711 25382 | YES | YES | 0 | 0.15211 | 0.15105 | 0.14684 | 0.14053 | 0.13421 | 0.080526 | 0.015263 | -0.051053 | -0.11526 | -0.22474 | -0.80263 | -1.5868 | -2.2005 | 0.15 | 0.14895 | 0.14579 | 0.14053 | 0.13632 | 0.083684 | 0.022632 | -0.043684 | -0.10368 | -0.21632 | -0.83316 | -1.7153 | -2.3521 | 0.15 | 0.14789 | 0.14368 | 0.13737 | 0.13105 | 0.09 | 0.040526 | -0.012105 | -0.058421 | -0.19947 | -0.91421 | -1.8174 | -2.4774
|  | OVERSCAIG | EE |  |  |  |  | 0.15211 | 0.15105 | 0.14684 | 0.14053 | 0.13421 | 0.094211 | 0.044737 | -0.0068421 | -0.052105 | -0.14158 | -0.79947 | -1.5447 | -2.2005 | 0.15 | 0.14895 | 0.14579 | 0.14053 | 0.13632 | 0.10368 | 0.064737 | 0.023684 | -0.012105 | -0.099474 | -0.77105 | -1.5405 | -2.2763 | 0.15 | 0.14789 | 0.14368 | 0.13737 | 0.13105 | 0.09 | 0.040526 | -0.012105 | -0.058421 | -0.15421 | -0.88579 | -1.7184 | -2.4774
|  | OVERSCAIG | HT |  |  |  |  | 0.15211 | 0.15211 | 0.14789 | 0.14684 | 0.14158 | 0.11 | 0.076316 | 0.019474 | -0.044737 | -0.17316 | -0.80263 | -1.5868 | -2.1426 | 0.15 | 0.15 | 0.14579 | 0.14368 | 0.13947 | 0.11526 | 0.088947 | 0.035263 | -0.024737 | -0.15737 | -0.83316 | -1.7153 | -2.3521 | 0.15 | 0.14895 | 0.14579 | 0.14474 | 0.13842 | 0.10789 | 0.073158 | 0.012105 | -0.056316 | -0.19947 | -0.91421 | -1.8174 | -2.4626
|  | OVERSCAIG | HE |  |  |  |  | 0.15211 | 0.15211 | 0.15 | 0.15 | 0.14895 | 0.080526 | 0.015263 | -0.051053 | -0.11526 | -0.22474 | -0.67316 | -1.2784 | -1.9416 | 0.15 | 0.15 | 0.14789 | 0.14789 | 0.14789 | 0.083684 | 0.022632 | -0.043684 | -0.10368 | -0.21632 | -0.67632 | -1.3247 | -2.0363 | 0.15 | 0.14895 | 0.14579 | 0.14474 | 0.13842 | 0.10789 | 0.073158 | 0.012105 | -0.056316 | -0.19947 | -0.91421 | -1.8174 | -2.4626
|  | OVERSCAIG | CF |  |  |  |  | 0.15316 | 0.15316 | 0.15105 | 0.15105 | 0.15 | 0.13421 | 0.12053 | 0.071053 | 0.022632 | -0.036316 | -0.28053 | -0.66474 | -1.1195 | 0.15105 | 0.15105 | 0.15 | 0.14895 | 0.14895 | 0.13632 | 0.12579 | 0.072105 | 0.020526 | -0.045789 | -0.30684 | -0.72053 | -1.2289 | 0.15105 | 0.15105 | 0.14895 | 0.14789 | 0.14789 | 0.13211 | 0.11842 | 0.062632 | 0.0078947 | -0.059474 | -0.33526 | -0.77105 | -1.2942
| KINTORE | PARK | MINIMUM HEADROOM | NO 79107 99434 | YES | YES | 0 | 1.3821 | 1.3368 | 1.2737 | 1.1768 | 1.0579 | 0.73895 | 0.38 | -0.012632 | -0.35263 | -0.84947 | -4.4189 | -8.6589 | -12.0705 | 1.0747 | 0.99053 | 0.88737 | 0.76105 | 0.62842 | 0.34842 | 0.084211 | -0.23263 | -0.50421 | -1.1084 | -4.7284 | -9.3021 | -12.5516 | 1.1768 | 1.0989 | 1 | 0.88 | 0.75579 | 0.42105 | 0.042105 | -0.36842 | -0.71895 | -1.1653 | -5.1232 | -9.8453 | -13.6442
|  | PARK | EE |  |  |  |  | 1.4021 | 1.3674 | 1.3116 | 1.2505 | 1.1653 | 0.80632 | 0.38 | -0.012632 | -0.35263 | -0.70211 | -4.4189 | -8.6589 | -12.0705 | 1.1126 | 1.0505 | 0.96737 | 0.86842 | 0.76105 | 0.45263 | 0.084211 | -0.23263 | -0.50421 | -0.78842 | -4.46 | -8.72 | -12.4958 | 1.2126 | 1.1547 | 1.0716 | 0.97263 | 0.86737 | 0.48947 | 0.042105 | -0.36842 | -0.71895 | -1.0779 | -5.0737 | -9.7389 | -13.6442
|  | PARK | HT |  |  |  |  | 1.3821 | 1.3368 | 1.2737 | 1.1768 | 1.0579 | 0.73895 | 0.44316 | 0.14421 | -0.20632 | -0.79474 | -4.3505 | -8.4811 | -11.3411 | 1.0747 | 0.99053 | 0.88737 | 0.76105 | 0.62842 | 0.34842 | 0.093684 | -0.16 | -0.44842 | -1.0168 | -4.7284 | -9.3021 | -12.5516 | 1.1768 | 1.0989 | 1 | 0.88 | 0.75579 | 0.42105 | 0.11158 | -0.2 | -0.56105 | -1.1653 | -5.1232 | -9.8453 | -13.1484
|  | PARK | HE |  |  |  |  | 1.4295 | 1.4074 | 1.3779 | 1.3453 | 1.3095 | 0.96211 | 0.61368 | 0.18737 | -0.22105 | -0.84947 | -3.4726 | -6.8084 | -10.4368 | 1.1642 | 1.1274 | 1.0747 | 1.0042 | 0.92737 | 0.61368 | 0.30105 | -0.10105 | -0.47474 | -1.1084 | -3.7032 | -7.1779 | -10.9663 | 1.1768 | 1.0989 | 1 | 0.88 | 0.75579 | 0.42105 | 0.11158 | -0.2 | -0.56105 | -1.1653 | -5.1232 | -9.8453 | -13.1484
|  | PARK | CF |  |  |  |  | 1.4442 | 1.4305 | 1.4158 | 1.3989 | 1.3811 | 1.2674 | 1.1632 | 1.0147 | 0.74632 | 0.43053 | -0.96105 | -3.0726 | -5.4716 | 1.1895 | 1.1653 | 1.1411 | 1.1095 | 1.0758 | 0.96105 | 0.84316 | 0.66842 | 0.37579 | 0.027368 | -1.4137 | -3.6274 | -6.2579 | 1.2832 | 1.2611 | 1.2368 | 1.2074 | 1.1747 | 1.0316 | 0.89158 | 0.70316 | 0.42 | 0.085263 | -1.4642 | -3.8284 | -6.5632
| ALNESS | PEDDIESTON | MINIMUM HEADROOM | NH 74198 63656 | NO | YES | 0 | 2.8611 | 2.8358 | 2.8074 | 2.7768 | 2.7453 | 2.6432 | 2.5453 | 2.4463 | 2.3421 | 2.2358 | 1.7221 | 1.1916 | 0.95895 | 2.66 | 2.6116 | 2.5621 | 2.5105 | 2.4621 | 2.3642 | 2.2684 | 2.1726 | 2.0758 | 1.9768 | 1.5337 | 1.0537 | 0.83474 | 2.6853 | 2.6389 | 2.5905 | 2.54 | 2.4926 | 2.3832 | 2.2768 | 2.1695 | 2.0579 | 1.9442 | 1.4 | 0.83053 | 0.58316
|  | PEDDIESTON | EE |  |  |  |  | 2.8705 | 2.8505 | 2.8253 | 2.7968 | 2.7695 | 2.6874 | 2.5779 | 2.46 | 2.3547 | 2.2547 | 1.7221 | 1.1916 | 0.95895 | 2.6811 | 2.6442 | 2.6021 | 2.56 | 2.5168 | 2.4232 | 2.3211 | 2.2116 | 2.1137 | 2.0221 | 1.5337 | 1.0537 | 0.83474 | 2.7053 | 2.6695 | 2.6274 | 2.5853 | 2.5421 | 2.4358 | 2.3158 | 2.1905 | 2.0779 | 1.9716 | 1.4 | 0.83053 | 0.58316
|  | PEDDIESTON | HT |  |  |  |  | 2.8611 | 2.8358 | 2.8074 | 2.7768 | 2.7453 | 2.6432 | 2.5453 | 2.4463 | 2.3421 | 2.2358 | 1.8053 | 1.4958 | 1.3011 | 2.66 | 2.6116 | 2.5621 | 2.5105 | 2.4621 | 2.3642 | 2.2684 | 2.1726 | 2.0758 | 1.9768 | 1.5695 | 1.2758 | 1.0811 | 2.6853 | 2.6389 | 2.5905 | 2.54 | 2.4926 | 2.3832 | 2.2768 | 2.1695 | 2.0579 | 1.9442 | 1.4811 | 1.1547 | 0.94632
|  | PEDDIESTON | HE |  |  |  |  | 2.8853 | 2.8716 | 2.8558 | 2.84 | 2.8211 | 2.7389 | 2.6684 | 2.5989 | 2.5295 | 2.4589 | 2.1105 | 1.7905 | 1.4284 | 2.7126 | 2.6895 | 2.6642 | 2.6389 | 2.6116 | 2.5263 | 2.4516 | 2.3768 | 2.3042 | 2.2326 | 1.9221 | 1.6326 | 1.2937 | 2.6853 | 2.6389 | 2.5905 | 2.54 | 2.4926 | 2.3832 | 2.2768 | 2.1695 | 2.0579 | 1.9442 | 1.4811 | 1.1547 | 0.94632
|  | PEDDIESTON | CF |  |  |  |  | 2.8926 | 2.8842 | 2.8758 | 2.8674 | 2.8579 | 2.8253 | 2.7947 | 2.7653 | 2.74 | 2.7179 | 2.58 | 2.3842 | 2.2253 | 2.7263 | 2.7116 | 2.6958 | 2.6811 | 2.6642 | 2.6263 | 2.5905 | 2.5558 | 2.5253 | 2.4979 | 2.3368 | 2.16 | 2.0063 | 2.7484 | 2.7337 | 2.7189 | 2.7032 | 2.6874 | 2.6442 | 2.6053 | 2.5653 | 2.5305 | 2.5011 | 2.3179 | 2.1095 | 1.9358
| PETERHEAD GRANGE | PETERHEAD GRANGE | MINIMUM HEADROOM | NK 11738 46516 | NO | YES | 0.21 | 24.5816 | 24.3332 | 24.0668 | 23.7963 | 23.4647 | 22.6458 | 21.8721 | 21.1511 | 20.3616 | 19.5111 | 15.5026 | 12.0437 | 8.9311 | 23.6805 | 23.29 | 22.6742 | 21.8342 | 21.0532 | 20.21 | 19.4163 | 18.6847 | 17.89 | 17.0205 | 12.77 | 8.9816 | 5.4395 | 23.5932 | 23.2384 | 22.71 | 22.01 | 21.3563 | 20.5911 | 19.8679 | 19.1921 | 18.4584 | 17.6689 | 13.9816 | 10.0468 | 6.4247
|  | PETERHEAD GRANGE | EE |  |  |  |  | 24.6805 | 24.4837 | 24.2626 | 24.0311 | 23.7932 | 23.3668 | 22.5732 | 21.8974 | 21.2721 | 20.63 | 16.4826 | 12.2468 | 9.0374 | 23.79 | 23.5247 | 23.1816 | 22.5089 | 21.8889 | 21.1047 | 20.2374 | 19.5889 | 18.9837 | 18.3574 | 14.1216 | 9.7489 | 6.1626 | 23.7005 | 23.4521 | 23.1384 | 22.5742 | 22.0479 | 21.3289 | 20.5353 | 19.9058 | 19.3237 | 18.7268 | 14.9247 | 10.4879 | 6.7732
|  | PETERHEAD GRANGE | HT |  |  |  |  | 24.5816 | 24.3332 | 24.0668 | 23.7963 | 23.4647 | 22.6458 | 21.8721 | 21.1511 | 20.3616 | 19.5111 | 15.5026 | 12.0437 | 8.9311 | 23.6805 | 23.29 | 22.6742 | 21.8342 | 21.0532 | 20.21 | 19.4163 | 18.6847 | 17.89 | 17.0205 | 12.77 | 8.9816 | 5.4395 | 23.5932 | 23.2384 | 22.71 | 22.01 | 21.3563 | 20.5911 | 19.8679 | 19.1921 | 18.4584 | 17.6689 | 13.9816 | 10.0468 | 6.4247
|  | PETERHEAD GRANGE | HE |  |  |  |  | 24.8142 | 24.6816 | 24.5332 | 24.3721 | 24.2005 | 23.8079 | 23.4668 | 22.9384 | 22.3468 | 21.73 | 18.4942 | 15.5995 | 12.7058 | 23.9237 | 23.7542 | 23.5574 | 23.1868 | 22.6605 | 21.9416 | 21.2153 | 20.6574 | 20.0668 | 19.4437 | 16.0689 | 13.03 | 9.9995 | 23.5932 | 23.2384 | 22.71 | 22.01 | 21.3563 | 20.5911 | 19.8679 | 19.1921 | 18.4584 | 17.6689 | 13.9816 | 10.0468 | 6.4247
|  | PETERHEAD GRANGE | CF |  |  |  |  | 24.8879 | 24.8089 | 24.7258 | 24.6395 | 24.5521 | 24.3858 | 24.2289 | 24.0732 | 23.9258 | 23.7984 | 22.7205 | 20.4826 | 18.5195 | 24.0089 | 23.9247 | 23.8342 | 23.7395 | 23.6416 | 23.4468 | 23.2332 | 23.0016 | 22.7616 | 22.4995 | 20.4268 | 18.0153 | 15.8511 | 23.9163 | 23.8342 | 23.7447 | 23.6511 | 23.5563 | 23.3584 | 23.1511 | 22.93 | 22.7058 | 22.4721 | 20.7037 | 18.6784 | 16.91
| PETERHEAD GRANGE | PETERHEAD NORTH STREET | MINIMUM HEADROOM | NK 13470 46450 | NO | YES | 0.332 | 24.7048 | 24.668 | 24.6291 | 24.5185 | 24.3912 | 24.2617 | 24.1322 | 24.0059 | 23.8827 | 23.7585 | 23.4196 | 22.9227 | 22.4585 | 23.1312 | 23.0248 | 22.9175 | 22.8122 | 22.7069 | 22.5975 | 22.468 | 22.3291 | 22.1933 | 22.0575 | 21.8069 | 21.2469 | 20.7206 | 24.0469 | 24.0006 | 23.8596 | 23.7227 | 23.5838 | 23.4427 | 23.3038 | 23.1659 | 23.0322 | 22.8996 | 22.6522 | 22.0996 | 21.5817
|  | PETERHEAD NORTH STREET | EE |  |  |  |  | 24.7217 | 24.6943 | 24.6638 | 24.6322 | 24.5701 | 24.4691 | 24.368 | 24.2701 | 24.1712 | 24.0764 | 23.6269 | 23.4406 | 23.0912 | 23.1512 | 23.1017 | 23.0196 | 22.9375 | 22.8543 | 22.7691 | 22.6859 | 22.6048 | 22.5185 | 22.4133 | 21.9206 | 21.8427 | 21.4469 | 24.0638 | 24.0364 | 23.9943 | 23.8859 | 23.7785 | 23.6691 | 23.5596 | 23.4543 | 23.3491 | 23.2459 | 22.7554 | 22.6754 | 22.2859
|  | PETERHEAD NORTH STREET | HT |  |  |  |  | 24.7048 | 24.668 | 24.6291 | 24.5185 | 24.3912 | 24.2617 | 24.1322 | 24.0059 | 23.8827 | 23.7585 | 23.4196 | 22.9227 | 22.4585 | 23.1312 | 23.0248 | 22.9175 | 22.8122 | 22.7069 | 22.5975 | 22.468 | 22.3291 | 22.1933 | 22.0575 | 21.8069 | 21.2469 | 20.7206 | 24.0469 | 24.0006 | 23.8596 | 23.7227 | 23.5838 | 23.4427 | 23.3038 | 23.1659 | 23.0322 | 22.8996 | 22.6522 | 22.0996 | 21.5817
|  | PETERHEAD NORTH STREET | HE |  |  |  |  | 24.7354 | 24.7133 | 24.688 | 24.6617 | 24.6333 | 24.5985 | 24.568 | 24.5375 | 24.5069 | 24.4448 | 24.1796 | 23.9575 | 23.7575 | 23.1648 | 23.1427 | 23.1175 | 23.0764 | 23.0185 | 22.9575 | 22.9006 | 22.8438 | 22.7901 | 22.7385 | 22.5217 | 22.2975 | 22.0754 | 24.0469 | 24.0006 | 23.8596 | 23.7227 | 23.5838 | 23.4427 | 23.3038 | 23.1659 | 23.0322 | 22.8996 | 22.6522 | 22.0996 | 21.5817
|  | PETERHEAD NORTH STREET | CF |  |  |  |  | 24.7427 | 24.7269 | 24.7112 | 24.6943 | 24.6775 | 24.6575 | 24.6396 | 24.6206 | 24.6017 | 24.5838 | 24.4427 | 24.2659 | 24.1154 | 23.1722 | 23.1564 | 23.1406 | 23.1238 | 23.1069 | 23.0775 | 23.0385 | 22.9996 | 22.9596 | 22.9206 | 22.7396 | 22.5975 | 22.4596 | 24.0848 | 24.0691 | 24.0533 | 24.0364 | 24.0196 | 24.0006 | 23.9806 | 23.9606 | 23.9322 | 23.8827 | 23.6491 | 23.4554 | 23.288
| FORT WILLIAM | PINEGROVE | MINIMUM HEADROOM | NN 10496 73556 | NO | NO | 0 | 13.9474 | 13.7389 | 13.5537 | 13.3558 | 13.1442 | 12.8842 | 12.6295 | 12.38 | 12.1337 | 11.9884 | 11.3389 | 10.8379 | 10.4368 | 12.3316 | 12.2526 | 12.1758 | 12.0979 | 11.8758 | 11.5958 | 11.32 | 11.0495 | 10.7832 | 10.6389 | 9.9663 | 9.4358 | 8.9968 | 12.7379 | 12.6684 | 12.5516 | 12.3705 | 12.1579 | 11.9011 | 11.6495 | 11.3916 | 11.1189 | 10.9663 | 10.2642 | 9.7158 | 9.2705
|  | PINEGROVE | EE |  |  |  |  | 13.9768 | 13.8232 | 13.6642 | 13.4916 | 13.2989 | 13.0674 | 12.8337 | 12.5968 | 12.3674 | 12.2453 | 11.6358 | 11.12 | 10.7821 | 12.3589 | 12.2979 | 12.2347 | 12.1684 | 12.0463 | 11.7979 | 11.5474 | 11.2958 | 11.0495 | 10.9295 | 10.3253 | 9.82 | 9.4611 | 12.7642 | 12.7105 | 12.6516 | 12.4958 | 12.3137 | 12.0853 | 11.8526 | 11.6189 | 11.3758 | 11.2463 | 10.5989 | 10.0453 | 9.6726
|  | PINEGROVE | HT |  |  |  |  | 13.9474 | 13.7389 | 13.5537 | 13.3558 | 13.1442 | 12.8842 | 12.6295 | 12.38 | 12.1337 | 11.9884 | 11.3389 | 10.8379 | 10.4368 | 12.3316 | 12.2526 | 12.1758 | 12.0979 | 11.8758 | 11.5958 | 11.32 | 11.0495 | 10.7832 | 10.6389 | 9.9663 | 9.4358 | 8.9968 | 12.7379 | 12.6684 | 12.5516 | 12.3705 | 12.1579 | 11.9011 | 11.6495 | 11.3916 | 11.1189 | 10.9663 | 10.2642 | 9.7158 | 9.2705
|  | PINEGROVE | HE |  |  |  |  | 14.0168 | 13.9326 | 13.8084 | 13.6663 | 13.5074 | 13.3011 | 13.1053 | 12.9095 | 12.7189 | 12.6326 | 12.2884 | 12.0347 | 11.7958 | 12.3958 | 12.3505 | 12.3042 | 12.2547 | 12.2 | 12.0516 | 11.84 | 11.6326 | 11.4253 | 11.3421 | 11.0147 | 10.7768 | 10.5547 | 12.7379 | 12.6684 | 12.5516 | 12.3705 | 12.1579 | 11.9011 | 11.6495 | 11.3916 | 11.1189 | 10.9663 | 10.2642 | 9.7158 | 9.2705
|  | PINEGROVE | CF |  |  |  |  | 14.0358 | 14.0105 | 13.9779 | 13.9253 | 13.8421 | 13.7432 | 13.6379 | 13.5316 | 13.4179 | 13.3611 | 13.1095 | 12.9116 | 12.7621 | 12.4179 | 12.3905 | 12.3632 | 12.3347 | 12.3063 | 12.2716 | 12.2379 | 12.2032 | 12.1684 | 12.1274 | 11.8726 | 11.6789 | 11.5295 | 12.8179 | 12.7937 | 12.7695 | 12.7432 | 12.7179 | 12.6821 | 12.6326 | 12.5358 | 12.4337 | 12.3779 | 12.1316 | 11.9379 | 11.7926
| TUMMEL BRIDGE | PITLOCHRY | MINIMUM HEADROOM | NN 95756 58991 | NO | YES | 0 | 5.7951 | 5.652 | 5.4867 | 5.3141 | 5.133 | 4.7678 | 4.4257 | 4.0846 | 3.7078 | 3.3783 | 1.8436 | -0.38171 | -1.8375 | 5.5416 | 5.3837 | 5.2047 | 5.0153 | 4.8184 | 4.4816 | 4.1637 | 3.8468 | 3.5079 | 3.2226 | 2.0163 | -0.079474 | -1.6416 | 5.4999 | 5.4284 | 5.2568 | 5.0652 | 4.8641 | 4.4915 | 4.1389 | 3.7905 | 3.4073 | 3.0841 | 1.5684 | -0.80112 | -2.4948
|  | PITLOCHRY | EE |  |  |  |  | 5.852 | 5.7372 | 5.5993 | 5.453 | 5.3014 | 4.9372 | 4.5393 | 4.1393 | 3.7793 | 3.4636 | 1.8436 | -0.38171 | -1.8375 | 5.6047 | 5.4763 | 5.33 | 5.1742 | 5.01 | 4.6932 | 4.3479 | 4.0016 | 3.6753 | 3.4026 | 2.0163 | -0.079474 | -1.6416 | 5.5305 | 5.4747 | 5.381 | 5.2189 | 5.0494 | 4.682 | 4.2831 | 3.8831 | 3.5199 | 3.2136 | 1.5684 | -0.80112 | -2.4948
|  | PITLOCHRY | HT |  |  |  |  | 5.7951 | 5.652 | 5.4867 | 5.3141 | 5.133 | 4.7678 | 4.4257 | 4.0846 | 3.7078 | 3.3783 | 2.092 | 0.27303 | -0.90487 | 5.5416 | 5.3837 | 5.2047 | 5.0153 | 4.8184 | 4.4816 | 4.1637 | 3.8468 | 3.5079 | 3.2226 | 2.0784 | 0.084737 | -1.2721 | 5.4999 | 5.4284 | 5.2568 | 5.0652 | 4.8641 | 4.4915 | 4.1389 | 3.7905 | 3.4073 | 3.0841 | 1.7852 | -0.3327 | -1.7464
|  | PITLOCHRY | HE |  |  |  |  | 5.8888 | 5.8446 | 5.7541 | 5.6551 | 5.5436 | 5.1962 | 4.8951 | 4.5951 | 4.2983 | 4.0541 | 2.7899 | 1.1488 | -0.60592 | 5.6416 | 5.5963 | 5.4963 | 5.3847 | 5.2626 | 4.9742 | 4.71 | 4.4458 | 4.1774 | 3.9679 | 2.8395 | 1.2184 | -0.53632 | 5.4999 | 5.4284 | 5.2568 | 5.0652 | 4.8641 | 4.4915 | 4.1389 | 3.7905 | 3.4073 | 3.0841 | 1.7852 | -0.3327 | -1.7464
|  | PITLOCHRY | CF |  |  |  |  | 5.9099 | 5.8899 | 5.8657 | 5.812 | 5.7551 | 5.613 | 5.4793 | 5.3446 | 5.2172 | 5.133 | 4.4909 | 3.4604 | 2.433 | 5.6626 | 5.6426 | 5.6205 | 5.5605 | 5.4974 | 5.3753 | 5.2584 | 5.1395 | 5.0216 | 4.9458 | 4.3479 | 3.31 | 2.1932 | 5.5884 | 5.5684 | 5.5452 | 5.521 | 5.4968 | 5.4052 | 5.2705 | 5.1315 | 4.9989 | 4.9147 | 4.2515 | 3.142 | 1.9515
| ARDMORE | POLLACHAR | MINIMUM HEADROOM | NF 75073 14513 | NO | YES | 0 | 3.8726 | 3.7758 | 3.6821 | 3.5874 | 3.4926 | 3.3958 | 3.3032 | 3.2137 | 3.1274 | 3.0453 | 1.9042 | 1.6442 | 1.4232 | 3.6958 | 3.5884 | 3.4779 | 3.3684 | 3.2589 | 3.1484 | 3.0421 | 2.9411 | 2.8421 | 2.7484 | 1.7632 | 1.4453 | 1.1705 | 3.5095 | 3.4526 | 3.3958 | 3.3368 | 3.2768 | 3.2116 | 3.1495 | 3.0895 | 3 | 2.9063 | 1.7284 | 1.4105 | 1.1347
|  | POLLACHAR | EE |  |  |  |  | 3.9105 | 3.8347 | 3.7579 | 3.68 | 3.6011 | 3.5242 | 3.4484 | 3.3758 | 3.3084 | 3.2432 | 3.4884 | 3.2916 | 3.1316 | 3.7137 | 3.66 | 3.5716 | 3.4821 | 3.3916 | 3.3032 | 3.2179 | 3.1358 | 3.0579 | 2.9842 | 3.7211 | 3.4821 | 3.2811 | 3.5274 | 3.4811 | 3.4326 | 3.3821 | 3.3295 | 3.2768 | 3.2253 | 3.1758 | 3.1295 | 3.0853 | 3.4695 | 3.2758 | 3.0789
|  | POLLACHAR | HT |  |  |  |  | 3.8726 | 3.7758 | 3.6821 | 3.5874 | 3.4926 | 3.3958 | 3.3032 | 3.2137 | 3.1274 | 3.0453 | 1.9042 | 1.6442 | 1.4232 | 3.6958 | 3.5884 | 3.4779 | 3.3684 | 3.2589 | 3.1484 | 3.0421 | 2.9411 | 2.8421 | 2.7484 | 1.7632 | 1.4453 | 1.1705 | 3.5095 | 3.4526 | 3.3958 | 3.3368 | 3.2768 | 3.2116 | 3.1495 | 3.0895 | 3 | 2.9063 | 1.7284 | 1.4105 | 1.1347
|  | POLLACHAR | HE |  |  |  |  | 3.9716 | 3.9232 | 3.8737 | 3.8211 | 3.7653 | 3.7105 | 3.66 | 3.6095 | 3.5621 | 3.5179 | 2.9505 | 2.8474 | 2.7758 | 3.7463 | 3.7147 | 3.6811 | 3.6442 | 3.5884 | 3.5274 | 3.4716 | 3.4158 | 3.3632 | 3.3137 | 2.8316 | 2.7074 | 2.6168 | 3.5095 | 3.4526 | 3.3958 | 3.3368 | 3.2768 | 3.2116 | 3.1495 | 3.0895 | 3 | 2.9063 | 1.7284 | 1.4105 | 1.1347
|  | POLLACHAR | CF |  |  |  |  | 4.0021 | 3.9747 | 3.9453 | 3.9147 | 3.8842 | 3.8547 | 3.8242 | 3.7947 | 3.7642 | 3.7326 | 3.5989 | 3.5116 | 3.4474 | 3.7642 | 3.7474 | 3.7284 | 3.7095 | 3.6905 | 3.6716 | 3.6516 | 3.6179 | 3.5821 | 3.5474 | 3.3916 | 3.2842 | 3.2021 | 3.5779 | 3.5611 | 3.5421 | 3.5232 | 3.5042 | 3.4853 | 3.4653 | 3.4463 | 3.4263 | 3.4063 | 3.3232 | 3.2821 | 3.2611
| FORT WILLIAM | POOR HOUSE | MINIMUM HEADROOM | NM 71766 70148 | YES | NO | 0 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10316 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.096842 | 0.093684 | 0.089474 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.092632 | 0.089474 | 0.085263 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.093684 | 0.090526 | 0.086316
|  | POOR HOUSE | EE |  |  |  |  | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10316 | 0.10211 | 0.10105 | 0.098947 | 0.096842 | 0.093684 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.098947 | 0.095789 | 0.092632 | 0.090526 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.1 | 0.096842 | 0.093684 | 0.091579
|  | POOR HOUSE | HT |  |  |  |  | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10316 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.096842 | 0.093684 | 0.089474 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.10105 | 0.098947 | 0.098947 | 0.097895 | 0.096842 | 0.092632 | 0.089474 | 0.085263 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.093684 | 0.090526 | 0.086316
|  | POOR HOUSE | HE |  |  |  |  | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10211 | 0.10105 | 0.1 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.1 | 0.098947 | 0.096842 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.1 | 0.1 | 0.098947 | 0.097895 | 0.093684 | 0.090526 | 0.086316
|  | POOR HOUSE | CF |  |  |  |  | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10316 | 0.10211 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.1 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10105
| PORT ANN | PORT ASKAIG | MINIMUM HEADROOM | NR 42082 68818 | NO | YES | 0 | 1.6313 | 1.6155 | 1.5997 | 1.5818 | 1.5439 | 1.5028 | 1.4586 | 1.4186 | 1.3797 | 1.3428 | 1.1934 | 1.0144 | 0.89021 | 1.4997 | 1.4828 | 1.4618 | 1.4239 | 1.3818 | 1.3376 | 1.2881 | 1.2439 | 1.1997 | 1.1597 | 0.99126 | 0.80389 | 0.66074 | 1.5755 | 1.5597 | 1.5292 | 1.4902 | 1.4492 | 1.406 | 1.3586 | 1.3144 | 1.2723 | 1.2334 | 1.0692 | 0.87758 | 0.73968
|  | PORT ASKAIG | EE |  |  |  |  | 1.6376 | 1.6249 | 1.6123 | 1.5986 | 1.5839 | 1.5639 | 1.5334 | 1.4997 | 1.4702 | 1.4397 | 1.3144 | 1.1702 | 1.0765 | 1.5071 | 1.4934 | 1.4797 | 1.4639 | 1.4386 | 1.4049 | 1.3723 | 1.3355 | 1.3018 | 1.2681 | 1.1281 | 0.97863 | 0.87126 | 1.5818 | 1.5692 | 1.5565 | 1.5323 | 1.5049 | 1.4723 | 1.4397 | 1.4039 | 1.3702 | 1.3376 | 1.2018 | 1.0481 | 0.94389
|  | PORT ASKAIG | HT |  |  |  |  | 1.6313 | 1.6155 | 1.5997 | 1.5818 | 1.5439 | 1.5028 | 1.4586 | 1.4186 | 1.3797 | 1.3428 | 1.1934 | 1.0144 | 0.89021 | 1.4997 | 1.4828 | 1.4618 | 1.4239 | 1.3818 | 1.3376 | 1.2881 | 1.2439 | 1.1997 | 1.1597 | 0.99126 | 0.80389 | 0.66074 | 1.5755 | 1.5597 | 1.5292 | 1.4902 | 1.4492 | 1.406 | 1.3586 | 1.3144 | 1.2723 | 1.2334 | 1.0692 | 0.87758 | 0.73968
|  | PORT ASKAIG | HE |  |  |  |  | 1.646 | 1.6386 | 1.6292 | 1.6197 | 1.6092 | 1.5986 | 1.5892 | 1.5786 | 1.5702 | 1.5618 | 1.4881 | 1.4092 | 1.3607 | 1.5155 | 1.5081 | 1.4986 | 1.4881 | 1.4776 | 1.466 | 1.4565 | 1.4439 | 1.426 | 1.4039 | 1.3228 | 1.2407 | 1.1849 | 1.5755 | 1.5597 | 1.5292 | 1.4902 | 1.4492 | 1.406 | 1.3586 | 1.3144 | 1.2723 | 1.2334 | 1.0692 | 0.87758 | 0.73968
|  | PORT ASKAIG | CF |  |  |  |  | 1.6513 | 1.6471 | 1.6418 | 1.6376 | 1.6323 | 1.6281 | 1.6228 | 1.6176 | 1.6134 | 1.6081 | 1.586 | 1.5386 | 1.5007 | 1.5207 | 1.5165 | 1.5113 | 1.5071 | 1.5018 | 1.4976 | 1.4913 | 1.486 | 1.4807 | 1.4755 | 1.4281 | 1.3744 | 1.3302 | 1.5955 | 1.5913 | 1.586 | 1.5818 | 1.5765 | 1.5723 | 1.5671 | 1.5618 | 1.5576 | 1.5523 | 1.4944 | 1.4418 | 1.3997
| PORT ANN | PORT ELLEN | MINIMUM HEADROOM | NR 36459 45513 | YES | YES | 0 | 4.8895 | 4.7937 | 4.7053 | 4.6516 | 4.6021 | 4.5579 | 4.5137 | 4.4737 | 4.4326 | 4.3947 | 4.2295 | 4.0589 | 3.9063 | 4.5326 | 4.42 | 4.3063 | 4.2432 | 4.1832 | 4.1326 | 4.0832 | 4.0368 | 3.9905 | 3.9484 | 3.7484 | 3.5316 | 3.3326 | 4.8589 | 4.8326 | 4.7442 | 4.6853 | 4.6305 | 4.5832 | 4.5368 | 4.4926 | 4.4495 | 4.4095 | 4.2253 | 4.0305 | 3.8368
|  | PORT ELLEN | EE |  |  |  |  | 4.9074 | 4.8221 | 4.7411 | 4.6968 | 4.6537 | 4.6179 | 4.5842 | 4.5516 | 4.5211 | 4.4895 | 4.3611 | 4.2495 | 4.1368 | 4.5526 | 4.4526 | 4.3495 | 4.2968 | 4.2463 | 4.2053 | 4.1674 | 4.1305 | 4.0947 | 4.06 | 3.9116 | 3.7716 | 3.6242 | 4.8674 | 4.8474 | 4.7842 | 4.7358 | 4.6884 | 4.6505 | 4.6137 | 4.5789 | 4.5453 | 4.5126 | 4.3737 | 4.2474 | 4.1168
|  | PORT ELLEN | HT |  |  |  |  | 4.8895 | 4.7937 | 4.7053 | 4.6516 | 4.6021 | 4.5579 | 4.5137 | 4.4737 | 4.4326 | 4.3947 | 4.2295 | 4.0589 | 3.9063 | 4.5326 | 4.42 | 4.3063 | 4.2432 | 4.1832 | 4.1326 | 4.0832 | 4.0368 | 3.9905 | 3.9484 | 3.7484 | 3.5316 | 3.3326 | 4.8589 | 4.8326 | 4.7442 | 4.6853 | 4.6305 | 4.5832 | 4.5368 | 4.4926 | 4.4495 | 4.4095 | 4.2253 | 4.0305 | 3.8368
|  | PORT ELLEN | HE |  |  |  |  | 4.9337 | 4.8611 | 4.7916 | 4.7589 | 4.7274 | 4.7021 | 4.6779 | 4.6547 | 4.6347 | 4.6147 | 4.5411 | 4.4926 | 4.4589 | 4.5832 | 4.4958 | 4.4105 | 4.3716 | 4.3337 | 4.3063 | 4.2789 | 4.2537 | 4.2316 | 4.2095 | 4.1253 | 4.0674 | 4.0242 | 4.8589 | 4.8326 | 4.7442 | 4.6853 | 4.6305 | 4.5832 | 4.5368 | 4.4926 | 4.4495 | 4.4095 | 4.2253 | 4.0305 | 3.8368
|  | PORT ELLEN | CF |  |  |  |  | 4.9547 | 4.9147 | 4.8789 | 4.8611 | 4.8432 | 4.8284 | 4.8126 | 4.7989 | 4.7842 | 4.7695 | 4.7042 | 4.6611 | 4.6305 | 4.6063 | 4.5589 | 4.5168 | 4.4958 | 4.4768 | 4.4611 | 4.4442 | 4.4284 | 4.4126 | 4.3968 | 4.3221 | 4.2695 | 4.2305 | 4.8895 | 4.8811 | 4.8726 | 4.8632 | 4.8537 | 4.8442 | 4.8347 | 4.8253 | 4.8158 | 4.8063 | 4.7516 | 4.7042 | 4.6695
| DUNVEGAN | PORTREE | MINIMUM HEADROOM | NG 48102 44602 | NO | YES | 0 | 9.0158 | 8.9274 | 8.8316 | 8.7337 | 8.6368 | 7.8326 | 7.3368 | 6.8442 | 6.4884 | 6.1337 | 4.9842 | 3.8989 | 3.3042 | 7.8453 | 7.76 | 7.6705 | 7.5789 | 7.4874 | 6.54 | 5.9853 | 5.4358 | 5.0653 | 4.6979 | 3.74 | 2.9074 | 2.3695 | 8.3695 | 8.2789 | 8.1821 | 8.0832 | 7.9842 | 6.8884 | 6.3095 | 5.7337 | 5.3316 | 4.9316 | 3.7316 | 2.5737 | 1.9168
|  | PORTREE | EE |  |  |  |  | 9.0495 | 8.9621 | 8.8653 | 8.7642 | 8.6611 | 8.1779 | 7.9147 | 7.3937 | 6.8916 | 6.3947 | 4.9842 | 3.8989 | 3.3042 | 7.8789 | 7.8032 | 7.7232 | 7.6379 | 7.5495 | 7.0389 | 6.8063 | 6.2505 | 5.7105 | 5.1779 | 3.8537 | 2.9074 | 2.3695 | 8.4032 | 8.3095 | 8.2074 | 8.1 | 7.9895 | 7.32 | 7.0432 | 6.4389 | 5.8547 | 5.2768 | 3.7316 | 2.5737 | 1.9168
|  | PORTREE | HT |  |  |  |  | 9.0158 | 8.9274 | 8.8316 | 8.7337 | 8.6368 | 7.8326 | 7.3368 | 6.8442 | 6.4884 | 6.1337 | 5.1442 | 4.4189 | 3.8916 | 7.8453 | 7.76 | 7.6705 | 7.5789 | 7.4874 | 6.54 | 5.9853 | 5.4358 | 5.0653 | 4.6979 | 3.74 | 3.0232 | 2.4958 | 8.3695 | 8.2789 | 8.1821 | 8.0832 | 7.9842 | 6.8884 | 6.3095 | 5.7337 | 5.3316 | 4.9316 | 3.8558 | 3.0558 | 2.4768
|  | PORTREE | HE |  |  |  |  | 9.0947 | 9.0463 | 8.9905 | 8.9316 | 8.8695 | 8.5768 | 8.4032 | 8.06 | 7.7179 | 7.3832 | 6.1968 | 5.6158 | 5.0389 | 7.9242 | 7.8789 | 7.8274 | 7.7737 | 7.7147 | 7.4116 | 7.2579 | 6.8884 | 6.5211 | 6.1611 | 4.9411 | 4.4453 | 3.9589 | 8.3695 | 8.2789 | 8.1821 | 8.0832 | 7.9842 | 6.8884 | 6.3095 | 5.7337 | 5.3316 | 4.9316 | 3.8558 | 3.0558 | 2.4768
|  | PORTREE | CF |  |  |  |  | 9.1211 | 9.0947 | 9.0674 | 9.0389 | 9.0105 | 8.9463 | 8.8874 | 8.8305 | 8.7747 | 8.6968 | 7.9063 | 7.54 | 7.2716 | 7.9505 | 7.9253 | 7.8989 | 7.8726 | 7.8453 | 7.8011 | 7.7568 | 7.7137 | 7.6737 | 7.5568 | 6.68 | 6.3474 | 6.0989 | 8.4747 | 8.4484 | 8.42 | 8.3916 | 8.3621 | 8.3011 | 8.2421 | 8.1853 | 8.1116 | 7.9126 | 6.9874 | 6.5979 | 6.3095
| MACDUFF | PORTSOY | MINIMUM HEADROOM | NJ 58491 65037 | YES | YES | 0.18 | 1.6001 | 1.5601 | 1.5096 | -0.31779 | -0.35358 | -0.622 | -0.88411 | -1.1515 | -1.3831 | -1.6188 | -3.6641 | -6.3609 | -8.3104 | 2.0527 | 2.0096 | 1.9612 | 0.418 | 0.35589 | 0.080105 | -0.18832 | -0.45779 | -0.69147 | -0.92937 | -3.1325 | -5.7536 | -7.862 | 2.2191 | 2.1569 | 2.0833 | 0.030632 | -0.022 | -0.33463 | -0.63989 | -0.95042 | -1.2178 | -1.4915 | -3.7294 | -6.5946 | -8.7273
|  | PORTSOY | EE |  |  |  |  | 1.6159 | 1.5833 | 1.5359 | -0.31779 | -0.35358 | -0.622 | -0.88411 | -1.1515 | -1.3831 | -1.6188 | -3.6641 | -6.3609 | -8.3104 | 2.0696 | 2.0348 | 1.9938 | 0.418 | 0.35589 | 0.080105 | -0.18832 | -0.45779 | -0.69147 | -0.92937 | -3.1325 | -5.7536 | -7.862 | 2.2454 | 2.1969 | 2.1317 | 0.030632 | -0.022 | -0.33463 | -0.63989 | -0.95042 | -1.2178 | -1.4915 | -3.7294 | -6.5946 | -8.7273
|  | PORTSOY | HT |  |  |  |  | 1.6001 | 1.5601 | 1.5096 | 1.458 | 1.4064 | 1.2096 | 1.0117 | 0.81484 | 0.58537 | 0.35379 | -1.3662 | -3.8441 | -5.3673 | 2.0527 | 2.0096 | 1.9612 | 1.9106 | 1.8612 | 1.6759 | 1.4622 | 1.2506 | 1.0096 | 0.72853 | -1.4967 | -4.1388 | -5.8409 | 2.2191 | 2.1569 | 2.0833 | 2.0096 | 1.9369 | 1.7012 | 1.4654 | 1.2317 | 0.95905 | 0.66221 | -1.4325 | -4.1325 | -5.8631
|  | PORTSOY | HE |  |  |  |  | 1.638 | 1.6169 | 1.5917 | 1.5654 | 1.5359 | 1.3043 | 1.1096 | 0.91484 | 0.72221 | 0.53484 | -0.81989 | -2.8557 | -5.0599 | 2.0938 | 2.0717 | 2.0464 | 2.0201 | 1.9906 | 1.8664 | 1.6864 | 1.4127 | 1.1517 | 0.76221 | -0.87147 | -2.9262 | -5.1546 | 2.2191 | 2.1569 | 2.0833 | 2.0096 | 1.9369 | 1.7012 | 1.4654 | 1.2317 | 0.95905 | 0.66221 | -1.4325 | -4.1325 | -5.8631
|  | PORTSOY | CF |  |  |  |  | 1.6506 | 1.638 | 1.6233 | 1.6085 | 1.5917 | 1.5033 | 1.4243 | 1.3443 | 1.2738 | 1.2222 | 0.85063 | -0.35989 | -1.7515 | 2.1075 | 2.0948 | 2.0801 | 2.0654 | 2.0485 | 1.9991 | 1.9548 | 1.9064 | 1.7822 | 1.5822 | 0.70326 | -0.60305 | -2.0799 | 2.3012 | 2.2822 | 2.2612 | 2.2412 | 2.2159 | 2.1117 | 2.0169 | 1.9127 | 1.7727 | 1.6296 | 0.91168 | -0.39884 | -1.9052
| WOODHILL | QUEENS LANE NORTH | MINIMUM HEADROOM | NJ 92224 05823 | NO | NO | 0 | 15.2703 | 15.1208 | 14.9671 | 14.8113 | 31.6242 | 31.4389 | 31.2579 | 31.0821 | 30.9084 | 30.7411 | 29.7232 | 28.8179 | 27.9926 | 13.6811 | 13.5242 | 13.3621 | 13.2 | 29.1316 | 28.9453 | 28.76 | 28.5653 | 28.2726 | 27.9811 | 26.7989 | 25.7716 | 24.8105 | 14.0546 | 13.9051 | 13.7514 | 13.5957 | 29.9721 | 29.7868 | 29.6068 | 29.4311 | 29.2058 | 28.9142 | 27.7363 | 26.7153 | 25.7689
|  | QUEENS LANE NORTH | EE |  |  |  |  | 15.3345 | 15.2197 | 15.0987 | 14.9724 | 31.8147 | 31.6663 | 31.52 | 31.3768 | 31.24 | 31.1084 | 30.4779 | 29.7505 | 29.1568 | 13.7484 | 13.6274 | 13.5 | 13.3684 | 29.3316 | 29.1853 | 29.0411 | 28.9011 | 28.7663 | 28.6295 | 27.66 | 26.8537 | 26.1674 | 14.1188 | 14.0041 | 13.883 | 13.7578 | 30.1616 | 30.0142 | 29.8689 | 29.7268 | 29.5911 | 29.4605 | 28.5732 | 27.7584 | 27.0784
|  | QUEENS LANE NORTH | HT |  |  |  |  | 15.2703 | 15.1208 | 14.9671 | 14.8113 | 31.6242 | 31.4389 | 31.2579 | 31.0821 | 30.9084 | 30.7411 | 29.7232 | 28.8179 | 27.9926 | 13.6811 | 13.5242 | 13.3621 | 13.2 | 29.1316 | 28.9453 | 28.76 | 28.5653 | 28.2726 | 27.9811 | 26.7989 | 25.7716 | 24.8105 | 14.0546 | 13.9051 | 13.7514 | 13.5957 | 29.9721 | 29.7868 | 29.6068 | 29.4311 | 29.2058 | 28.9142 | 27.7363 | 26.7153 | 25.7689
|  | QUEENS LANE NORTH | HE |  |  |  |  | 15.3966 | 15.3092 | 15.2145 | 15.1113 | 31.9758 | 31.8484 | 31.7316 | 31.6179 | 31.5084 | 31.4105 | 31.0547 | 30.8484 | 30.7137 | 13.8158 | 13.7232 | 13.6232 | 13.5168 | 29.5053 | 29.38 | 29.2663 | 29.1547 | 29.0484 | 28.9537 | 28.6116 | 28.4074 | 28.0632 | 14.0546 | 13.9051 | 13.7514 | 13.5957 | 29.9721 | 29.7868 | 29.6068 | 29.4311 | 29.2058 | 28.9142 | 27.7363 | 26.7153 | 25.7689
|  | QUEENS LANE NORTH | CF |  |  |  |  | 15.4239 | 15.3629 | 15.2997 | 15.2345 | 32.1432 | 32.0716 | 32 | 31.9274 | 31.8558 | 31.7863 | 31.4768 | 31.3053 | 31.2147 | 13.8442 | 13.78 | 13.7126 | 13.6453 | 29.6768 | 29.6053 | 29.5326 | 29.46 | 29.3874 | 29.3168 | 29.0063 | 28.8368 | 28.6674 | 14.2083 | 14.1472 | 14.0841 | 14.0188 | 30.49 | 30.4195 | 30.3468 | 30.2753 | 30.2037 | 30.1342 | 29.8268 | 29.6574 | 29.5679
| THURSO | RACKWICK | MINIMUM HEADROOM | ND 20206 99857 | YES | YES | 0 | 0.10526 | 0.10421 | 0.10421 | 0.10316 | 0.1 | 0.1 | 0.097895 | 0.095789 | 0.094737 | 0.092632 | 0.086316 | 0.08 | 0.074737 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.091579 | 0.090526 | 0.088421 | 0.086316 | 0.085263 | 0.083158 | 0.075789 | 0.068421 | 0.062105 | 0.1 | 0.098947 | 0.098947 | 0.096842 | 0.093684 | 0.092632 | 0.091579 | 0.089474 | 0.087368 | 0.085263 | 0.077895 | 0.071579 | 0.065263
|  | RACKWICK | EE |  |  |  |  | 0.10526 | 0.10526 | 0.10421 | 0.10316 | 0.10316 | 0.10105 | 0.1 | 0.098947 | 0.098947 | 0.096842 | 0.090526 | 0.086316 | 0.083158 | 0.098947 | 0.097895 | 0.096842 | 0.094737 | 0.094737 | 0.092632 | 0.091579 | 0.090526 | 0.089474 | 0.087368 | 0.081053 | 0.075789 | 0.071579 | 0.10105 | 0.1 | 0.098947 | 0.097895 | 0.096842 | 0.094737 | 0.093684 | 0.092632 | 0.091579 | 0.090526 | 0.084211 | 0.077895 | 0.074737
|  | RACKWICK | HT |  |  |  |  | 0.10526 | 0.10421 | 0.10421 | 0.10316 | 0.1 | 0.1 | 0.097895 | 0.095789 | 0.094737 | 0.092632 | 0.086316 | 0.08 | 0.074737 | 0.097895 | 0.096842 | 0.095789 | 0.094737 | 0.091579 | 0.090526 | 0.088421 | 0.086316 | 0.085263 | 0.083158 | 0.075789 | 0.068421 | 0.062105 | 0.1 | 0.098947 | 0.098947 | 0.096842 | 0.093684 | 0.092632 | 0.091579 | 0.089474 | 0.087368 | 0.085263 | 0.077895 | 0.071579 | 0.065263
|  | RACKWICK | HE |  |  |  |  | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.098947 | 0.095789 | 0.094737 | 0.098947 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.095789 | 0.095789 | 0.094737 | 0.093684 | 0.093684 | 0.090526 | 0.086316 | 0.085263 | 0.1 | 0.098947 | 0.098947 | 0.096842 | 0.093684 | 0.092632 | 0.091579 | 0.089474 | 0.087368 | 0.085263 | 0.077895 | 0.071579 | 0.065263
|  | RACKWICK | CF |  |  |  |  | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.1 | 0.098947 | 0.10105 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.096842 | 0.096842 | 0.096842 | 0.096842 | 0.094737 | 0.091579 | 0.089474 | 0.10211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.098947 | 0.098947 | 0.098947 | 0.098947 | 0.096842 | 0.093684 | 0.092632
| FORT WILLIAM | RAHOY | MINIMUM HEADROOM | NM 69621 49222 | YES | NO | 0 | 1.0095 | 1.0032 | 0.99263 | 0.98211 | 0.97053 | 0.95789 | 0.94842 | 0.93789 | 0.92737 | 0.91684 | 0.86842 | 0.82632 | 0.78316 | 1.0053 | 1 | 0.99053 | 0.98 | 0.96947 | 0.95789 | 0.94842 | 0.93895 | 0.92842 | 0.91789 | 0.87158 | 0.83158 | 0.79053 | 1.0074 | 0.99789 | 0.98947 | 0.97895 | 0.96737 | 0.95474 | 0.94526 | 0.93474 | 0.92421 | 0.91368 | 0.86421 | 0.82211 | 0.77895
|  | RAHOY | EE |  |  |  |  | 1.0095 | 1.0032 | 0.99263 | 0.98211 | 0.97053 | 0.95789 | 0.94842 | 0.93789 | 0.92737 | 0.91684 | 0.86842 | 0.82632 | 0.78316 | 1.0053 | 1 | 0.99053 | 0.98 | 0.96947 | 0.95789 | 0.94842 | 0.93895 | 0.92842 | 0.91789 | 0.87158 | 0.83158 | 0.79053 | 1.0074 | 0.99789 | 0.98947 | 0.97895 | 0.96737 | 0.95474 | 0.94526 | 0.93474 | 0.92421 | 0.91368 | 0.86421 | 0.82211 | 0.77895
|  | RAHOY | HT |  |  |  |  | 1.0095 | 1.0074 | 1.0053 | 1.0032 | 0.99895 | 0.99579 | 0.99263 | 0.99053 | 0.98737 | 0.98421 | 0.96947 | 0.95263 | 0.93474 | 1.0053 | 1.0042 | 1.0032 | 1.0011 | 0.99684 | 0.99368 | 0.99158 | 0.98947 | 0.98632 | 0.98316 | 0.96842 | 0.95263 | 0.93579 | 1.0074 | 1.0042 | 1.0021 | 0.99895 | 0.99474 | 0.99263 | 0.98947 | 0.98737 | 0.98421 | 0.98211 | 0.96632 | 0.94947 | 0.93158
|  | RAHOY | HE |  |  |  |  | 1.0095 | 1.0074 | 1.0053 | 1.0032 | 1 | 0.99684 | 0.99474 | 0.99158 | 0.98737 | 0.98421 | 0.96842 | 0.95263 | 0.93579 | 1.0053 | 1.0042 | 1.0032 | 1.0011 | 0.99789 | 0.99474 | 0.99263 | 0.98947 | 0.98632 | 0.98316 | 0.96737 | 0.95263 | 0.93684 | 1.0074 | 1.0042 | 1.0021 | 0.99895 | 0.99474 | 0.99263 | 0.98947 | 0.98737 | 0.98421 | 0.98211 | 0.96632 | 0.94947 | 0.93158
|  | RAHOY | CF |  |  |  |  | 1.0095 | 1.0095 | 1.0084 | 1.0084 | 1.0074 | 1.0074 | 1.0063 | 1.0063 | 1.0063 | 1.0053 | 1.0032 | 1 | 0.99789 | 1.0053 | 1.0053 | 1.0053 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0032 | 1.0032 | 1.0032 | 1.0011 | 0.99789 | 0.99579 | 1.0074 | 1.0063 | 1.0063 | 1.0053 | 1.0042 | 1.0042 | 1.0032 | 1.0021 | 1.0021 | 1.0021 | 0.99895 | 0.99579 | 0.99368
| INVERNESS | RAIGMORE | MINIMUM HEADROOM | NH 68427 44693 | NO | YES | 0 | 25.331 | 25.2049 | 25.0666 | 22.4423 | 22.3735 | 22.2961 | 22.2459 | 22.1742 | 22.1062 | 22.0323 | 21.6962 | 21.4433 | 21.2283 | 25.055 | 24.9447 | 24.825 | 22.6772 | 22.6084 | 22.5332 | 22.4966 | 22.4271 | 22.3605 | 22.2788 | 21.8717 | 21.5464 | 21.254 | 25.6799 | 25.6025 | 25.5222 | 22.6156 | 22.5468 | 22.4701 | 22.4364 | 22.3655 | 22.2974 | 22.215 | 21.8029 | 21.4718 | 21.1801
|  | RAIGMORE | EE |  |  |  |  | 25.3496 | 25.2565 | 25.1432 | 22.4423 | 22.3735 | 22.2961 | 22.2459 | 22.1742 | 22.1062 | 22.0323 | 21.6962 | 21.4433 | 21.2283 | 25.0729 | 24.9898 | 24.8931 | 22.6772 | 22.6084 | 22.5332 | 22.4966 | 22.4271 | 22.3605 | 22.2788 | 21.8717 | 21.5464 | 21.254 | 25.6964 | 25.6354 | 25.5709 | 22.6156 | 22.5468 | 22.4701 | 22.4364 | 22.3655 | 22.2974 | 22.215 | 21.8029 | 21.4718 | 21.1801
|  | RAIGMORE | HT |  |  |  |  | 25.331 | 25.2049 | 25.0666 | 24.9247 | 24.8057 | 24.6538 | 24.5406 | 24.4323 | 24.327 | 24.236 | 23.8963 | 23.5631 | 23.2693 | 25.055 | 24.9447 | 24.825 | 24.7031 | 24.6186 | 24.4867 | 24.3835 | 24.2846 | 24.1886 | 24.1033 | 23.7966 | 23.3616 | 22.8836 | 25.6799 | 25.6025 | 25.5222 | 25.4405 | 25.3753 | 25.199 | 25.0621 | 24.9317 | 24.8049 | 24.7045 | 24.2953 | 23.803 | 23.3315
|  | RAIGMORE | HE |  |  |  |  | 25.3697 | 25.3031 | 25.2249 | 25.1354 | 25.0365 | 24.9275 | 24.858 | 24.7914 | 24.7369 | 24.6868 | 24.5033 | 24.3707 | 24.2489 | 25.093 | 25.0342 | 24.9669 | 24.8909 | 24.8063 | 24.7168 | 24.6551 | 24.5949 | 24.5441 | 24.4975 | 24.3326 | 24.2244 | 24.1141 | 25.6799 | 25.6025 | 25.5222 | 25.4405 | 25.3753 | 25.199 | 25.0621 | 24.9317 | 24.8049 | 24.7045 | 24.2953 | 23.803 | 23.3315
|  | RAIGMORE | CF |  |  |  |  | 25.3984 | 25.369 | 25.336 | 25.3023 | 25.2679 | 25.2264 | 25.1819 | 25.1368 | 25.0916 | 25.0465 | 24.8709 | 24.7606 | 24.6932 | 25.1166 | 25.0887 | 25.0586 | 25.0271 | 24.9948 | 24.9583 | 24.9196 | 24.8816 | 24.8422 | 24.8028 | 24.6487 | 24.5584 | 24.5054 | 25.73 | 25.7057 | 25.6799 | 25.6534 | 25.6268 | 25.5975 | 25.5688 | 25.5401 | 25.5107 | 25.4821 | 25.3581 | 25.2893 | 25.2542
| ARBROATH | REDFORD | MINIMUM HEADROOM | NO 55879 44046 | YES | YES | 0 | 0.38105 | 0.30421 | -2.3105 | -2.3758 | -2.4411 | -2.8442 | -3.3232 | -3.8116 | -4.2347 | -4.92 | -9.2811 | -15.9053 | -19.4505 | -0.19158 | -0.27579 | -3.3558 | -3.4147 | -3.4737 | -3.7905 | -4.1653 | -4.5463 | -4.8779 | -5.5126 | -9.7316 | -16.54 | -20.3947 | 0.016842 | -0.068421 | -3.1642 | -3.2305 | -3.2947 | -3.6979 | -4.1768 | -4.6663 | -5.0895 | -5.8179 | -10.5389 | -17.9053 | -21.9358
|  | REDFORD | EE |  |  |  |  | 0.41579 | 0.35684 | -2.3105 | -2.3758 | -2.4411 | -2.8442 | -3.3232 | -3.8116 | -4.2347 | -4.92 | -9.2811 | -15.9053 | -19.4505 | -0.15263 | -0.21684 | -3.3558 | -3.4147 | -3.4737 | -3.7905 | -4.1653 | -4.5463 | -4.8779 | -5.5126 | -9.7316 | -16.54 | -20.3947 | 0.055789 | -0.0084211 | -3.1642 | -3.2305 | -3.2947 | -3.6979 | -4.1768 | -4.6663 | -5.0895 | -5.8179 | -10.5389 | -17.9053 | -21.9358
|  | REDFORD | HT |  |  |  |  | 0.38105 | 0.30421 | 0.21053 | 0.11895 | 0.028421 | -0.33684 | -0.7 | -1.0726 | -1.5137 | -2.3105 | -5.8253 | -10.1221 | -13.0263 | -0.19158 | -0.27579 | -0.37263 | -0.46842 | -0.56211 | -0.87474 | -1.1884 | -1.5053 | -1.8779 | -2.6474 | -6.1495 | -10.7958 | -14.0547 | 0.016842 | -0.068421 | -0.17053 | -0.26947 | -0.36842 | -0.74211 | -1.1158 | -1.4916 | -1.9316 | -2.7979 | -6.6663 | -11.5442 | -14.8853
|  | REDFORD | HE |  |  |  |  | 0.45474 | 0.42526 | 0.38526 | 0.34211 | 0.29684 | -0.16316 | -0.65263 | -1.1684 | -1.6611 | -2.3632 | -5.3474 | -10.8463 | -14.82 | -0.10105 | -0.13895 | -0.18316 | -0.22842 | -0.27474 | -0.66842 | -1.1253 | -1.5958 | -2.0411 | -2.7263 | -5.6011 | -11.4326 | -15.4653 | 0.016842 | -0.068421 | -0.17053 | -0.26947 | -0.36842 | -0.74211 | -1.1158 | -1.4916 | -1.9316 | -2.7979 | -6.6663 | -11.5442 | -14.8853
|  | REDFORD | CF |  |  |  |  | 0.47579 | 0.45789 | 0.43579 | 0.41263 | 0.38737 | 0.22 | 0.067368 | -0.16842 | -0.45684 | -0.78947 | -2.3253 | -4.6274 | -7.1453 | -0.074737 | -0.097895 | -0.12526 | -0.15263 | -0.18 | -0.32 | -0.44842 | -0.68526 | -0.99158 | -1.3442 | -2.8789 | -5.2263 | -7.9295 | 0.13474 | 0.11158 | 0.083158 | 0.054737 | 0.026316 | -0.14421 | -0.29789 | -0.56526 | -0.89895 | -1.2768 | -2.9642 | -5.5147 | -8.3632
| BURGHMUIR | REDGORTON | MINIMUM HEADROOM | NO 07650 28860 | NO | YES | 0 | 15.4005 | 14.9363 | 14.3363 | 13.6426 | 12.8489 | 11.3689 | 9.9479 | 8.4037 | 6.9489 | 5.4447 | -2.2837 | -8.2837 | -12.1068 | 13.7368 | 13.1842 | 12.4768 | 11.6526 | 10.7063 | 9.1674 | 7.7642 | 6.3611 | 4.9242 | 3.3821 | -3.7747 | -8.9389 | -12.8579 | 14.4308 | 13.9382 | 13.2529 | 12.4371 | 11.5034 | 9.8329 | 8.2561 | 6.5497 | 4.9782 | 3.3634 | -4.9145 | -11.1461 | -15.3682
|  | REDGORTON | EE |  |  |  |  | 15.4953 | 15.0826 | 14.5216 | 13.8668 | 13.1226 | 11.57 | 9.9479 | 8.4037 | 6.9489 | 5.4447 | -2.2837 | -8.2837 | -12.1068 | 13.8442 | 13.3495 | 12.6916 | 11.9168 | 11.0305 | 9.4568 | 7.8537 | 6.3611 | 4.9684 | 3.5316 | -3.7747 | -8.9389 | -12.8579 | 14.5297 | 14.0908 | 13.4582 | 12.6855 | 11.8045 | 10.0634 | 8.2561 | 6.5497 | 4.9782 | 3.3634 | -4.9145 | -11.1461 | -15.3682
|  | REDGORTON | HT |  |  |  |  | 15.4005 | 14.9363 | 14.3363 | 13.6426 | 12.8489 | 11.3689 | 10.0058 | 8.6774 | 7.1742 | 5.59 | -0.67421 | -4.0016 | -8.9837 | 13.7368 | 13.1842 | 12.4768 | 11.6526 | 10.7063 | 9.1674 | 7.7642 | 6.4084 | 4.9242 | 3.3821 | -2.7768 | -5.94 | -11.4632 | 14.4308 | 13.9382 | 13.2529 | 12.4371 | 11.5034 | 9.8329 | 8.3013 | 6.8118 | 5.1624 | 3.4518 | -3.3713 | -6.9292 | -12.6271
|  | REDGORTON | HE |  |  |  |  | 15.6247 | 15.2742 | 14.8121 | 14.2532 | 13.5953 | 12.0416 | 10.6679 | 9.3784 | 8.0647 | 6.6963 | 0.71632 | -3.2942 | -8.3111 | 13.9905 | 13.5663 | 13.0032 | 12.3221 | 11.5189 | 9.9558 | 8.5537 | 7.2558 | 5.9411 | 4.6042 | -1.1832 | -4.7442 | -9.4242 | 14.4308 | 13.9382 | 13.2529 | 12.4371 | 11.5034 | 9.8329 | 8.3013 | 6.8118 | 5.1624 | 3.4518 | -3.3713 | -6.9292 | -12.6271
|  | REDGORTON | CF |  |  |  |  | 15.7437 | 15.5511 | 15.3184 | 15.0542 | 14.7647 | 14.1626 | 13.5963 | 13.0247 | 12.4742 | 11.9447 | 8.7637 | 6.2711 | 2.5921 | 14.1305 | 13.8979 | 13.6179 | 13.2989 | 12.9474 | 12.34 | 11.7558 | 11.1653 | 10.5832 | 9.9979 | 6.6011 | 4.3705 | 0.50737 | 14.7897 | 14.5855 | 14.3361 | 14.0539 | 13.7182 | 13.0434 | 12.4045 | 11.7592 | 11.1308 | 10.5192 | 6.8739 | 4.2403 | 0.12342
| REDMOSS | REDMOSS | MINIMUM HEADROOM | NJ 94562 01919 | NO | YES | 1.04 | 39.4368 | 39.3116 | 39.0232 | 38.1284 | 36.8895 | 35.6179 | 34.3589 | 33.1421 | 31.8768 | 30.5326 | 28.0105 | 27.2221 | 26.4842 | 38.3337 | 38.2084 | 37.9137 | 36.8168 | 35.2779 | 33.7495 | 32.2389 | 30.7768 | 29.2653 | 27.6516 | 25.4989 | 24.3758 | 23.4095 | 39.8179 | 39.6926 | 39.3989 | 38.3621 | 36.8589 | 35.3389 | 33.8368 | 32.3611 | 30.8221 | 29.1789 | 26.9358 | 25.7463 | 24.7558
|  | REDMOSS | EE |  |  |  |  | 39.4368 | 39.3116 | 39.1695 | 38.6379 | 37.5747 | 36.2379 | 34.6589 | 33.5347 | 32.4316 | 31.2874 | 28.8821 | 27.5274 | 26.7789 | 38.3337 | 38.2084 | 38.0695 | 37.4316 | 36.1095 | 34.5011 | 32.5937 | 31.2716 | 29.96 | 28.5979 | 25.9568 | 24.7 | 23.9158 | 39.8179 | 39.6926 | 39.5505 | 38.9463 | 37.6716 | 36.0674 | 34.1674 | 32.8253 | 31.4863 | 30.0916 | 27.3211 | 25.8926 | 25.0537
|  | REDMOSS | HT |  |  |  |  | 40.0242 | 39.5663 | 39.0232 | 38.1284 | 36.8895 | 35.6179 | 34.3589 | 33.1421 | 31.8768 | 30.5326 | 28.5737 | 27.5 | 26.6442 | 39.1 | 38.5621 | 37.9137 | 36.8168 | 35.2779 | 33.7495 | 32.2389 | 30.7768 | 29.2653 | 27.6516 | 25.4989 | 24.3758 | 23.4095 | 40.5274 | 40.0137 | 39.3989 | 38.3621 | 36.8589 | 35.3389 | 33.8368 | 32.3611 | 30.8221 | 29.1789 | 26.9358 | 25.7463 | 24.7558
|  | REDMOSS | HE |  |  |  |  | 39.5263 | 39.4432 | 39.3495 | 38.9758 | 37.9158 | 36.6084 | 35.1547 | 34.0832 | 32.9674 | 31.7158 | 28.0105 | 27.2221 | 26.4842 | 38.4232 | 38.34 | 38.2474 | 37.7958 | 36.4663 | 34.8916 | 33.1126 | 31.8263 | 30.48 | 28.9568 | 25.8063 | 25.0863 | 24.4326 | 40.5274 | 40.0137 | 39.3989 | 38.3621 | 36.8589 | 35.3389 | 33.8368 | 32.3611 | 30.8221 | 29.1789 | 26.9358 | 25.7463 | 24.7558
|  | REDMOSS | CF |  |  |  |  | 40.3347 | 39.5232 | 39.4705 | 39.4179 | 39.3642 | 39.2621 | 38.7937 | 38.1653 | 37.5874 | 36.9263 | 33.1347 | 32.5747 | 32.1758 | 39.4463 | 38.42 | 38.3684 | 38.3158 | 38.2621 | 38.1726 | 37.6095 | 36.8411 | 36.1368 | 35.3158 | 31.8758 | 31.3368 | 30.9484 | 40.8653 | 39.9042 | 39.8516 | 39.7989 | 39.7453 | 39.6432 | 39.1042 | 38.3621 | 37.6642 | 36.8579 | 32.8305 | 32.2316 | 31.7979
| CASSLEY | RHICONICH | MINIMUM HEADROOM | NC 25554 52924 | YES | YES | 0.145 | 1.0487 | 1.0161 | 0.98342 | 0.94868 | 0.915 | 0.875 | 0.82026 | 0.76763 | 0.71816 | 0.66974 | 0.46132 | 0.29921 | 0.13921 | 0.88658 | 0.85395 | 0.81395 | 0.75289 | 0.69395 | 0.635 | 0.57711 | 0.52237 | 0.46974 | 0.41921 | 0.19395 | 0.015 | -0.16079 | 0.915 | 0.88132 | 0.84868 | 0.815 | 0.78026 | 0.72237 | 0.66447 | 0.60868 | 0.55605 | 0.50553 | 0.27816 | 0.098158 | -0.080789
|  | RHICONICH | EE |  |  |  |  | 1.0613 | 1.0361 | 1.0087 | 0.98026 | 0.95079 | 0.92237 | 0.89395 | 0.86553 | 0.83289 | 0.795 | 0.62026 | 0.49921 | 0.38342 | 0.89921 | 0.875 | 0.84763 | 0.82026 | 0.77289 | 0.72763 | 0.68132 | 0.63816 | 0.59816 | 0.55921 | 0.375 | 0.24342 | 0.11711 | 0.92763 | 0.90237 | 0.87395 | 0.84553 | 0.81605 | 0.78658 | 0.75816 | 0.72026 | 0.67921 | 0.63921 | 0.45079 | 0.31605 | 0.18553
|  | RHICONICH | HT |  |  |  |  | 1.0487 | 1.0161 | 0.98342 | 0.94868 | 0.915 | 0.875 | 0.82026 | 0.76763 | 0.71816 | 0.66974 | 0.46132 | 0.29921 | 0.13921 | 0.88658 | 0.85395 | 0.81395 | 0.75289 | 0.69395 | 0.635 | 0.57711 | 0.52237 | 0.46974 | 0.41921 | 0.19395 | 0.015 | -0.16079 | 0.915 | 0.88132 | 0.84868 | 0.815 | 0.78026 | 0.72237 | 0.66447 | 0.60868 | 0.55605 | 0.50553 | 0.27816 | 0.098158 | -0.080789
|  | RHICONICH | HE |  |  |  |  | 1.0803 | 1.0645 | 1.0455 | 1.0266 | 1.0066 | 0.98447 | 0.96447 | 0.94553 | 0.92658 | 0.90974 | 0.85289 | 0.82447 | 0.76342 | 0.91816 | 0.90237 | 0.88447 | 0.86553 | 0.84447 | 0.82342 | 0.80342 | 0.78447 | 0.76658 | 0.74237 | 0.64868 | 0.58763 | 0.52026 | 0.915 | 0.88132 | 0.84868 | 0.815 | 0.78026 | 0.72237 | 0.66447 | 0.60868 | 0.55605 | 0.50553 | 0.27816 | 0.098158 | -0.080789
|  | RHICONICH | CF |  |  |  |  | 1.0908 | 1.0813 | 1.0729 | 1.0634 | 1.0539 | 1.0445 | 1.035 | 1.0255 | 1.0161 | 1.0055 | 0.96447 | 0.94447 | 0.935 | 0.92868 | 0.91921 | 0.91079 | 0.90132 | 0.89184 | 0.88237 | 0.87289 | 0.86342 | 0.85395 | 0.84447 | 0.79079 | 0.73816 | 0.69921 | 0.95711 | 0.94763 | 0.93921 | 0.92868 | 0.91921 | 0.90974 | 0.90026 | 0.89079 | 0.88132 | 0.87184 | 0.83079 | 0.80974 | 0.78658
| DUDHOPE | ROSEBANK STREET | MINIMUM HEADROOM | NO 39943 31150 | NO | YES | 0 | 25.6016 | 25.4153 | 25.2226 | 25.0226 | 24.8068 | 24.5595 | 24.3174 | 24.0774 | 23.8437 | 23.6132 | 22.0289 | 20.5963 | 19.3732 | 22.1695 | 21.96 | 21.6789 | 21.3263 | 21.0368 | 20.7232 | 20.4105 | 20.0958 | 19.7979 | 19.4979 | 17.8 | 16.1968 | 14.8116 | 22.8561 | 22.6308 | 22.4013 | 22.1392 | 21.7961 | 21.4182 | 21.0371 | 20.6497 | 20.2887 | 19.9182 | 17.9529 | 16.4171 | 15.0982
|  | ROSEBANK STREET | EE |  |  |  |  | 25.7005 | 25.5668 | 25.4258 | 25.2784 | 25.1195 | 24.9363 | 24.7532 | 24.5668 | 24.3879 | 24.2163 | 23.31 | 22.1668 | 21.2753 | 22.2684 | 22.1347 | 21.9705 | 21.7168 | 21.4726 | 21.2295 | 20.9916 | 20.7358 | 20.4895 | 20.2632 | 19.1484 | 17.9653 | 16.9579 | 22.9739 | 22.8118 | 22.6413 | 22.4497 | 22.255 | 22.0266 | 21.7318 | 21.4045 | 21.0908 | 20.8055 | 19.3108 | 18.0855 | 17.1234
|  | ROSEBANK STREET | HT |  |  |  |  | 25.6016 | 25.4153 | 25.2226 | 25.0226 | 24.8068 | 24.5595 | 24.3174 | 24.0774 | 23.8437 | 23.6132 | 22.0289 | 20.5963 | 19.3732 | 22.1695 | 21.96 | 21.6789 | 21.3263 | 21.0368 | 20.7232 | 20.4105 | 20.0958 | 19.7979 | 19.4979 | 17.8 | 16.1968 | 14.8116 | 22.8561 | 22.6308 | 22.4013 | 22.1392 | 21.7961 | 21.4182 | 21.0371 | 20.6497 | 20.2887 | 19.9182 | 17.9529 | 16.4171 | 15.0982
|  | ROSEBANK STREET | HE |  |  |  |  | 25.7542 | 25.6416 | 25.5184 | 25.3847 | 25.2416 | 25.0805 | 24.9311 | 24.7858 | 24.6479 | 24.5163 | 23.9984 | 23.69 | 23.2521 | 22.3221 | 22.2095 | 22.0863 | 21.9526 | 21.7621 | 21.5632 | 21.3811 | 21.1947 | 21.0116 | 20.8368 | 20.0084 | 19.4842 | 19.1221 | 22.8561 | 22.6308 | 22.4013 | 22.1392 | 21.7961 | 21.4182 | 21.0371 | 20.6497 | 20.2887 | 19.9182 | 17.9529 | 16.4171 | 15.0982
|  | ROSEBANK STREET | CF |  |  |  |  | 25.7837 | 25.7016 | 25.6163 | 25.5289 | 25.4384 | 25.3437 | 25.2479 | 25.1511 | 25.0563 | 24.9616 | 24.5405 | 24.2858 | 24.1416 | 22.3516 | 22.2695 | 22.1842 | 22.0968 | 22.0074 | 21.9137 | 21.8095 | 21.6768 | 21.5432 | 21.4126 | 20.8168 | 20.3874 | 20.0916 | 23.0929 | 22.9982 | 22.8992 | 22.7971 | 22.6908 | 22.5813 | 22.4697 | 22.3571 | 22.2445 | 22.1361 | 21.5803 | 20.9782 | 20.5361
| KEITH 2 | ROTHES | MINIMUM HEADROOM | NJ 27901 49693 | NO | YES | 0 | 5.72 | 5.6589 | 5.5758 | 5.4926 | 5.4105 | 4.9274 | 1.2442 | 0.63368 | 0.047368 | -0.75789 | -3.8179 | -3.34 | -6.1516 | 4.3695 | 4.3084 | 4.2305 | 4.1516 | 4.0747 | 3.6989 | 0.66316 | 0.11158 | -0.41474 | -1.1863 | -4.1316 | -3.9768 | -6.9842 | 5.3589 | 5.2979 | 5.2137 | 5.1305 | 5.0474 | 4.5421 | 1.6937 | 1.2779 | 0.89263 | 0.46737 | -2.3832 | -4.3032 | -7.4568
|  | ROTHES | EE |  |  |  |  | 6.76 | 5.6874 | 5.6042 | 5.5168 | 5.4305 | 4.9274 | 4.8737 | 4.2737 | 3.7484 | 2.9358 | -1.5326 | 1.2821 | -2.6621 | 5.8663 | 4.3368 | 4.26 | 4.1811 | 4.1011 | 3.7011 | 3.6474 | 3.1737 | 2.7316 | 1.9832 | -2.3705 | 0.63789 | -3.6084 | 6.8632 | 5.3263 | 5.2411 | 5.1526 | 5.0642 | 4.5421 | 4.4884 | 3.8653 | 3.3232 | 2.4642 | -2.3832 | -0.012632 | -4.4653
|  | ROTHES | HT |  |  |  |  | 5.72 | 5.6589 | 5.5758 | 5.4926 | 5.4105 | 4.9832 | 4.9179 | 4.3568 | 3.7337 | 2.7568 | -1.1137 | 2.4411 | -0.78632 | 4.3695 | 4.3084 | 4.2305 | 4.1516 | 4.0747 | 3.7295 | 3.6642 | 3.1495 | 2.6032 | 1.6526 | -2.3811 | 0.81368 | -2.7821 | 5.3589 | 5.2979 | 5.2137 | 5.1305 | 5.0474 | 4.6042 | 4.5389 | 3.9295 | 3.2663 | 2.2084 | -2.0853 | 0.85579 | -2.8316
|  | ROTHES | HE |  |  |  |  | 6.7926 | 5.7389 | 5.7011 | 5.6579 | 5.6158 | 4.9737 | 1.2442 | 0.63368 | 0.047368 | -0.75789 | -3.8179 | 0.40632 | -4.0474 | 5.9 | 4.3884 | 4.3516 | 4.3105 | 4.2695 | 3.6989 | 0.66316 | 0.11158 | -0.41474 | -1.1863 | -4.1316 | 0.13895 | -4.3495 | 5.3589 | 5.2979 | 5.2137 | 5.1305 | 5.0474 | 4.6042 | 4.5389 | 3.9295 | 3.2663 | 2.2084 | -2.0853 | 0.85579 | -2.8316
|  | ROTHES | CF |  |  |  |  | 6.7979 | 6.7684 | 5.7095 | 5.6747 | 5.6389 | 5.4284 | 2.1274 | 1.7453 | 1.3926 | 1.0116 | -0.69579 | -3.34 | -6.1516 | 5.9063 | 5.8758 | 4.36 | 4.3263 | 4.2916 | 4.1221 | 1.4737 | 1.0979 | 0.74842 | 0.35474 | -1.3358 | -3.9768 | -6.9842 | 6.9368 | 6.9 | 5.3484 | 5.3137 | 5.2768 | 5.0589 | 1.6937 | 1.2779 | 0.89263 | 0.46737 | -1.4 | -4.3032 | -7.4568
| DUNOON | ROTHESAY | MINIMUM HEADROOM | NS 08636 64647 | NO | YES | 0.352 | 15.9191 | 15.8191 | 15.7169 | 15.6138 | 15.5075 | 15.3917 | 15.258 | 15.0759 | 14.898 | 14.7243 | 14.0064 | 13.3864 | 12.8317 | 14.0659 | 13.9669 | 13.8659 | 13.7648 | 13.6585 | 13.5354 | 13.3406 | 13.1512 | 12.9659 | 12.7848 | 12.0312 | 11.3754 | 10.7733 | 14.9788 | 14.8798 | 14.7683 | 14.5935 | 14.4114 | 14.2072 | 14.0062 | 13.8093 | 13.6177 | 13.4304 | 12.6451 | 11.9588 | 11.3377
|  | ROTHESAY | EE |  |  |  |  | 15.958 | 15.8833 | 15.8022 | 15.7191 | 15.6306 | 15.5401 | 15.4527 | 15.3664 | 15.2854 | 15.1685 | 14.5664 | 14.0991 | 13.6927 | 14.1038 | 14.0301 | 13.9501 | 13.868 | 13.7796 | 13.6901 | 13.6048 | 13.5196 | 13.3901 | 13.2501 | 12.6206 | 12.1259 | 11.6922 | 15.0167 | 14.943 | 14.863 | 14.7798 | 14.6451 | 14.503 | 14.3588 | 14.2062 | 14.0577 | 13.9135 | 13.2598 | 12.7419 | 12.2851
|  | ROTHESAY | HT |  |  |  |  | 15.9191 | 15.8191 | 15.7169 | 15.6138 | 15.5075 | 15.3917 | 15.258 | 15.0759 | 14.898 | 14.7243 | 14.0064 | 13.3864 | 12.8317 | 14.0659 | 13.9669 | 13.8659 | 13.7648 | 13.6585 | 13.5354 | 13.3406 | 13.1512 | 12.9659 | 12.7848 | 12.0312 | 11.3754 | 10.7733 | 14.9788 | 14.8798 | 14.7683 | 14.5935 | 14.4114 | 14.2072 | 14.0062 | 13.8093 | 13.6177 | 13.4304 | 12.6451 | 11.9588 | 11.3377
|  | ROTHESAY | HE |  |  |  |  | 15.998 | 15.9443 | 15.8854 | 15.8191 | 15.7485 | 15.6738 | 15.6033 | 15.5348 | 15.4696 | 15.4117 | 15.2106 | 15.0338 | 14.8222 | 14.1438 | 14.0901 | 14.0312 | 13.9659 | 13.8954 | 13.8217 | 13.7522 | 13.6838 | 13.6196 | 13.5617 | 13.3638 | 13.1133 | 12.8869 | 14.9788 | 14.8798 | 14.7683 | 14.5935 | 14.4114 | 14.2072 | 14.0062 | 13.8093 | 13.6177 | 13.4304 | 12.6451 | 11.9588 | 11.3377
|  | ROTHESAY | CF |  |  |  |  | 16.0191 | 15.9833 | 15.9464 | 15.9085 | 15.8696 | 15.8296 | 15.7864 | 15.7454 | 15.7033 | 15.6612 | 15.4812 | 15.3843 | 15.318 | 14.1648 | 14.1291 | 14.0922 | 14.0543 | 14.0154 | 13.9754 | 13.9333 | 13.8922 | 13.8512 | 13.8091 | 13.6312 | 13.5364 | 13.4017 | 15.0777 | 15.0419 | 15.0051 | 14.9672 | 14.9283 | 14.8883 | 14.8462 | 14.8051 | 14.7641 | 14.7219 | 14.4704 | 14.2556 | 14.0672
| THURSO | ROUSAY | MINIMUM HEADROOM | HY 43876 30573 | YES | YES | 0 | -0.20526 | -0.21368 | -0.22105 | -0.22842 | -0.23789 | -0.24947 | -0.26105 | -0.27368 | -0.28316 | -0.29368 | -0.33263 | -0.36421 | -1.2632 | -0.14632 | -0.16 | -0.17158 | -0.18526 | -0.19684 | -0.21053 | -0.22211 | -0.23579 | -0.24632 | -0.25684 | -0.30105 | -0.33684 | -1.0695 | -0.29263 | -0.30526 | -0.31579 | -0.32737 | -0.33789 | -0.35053 | -0.36105 | -0.37263 | -0.38211 | -0.39263 | -0.43895 | -0.47684 | -1.3768
|  | ROUSAY | EE |  |  |  |  | -0.20316 | -0.20947 | -0.21579 | -0.22316 | -0.22947 | -0.23579 | -0.24316 | -0.25158 | -0.26 | -0.26737 | -0.30211 | -0.32526 | -1.2158 | -0.14105 | -0.15158 | -0.16105 | -0.17263 | -0.18316 | -0.19263 | -0.20211 | -0.21053 | -0.22 | -0.22947 | -0.26632 | -0.29263 | -1.0189 | -0.28842 | -0.29684 | -0.30632 | -0.31684 | -0.32526 | -0.33474 | -0.34421 | -0.35158 | -0.36 | -0.36737 | -0.40105 | -0.42947 | -1.3284
|  | ROUSAY | HT |  |  |  |  | -0.20526 | -0.21368 | -0.22105 | -0.22842 | -0.23789 | -0.24947 | -0.26105 | -0.27368 | -0.28316 | -0.29368 | -0.33263 | -0.36421 | -1.2632 | -0.14632 | -0.16 | -0.17158 | -0.18526 | -0.19684 | -0.21053 | -0.22211 | -0.23579 | -0.24632 | -0.25684 | -0.30105 | -0.33684 | -1.0695 | -0.29263 | -0.30526 | -0.31579 | -0.32737 | -0.33789 | -0.35053 | -0.36105 | -0.37263 | -0.38211 | -0.39263 | -0.43895 | -0.47684 | -1.3768
|  | ROUSAY | HE |  |  |  |  | -0.19895 | -0.20211 | -0.20632 | -0.21158 | -0.21684 | -0.22211 | -0.22632 | -0.23053 | -0.23684 | -0.24 | -0.25474 | -0.26526 | -0.70947 | -0.13368 | -0.13895 | -0.14526 | -0.15263 | -0.15895 | -0.16737 | -0.17263 | -0.17895 | -0.18632 | -0.19053 | -0.21263 | -0.22632 | -0.58842 | -0.29263 | -0.30526 | -0.31579 | -0.32737 | -0.33789 | -0.35053 | -0.36105 | -0.37263 | -0.38211 | -0.39263 | -0.43895 | -0.47684 | -1.3768
|  | ROUSAY | CF |  |  |  |  | -0.19579 | -0.19895 | -0.20105 | -0.20316 | -0.20632 | -0.20842 | -0.21158 | -0.21474 | -0.21684 | -0.21895 | -0.23053 | -0.23789 | -0.24632 | -0.12947 | -0.13368 | -0.13684 | -0.14105 | -0.14632 | -0.14947 | -0.15368 | -0.15895 | -0.16211 | -0.16632 | -0.18526 | -0.19789 | -0.20737 | -0.27789 | -0.28105 | -0.28421 | -0.28842 | -0.29263 | -0.29579 | -0.3 | -0.30421 | -0.30737 | -0.31053 | -0.32842 | -0.33895 | -0.34632
| CRAIGIEBUCKLER | RUTHRIESTON | MINIMUM HEADROOM | NJ 92574 04060 | NO | YES | 0.19 | 25.1647 | 25.01 | 24.85 | 24.6879 | 24.5226 | 24.3279 | 24.1405 | 23.9595 | 23.7795 | 23.5279 | 22.5111 | 21.5826 | 20.7342 | 23.4921 | 23.3342 | 23.1689 | 22.9984 | 22.7342 | 22.4237 | 22.1258 | 21.8332 | 21.5468 | 21.2668 | 20.2932 | 19.3553 | 18.4921 | 24.1584 | 24.0037 | 23.8353 | 23.6637 | 23.4911 | 23.2889 | 23.0963 | 22.9079 | 22.6174 | 22.3195 | 21.2932 | 20.2805 | 19.3405
|  | RUTHRIESTON | EE |  |  |  |  | 25.2268 | 25.1068 | 24.9784 | 24.8458 | 24.7058 | 24.5489 | 24.3953 | 24.2426 | 24.0995 | 23.9626 | 23.1732 | 22.5058 | 21.8995 | 23.5542 | 23.4332 | 23.3037 | 23.1658 | 23.0216 | 22.85 | 22.6068 | 22.3668 | 22.1395 | 21.9195 | 20.9237 | 20.3111 | 19.6984 | 24.2205 | 24.1005 | 23.9721 | 23.8321 | 23.6858 | 23.5237 | 23.3668 | 23.21 | 23.0626 | 22.9205 | 21.9468 | 21.2911 | 20.6216
|  | RUTHRIESTON | HT |  |  |  |  | 25.1647 | 25.01 | 24.85 | 24.6879 | 24.5226 | 24.3279 | 24.1405 | 23.9595 | 23.7795 | 23.5279 | 22.5111 | 21.5826 | 20.7342 | 23.4921 | 23.3342 | 23.1689 | 22.9984 | 22.7342 | 22.4237 | 22.1258 | 21.8332 | 21.5468 | 21.2668 | 20.2932 | 19.3553 | 18.4921 | 24.1584 | 24.0037 | 23.8353 | 23.6637 | 23.4911 | 23.2889 | 23.0963 | 22.9079 | 22.6174 | 22.3195 | 21.2932 | 20.2805 | 19.3405
|  | RUTHRIESTON | HE |  |  |  |  | 25.3005 | 25.2132 | 25.1174 | 25.0121 | 24.9016 | 24.77 | 24.65 | 24.5311 | 24.4195 | 24.3174 | 23.95 | 23.7342 | 23.5921 | 23.6279 | 23.5405 | 23.4447 | 23.3395 | 23.2289 | 23.1037 | 22.9868 | 22.8732 | 22.7647 | 22.6668 | 22.1079 | 21.6879 | 21.3637 | 24.1584 | 24.0037 | 23.8353 | 23.6637 | 23.4911 | 23.2889 | 23.0963 | 22.9079 | 22.6174 | 22.3195 | 21.2932 | 20.2805 | 19.3405
|  | RUTHRIESTON | CF |  |  |  |  | 25.3374 | 25.2805 | 25.2216 | 25.1616 | 25.0984 | 25.0311 | 24.9637 | 24.8942 | 24.8258 | 24.7595 | 24.4668 | 24.2984 | 24.2079 | 23.6647 | 23.6079 | 23.5489 | 23.4889 | 23.4268 | 23.3605 | 23.2953 | 23.2279 | 23.1584 | 23.0921 | 22.7521 | 22.3847 | 22.1121 | 24.3311 | 24.2742 | 24.2153 | 24.1553 | 24.0921 | 24.0258 | 23.9574 | 23.89 | 23.8184 | 23.75 | 23.4437 | 23.2658 | 23.1647
| TAYNUILT | SALEN | MINIMUM HEADROOM | NM 57252 42849 | NO | YES | 0 | 6.9147 | 6.8842 | 6.84 | 6.72 | 6.5874 | 6.4032 | 6.2674 | 6.2074 | 6.1442 | 6.0863 | 5.9032 | 5.7547 | 5.58 | 6.5863 | 6.5558 | 6.5032 | 6.3663 | 6.2158 | 6.0032 | 5.8484 | 5.7832 | 5.7126 | 5.6516 | 5.4537 | 5.2916 | 5.0937 | 6.6358 | 6.6042 | 6.5726 | 6.5179 | 6.3653 | 6.1495 | 5.9926 | 5.9274 | 5.8568 | 5.7958 | 5.5937 | 5.4295 | 5.2284
|  | SALEN | EE |  |  |  |  | 6.9274 | 6.9021 | 6.8758 | 6.7842 | 6.66 | 6.4863 | 6.3621 | 6.3158 | 6.2716 | 6.22 | 6.04 | 5.9263 | 5.8326 | 6.5989 | 6.5737 | 6.5484 | 6.4389 | 6.2979 | 6.0968 | 5.9558 | 5.9063 | 5.86 | 5.8042 | 5.6116 | 5.4895 | 5.3884 | 6.6484 | 6.6221 | 6.5958 | 6.5684 | 6.4453 | 6.2411 | 6.0968 | 6.0474 | 5.9989 | 5.9421 | 5.7442 | 5.6168 | 5.5105
|  | SALEN | HT |  |  |  |  | 6.9147 | 6.8842 | 6.84 | 6.72 | 6.5874 | 6.4032 | 6.2674 | 6.2074 | 6.1442 | 6.0863 | 5.9032 | 5.7547 | 5.58 | 6.5863 | 6.5558 | 6.5032 | 6.3663 | 6.2158 | 6.0032 | 5.8484 | 5.7832 | 5.7126 | 5.6516 | 5.4537 | 5.2916 | 5.0937 | 6.6358 | 6.6042 | 6.5726 | 6.5179 | 6.3653 | 6.1495 | 5.9926 | 5.9274 | 5.8568 | 5.7958 | 5.5937 | 5.4295 | 5.2284
|  | SALEN | HE |  |  |  |  | 6.9442 | 6.9284 | 6.9095 | 6.8642 | 6.7558 | 6.5863 | 6.4705 | 6.4337 | 6.3979 | 6.3705 | 6.2811 | 6.2221 | 6.18 | 6.6158 | 6.6 | 6.5821 | 6.5253 | 6.4011 | 6.2021 | 6.0695 | 6.0284 | 5.9895 | 5.96 | 5.8663 | 5.8032 | 5.7568 | 6.6358 | 6.6042 | 6.5726 | 6.5179 | 6.3653 | 6.1495 | 5.9926 | 5.9274 | 5.8568 | 5.7958 | 5.5937 | 5.4295 | 5.2284
|  | SALEN | CF |  |  |  |  | 6.9537 | 6.9442 | 6.9347 | 6.9253 | 6.9147 | 6.8558 | 6.8042 | 6.7832 | 6.7579 | 6.7295 | 6.6305 | 6.5789 | 6.5421 | 6.6253 | 6.6158 | 6.6063 | 6.5968 | 6.5821 | 6.5126 | 6.4537 | 6.4295 | 6.4021 | 6.3695 | 6.2589 | 6.2042 | 6.1621 | 6.6747 | 6.6653 | 6.6558 | 6.6453 | 6.6347 | 6.6253 | 6.6042 | 6.5811 | 6.5526 | 6.52 | 6.4095 | 6.3526 | 6.3105
| FORT WILLIAM | SALEN 2 | MINIMUM HEADROOM | NM 69002 65519 | YES | NO | 0 | 2.5389 | 3.6353 | 3.5805 | 3.5268 | 3.4742 | 3.4216 | 3.3689 | 3.3205 | 3.2732 | 3.2279 | 3.0584 | 2.9121 | 2.7974 | 2.7011 | 3.7942 | 3.7374 | 3.6805 | 3.6258 | 3.57 | 3.5163 | 3.4658 | 3.4163 | 3.3689 | 3.1995 | 3.0363 | 2.9089 | 2.6263 | 3.7195 | 3.6626 | 3.6068 | 3.5511 | 3.4963 | 3.4426 | 3.3911 | 3.3426 | 3.2953 | 3.1353 | 2.9784 | 2.8563
|  | SALEN 2 | EE |  |  |  |  | 2.5642 | 3.6721 | 3.63 | 3.5879 | 3.5458 | 3.5058 | 3.4647 | 3.4268 | 3.3921 | 3.3563 | 3.23 | 3.1195 | 3.0395 | 2.7284 | 3.8332 | 3.79 | 3.7447 | 3.7016 | 3.6595 | 3.6163 | 3.5774 | 3.5405 | 3.5037 | 3.3847 | 3.2647 | 3.1742 | 2.6537 | 3.7595 | 3.7153 | 3.6711 | 3.6279 | 3.5847 | 3.5426 | 3.5037 | 3.4668 | 3.43 | 3.3163 | 3.1984 | 3.1121
|  | SALEN 2 | HT |  |  |  |  | 2.5389 | 3.6353 | 3.5805 | 3.5268 | 3.4742 | 3.4216 | 3.3689 | 3.3205 | 3.2732 | 3.2279 | 3.0584 | 2.9121 | 2.7974 | 2.7011 | 3.7942 | 3.7374 | 3.6805 | 3.6258 | 3.57 | 3.5163 | 3.4658 | 3.4163 | 3.3689 | 3.1995 | 3.0363 | 2.9089 | 2.6263 | 3.7195 | 3.6626 | 3.6068 | 3.5511 | 3.4963 | 3.4426 | 3.3911 | 3.3426 | 3.2953 | 3.1353 | 2.9784 | 2.8563
|  | SALEN 2 | HE |  |  |  |  | 2.5989 | 3.7226 | 3.6974 | 3.6689 | 3.6416 | 3.6132 | 3.5868 | 3.5605 | 3.5374 | 3.5142 | 3.4332 | 3.3805 | 3.3437 | 2.7642 | 3.8868 | 3.8605 | 3.8311 | 3.8026 | 3.7732 | 3.7458 | 3.7184 | 3.6942 | 3.6711 | 3.5858 | 3.53 | 3.49 | 2.6263 | 3.7195 | 3.6626 | 3.6068 | 3.5511 | 3.4963 | 3.4426 | 3.3911 | 3.3426 | 3.2953 | 3.1353 | 2.9784 | 2.8563
|  | SALEN 2 | CF |  |  |  |  | 2.6158 | 3.7511 | 3.7353 | 3.7205 | 3.7037 | 3.6889 | 3.6732 | 3.6574 | 3.6405 | 3.6258 | 3.5574 | 3.5111 | 3.4784 | 2.78 | 3.9163 | 3.9005 | 3.8847 | 3.8668 | 3.8511 | 3.8353 | 3.8184 | 3.8005 | 3.7858 | 3.7132 | 3.6637 | 3.6279 | 2.7084 | 3.8416 | 3.8258 | 3.81 | 3.7932 | 3.7763 | 3.7605 | 3.7437 | 3.7268 | 3.7111 | 3.6395 | 3.59 | 3.5542
| THURSO | SANDAY | MINIMUM HEADROOM | HY 61184 35797 | YES | YES | 0 | 1.1495 | 1.1263 | 1.1011 | 1.0747 | 1.0474 | -2.4558 | -2.5589 | -2.6589 | -2.7474 | -2.8358 | -5.6379 | -6.2832 | -6.6621 | 1.1611 | 1.1379 | 1.1105 | 1.0842 | 1.0558 | -1.7526 | -1.8411 | -1.9253 | -2 | -2.0758 | -4.3684 | -4.9547 | -5.3347 | 1.1284 | 1.1063 | 1.0789 | 1.0547 | 1.0274 | -2.5 | -2.6053 | -2.7053 | -2.7926 | -2.8832 | -5.7011 | -6.3453 | -6.7484
|  | SANDAY | EE |  |  |  |  | 1.16 | 1.1421 | 1.1179 | 1.0937 | 1.0695 | -2.4558 | -2.5589 | -2.6589 | -2.7474 | -2.8358 | -5.6379 | -6.2832 | -6.6621 | 1.1726 | 1.1537 | 1.1305 | 1.1063 | 1.0811 | -1.7526 | -1.8411 | -1.9253 | -2 | -2.0758 | -4.3684 | -4.9547 | -5.3347 | 1.1347 | 1.1211 | 1.0979 | 1.0726 | 1.0484 | -2.5 | -2.6053 | -2.7053 | -2.7926 | -2.8832 | -5.7011 | -6.3453 | -6.7484
|  | SANDAY | HT |  |  |  |  | 1.1495 | 1.1263 | 1.1011 | 1.0747 | 1.0474 | -1.7821 | -1.8589 | -1.9347 | -2.0221 | -2.1116 | -4.8189 | -5.2853 | -5.5768 | 1.1611 | 1.1379 | 1.1105 | 1.0842 | 1.0558 | -1.22 | -1.2863 | -1.3526 | -1.4274 | -1.5053 | -3.7358 | -4.2032 | -4.5126 | 1.1284 | 1.1063 | 1.0789 | 1.0547 | 1.0274 | -1.8221 | -1.8979 | -1.9747 | -2.0632 | -2.1526 | -4.8747 | -5.3558 | -5.6863
|  | SANDAY | HE |  |  |  |  | 1.1747 | 1.1632 | 1.1505 | 1.1368 | 1.1221 | -0.68316 | -0.75895 | -0.83263 | -0.90842 | -1.0053 | -2.5495 | -3.0053 | -3.4937 | 1.1832 | 1.1758 | 1.1632 | 1.1495 | 1.1358 | -0.31789 | -0.38316 | -0.44421 | -0.51053 | -0.59789 | -1.88 | -2.3053 | -2.7705 | 1.1284 | 1.1063 | 1.0789 | 1.0547 | 1.0274 | -1.8221 | -1.8979 | -1.9747 | -2.0632 | -2.1526 | -4.8747 | -5.3558 | -5.6863
|  | SANDAY | CF |  |  |  |  | 1.1821 | 1.1747 | 1.1663 | 1.1589 | 1.1495 | -0.60526 | -0.63789 | -0.66737 | -0.69684 | -0.73474 | -0.93684 | -1.2211 | -1.4958 | 1.1874 | 1.1832 | 1.1789 | 1.1726 | 1.1632 | -0.24737 | -0.27684 | -0.30211 | -0.32632 | -0.36421 | -0.55368 | -0.82105 | -1.1 | 1.1474 | 1.1432 | 1.1368 | 1.1326 | 1.1263 | -0.63789 | -0.67158 | -0.70105 | -0.72947 | -0.76737 | -0.96947 | -1.2516 | -1.5516
| DUNOON | SANDBANK | MINIMUM HEADROOM | NS 15274 81386 | NO | YES | 0.67 | 7.2374 | 7.1584 | 7.0574 | 6.9542 | 6.8511 | 6.7447 | 6.6268 | 6.4942 | 6.3416 | 6.1711 | 5.8153 | 5.5258 | 5.2795 | 6.2142 | 6.1553 | 6.0584 | 5.9511 | 5.8437 | 5.7311 | 5.6089 | 5.4679 | 5.3026 | 5.1195 | 4.7447 | 4.4258 | 4.1532 | 6.6668 | 6.5563 | 6.4468 | 6.3363 | 6.2258 | 6.1121 | 5.9847 | 5.8395 | 5.6689 | 5.4795 | 5.0932 | 4.7753 | 4.5016
|  | SANDBANK | EE |  |  |  |  | 7.2595 | 7.2121 | 7.1426 | 7.0595 | 6.9732 | 6.8879 | 6.7847 | 6.6932 | 6.5932 | 6.4721 | 6.0774 | 5.8553 | 5.6732 | 6.2363 | 6.1889 | 6.1405 | 6.0626 | 5.9742 | 5.8858 | 5.7774 | 5.6805 | 5.5742 | 5.4447 | 5.0289 | 4.7953 | 4.5984 | 6.6921 | 6.6268 | 6.5395 | 6.4489 | 6.3584 | 6.2679 | 6.1553 | 6.0553 | 5.9468 | 5.8121 | 5.3795 | 5.1353 | 4.9311
|  | SANDBANK | HT |  |  |  |  | 7.2374 | 7.1584 | 7.0574 | 6.9542 | 6.8511 | 6.7447 | 6.6268 | 6.4942 | 6.3416 | 6.1711 | 5.8153 | 5.5258 | 5.2795 | 6.2142 | 6.1553 | 6.0584 | 5.9511 | 5.8437 | 5.7311 | 5.6089 | 5.4679 | 5.3026 | 5.1195 | 4.7447 | 4.4258 | 4.1532 | 6.6668 | 6.5563 | 6.4468 | 6.3363 | 6.2258 | 6.1121 | 5.9847 | 5.8395 | 5.6689 | 5.4795 | 5.0932 | 4.7753 | 4.5016
|  | SANDBANK | HE |  |  |  |  | 7.2921 | 7.2605 | 7.2258 | 7.19 | 7.15 | 7.09 | 6.9911 | 6.9005 | 6.7911 | 6.6995 | 6.5258 | 6.4121 | 6.3268 | 6.2689 | 6.2374 | 6.2037 | 6.1679 | 6.1279 | 6.0868 | 5.9921 | 5.8932 | 5.7753 | 5.6774 | 5.4984 | 5.3784 | 5.2879 | 6.6668 | 6.5563 | 6.4468 | 6.3363 | 6.2258 | 6.1121 | 5.9847 | 5.8395 | 5.6689 | 5.4795 | 5.0932 | 4.7753 | 4.5016
|  | SANDBANK | CF |  |  |  |  | 7.31 | 7.2921 | 7.2742 | 7.2553 | 7.2363 | 7.2163 | 7.1963 | 7.17 | 7.1363 | 7.1037 | 6.8963 | 6.7942 | 6.7216 | 6.2868 | 6.2689 | 6.2511 | 6.2321 | 6.2132 | 6.1932 | 6.1742 | 6.1542 | 6.1342 | 6.1089 | 5.8858 | 5.7795 | 5.7005 | 6.7426 | 6.7247 | 6.7068 | 6.6868 | 6.6679 | 6.6405 | 6.6047 | 6.5689 | 6.5332 | 6.4984 | 6.2668 | 6.1563 | 6.0742
| SHETLAND | SANDWICK | MINIMUM HEADROOM | HU4308625957 | YES | YES | 0 | 3.6305 | 3.5432 | 3.4526 | 8.1242 | 8.0368 | 7.9232 | 7.8137 | 7.7063 | 7.5947 | 7.4863 | 7.0684 | 6.7558 | 6.5274 | 3.3653 | 3.2663 | 3.1684 | 7.4295 | 7.3337 | 7.2189 | 7.1074 | 6.9979 | 6.8884 | 6.78 | 6.3579 | 6.0295 | 5.7768 | 3.4305 | 3.3379 | 3.2453 | 7.7095 | 7.6137 | 7.4937 | 7.3768 | 7.2632 | 7.1484 | 7.0337 | 6.5832 | 6.2379 | 5.9768
|  | SANDWICK | EE |  |  |  |  | 3.6684 | 3.6 | 3.5274 | 8.2137 | 8.14 | 8.0389 | 7.9326 | 7.8284 | 7.7337 | 7.64 | 7.1937 | 6.8158 | 6.6095 | 3.3895 | 3.3316 | 3.2526 | 7.5316 | 7.4516 | 7.3516 | 7.2495 | 7.1505 | 7.0568 | 6.9663 | 6.5379 | 6.1842 | 5.9705 | 3.4695 | 3.3989 | 3.3232 | 7.8074 | 7.7305 | 7.6253 | 7.5158 | 7.4084 | 7.3095 | 7.2137 | 6.7442 | 6.3463 | 6.1168
|  | SANDWICK | HT |  |  |  |  | 3.6305 | 3.5432 | 3.4526 | 8.1242 | 8.0368 | 7.9232 | 7.8137 | 7.7063 | 7.5947 | 7.4863 | 7.0684 | 6.7558 | 6.5274 | 3.3653 | 3.2663 | 3.1684 | 7.4295 | 7.3337 | 7.2189 | 7.1074 | 6.9979 | 6.8884 | 6.78 | 6.3579 | 6.0295 | 5.7768 | 3.4305 | 3.3379 | 3.2453 | 7.7095 | 7.6137 | 7.4937 | 7.3768 | 7.2632 | 7.1484 | 7.0337 | 6.5832 | 6.2379 | 5.9768
|  | SANDWICK | HE |  |  |  |  | 3.7253 | 3.6811 | 3.6347 | 8.3484 | 8.3 | 8.2168 | 8.1421 | 8.0695 | 7.9989 | 7.9326 | 7.6568 | 7.4411 | 7.2411 | 3.4189 | 3.3916 | 3.3621 | 7.6832 | 7.6305 | 7.5516 | 7.4811 | 7.4126 | 7.3453 | 7.2832 | 7.0274 | 6.8284 | 6.6505 | 3.4305 | 3.3379 | 3.2453 | 7.7095 | 7.6137 | 7.4937 | 7.3768 | 7.2632 | 7.1484 | 7.0337 | 6.5832 | 6.2379 | 5.9768
|  | SANDWICK | CF |  |  |  |  | 3.7516 | 3.7253 | 3.6979 | 8.4295 | 8.4011 | 8.3611 | 8.3211 | 8.2821 | 8.2442 | 8.2105 | 8.0316 | 7.8768 | 7.7642 | 3.4337 | 3.4189 | 3.4032 | 7.7474 | 7.7305 | 7.6989 | 7.6589 | 7.6211 | 7.5821 | 7.5463 | 7.3663 | 7.2179 | 7.1063 | 3.5137 | 3.4989 | 3.4832 | 8.0263 | 8.0021 | 7.9611 | 7.92 | 7.88 | 7.8411 | 7.8063 | 7.6221 | 7.4621 | 7.3442
| SHETLAND | SCALLOWAY | MINIMUM HEADROOM | HU4139939639 | YES | YES | 0 | 2.3789 | 2.2274 | 2.0474 | 8.6158 | 8.4874 | 8.2326 | 7.9811 | 7.7316 | 7.4568 | 7.18 | 5.6158 | 3.3884 | 1.7537 | 1.7126 | 1.5326 | 1.3326 | 7.48 | 7.3421 | 7.1032 | 6.8674 | 6.6347 | 6.3842 | 6.1284 | 4.68 | 2.5305 | 0.85895 | 1.8379 | 1.68 | 1.4789 | 7.8253 | 7.6863 | 7.4253 | 7.1684 | 6.9147 | 6.6358 | 6.3537 | 4.7305 | 2.3253 | 0.50737
|  | SCALLOWAY | EE |  |  |  |  | 2.4042 | 2.3411 | 2.1821 | 8.7695 | 8.5853 | 8.3253 | 8.0347 | 7.74 | 7.48 | 7.2189 | 5.6158 | 3.3884 | 1.7537 | 1.7684 | 1.6642 | 1.4874 | 7.6579 | 7.4505 | 7.2147 | 6.9537 | 6.6916 | 6.4589 | 6.2242 | 4.7505 | 2.5968 | 0.85895 | 1.8632 | 1.8074 | 1.6326 | 8 | 7.7926 | 7.5295 | 7.2379 | 6.9411 | 6.6789 | 6.4158 | 4.7305 | 2.3253 | 0.50737
|  | SCALLOWAY | HT |  |  |  |  | 2.3789 | 2.2274 | 2.0474 | 8.6158 | 8.4874 | 8.2326 | 7.9811 | 7.7316 | 7.4568 | 7.18 | 5.6863 | 3.66 | 2.2874 | 1.7126 | 1.5326 | 1.3326 | 7.48 | 7.3421 | 7.1032 | 6.8674 | 6.6347 | 6.3842 | 6.1284 | 4.68 | 2.5305 | 1.0368 | 1.8379 | 1.68 | 1.4789 | 7.8253 | 7.6863 | 7.4253 | 7.1684 | 6.9147 | 6.6358 | 6.3537 | 4.7705 | 2.5211 | 0.95579
|  | SCALLOWAY | HE |  |  |  |  | 2.4442 | 2.4074 | 2.36 | 9.0116 | 8.8958 | 8.5937 | 8.3558 | 8.1453 | 7.94 | 7.74 | 6.3653 | 4.6842 | 2.8842 | 1.8084 | 1.7716 | 1.6832 | 7.9232 | 7.7916 | 7.5074 | 7.2863 | 7.1021 | 6.9189 | 6.74 | 5.4137 | 3.7274 | 1.9179 | 1.8379 | 1.68 | 1.4789 | 7.8253 | 7.6863 | 7.4253 | 7.1684 | 6.9147 | 6.6358 | 6.3537 | 4.7705 | 2.5211 | 0.95579
|  | SCALLOWAY | CF |  |  |  |  | 2.4663 | 2.4453 | 2.4221 | 9.1568 | 9.1221 | 8.9947 | 8.8747 | 8.7642 | 8.6779 | 8.6032 | 7.8895 | 6.8295 | 5.6895 | 1.8305 | 1.8095 | 1.7863 | 8.1137 | 8.0442 | 7.9221 | 7.8042 | 7.6979 | 7.6179 | 7.5463 | 6.8084 | 5.7316 | 4.5316 | 1.9253 | 1.9042 | 1.8811 | 8.4168 | 8.3895 | 8.2568 | 8.1284 | 8.0147 | 7.9263 | 7.8495 | 7.0684 | 5.9316 | 4.6642
| TAYNUILT | SCAMMADALE | MINIMUM HEADROOM | NM 84207 19638 | YES | YES | 0 | 0.12 | 0.11789 | 0.11474 | 0.11368 | 0.11158 | 0.10947 | 0.10737 | 0.10526 | 0.10316 | 0.10105 | 0.094737 | 0.089474 | 0.084211 | 0.11053 | 0.10947 | 0.10737 | 0.10632 | 0.10526 | 0.10421 | 0.10105 | 0.1 | 0.097895 | 0.095789 | 0.088421 | 0.082105 | 0.076842 | 0.11263 | 0.11158 | 0.10842 | 0.10632 | 0.10421 | 0.10211 | 0.098947 | 0.096842 | 0.094737 | 0.093684 | 0.085263 | 0.08 | 0.073684
|  | SCAMMADALE | EE |  |  |  |  | 0.12105 | 0.11895 | 0.11684 | 0.11474 | 0.11368 | 0.11263 | 0.11053 | 0.10842 | 0.10842 | 0.10737 | 0.1 | 0.096842 | 0.092632 | 0.11053 | 0.10947 | 0.10842 | 0.10737 | 0.10632 | 0.10526 | 0.10421 | 0.10316 | 0.10211 | 0.10105 | 0.094737 | 0.090526 | 0.086316 | 0.11368 | 0.11158 | 0.11053 | 0.10842 | 0.10632 | 0.10526 | 0.10316 | 0.10105 | 0.1 | 0.098947 | 0.092632 | 0.088421 | 0.083158
|  | SCAMMADALE | HT |  |  |  |  | 0.12 | 0.11789 | 0.11474 | 0.11368 | 0.11158 | 0.10947 | 0.10737 | 0.10526 | 0.10316 | 0.10105 | 0.094737 | 0.089474 | 0.084211 | 0.11053 | 0.10947 | 0.10737 | 0.10632 | 0.10526 | 0.10421 | 0.10105 | 0.1 | 0.097895 | 0.095789 | 0.088421 | 0.082105 | 0.076842 | 0.11263 | 0.11158 | 0.10842 | 0.10632 | 0.10421 | 0.10211 | 0.098947 | 0.096842 | 0.094737 | 0.093684 | 0.085263 | 0.08 | 0.073684
|  | SCAMMADALE | HE |  |  |  |  | 0.12211 | 0.12105 | 0.12105 | 0.11895 | 0.11789 | 0.11684 | 0.11579 | 0.11474 | 0.11263 | 0.11263 | 0.10947 | 0.10737 | 0.10526 | 0.11158 | 0.11053 | 0.11053 | 0.10947 | 0.10842 | 0.10842 | 0.10737 | 0.10632 | 0.10526 | 0.10526 | 0.10316 | 0.10211 | 0.1 | 0.11263 | 0.11158 | 0.10842 | 0.10632 | 0.10421 | 0.10211 | 0.098947 | 0.096842 | 0.094737 | 0.093684 | 0.085263 | 0.08 | 0.073684
|  | SCAMMADALE | CF |  |  |  |  | 0.12211 | 0.12211 | 0.12211 | 0.12105 | 0.12105 | 0.12105 | 0.11895 | 0.11895 | 0.11789 | 0.11684 | 0.11474 | 0.11263 | 0.11158 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.11053 | 0.11053 | 0.10947 | 0.10947 | 0.10947 | 0.10842 | 0.10737 | 0.10632 | 0.10632 | 0.11474 | 0.11474 | 0.11474 | 0.11368 | 0.11368 | 0.11368 | 0.11158 | 0.11158 | 0.11158 | 0.11053 | 0.10842 | 0.10526 | 0.10421
| ABERNETHY | SCONE | MINIMUM HEADROOM | NO 14401 25495 | NO | YES | 0.426 | 15.1324 | 14.8682 | 14.5345 | 14.1672 | 13.7703 | 13.2787 | 12.8082 | 12.3451 | 11.8819 | 11.4198 | 9.4072 | 8.4198 | 7.804 | 13.5593 | 13.2435 | 12.8603 | 12.4403 | 11.9845 | 11.4519 | 10.9435 | 10.4435 | 9.9435 | 9.4529 | 7.2898 | 6.2498 | 5.5951 | 14.2785 | 13.9564 | 13.5648 | 13.1353 | 12.6701 | 12.1185 | 11.5922 | 11.0732 | 10.5532 | 10.0416 | 7.789 | 6.7037 | 6.0269
|  | SCONE | EE |  |  |  |  | 15.2261 | 15.0124 | 14.744 | 14.3429 | 14.0977 | 13.6798 | 13.2493 | 12.8261 | 12.4208 | 12.0166 | 10.0545 | 9.0535 | 8.5556 | 13.6698 | 13.4119 | 13.0908 | 12.6203 | 12.3445 | 11.8824 | 11.4203 | 10.9687 | 10.534 | 10.0972 | 8.0151 | 7.0129 | 6.4982 | 14.3911 | 14.1269 | 13.7995 | 13.3164 | 13.0353 | 12.5522 | 12.0679 | 11.5953 | 11.1385 | 10.6816 | 8.4911 | 7.4079 | 6.8637
|  | SCONE | HT |  |  |  |  | 15.1324 | 14.8682 | 14.5345 | 14.1672 | 13.7703 | 13.2787 | 12.8082 | 12.3451 | 11.8819 | 11.4198 | 9.4072 | 8.4198 | 7.804 | 13.5593 | 13.2435 | 12.8603 | 12.4403 | 11.9845 | 11.4519 | 10.9435 | 10.4435 | 9.9435 | 9.4529 | 7.2898 | 6.2498 | 5.5951 | 14.2785 | 13.9564 | 13.5648 | 13.1353 | 12.6701 | 12.1185 | 11.5922 | 11.0732 | 10.5532 | 10.0416 | 7.789 | 6.7037 | 6.0269
|  | SCONE | HE |  |  |  |  | 15.3503 | 15.1956 | 14.9924 | 14.7493 | 14.4682 | 14.1008 | 13.7472 | 13.3882 | 13.0345 | 12.6903 | 11.1114 | 10.464 | 10.0787 | 13.8161 | 13.6266 | 13.374 | 13.0845 | 12.7572 | 12.3477 | 11.954 | 11.5656 | 11.1845 | 10.8098 | 9.1056 | 8.4508 | 8.0929 | 14.2785 | 13.9564 | 13.5648 | 13.1353 | 12.6701 | 12.1185 | 11.5922 | 11.0732 | 10.5532 | 10.0416 | 7.789 | 6.7037 | 6.0269
|  | SCONE | CF |  |  |  |  | 15.424 | 15.3335 | 15.224 | 15.1061 | 14.9787 | 14.8145 | 14.6429 | 14.4608 | 14.2787 | 14.0872 | 13.0661 | 12.6008 | 12.3482 | 13.9035 | 13.7929 | 13.6582 | 13.5098 | 13.3519 | 13.1645 | 12.9698 | 12.7635 | 12.5529 | 12.3319 | 11.194 | 10.7108 | 10.4561 | 14.6206 | 14.5164 | 14.3774 | 14.2269 | 14.0637 | 13.869 | 13.6658 | 13.4511 | 13.2332 | 13.0048 | 11.8206 | 11.3048 | 11.029
| THURSO | SHAPINSAY | MINIMUM HEADROOM | HY 48313 17148 | YES | YES | 0 | 1.0105 | 1 | 0.98316 | 0.96842 | 0.95158 | 0.82737 | 0.67579 | 0.51684 | 0.36316 | 0.14 | -1.1726 | -2.6958 | -3.8358 | 0.97684 | 0.96421 | 0.94842 | 0.93158 | 0.91474 | 0.82 | 0.68105 | 0.53368 | 0.39474 | 0.17789 | -1.0284 | -2.52 | -3.7558 | 0.97684 | 0.96421 | 0.94632 | 0.92947 | 0.91158 | 0.78842 | 0.63368 | 0.47474 | 0.33789 | 0.12421 | -1.3411 | -3 | -4.2916
|  | SHAPINSAY | EE |  |  |  |  | 1.0158 | 1.0074 | 0.98947 | 0.97263 | 0.95474 | 0.82737 | 0.67579 | 0.52105 | 0.38526 | 0.20526 | -1.1726 | -2.6958 | -3.8358 | 0.98211 | 0.97263 | 0.95579 | 0.93895 | 0.92316 | 0.82 | 0.69474 | 0.56737 | 0.45579 | 0.29579 | -1.0284 | -2.52 | -3.7558 | 0.98316 | 0.97263 | 0.95368 | 0.93474 | 0.91684 | 0.78842 | 0.63368 | 0.47474 | 0.33789 | 0.15053 | -1.3411 | -3 | -4.2916
|  | SHAPINSAY | HT |  |  |  |  | 1.0105 | 1 | 0.98316 | 0.96842 | 0.95158 | 0.84421 | 0.73789 | 0.62737 | 0.46526 | 0.2 | -1.0242 | -2.4011 | -3.3316 | 0.97684 | 0.96421 | 0.94842 | 0.93158 | 0.91474 | 0.83053 | 0.74105 | 0.64737 | 0.50421 | 0.24421 | -1.0011 | -2.4926 | -3.54 | 0.97684 | 0.96421 | 0.94632 | 0.92947 | 0.91158 | 0.80421 | 0.69579 | 0.58211 | 0.41474 | 0.12421 | -1.2242 | -2.7905 | -3.8642
|  | SHAPINSAY | HE |  |  |  |  | 1.0211 | 1.0168 | 1.0095 | 1.0021 | 0.99474 | 0.83474 | 0.67789 | 0.51684 | 0.36316 | 0.14 | -0.80737 | -1.98 | -3.2589 | 0.98947 | 0.98421 | 0.97684 | 0.96842 | 0.96105 | 0.82316 | 0.68105 | 0.53368 | 0.39474 | 0.17789 | -0.73789 | -1.9284 | -3.2295 | 0.97684 | 0.96421 | 0.94632 | 0.92947 | 0.91158 | 0.80421 | 0.69579 | 0.58211 | 0.41474 | 0.12421 | -1.2242 | -2.7905 | -3.8642
|  | SHAPINSAY | CF |  |  |  |  | 1.0253 | 1.0211 | 1.0158 | 1.0126 | 1.0074 | 0.95684 | 0.91368 | 0.82316 | 0.72737 | 0.62316 | 0.13684 | -0.60105 | -1.4147 | 0.99368 | 0.98947 | 0.98421 | 0.97895 | 0.97474 | 0.93474 | 0.89684 | 0.80842 | 0.71053 | 0.59789 | 0.10737 | -0.64632 | -1.52 | 0.99263 | 0.98947 | 0.98316 | 0.97895 | 0.97368 | 0.92105 | 0.87474 | 0.77684 | 0.67158 | 0.55368 | 0.022105 | -0.79684 | -1.7179
| BROADFORD | SHIELDAIG | MINIMUM HEADROOM | NG 81637 52250 | YES | YES | 0 | -1.4747 | -1.5168 | -1.5632 | -1.6116 | -1.6611 | -1.7116 | -1.7558 | -1.8 | -1.8463 | -1.8926 | -2.1042 | -2.2789 | -2.4537 | -1.3568 | -1.3968 | -1.4421 | -1.4895 | -1.5368 | -1.5863 | -1.6305 | -1.6737 | -1.72 | -1.7653 | -1.9747 | -2.1474 | -2.3211 | -1.4958 | -1.5389 | -1.5853 | -1.6347 | -1.6842 | -1.7347 | -1.7811 | -1.8263 | -1.8737 | -1.92 | -2.1368 | -2.3147 | -2.4926
|  | SHIELDAIG | EE |  |  |  |  | -1.4726 | -1.5168 | -1.5632 | -1.6116 | -1.6611 | -1.7116 | -1.7558 | -1.8 | -1.8463 | -1.8926 | -2.1042 | -2.2789 | -2.4537 | -1.3537 | -1.3968 | -1.4421 | -1.4895 | -1.5368 | -1.5863 | -1.6305 | -1.6737 | -1.72 | -1.7653 | -1.9747 | -2.1474 | -2.3211 | -1.4937 | -1.5389 | -1.5853 | -1.6347 | -1.6842 | -1.7347 | -1.7811 | -1.8263 | -1.8737 | -1.92 | -2.1368 | -2.3147 | -2.4926
|  | SHIELDAIG | HT |  |  |  |  | -1.4747 | -1.4926 | -1.5095 | -1.5274 | -1.5453 | -1.5642 | -1.5821 | -1.6 | -1.6179 | -1.6347 | -1.7147 | -1.7895 | -1.8653 | -1.3568 | -1.3747 | -1.3926 | -1.4105 | -1.4295 | -1.4505 | -1.4695 | -1.4884 | -1.5074 | -1.5263 | -1.6126 | -1.6937 | -1.7737 | -1.4958 | -1.5137 | -1.5326 | -1.5505 | -1.5684 | -1.5874 | -1.6063 | -1.6263 | -1.6442 | -1.6621 | -1.7463 | -1.8242 | -1.9032
|  | SHIELDAIG | HE |  |  |  |  | -1.4695 | -1.4842 | -1.4989 | -1.5147 | -1.5305 | -1.5463 | -1.5621 | -1.5779 | -1.5926 | -1.6084 | -1.68 | -1.7495 | -1.8189 | -1.3495 | -1.3642 | -1.3789 | -1.3947 | -1.4105 | -1.4263 | -1.4411 | -1.4568 | -1.4716 | -1.4874 | -1.56 | -1.6305 | -1.6989 | -1.4958 | -1.5137 | -1.5326 | -1.5505 | -1.5684 | -1.5874 | -1.6063 | -1.6263 | -1.6442 | -1.6621 | -1.7463 | -1.8242 | -1.9032
|  | SHIELDAIG | CF |  |  |  |  | 0.99474 | -1.4716 | -1.4768 | -1.4811 | -1.4863 | -1.4895 | -1.4947 | -1.4989 | -1.5042 | -1.5074 | -1.5263 | -1.54 | -1.5505 | 0.99474 | -1.3516 | -1.3579 | -1.3611 | -1.3663 | -1.3695 | -1.3758 | -1.3789 | -1.3853 | -1.3884 | -1.4095 | -1.4253 | -1.4389 | 0.99474 | -1.4916 | -1.4979 | -1.5021 | -1.5074 | -1.5116 | -1.5168 | -1.52 | -1.5253 | -1.5284 | -1.5495 | -1.5632 | -1.5758
| SHIN | SHIN | MINIMUM HEADROOM | NH 57246 97463 | YES | NO | 0 | 2.5558 | 2.1158 | 1.6116 | 1.0832 | 0.53263 | -0.082105 | -0.64421 | -1.2168 | -1.7926 | -2.3779 | -5.1095 | -7.5074 | -9.6832 | 2.4979 | 2.0758 | 1.58 | 1.0695 | 0.54632 | -0.031579 | -0.55684 | -1.0895 | -1.6284 | -2.1758 | -4.8179 | -7.16 | -9.3526 | 2.4989 | 2.0421 | 1.54 | 1.0105 | 0.46 | -0.16211 | -0.73053 | -1.3095 | -1.8905 | -2.4811 | -5.3011 | -7.8253 | -10.1305
|  | SHIN | EE |  |  |  |  | 2.5632 | 2.1158 | 1.6116 | 1.0832 | 0.53263 | -0.082105 | -0.64421 | -1.2168 | -1.7926 | -2.3779 | -5.1095 | -7.5074 | -9.6832 | 2.5063 | 2.0758 | 1.58 | 1.0695 | 0.54632 | -0.031579 | -0.55684 | -1.0895 | -1.6284 | -2.1758 | -4.8179 | -7.16 | -9.3526 | 2.5074 | 2.0421 | 1.54 | 1.0105 | 0.46 | -0.16211 | -0.73053 | -1.3095 | -1.8905 | -2.4811 | -5.3011 | -7.8253 | -10.1305
|  | SHIN | HT |  |  |  |  | 2.5558 | 2.4326 | 2.2821 | 2.1284 | 1.9695 | 1.7663 | 1.5621 | 1.3589 | 1.1442 | 0.92211 | -0.12842 | -1.3758 | -2.4253 | 2.4979 | 2.3884 | 2.24 | 2.0842 | 1.9284 | 1.7379 | 1.5453 | 1.3558 | 1.1558 | 0.94 | -0.13158 | -1.2905 | -2.3642 | 2.4989 | 2.3579 | 2.2011 | 2.0442 | 1.8874 | 1.6842 | 1.48 | 1.2747 | 1.0558 | 0.81684 | -0.39684 | -1.8453 | -3.0484
|  | SHIN | HE |  |  |  |  | 2.5726 | 2.4516 | 2.3032 | 2.1558 | 2.0032 | 1.7916 | 1.5853 | 1.3737 | 1.1674 | 0.96105 | -0.068421 | -1.1568 | -2.3821 | 2.5179 | 2.4126 | 2.2621 | 2.1158 | 1.9642 | 1.7695 | 1.5747 | 1.3726 | 1.1768 | 0.97158 | -0.038947 | -1.1137 | -2.2358 | 2.4989 | 2.3579 | 2.2011 | 2.0442 | 1.8874 | 1.6842 | 1.48 | 1.2747 | 1.0558 | 0.81684 | -0.39684 | -1.8453 | -3.0484
|  | SHIN | CF |  |  |  |  | 2.5779 | 2.5484 | 2.5147 | 2.48 | 2.4453 | 2.3863 | 2.3305 | 2.2716 | 2.2074 | 2.1347 | 1.78 | 1.3021 | 0.79579 | 2.5242 | 2.5042 | 2.4705 | 2.4389 | 2.4063 | 2.3526 | 2.3021 | 2.2463 | 2.1905 | 2.1221 | 1.8011 | 1.38 | 0.89789 | 2.5253 | 2.4884 | 2.4463 | 2.4084 | 2.3705 | 2.3105 | 2.2526 | 2.1884 | 2.1232 | 2.0337 | 1.6326 | 1.1021 | 0.53053
| FORT WILLIAM | SHONA BEG | MINIMUM HEADROOM | NM 67173 74363 | YES | NO | 0 | 0.10737 | 0.10737 | 0.10737 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10211 | 0.10105 | 0.098947 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.098947 | 0.096842 | 0.094737 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.098947 | 0.096842
|  | SHONA BEG | EE |  |  |  |  | 0.10842 | 0.10737 | 0.10737 | 0.10737 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10421 | 0.10316 | 0.10105 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10105 | 0.1 | 0.1 | 0.097895 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.1
|  | SHONA BEG | HT |  |  |  |  | 0.10737 | 0.10737 | 0.10737 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10211 | 0.10105 | 0.098947 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.098947 | 0.096842 | 0.094737 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.098947 | 0.096842
|  | SHONA BEG | HE |  |  |  |  | 0.10842 | 0.10842 | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10211 | 0.10211 | 0.10105 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10316 | 0.10105 | 0.098947 | 0.096842
|  | SHONA BEG | CF |  |  |  |  | 0.10842 | 0.10842 | 0.10842 | 0.10842 | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10737 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10421 | 0.10316 | 0.10316 | 0.10316 | 0.10632 | 0.10632 | 0.10632 | 0.10632 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10526 | 0.10421 | 0.10421 | 0.10421
| KINTORE | SKENE | MINIMUM HEADROOM | NJ 82203 06495 | NO | YES | 0 | 32.6284 | 32.4337 | 32.2253 | 32.0116 | 31.7042 | 31.1874 | 30.5779 | 29.9642 | 29.2653 | 28.4653 | 26.0947 | 24.3558 | 22.7853 | 29.68 | 29.4853 | 29.2811 | 29.0726 | 28.76 | 28.2726 | 27.6684 | 27.0611 | 26.3621 | 25.5126 | 23.1105 | 21.6389 | 19.7674 | 27.9374 | 27.6963 | 27.4416 | 27.1847 | 26.9258 | 26.5037 | 26.0563 | 25.6142 | 25.1268 | 24.6111 | 22.9279 | 21.2511 | 20.3742
|  | SKENE | EE |  |  |  |  | 32.7105 | 32.56 | 32.3874 | 32.2084 | 32.0242 | 31.6463 | 31.1274 | 30.5568 | 30.0274 | 29.4663 | 26.3895 | 24.3558 | 22.7853 | 29.7621 | 29.6116 | 29.4463 | 29.2747 | 29.0968 | 28.8 | 28.3442 | 27.8263 | 27.3189 | 26.7642 | 23.66 | 21.8253 | 20.1505 | 28.0416 | 27.8574 | 27.6489 | 27.4332 | 27.2153 | 26.8079 | 26.37 | 25.9142 | 25.5037 | 25.0847 | 22.9416 | 21.2511 | 20.3742
|  | SKENE | HT |  |  |  |  | 32.6284 | 32.4337 | 32.2253 | 32.0116 | 31.7042 | 31.1874 | 30.5779 | 29.9642 | 29.2653 | 28.4653 | 26.0947 | 24.62 | 22.9337 | 29.68 | 29.4853 | 29.2811 | 29.0726 | 28.76 | 28.2726 | 27.6684 | 27.0611 | 26.3621 | 25.5126 | 23.1105 | 21.6389 | 19.7674 | 27.9374 | 27.6963 | 27.4416 | 27.1847 | 26.9258 | 26.5037 | 26.0563 | 25.6142 | 25.1268 | 24.6111 | 22.9279 | 21.8711 | 20.6763
|  | SKENE | HE |  |  |  |  | 32.8221 | 32.7242 | 32.6147 | 32.4958 | 32.3695 | 32.0442 | 31.76 | 31.4789 | 31.1337 | 30.7116 | 28.8611 | 27.0579 | 24.7389 | 29.8737 | 29.7758 | 29.6674 | 29.5495 | 29.4253 | 29.2021 | 29.0032 | 28.8074 | 28.4747 | 28.0747 | 26.2684 | 24.4495 | 22.0232 | 27.9374 | 27.6963 | 27.4416 | 27.1847 | 26.9258 | 26.5037 | 26.0563 | 25.6142 | 25.1268 | 24.6111 | 22.9279 | 21.8711 | 20.6763
|  | SKENE | CF |  |  |  |  | 32.88 | 32.8242 | 32.7653 | 32.7042 | 32.6432 | 32.5084 | 32.3821 | 32.2589 | 32.1421 | 32.0421 | 31.2484 | 30.0874 | 28.6274 | 29.9316 | 29.8758 | 29.8179 | 29.7579 | 29.6979 | 29.6021 | 29.5084 | 29.4179 | 29.3295 | 29.2495 | 28.5147 | 27.3526 | 25.7179 | 28.27 | 28.2005 | 28.1289 | 28.0532 | 27.9763 | 27.8195 | 27.6721 | 27.5279 | 27.3879 | 27.2626 | 26.5311 | 25.7679 | 25.0479
| BROADFORD | SKULAMUS | MINIMUM HEADROOM | NG 65881 22438 | YES | YES | 0 | 1.7937 | 7.0263 | 6.9232 | 6.8168 | 6.6853 | 6.3821 | 6.0821 | 5.7842 | 5.4937 | 5.2242 | 4.5411 | 3.7358 | 2.7189 | 1.3537 | 6.5463 | 6.4337 | 6.3179 | 6.1768 | 5.8747 | 5.5695 | 5.2589 | 4.9632 | 4.6916 | 4.0579 | 3.2232 | 2.2558 | 1.4126 | 6.6116 | 6.5042 | 6.3926 | 6.2579 | 5.9337 | 5.6042 | 5.2758 | 4.9589 | 4.6663 | 3.9558 | 3.0674 | 1.9863
|  | SKULAMUS | EE |  |  |  |  | 1.8137 | 7.0747 | 7 | 6.9074 | 6.7937 | 6.5895 | 6.3684 | 6.0516 | 5.7747 | 5.5263 | 4.5411 | 3.7358 | 2.7189 | 1.3789 | 6.6126 | 6.52 | 6.4211 | 6.2958 | 6.1095 | 5.9084 | 5.5905 | 5.3095 | 5.0642 | 4.14 | 3.4263 | 2.32 | 1.4547 | 6.6747 | 6.5842 | 6.4874 | 6.3674 | 6.1579 | 5.9326 | 5.5895 | 5.2874 | 5.0189 | 3.9779 | 3.1421 | 1.9863
|  | SKULAMUS | HT |  |  |  |  | 1.7937 | 7.0263 | 6.9232 | 6.8168 | 6.6853 | 6.3821 | 6.0821 | 5.7842 | 5.4937 | 5.2242 | 4.5442 | 3.7421 | 2.8716 | 1.3537 | 6.5463 | 6.4337 | 6.3179 | 6.1768 | 5.8747 | 5.5695 | 5.2589 | 4.9632 | 4.6916 | 4.0579 | 3.2232 | 2.2558 | 1.4126 | 6.6116 | 6.5042 | 6.3926 | 6.2579 | 5.9337 | 5.6042 | 5.2758 | 4.9589 | 4.6663 | 3.9558 | 3.0674 | 2.0737
|  | SKULAMUS | HE |  |  |  |  | 1.8432 | 7.1179 | 7.0895 | 7.0484 | 6.9632 | 6.7726 | 6.6021 | 6.3495 | 6.1168 | 5.9168 | 5.2042 | 4.4863 | 3.4063 | 1.4105 | 6.6832 | 6.6411 | 6.5716 | 6.4747 | 6.3053 | 6.1484 | 5.8926 | 5.6579 | 5.4579 | 4.7832 | 4.0853 | 2.9737 | 1.4126 | 6.6116 | 6.5042 | 6.3926 | 6.2579 | 5.9337 | 5.6042 | 5.2758 | 4.9589 | 4.6663 | 3.9558 | 3.0674 | 2.0737
|  | SKULAMUS | CF |  |  |  |  | 1.8589 | 7.1453 | 7.1295 | 7.1137 | 7.0979 | 7.0358 | 6.9589 | 6.8789 | 6.7589 | 6.6684 | 6.2242 | 5.7495 | 5.0474 | 1.4274 | 6.7126 | 6.6968 | 6.68 | 6.6442 | 6.5705 | 6.4968 | 6.4211 | 6.2937 | 6.1979 | 5.7547 | 5.2874 | 4.5284 | 1.5453 | 6.8168 | 6.7842 | 6.7484 | 6.7042 | 6.6211 | 6.5411 | 6.4579 | 6.3305 | 6.2358 | 5.7621 | 5.2463 | 4.4484
| WOODHILL | SPRINGHILL | MINIMUM HEADROOM | NJ 89850 06421 | NO | NO | 0.05 | 42.2795 | 41.67 | 41.1247 | 40.4795 | 39.8247 | 39.0395 | 38.0321 | 37.0121 | 35.8668 | 34.5111 | 29.47 | 25.2332 | 22.8405 | 40.5332 | 40.2132 | 39.9384 | 39.5995 | 38.9732 | 38.1542 | 37.0732 | 35.9742 | 34.7353 | 33.2321 | 27.6226 | 22.7995 | 20.0732 | 41.7584 | 41.4321 | 41.1753 | 40.83 | 40.2826 | 39.4447 | 38.3237 | 37.1826 | 35.8953 | 34.3511 | 28.59 | 23.6932 | 20.9395
|  | SPRINGHILL | EE |  |  |  |  | 42.5268 | 42.0447 | 41.5268 | 41.0742 | 40.5089 | 39.8205 | 39.1216 | 38.3089 | 37.4995 | 36.6374 | 31.3447 | 26.7911 | 24.27 | 40.6626 | 40.4111 | 40.1405 | 39.9184 | 39.6258 | 39.0079 | 38.2932 | 37.4447 | 36.5911 | 35.6732 | 29.8721 | 24.8721 | 22.0163 | 41.8889 | 41.6332 | 41.3553 | 41.1511 | 40.8511 | 40.2837 | 39.55 | 38.6584 | 37.7626 | 36.8005 | 30.7763 | 25.5668 | 22.6521
|  | SPRINGHILL | HT |  |  |  |  | 42.2795 | 41.67 | 41.1247 | 40.4795 | 39.8247 | 39.0395 | 38.0321 | 37.0121 | 35.8668 | 34.5111 | 29.47 | 25.2332 | 22.8405 | 40.5332 | 40.2132 | 39.9384 | 39.5995 | 38.9732 | 38.1542 | 37.0732 | 35.9742 | 34.7353 | 33.2321 | 27.6226 | 22.7995 | 20.0732 | 41.7584 | 41.4321 | 41.1753 | 40.83 | 40.2826 | 39.4447 | 38.3237 | 37.1826 | 35.8953 | 34.3511 | 28.59 | 23.6932 | 20.9395
|  | SPRINGHILL | HE |  |  |  |  | 42.8184 | 42.5226 | 42.1616 | 41.7689 | 41.3511 | 40.7763 | 40.1595 | 39.3616 | 38.4921 | 37.5195 | 33.3153 | 30.0079 | 27.7847 | 40.8268 | 40.6532 | 40.4605 | 40.2532 | 40.0321 | 39.7447 | 39.3311 | 38.4721 | 37.5311 | 36.4658 | 31.7984 | 28.1142 | 25.7047 | 41.7584 | 41.4321 | 41.1753 | 40.83 | 40.2826 | 39.4447 | 38.3237 | 37.1826 | 35.8953 | 34.3511 | 28.59 | 23.6932 | 20.9395
|  | SPRINGHILL | CF |  |  |  |  | 42.9016 | 42.7995 | 42.59 | 42.3616 | 42.1279 | 41.8363 | 41.5489 | 41.2542 | 40.9089 | 40.5195 | 37.7732 | 35.3732 | 33.57 | 40.9142 | 40.8068 | 40.6953 | 40.5795 | 40.4626 | 40.3226 | 40.1847 | 40.0458 | 39.9068 | 39.7195 | 36.67 | 33.9847 | 31.9447 | 42.1468 | 42.0363 | 41.9226 | 41.8047 | 41.6837 | 41.5216 | 41.3647 | 41.2068 | 41.05 | 40.8963 | 37.83 | 35.0489 | 32.9447
| BRIDGE OF DUN | ST CYRUS | MINIMUM HEADROOM | NO 74889 65577 | NO | YES | 0 | 3.8032 | 3.7442 | 3.6695 | 3.5779 | 3.4811 | 3.2263 | 2.9442 | 2.6032 | 2.3042 | 2.0432 | 0.63684 | -2.6684 | -3.7642 | 4.5347 | 4.4568 | 4.3632 | 4.2316 | 4.0884 | 3.8211 | 3.5558 | 3.2884 | 3.0126 | 2.7926 | 1.6105 | -1.5463 | -2.5547 | 3.8074 | 3.7316 | 3.6379 | 3.5105 | 3.3716 | 3.0695 | 2.7705 | 2.4126 | 2.1032 | 1.84 | 0.41263 | -3.1189 | -4.1726
|  | ST CYRUS | EE |  |  |  |  | 3.8211 | 3.7811 | 3.7147 | 3.6368 | 3.5453 | 3.2642 | 2.9442 | 2.6032 | 2.3042 | 2.0432 | 0.63684 | -2.1295 | -3.0958 | 4.5537 | 4.5053 | 4.4263 | 4.3232 | 4.1905 | 3.9074 | 3.5989 | 3.2947 | 3.0274 | 2.8074 | 1.6105 | -0.89474 | -1.9968 | 3.8253 | 3.7789 | 3.6979 | 3.5947 | 3.4642 | 3.1389 | 2.7726 | 2.4126 | 2.1032 | 1.84 | 0.41263 | -2.4874 | -3.6032
|  | ST CYRUS | HT |  |  |  |  | 3.8032 | 3.7442 | 3.6695 | 3.5779 | 3.4811 | 3.2263 | 2.9579 | 2.6705 | 2.3621 | 2.0958 | 0.94105 | -2.6684 | -3.5768 | 4.5347 | 4.4568 | 4.3632 | 4.2316 | 4.0884 | 3.8211 | 3.5558 | 3.2884 | 3.0126 | 2.7926 | 1.7463 | -1.5463 | -2.5547 | 3.8074 | 3.7316 | 3.6379 | 3.5105 | 3.3716 | 3.0695 | 2.7705 | 2.4674 | 2.1484 | 1.8768 | 0.67579 | -3.1189 | -4.1726
|  | ST CYRUS | HE |  |  |  |  | 3.8463 | 3.8211 | 3.7884 | 3.7474 | 3.6895 | 3.4063 | 3.1632 | 2.9221 | 2.6863 | 2.4811 | 1.3632 | -2.2021 | -3.7642 | 4.5789 | 4.5505 | 4.5126 | 4.4568 | 4.3674 | 4.0947 | 3.8505 | 3.6126 | 3.3916 | 3.22 | 2.2232 | -0.88842 | -2.4274 | 3.8074 | 3.7316 | 3.6379 | 3.5105 | 3.3716 | 3.0695 | 2.7705 | 2.4674 | 2.1484 | 1.8768 | 0.67579 | -3.1189 | -4.1726
|  | ST CYRUS | CF |  |  |  |  | 3.8611 | 3.8484 | 3.8326 | 3.8158 | 3.7989 | 3.7 | 3.5979 | 3.4947 | 3.4042 | 3.3442 | 2.8411 | 1.9305 | 1.0053 | 4.5947 | 4.5811 | 4.5653 | 4.5463 | 4.5284 | 4.4453 | 4.3379 | 4.2274 | 4.1326 | 4.0768 | 3.5274 | 2.6147 | 1.6263 | 3.8663 | 3.8526 | 3.8368 | 3.8179 | 3.7989 | 3.6958 | 3.5747 | 3.4484 | 3.3411 | 3.2768 | 2.6589 | 1.6684 | 0.62842
| ST FERGUS GAS | ST FERGUS GAS TERM | MINIMUM HEADROOM | NK 0916 5377 | NO | YES | 0 | 29.8947 | 29.8316 | 29.7505 | 29.6663 | 29.5779 | 29.3105 | 28.96 | 28.5853 | 28.2547 | 27.9284 | 20.7779 | 17.9389 | 16.0063 | 29.8863 | 29.8158 | 29.7316 | 29.6411 | 29.5484 | 29.3179 | 29.0411 | 28.7168 | 28.4284 | 28.1474 | 21.8358 | 18.8379 | 16.6632 | 29.8863 | 29.8168 | 29.7295 | 29.6368 | 29.5411 | 29.2653 | 28.9137 | 28.5274 | 28.1863 | 27.8526 | 20.4 | 17.1768 | 14.9621
|  | ST FERGUS GAS TERM | EE |  |  |  |  | 29.9189 | 29.8674 | 29.7947 | 29.7137 | 29.6284 | 29.32 | 28.96 | 28.5853 | 28.2547 | 27.9284 | 24.1211 | 20.9632 | 18.6032 | 29.9116 | 29.8558 | 29.7821 | 29.6979 | 29.6095 | 29.3474 | 29.0411 | 28.7168 | 28.4284 | 28.1474 | 24.6968 | 21.6358 | 19.06 | 29.9126 | 29.8558 | 29.7779 | 29.6895 | 29.5979 | 29.2811 | 28.9137 | 28.5274 | 28.1863 | 27.8526 | 23.8358 | 20.3947 | 17.7147
|  | ST FERGUS GAS TERM | HT |  |  |  |  | 29.8947 | 29.8316 | 29.7505 | 29.6663 | 29.5779 | 29.3105 | 29.0179 | 28.7189 | 28.3589 | 28.0137 | 20.7779 | 17.9389 | 16.0063 | 29.8863 | 29.8158 | 29.7316 | 29.6411 | 29.5484 | 29.3179 | 29.0568 | 28.7884 | 28.4653 | 28.1589 | 21.8358 | 18.8379 | 16.6632 | 29.8863 | 29.8168 | 29.7295 | 29.6368 | 29.5411 | 29.2653 | 28.9611 | 28.6484 | 28.2726 | 27.9137 | 20.4 | 17.1768 | 14.9621
|  | ST FERGUS GAS TERM | HE |  |  |  |  | 29.9526 | 29.9179 | 29.8737 | 29.8211 | 29.7653 | 29.4484 | 29.1768 | 28.8547 | 28.5316 | 28.0642 | 23.2937 | 20.8811 | 18.26 | 29.9495 | 29.9105 | 29.8632 | 29.8063 | 29.7442 | 29.48 | 29.2453 | 28.9537 | 28.6589 | 28.2063 | 24.0484 | 21.6368 | 18.9705 | 29.8863 | 29.8168 | 29.7295 | 29.6368 | 29.5411 | 29.2653 | 28.9611 | 28.6484 | 28.2726 | 27.9137 | 20.4 | 17.1768 | 14.9621
|  | ST FERGUS GAS TERM | CF |  |  |  |  | 29.9695 | 29.9495 | 29.9242 | 29.8979 | 29.8695 | 29.7505 | 29.6389 | 29.5232 | 29.3221 | 29.0958 | 26.0105 | 24.4916 | 22.8168 | 29.9674 | 29.9442 | 29.9189 | 29.8895 | 29.86 | 29.7589 | 29.6621 | 29.56 | 29.3558 | 29.1137 | 26.4389 | 24.9105 | 23.1084 | 29.9674 | 29.9442 | 29.9179 | 29.8884 | 29.8579 | 29.7347 | 29.62 | 29.5 | 29.2789 | 29.0232 | 25.8263 | 24.1421 | 22.2484
| PERSLEY | ST MACHAR | MINIMUM HEADROOM | NJ 93584 08102 | NO | NO | 0 | 23.5663 | 23.4432 | 23.3147 | 23.1842 | 23.0495 | 22.9937 | 22.8389 | 22.5884 | 22.2589 | 21.8758 | 20.7326 | 19.9095 | 19.1316 | 22.1063 | 21.8747 | 21.6347 | 21.3979 | 21.1568 | 21.2126 | 20.8979 | 20.5737 | 20.2095 | 19.7789 | 18.4842 | 17.5474 | 16.6389 | 21.3705 | 21.24 | 21.1042 | 20.9663 | 20.8242 | 20.8937 | 20.7274 | 20.4968 | 20.1179 | 19.6684 | 18.3526 | 17.4032 | 16.4853
|  | ST MACHAR | EE |  |  |  |  | 23.6326 | 23.5442 | 23.4505 | 23.3537 | 23.2474 | 23.1295 | 23.0116 | 22.9968 | 22.8832 | 22.7116 | 21.4495 | 20.7916 | 20.2358 | 22.2263 | 22.0537 | 21.8737 | 21.6937 | 21.5032 | 21.3063 | 21.1095 | 21.1958 | 20.9663 | 20.72 | 19.2905 | 18.56 | 17.9147 | 21.44 | 21.3463 | 21.2474 | 21.1442 | 21.0326 | 20.9105 | 20.7863 | 20.8958 | 20.7758 | 20.6337 | 19.1558 | 18.4053 | 17.7505
|  | ST MACHAR | HT |  |  |  |  | 23.5663 | 23.4432 | 23.3147 | 23.1842 | 23.0495 | 22.9937 | 22.8389 | 22.5884 | 22.2589 | 21.8758 | 20.7326 | 19.9095 | 19.1316 | 22.1063 | 21.8747 | 21.6347 | 21.3979 | 21.1568 | 21.2126 | 20.8979 | 20.5737 | 20.2095 | 19.7789 | 18.4842 | 17.5474 | 16.6389 | 21.3705 | 21.24 | 21.1042 | 20.9663 | 20.8242 | 20.8937 | 20.7274 | 20.4968 | 20.1179 | 19.6684 | 18.3526 | 17.4032 | 16.4853
|  | ST MACHAR | HE |  |  |  |  | 23.6674 | 23.5926 | 23.5105 | 23.4221 | 23.3263 | 23.2179 | 23.1168 | 22.9158 | 22.8232 | 22.7379 | 21.8989 | 21.5295 | 21.2326 | 22.3326 | 22.2074 | 22.0758 | 21.9379 | 21.7916 | 21.6326 | 21.4905 | 20.9695 | 20.7463 | 20.5053 | 19.5632 | 19.1674 | 18.8516 | 21.3705 | 21.24 | 21.1042 | 20.9663 | 20.8242 | 20.8937 | 20.7274 | 20.4968 | 20.1179 | 19.6684 | 18.3526 | 17.4032 | 16.4853
|  | ST MACHAR | CF |  |  |  |  | 23.6853 | 23.6305 | 23.5726 | 23.5147 | 23.4547 | 23.3895 | 23.3242 | 23.2589 | 23.1947 | 23.1305 | 22.6958 | 22.3684 | 22.1179 | 22.3695 | 22.2758 | 22.1789 | 22.0811 | 21.9811 | 21.8768 | 21.7695 | 21.6632 | 21.5474 | 21.42 | 20.5442 | 20.1895 | 19.9105 | 21.4989 | 21.4421 | 21.3811 | 21.3211 | 21.2579 | 21.1916 | 21.1221 | 21.0537 | 20.9874 | 20.9189 | 20.4695 | 20.0968 | 19.8011
| THURSO | ST MARYS | MINIMUM HEADROOM | HY 46965 01396 | YES | YES | 0.1 | 0.72947 | 0.64105 | 0.55158 | 0.45053 | 0.35474 | 0.25684 | 0.036842 | -0.23263 | -0.62737 | -1.0137 | -3.7432 | -4.0611 | -4.86 | 0.70316 | 0.60526 | 0.50526 | 0.39053 | 0.28421 | 0.17579 | -0.087368 | -0.41158 | -0.86632 | -1.3116 | -3.5305 | -3.8758 | -4.5989 | 0.71158 | 0.61474 | 0.51474 | 0.40105 | 0.29474 | 0.18526 | -0.076842 | -0.4 | -0.85474 | -1.2989 | -4.0726 | -4.42 | -5.26
|  | ST MARYS | EE |  |  |  |  | 0.76947 | 0.7 | 0.62842 | 0.54737 | 0.46737 | 0.38737 | 0.3 | 0.16632 | -0.015789 | -0.28 | -3.4937 | -3.7358 | -4.4547 | 0.74842 | 0.67053 | 0.59158 | 0.50105 | 0.41158 | 0.32316 | 0.22526 | 0.067368 | -0.15263 | -0.46737 | -3.2589 | -3.5263 | -4.1568 | 0.75474 | 0.67895 | 0.60105 | 0.51053 | 0.42211 | 0.33368 | 0.23579 | 0.077895 | -0.14211 | -0.45684 | -3.8011 | -4.0695 | -4.8158
|  | ST MARYS | HT |  |  |  |  | 0.72947 | 0.64105 | 0.55158 | 0.45053 | 0.35474 | 0.25684 | 0.036842 | -0.23263 | -0.62737 | -1.0137 | -3.7432 | -4.0611 | -4.86 | 0.70316 | 0.60526 | 0.50526 | 0.39053 | 0.28421 | 0.17579 | -0.087368 | -0.41158 | -0.86632 | -1.3116 | -3.5305 | -3.8758 | -4.5989 | 0.71158 | 0.61474 | 0.51474 | 0.40105 | 0.29474 | 0.18526 | -0.076842 | -0.4 | -0.85474 | -1.2989 | -4.0726 | -4.42 | -5.26
|  | ST MARYS | HE |  |  |  |  | 0.82632 | 0.78211 | 0.73474 | 0.68421 | 0.63158 | 0.57263 | 0.50842 | 0.34421 | 0.13895 | -0.12526 | -1.8832 | -2.0337 | -2.4095 | 0.81158 | 0.76421 | 0.71158 | 0.65579 | 0.59895 | 0.53368 | 0.46105 | 0.26105 | 0.010526 | -0.31053 | -1.8632 | -2.0284 | -2.3653 | 0.71158 | 0.61474 | 0.51474 | 0.40105 | 0.29474 | 0.18526 | -0.076842 | -0.4 | -0.85474 | -1.2989 | -4.0726 | -4.42 | -5.26
|  | ST MARYS | CF |  |  |  |  | 0.85368 | 0.82632 | 0.79895 | 0.77263 | 0.74316 | 0.71263 | 0.67579 | 0.64421 | 0.59368 | 0.52105 | -0.092632 | -0.19684 | -0.29158 | 0.84316 | 0.81263 | 0.78316 | 0.75368 | 0.72 | 0.68632 | 0.64421 | 0.60842 | 0.54947 | 0.46105 | -0.28526 | -0.40211 | -0.50947 | 0.84737 | 0.81789 | 0.78842 | 0.76 | 0.72737 | 0.69368 | 0.65368 | 0.61789 | 0.55895 | 0.47158 | -0.27474 | -0.39053 | -0.49789
| WILLOWDALE | ST NICHOLAS | MINIMUM HEADROOM | NJ 93737 06782 | NO | YES | 0 | 18.3705 | 18.2663 | 18.0779 | 17.7211 | 17.2453 | 16.64 | 16.4516 | 16.3379 | 16.2011 | 16.0537 | 15.4558 | 14.9337 | 14.4305 | 17.6168 | 17.5232 | 17.2274 | 16.8579 | 16.3 | 15.6147 | 15.3863 | 15.2674 | 15.1516 | 14.9968 | 14.3579 | 13.7905 | 13.2305 | 17.6442 | 17.5684 | 17.4695 | 17.1021 | 16.4916 | 15.7947 | 15.56 | 15.4379 | 15.3211 | 15.1695 | 14.5189 | 13.9432 | 13.3811
|  | ST NICHOLAS | EE |  |  |  |  | 18.4126 | 18.3495 | 18.2611 | 18.0084 | 17.5905 | 17.02 | 16.4516 | 16.3379 | 16.2284 | 16.12 | 15.6105 | 15.2168 | 14.8695 | 17.6589 | 17.5989 | 17.4926 | 17.1505 | 16.6811 | 16.0326 | 15.3863 | 15.2674 | 15.1516 | 15.0389 | 14.5 | 14.0779 | 13.6916 | 17.6842 | 17.6295 | 17.5705 | 17.48 | 16.8779 | 16.2179 | 15.56 | 15.4379 | 15.3211 | 15.2053 | 14.6547 | 14.2221 | 13.8337
|  | ST NICHOLAS | HT |  |  |  |  | 18.3705 | 18.2663 | 18.0779 | 17.7211 | 17.2453 | 16.64 | 16.4916 | 16.3442 | 16.2011 | 16.0537 | 15.4558 | 14.9337 | 14.4305 | 17.6168 | 17.5232 | 17.2274 | 16.8579 | 16.3 | 15.6147 | 15.4579 | 15.3042 | 15.1526 | 14.9968 | 14.3579 | 13.7905 | 13.2305 | 17.6442 | 17.5684 | 17.4695 | 17.1021 | 16.4916 | 15.7947 | 15.6358 | 15.48 | 15.3274 | 15.1695 | 14.5189 | 13.9432 | 13.3811
|  | ST NICHOLAS | HE |  |  |  |  | 18.4379 | 18.3853 | 18.3221 | 18.2547 | 18.1821 | 18.08 | 17.9558 | 17.8326 | 17.7116 | 17.5968 | 16.9632 | 16.3253 | 15.7326 | 17.6832 | 17.6326 | 17.5737 | 17.5116 | 17.3905 | 17.2358 | 17.1095 | 16.9811 | 16.8579 | 16.7389 | 16.0337 | 15.3158 | 14.6442 | 17.6442 | 17.5684 | 17.4695 | 17.1021 | 16.4916 | 15.7947 | 15.6358 | 15.48 | 15.3274 | 15.1695 | 14.5189 | 13.9432 | 13.3811
|  | ST NICHOLAS | CF |  |  |  |  | 18.4495 | 18.4116 | 18.3726 | 18.3295 | 18.2853 | 18.2389 | 18.1916 | 18.1463 | 18.1 | 18.0558 | 17.6884 | 17.3484 | 16.9505 | 17.6937 | 17.6568 | 17.6189 | 17.5789 | 17.5368 | 17.4926 | 17.4505 | 17.4063 | 17.3337 | 17.2495 | 16.8358 | 16.4926 | 16.0116 | 17.7158 | 17.6821 | 17.6453 | 17.6095 | 17.5716 | 17.5326 | 17.4916 | 17.4516 | 17.4095 | 17.3663 | 17.1684 | 16.6842 | 16.1937
| ARDMORE / HARRIS GRID | STOCKINISH | MINIMUM HEADROOM | NG 13447 94222 | YES | YES | 0 | 1.0126 | 0.99158 | 0.96842 | 0.94211 | 0.91474 | 0.85263 | 0.79053 | 0.72316 | 0.65579 | 0.58737 | 0.053684 | -0.58 | -1.0442 | 1.0221 | 1.0011 | 0.97158 | 0.94316 | 0.91579 | 0.86 | 0.80526 | 0.75158 | 0.69053 | 0.62842 | 0.12211 | -0.49368 | -0.98526 | 0.99158 | 0.96526 | 0.93684 | 0.90947 | 0.88316 | 0.81789 | 0.75263 | 0.67895 | 0.60842 | 0.53789 | -0.031579 | -0.71579 | -1.24
|  | STOCKINISH | EE |  |  |  |  | 1.0211 | 1.0042 | 0.98421 | 0.96316 | 0.94211 | 0.87579 | 0.8 | 0.72316 | 0.65579 | 0.58737 | 0.053684 | -0.58 | -1.0442 | 1.0263 | 1.0158 | 0.99474 | 0.97053 | 0.94632 | 0.88947 | 0.82526 | 0.75789 | 0.69895 | 0.63789 | 0.13053 | -0.48316 | -0.98526 | 1.0021 | 0.98211 | 0.95789 | 0.93368 | 0.90947 | 0.84 | 0.76 | 0.67895 | 0.60842 | 0.53789 | -0.031579 | -0.71579 | -1.24
|  | STOCKINISH | HT |  |  |  |  | 1.0126 | 0.99158 | 0.96842 | 0.94211 | 0.91474 | 0.85263 | 0.79053 | 0.72947 | 0.66 | 0.58947 | 0.088421 | -0.48211 | -0.86947 | 1.0221 | 1.0011 | 0.97158 | 0.94316 | 0.91579 | 0.86 | 0.80526 | 0.75158 | 0.69053 | 0.62842 | 0.12211 | -0.49368 | -0.92526 | 0.99158 | 0.96526 | 0.93684 | 0.90947 | 0.88316 | 0.81789 | 0.75263 | 0.68842 | 0.61579 | 0.54421 | -0.0063158 | -0.65158 | -1.0947
|  | STOCKINISH | HE |  |  |  |  | 1.0337 | 1.0232 | 1.0116 | 0.99789 | 0.98632 | 0.92526 | 0.87263 | 0.80632 | 0.73895 | 0.64316 | 0.24421 | -0.23474 | -0.75053 | 1.0347 | 1.0274 | 1.0189 | 1.0084 | 0.99895 | 0.94842 | 0.90211 | 0.83789 | 0.77474 | 0.68211 | 0.29474 | -0.18947 | -0.71263 | 0.99158 | 0.96526 | 0.93684 | 0.90947 | 0.88316 | 0.81789 | 0.75263 | 0.68842 | 0.61579 | 0.54421 | -0.0063158 | -0.65158 | -1.0947
|  | STOCKINISH | CF |  |  |  |  | 1.0389 | 1.0337 | 1.0263 | 1.02 | 1.0116 | 0.98737 | 0.96526 | 0.94316 | 0.91474 | 0.86842 | 0.66 | 0.35895 | 0.034737 | 1.0389 | 1.0347 | 1.0305 | 1.0253 | 1.02 | 1.0042 | 0.98842 | 0.96632 | 0.93263 | 0.88316 | 0.67474 | 0.36526 | 0.016842 | 1.0253 | 1.0189 | 1.0105 | 1.0021 | 0.99263 | 0.96421 | 0.93895 | 0.91368 | 0.87895 | 0.83053 | 0.60316 | 0.26737 | -0.1
| PORT ANN | STONEFIELD | MINIMUM HEADROOM | NR 86244 73400 | YES | YES | 0 | 0.32342 | 0.32237 | 0.31711 | 0.31395 | 0.30974 | 0.295 | 0.21605 | 0.13711 | 0.11395 | 0.090789 | -0.040789 | -0.285 | -0.50711 | 0.32026 | 0.31816 | 0.31289 | 0.30974 | 0.30658 | 0.29289 | 0.20553 | 0.11816 | 0.098158 | 0.077105 | -0.032368 | -0.32395 | -0.53658 | 0.32132 | 0.32026 | 0.31395 | 0.31079 | 0.30763 | 0.29184 | 0.20132 | 0.11079 | 0.086579 | 0.061316 | -0.072368 | -0.36184 | -0.59763
|  | STONEFIELD | EE |  |  |  |  | 0.32342 | 0.32342 | 0.32026 | 0.31605 | 0.31395 | 0.29605 | 0.27395 | 0.21184 | 0.14763 | 0.092895 | -0.040789 | -0.285 | -0.50711 | 0.32026 | 0.32026 | 0.31711 | 0.31289 | 0.30974 | 0.295 | 0.27816 | 0.21289 | 0.14447 | 0.087632 | -0.032368 | -0.28079 | -0.52605 | 0.32132 | 0.32132 | 0.31816 | 0.31395 | 0.31184 | 0.29184 | 0.27079 | 0.20132 | 0.12868 | 0.067632 | -0.072368 | -0.34289 | -0.59763
|  | STONEFIELD | HT |  |  |  |  | 0.32342 | 0.32237 | 0.31711 | 0.31395 | 0.30974 | 0.295 | 0.21605 | 0.13711 | 0.11395 | 0.090789 | -0.018684 | -0.285 | -0.47237 | 0.32026 | 0.31816 | 0.31289 | 0.30974 | 0.30658 | 0.29289 | 0.20553 | 0.11816 | 0.098158 | 0.077105 | -0.027105 | -0.32395 | -0.53658 | 0.32132 | 0.32026 | 0.31395 | 0.31079 | 0.30763 | 0.29184 | 0.20132 | 0.11079 | 0.086579 | 0.061316 | -0.055526 | -0.36184 | -0.57868
|  | STONEFIELD | HE |  |  |  |  | 0.32553 | 0.32342 | 0.32342 | 0.32342 | 0.32237 | 0.29605 | 0.27289 | 0.23289 | 0.17184 | 0.11921 | 0.018158 | -0.18711 | -0.41868 | 0.32237 | 0.32026 | 0.32026 | 0.32026 | 0.31816 | 0.29605 | 0.27289 | 0.23184 | 0.16658 | 0.11079 | 0.018158 | -0.19763 | -0.44079 | 0.32132 | 0.32026 | 0.31395 | 0.31079 | 0.30763 | 0.29184 | 0.20132 | 0.11079 | 0.086579 | 0.061316 | -0.055526 | -0.36184 | -0.57868
|  | STONEFIELD | CF |  |  |  |  | 0.32553 | 0.32553 | 0.32447 | 0.32342 | 0.32237 | 0.31605 | 0.31079 | 0.29289 | 0.27711 | 0.25711 | 0.16974 | 0.037105 | -0.11868 | 0.32237 | 0.32237 | 0.32132 | 0.32026 | 0.31921 | 0.31395 | 0.30974 | 0.29184 | 0.275 | 0.25184 | 0.16237 | 0.019211 | -0.15237 | 0.32342 | 0.32342 | 0.32237 | 0.32132 | 0.32026 | 0.315 | 0.30974 | 0.28974 | 0.27184 | 0.24868 | 0.15184 | 0.0013158 | -0.17763
| FIDDES | STONEHAVEN | MINIMUM HEADROOM | NO 85903 85641 | NO | YES | 0.512 | 23.5691 | 23.3722 | 23.1375 | 22.7543 | 22.2069 | 21.4627 | 20.1785 | 18.9375 | 17.8627 | 16.8817 | 10.4333 | 0.37537 | -7.3131 | 22.0606 | 21.4848 | 20.7722 | 20.1754 | 19.5796 | 18.8554 | 17.8891 | 16.8238 | 15.8996 | 15.0933 | 8.4543 | -1.8173 | -9.4646 | 22.6248 | 22.128 | 21.4396 | 20.8596 | 20.268 | 19.4859 | 18.1269 | 16.8206 | 15.688 | 14.6606 | 7.6564 | -3.2983 | -11.9152
|  | STONEHAVEN | EE |  |  |  |  | 23.6501 | 23.4975 | 23.2869 | 23.068 | 22.5891 | 21.4627 | 20.1785 | 18.9375 | 17.8627 | 16.8817 | 10.4333 | 0.37537 | -7.3131 | 22.2343 | 21.7743 | 21.1396 | 20.6027 | 20.0122 | 19.0154 | 17.8891 | 16.8238 | 15.8996 | 15.0933 | 8.8269 | -1.0583 | -9.4646 | 22.7585 | 22.4112 | 21.7859 | 21.2575 | 20.6775 | 19.4859 | 18.1269 | 16.8206 | 15.688 | 14.6606 | 7.6564 | -3.2983 | -11.9152
|  | STONEHAVEN | HT |  |  |  |  | 23.5691 | 23.3722 | 23.1375 | 22.7543 | 22.2069 | 21.5459 | 20.708 | 19.7512 | 18.6817 | 17.7133 | 10.7164 | 1.3375 | -5.0383 | 22.0606 | 21.4848 | 20.7722 | 20.1754 | 19.5796 | 18.8554 | 18.0869 | 17.2417 | 16.3164 | 15.5122 | 8.4543 | -1.8173 | -9.0046 | 22.6248 | 22.128 | 21.4396 | 20.8596 | 20.268 | 19.5459 | 18.6617 | 17.6554 | 16.5354 | 15.5269 | 7.9238 | -2.6625 | -10.0215
|  | STONEHAVEN | HE |  |  |  |  | 23.7564 | 23.6533 | 23.5322 | 23.3996 | 23.2596 | 22.0869 | 21.1038 | 20.188 | 19.3848 | 18.4312 | 10.6091 | 2.8048 | -5.652 | 22.468 | 22.1238 | 21.6648 | 21.2954 | 20.8891 | 19.6606 | 18.7912 | 17.9996 | 17.3396 | 16.4996 | 9.1206 | 1.0996 | -7.5804 | 22.6248 | 22.128 | 21.4396 | 20.8596 | 20.268 | 19.5459 | 18.6617 | 17.6554 | 16.5354 | 15.5269 | 7.9238 | -2.6625 | -10.0215
|  | STONEHAVEN | CF |  |  |  |  | 23.8122 | 23.7512 | 23.6817 | 23.608 | 23.5354 | 23.1943 | 22.8796 | 22.568 | 22.2912 | 21.9522 | 13.1312 | 8.2133 | 2.8291 | 22.5385 | 22.3848 | 22.1501 | 21.9596 | 21.7585 | 21.3038 | 20.9301 | 20.5722 | 20.2648 | 19.6427 | 11.9522 | 6.8427 | 1.0006 | 23.0038 | 22.8891 | 22.7217 | 22.5785 | 22.3869 | 21.8606 | 21.4206 | 20.9985 | 20.6333 | 19.9996 | 10.6238 | 5.1448 | -0.90568
| STRICHEN | STONEYHILL | MINIMUM HEADROOM | NK 6773 4109 | YES | YES | 0 | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6874 | 3.6853 | 3.6832 | 3.68 | 3.6779 | 3.6579 | 3.6337 | 3.6168 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3832 | 3.3811 | 3.38 | 3.3779 | 3.3737 | 3.3579 | 3.3379 | 3.32 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5674 | 3.5663 | 3.5632 | 3.5611 | 3.5579 | 3.5347 | 3.5095 | 3.4916
|  | STONEYHILL | EE |  |  |  |  | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6874 | 3.6853 | 3.6832 | 3.6811 | 3.6789 | 3.6579 | 3.6337 | 3.6168 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3832 | 3.3821 | 3.3811 | 3.3789 | 3.3758 | 3.3579 | 3.3379 | 3.32 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5674 | 3.5663 | 3.5632 | 3.5611 | 3.5579 | 3.5347 | 3.5095 | 3.4916
|  | STONEYHILL | HT |  |  |  |  | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6874 | 3.6863 | 3.6842 | 3.6821 | 3.6789 | 3.6611 | 3.64 | 3.6253 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3842 | 3.3832 | 3.3811 | 3.3789 | 3.3758 | 3.3589 | 3.3379 | 3.3232 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5684 | 3.5674 | 3.5642 | 3.5611 | 3.5579 | 3.5379 | 3.5147 | 3.4989
|  | STONEYHILL | HE |  |  |  |  | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6874 | 3.6863 | 3.6832 | 3.68 | 3.6779 | 3.6632 | 3.6453 | 3.6263 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3832 | 3.3811 | 3.38 | 3.3779 | 3.3737 | 3.3611 | 3.3453 | 3.3284 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5684 | 3.5674 | 3.5642 | 3.5611 | 3.5579 | 3.5379 | 3.5147 | 3.4989
|  | STONEYHILL | CF |  |  |  |  | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6895 | 3.6884 | 3.6874 | 3.6874 | 3.6874 | 3.6842 | 3.6768 | 3.6663 | 3.6537 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3853 | 3.3842 | 3.3842 | 3.3832 | 3.3811 | 3.38 | 3.3726 | 3.3621 | 3.3505 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5705 | 3.5695 | 3.5684 | 3.5674 | 3.5653 | 3.5642 | 3.5558 | 3.5442 | 3.5295
| PERSLEY | STONEYWOOD T1&T2 | MINIMUM HEADROOM | NJ 89285 11082 | NO | NO | 0 | 24.82 | 24.3032 | 23.6347 | 22.8926 | 22.2032 | 21.3789 | 20.2737 | 19.1326 | 18.3842 | 17.4895 | 15.5242 | 13.0642 | 11.6158 | 23.7347 | 23.1505 | 22.3579 | 21.4768 | 20.6611 | 19.6979 | 18.3958 | 17.0495 | 16.1832 | 15.1368 | 12.3979 | 9.4968 | 7.8453 | 24.1326 | 23.9221 | 23.1842 | 22.3632 | 21.6021 | 20.6684 | 19.36 | 18.0095 | 17.1326 | 16.08 | 14.3863 | 11.7463 | 10.7358
|  | STONEYWOOD T1&T2 | EE |  |  |  |  | 24.8768 | 24.3884 | 23.7474 | 23.0242 | 22.3579 | 21.5505 | 20.7389 | 19.7695 | 19.3147 | 18.9011 | 16.4337 | 13.9568 | 12.6221 | 23.7621 | 23.2442 | 22.4811 | 21.6232 | 20.8316 | 19.8916 | 18.9495 | 17.8168 | 17.3021 | 16.8368 | 14.4168 | 11.6095 | 10.0589 | 24.16 | 24.0126 | 23.3032 | 22.5032 | 21.7653 | 20.8579 | 19.9053 | 18.7611 | 18.2368 | 17.7611 | 15.4463 | 12.5832 | 11.0105
|  | STONEYWOOD T1&T2 | HT |  |  |  |  | 24.82 | 24.3032 | 23.6347 | 22.8926 | 22.2032 | 21.3789 | 20.2737 | 19.1326 | 18.3842 | 17.4895 | 15.5263 | 13.2874 | 12.4189 | 23.7347 | 23.1505 | 22.3579 | 21.4768 | 20.6611 | 19.6979 | 18.3958 | 17.0495 | 16.1832 | 15.1368 | 13.3105 | 10.6968 | 9.6958 | 24.1326 | 23.9221 | 23.1842 | 22.3632 | 21.6021 | 20.6684 | 19.36 | 18.0095 | 17.1326 | 16.08 | 14.3863 | 11.7463 | 10.7358
|  | STONEYWOOD T1&T2 | HE |  |  |  |  | 24.9537 | 24.5011 | 23.8947 | 23.2126 | 22.5779 | 21.7968 | 21.0305 | 20.0179 | 19.4737 | 18.9547 | 15.5242 | 13.0642 | 11.6158 | 23.7989 | 23.3695 | 22.6453 | 21.8295 | 21.0747 | 20.1642 | 19.2663 | 18.0716 | 17.4421 | 16.8421 | 12.3979 | 9.4968 | 7.8453 | 24.1326 | 23.9221 | 23.1842 | 22.3632 | 21.6021 | 20.6684 | 19.36 | 18.0095 | 17.1326 | 16.08 | 14.3863 | 11.7463 | 10.7358
|  | STONEYWOOD T1&T2 | CF |  |  |  |  | 25.0726 | 24.8295 | 24.5358 | 24.2263 | 23.9495 | 23.6242 | 23.2716 | 22.8895 | 22.7168 | 22.5726 | 21.2337 | 19.4347 | 18.0653 | 23.8179 | 23.7589 | 23.4095 | 23.0411 | 22.7126 | 22.3337 | 21.92 | 21.4705 | 21.2747 | 21.1116 | 19.5516 | 17.4389 | 15.8242 | 24.2158 | 24.1916 | 24.1653 | 23.8263 | 23.5211 | 23.1632 | 22.7726 | 22.3516 | 22.1632 | 22.0063 | 20.4958 | 18.3632 | 16.7347
| DYCE | STONEYWOOD T3 | MINIMUM HEADROOM | NJ 89285 11082 | NO | YES | 0 | 23.0926 | 23.0684 | 23.0442 | 23.0211 | 22.9968 | 22.9695 | 22.9432 | 22.9189 | 22.8926 | 22.8705 | 22.7842 | 22.72 | 22.6695 | 22.9074 | 22.8895 | 22.8716 | 22.8537 | 22.8347 | 22.8137 | 22.7937 | 22.7684 | 22.7358 | 22.7063 | 22.5842 | 22.4863 | 22.4021 | 23.6421 | 23.6242 | 23.6063 | 23.5884 | 23.5695 | 23.5474 | 23.5263 | 23.5021 | 23.4695 | 23.4389 | 23.3158 | 23.2158 | 23.1326
|  | STONEYWOOD T3 | EE |  |  |  |  | 23.1021 | 23.0832 | 23.0632 | 23.0442 | 23.0221 | 23.0011 | 22.9789 | 22.9568 | 22.9368 | 22.92 | 22.8368 | 22.7789 | 22.74 | 22.9137 | 22.8989 | 22.8842 | 22.8695 | 22.8526 | 22.8358 | 22.8189 | 22.8021 | 22.7863 | 22.7737 | 22.6705 | 22.5884 | 22.5253 | 23.6484 | 23.6337 | 23.6189 | 23.6042 | 23.5863 | 23.5695 | 23.5516 | 23.5337 | 23.5168 | 23.5021 | 23.4 | 23.3158 | 23.2526
|  | STONEYWOOD T3 | HT |  |  |  |  | 23.0926 | 23.0684 | 23.0442 | 23.0211 | 22.9968 | 22.9695 | 22.9432 | 22.9189 | 22.8926 | 22.8705 | 22.7842 | 22.72 | 22.6695 | 22.9074 | 22.8895 | 22.8716 | 22.8537 | 22.8347 | 22.8137 | 22.7937 | 22.7684 | 22.7358 | 22.7063 | 22.5842 | 22.4863 | 22.4021 | 23.6421 | 23.6242 | 23.6063 | 23.5884 | 23.5695 | 23.5474 | 23.5263 | 23.5021 | 23.4695 | 23.4389 | 23.3158 | 23.2158 | 23.1326
|  | STONEYWOOD T3 | HE |  |  |  |  | 23.1168 | 23.1042 | 23.0916 | 23.0779 | 23.0642 | 23.0474 | 23.0316 | 23.0158 | 23.0011 | 22.9884 | 22.9379 | 22.9063 | 22.8821 | 22.9232 | 22.9137 | 22.9032 | 22.8926 | 22.8811 | 22.8674 | 22.8547 | 22.8421 | 22.8305 | 22.8211 | 22.7832 | 22.7642 | 22.74 | 23.6421 | 23.6242 | 23.6063 | 23.5884 | 23.5695 | 23.5474 | 23.5263 | 23.5021 | 23.4695 | 23.4389 | 23.3158 | 23.2158 | 23.1326
|  | STONEYWOOD T3 | CF |  |  |  |  | 23.1232 | 23.1168 | 23.1095 | 23.1021 | 23.0937 | 23.0853 | 23.0768 | 23.0684 | 23.06 | 23.0526 | 23.0137 | 22.9895 | 22.9726 | 22.9284 | 22.9232 | 22.9179 | 22.9126 | 22.9063 | 22.9 | 22.8937 | 22.8874 | 22.8811 | 22.8758 | 22.8474 | 22.8326 | 22.8242 | 23.6632 | 23.6579 | 23.6526 | 23.6474 | 23.6411 | 23.6337 | 23.6284 | 23.6211 | 23.6137 | 23.6084 | 23.5779 | 23.5611 | 23.5516
| CLACHAN | STRACHUR | MINIMUM HEADROOM | NN 08672 01180 | YES | YES | 0 | 0.99158 | 0.96526 | 0.93158 | 0.9 | 0.86421 | 0.79895 | 0.73368 | 0.69158 | 0.64421 | 0.57579 | 0.39895 | 0.25158 | 0.16211 | 0.94842 | 0.92105 | 0.88526 | 0.84947 | 0.81263 | 0.74316 | 0.68105 | 0.63789 | 0.58316 | 0.51053 | 0.38526 | 0.26842 | 0.18947 | 0.94842 | 0.92 | 0.88211 | 0.84737 | 0.80737 | 0.73684 | 0.66316 | 0.61789 | 0.56526 | 0.49053 | 0.30105 | 0.14526 | 0.047368
|  | STRACHUR | EE |  |  |  |  | 1.0032 | 0.97684 | 0.94632 | 0.91474 | 0.88211 | 0.81684 | 0.73368 | 0.69158 | 0.65158 | 0.60947 | 0.39895 | 0.25158 | 0.16211 | 0.96105 | 0.93579 | 0.90526 | 0.87474 | 0.84105 | 0.77684 | 0.69158 | 0.65474 | 0.61789 | 0.58105 | 0.38842 | 0.26842 | 0.18947 | 0.96 | 0.93158 | 0.89789 | 0.86421 | 0.82842 | 0.75579 | 0.66316 | 0.61789 | 0.57368 | 0.52947 | 0.30105 | 0.14526 | 0.047368
|  | STRACHUR | HT |  |  |  |  | 0.99158 | 0.96526 | 0.93158 | 0.9 | 0.86421 | 0.79895 | 0.74 | 0.69895 | 0.64421 | 0.57579 | 0.44211 | 0.33895 | 0.26421 | 0.94842 | 0.92105 | 0.88526 | 0.84947 | 0.81263 | 0.74316 | 0.68105 | 0.63789 | 0.58316 | 0.51053 | 0.38526 | 0.28737 | 0.21474 | 0.94842 | 0.92 | 0.88211 | 0.84737 | 0.80737 | 0.73684 | 0.67158 | 0.62526 | 0.56526 | 0.49053 | 0.34737 | 0.23474 | 0.15368
|  | STRACHUR | HE |  |  |  |  | 1.0168 | 1.0042 | 0.98737 | 0.96947 | 0.94526 | 0.87789 | 0.80842 | 0.77789 | 0.74632 | 0.71263 | 0.60211 | 0.52526 | 0.44842 | 0.97789 | 0.96421 | 0.94526 | 0.92632 | 0.90105 | 0.83053 | 0.75263 | 0.72526 | 0.69368 | 0.66211 | 0.56316 | 0.5 | 0.43684 | 0.94842 | 0.92 | 0.88211 | 0.84737 | 0.80737 | 0.73684 | 0.67158 | 0.62526 | 0.56526 | 0.49053 | 0.34737 | 0.23474 | 0.15368
|  | STRACHUR | CF |  |  |  |  | 1.0232 | 1.0168 | 1.0095 | 1.0021 | 0.99474 | 0.97895 | 0.96105 | 0.94526 | 0.93158 | 0.91684 | 0.80421 | 0.75474 | 0.71789 | 0.98526 | 0.97895 | 0.96947 | 0.96211 | 0.95368 | 0.93684 | 0.91895 | 0.90211 | 0.88842 | 0.87368 | 0.75053 | 0.70632 | 0.67368 | 0.98421 | 0.97684 | 0.96947 | 0.96 | 0.95263 | 0.93474 | 0.91368 | 0.89789 | 0.88316 | 0.86632 | 0.74 | 0.68947 | 0.65053
| TARLAND | STRATHDON | MINIMUM HEADROOM | NJ 37343 11904 | YES | YES | 0 | 1.0537 | 1.0305 | 1.0032 | 0.97684 | 0.94316 | 0.86737 | 0.79158 | 0.71474 | 0.63053 | 0.54421 | -0.04 | -0.74421 | -1.2653 | 1.0189 | 0.99368 | 0.96421 | 0.93474 | 0.89789 | 0.83053 | 0.76316 | 0.69474 | 0.62 | 0.54526 | -0.0031579 | -0.70737 | -1.2684 | 0.99895 | 0.97368 | 0.94316 | 0.91368 | 0.87684 | 0.79684 | 0.71895 | 0.63895 | 0.55158 | 0.46421 | -0.15895 | -0.94105 | -1.5368
|  | STRATHDON | EE |  |  |  |  | 1.0642 | 1.0474 | 1.0232 | 1.0011 | 0.97895 | 0.89789 | 0.80737 | 0.71579 | 0.63263 | 0.54842 | -0.04 | -0.74421 | -1.2653 | 1.0316 | 1.0116 | 0.98737 | 0.96421 | 0.94 | 0.87368 | 0.79789 | 0.71789 | 0.64632 | 0.57263 | 0.011579 | -0.69158 | -1.2684 | 1.0116 | 0.99158 | 0.96632 | 0.94211 | 0.91789 | 0.83579 | 0.74316 | 0.64842 | 0.56421 | 0.47789 | -0.15895 | -0.94105 | -1.5368
|  | STRATHDON | HT |  |  |  |  | 1.0537 | 1.0305 | 1.0032 | 0.97684 | 0.94316 | 0.86737 | 0.79158 | 0.71474 | 0.63053 | 0.54421 | 0.014737 | -0.62211 | -1.0642 | 1.0189 | 0.99368 | 0.96421 | 0.93474 | 0.89789 | 0.83053 | 0.76316 | 0.69474 | 0.62 | 0.54526 | -0.0031579 | -0.70737 | -1.2 | 0.99895 | 0.97368 | 0.94316 | 0.91368 | 0.87684 | 0.79684 | 0.71895 | 0.63895 | 0.55158 | 0.46421 | -0.13158 | -0.85789 | -1.3642
|  | STRATHDON | HE |  |  |  |  | 1.0779 | 1.0684 | 1.0558 | 1.0432 | 1.0295 | 0.95684 | 0.88737 | 0.80632 | 0.73053 | 0.62421 | 0.17579 | -0.35368 | -0.94211 | 1.0484 | 1.0368 | 1.0221 | 1.0095 | 0.99579 | 0.93789 | 0.87895 | 0.80421 | 0.73474 | 0.63053 | 0.18842 | -0.36842 | -0.97053 | 0.99895 | 0.97368 | 0.94316 | 0.91368 | 0.87684 | 0.79684 | 0.71895 | 0.63895 | 0.55158 | 0.46421 | -0.13158 | -0.85789 | -1.3642
|  | STRATHDON | CF |  |  |  |  | 1.0832 | 1.08 | 1.0726 | 1.0663 | 1.0579 | 1.0274 | 1.0011 | 0.97579 | 0.93053 | 0.88105 | 0.65053 | 0.31579 | -0.048421 | 1.0568 | 1.0505 | 1.0411 | 1.0337 | 1.0253 | 1.0011 | 0.98 | 0.95789 | 0.91053 | 0.85579 | 0.61684 | 0.26211 | -0.14 | 1.0358 | 1.0295 | 1.0211 | 1.0126 | 1.0042 | 0.97368 | 0.94737 | 0.92105 | 0.86947 | 0.81158 | 0.55368 | 0.17158 | -0.24632
| STRICHEN | STRICHEN | MINIMUM HEADROOM | NJ 95900 55137 | NO | YES | 0.65 | 5.8363 | 5.6868 | 5.4595 | 4.4658 | 4.1921 | 4.01 | 3.1889 | 2.3374 | 1.6037 | 0.85526 | -7.8016 | -15.43 | -20.7205 | 6.3647 | 6.2532 | 6.0995 | 5.5932 | 5.3268 | 5.0942 | 4.4311 | 3.7521 | 3.1668 | 2.57 | -4.8984 | -12.1637 | -17.8816 | 6.7574 | 6.5711 | 6.2889 | 5.2163 | 4.8521 | 4.6174 | 3.7858 | 2.9321 | 2.1995 | 1.4489 | -7.4342 | -15.6816 | -21.7321
|  | STRICHEN | EE |  |  |  |  | 5.8584 | 5.7384 | 5.5111 | 4.4658 | 4.1921 | 4.01 | 3.1889 | 2.3374 | 1.6037 | 0.85526 | -7.8016 | -15.43 | -20.7205 | 6.3868 | 6.2984 | 6.1489 | 5.5932 | 5.3268 | 5.0942 | 4.4311 | 3.7521 | 3.1668 | 2.57 | -4.8984 | -12.1637 | -17.8816 | 6.7805 | 6.63 | 6.3489 | 5.2163 | 4.8521 | 4.6174 | 3.7858 | 2.9321 | 2.1995 | 1.4489 | -7.4342 | -15.6816 | -21.7321
|  | STRICHEN | HT |  |  |  |  | 5.8363 | 5.6868 | 5.4595 | 5.1889 | 4.87 | 4.1553 | 3.5732 | 2.9742 | 2.2605 | 1.5511 | -7.0542 | -13.5205 | -17.8142 | 6.3647 | 6.2532 | 6.0995 | 5.9184 | 5.7079 | 5.1721 | 4.6921 | 4.2068 | 3.6332 | 3.0721 | -4.71 | -11.6247 | -16.3679 | 6.7574 | 6.5711 | 6.2889 | 5.9437 | 5.5332 | 4.7532 | 4.1605 | 3.5605 | 2.8447 | 2.1437 | -6.9184 | -14.2342 | -19.1584
|  | STRICHEN | HE |  |  |  |  | 5.8911 | 5.7932 | 5.6395 | 5.43 | 5.1668 | 4.4353 | 3.8226 | 3.2111 | 2.6068 | 1.9974 | -7.1795 | -12.8784 | -19.0805 | 6.4195 | 6.35 | 6.2458 | 6.1079 | 5.9384 | 5.5542 | 5.0521 | 4.5532 | 4.0584 | 3.5647 | -4.3753 | -10.0437 | -16.2511 | 6.7574 | 6.5711 | 6.2889 | 5.9437 | 5.5332 | 4.7532 | 4.1605 | 3.5605 | 2.8447 | 2.1437 | -6.9184 | -14.2342 | -19.1584
|  | STRICHEN | CF |  |  |  |  | 5.9247 | 5.89 | 5.8342 | 5.7658 | 5.6858 | 5.3784 | 5.0995 | 4.8205 | 4.5774 | 4.3879 | 0.72895 | -2.8668 | -6.6995 | 6.4458 | 6.4195 | 6.3795 | 6.3332 | 6.2805 | 6.1163 | 5.9658 | 5.8163 | 5.6837 | 5.5774 | 2.3121 | -1.29 | -5.3268 | 6.8532 | 6.8121 | 6.7416 | 6.6574 | 6.5553 | 6.2279 | 5.9279 | 5.63 | 5.3668 | 5.1595 | 1.2268 | -2.7289 | -7.0384
| THURSO | STROMNESS | MINIMUM HEADROOM | HY 25978 10409 | NO | YES | 1 | 8.1558 | 8.0621 | 7.9653 | 7.8674 | 7.7137 | 7.4232 | 7.2295 | 7.0632 | 6.9126 | 6.7126 | 6.0926 | 5.5411 | 3.9768 | 7.2568 | 7.0474 | 6.8295 | 6.5884 | 6.2674 | 5.9358 | 5.7242 | 5.5442 | 5.3821 | 5.1611 | 4.4747 | 3.8589 | 2.4905 | 7.2979 | 7.1042 | 6.9042 | 6.6842 | 6.3947 | 6.0947 | 5.8989 | 5.7295 | 5.5779 | 5.3747 | 4.7421 | 4.1263 | 2.5063
|  | STROMNESS | EE |  |  |  |  | 8.1905 | 8.1137 | 8.0347 | 7.9516 | 7.8653 | 7.6747 | 7.5021 | 7.3579 | 7.2295 | 7.1484 | 6.5411 | 6.1211 | 4.6863 | 7.34 | 7.1695 | 6.9905 | 6.7895 | 6.5074 | 6.2147 | 6.0242 | 5.8663 | 5.7284 | 5.6442 | 4.9716 | 4.4968 | 3.2811 | 7.3432 | 7.2168 | 7.0526 | 6.8674 | 6.6137 | 6.3505 | 6.1758 | 6.0295 | 5.8989 | 5.8179 | 5.2 | 4.7632 | 3.2968
|  | STROMNESS | HT |  |  |  |  | 8.1558 | 8.0621 | 7.9653 | 7.8674 | 7.7137 | 7.4232 | 7.2295 | 7.0632 | 6.9126 | 6.7126 | 6.0926 | 5.5411 | 3.9768 | 7.2568 | 7.0474 | 6.8295 | 6.5884 | 6.2674 | 5.9358 | 5.7242 | 5.5442 | 5.3821 | 5.1611 | 4.4747 | 3.8589 | 2.4905 | 7.2979 | 7.1042 | 6.9042 | 6.6842 | 6.3947 | 6.0947 | 5.8989 | 5.7295 | 5.5779 | 5.3747 | 4.7421 | 4.1263 | 2.5063
|  | STROMNESS | HE |  |  |  |  | 8.2442 | 8.1937 | 8.1379 | 8.0789 | 8.0147 | 7.9389 | 7.8053 | 7.6947 | 7.6305 | 7.5726 | 7.2758 | 7.0253 | 6.2832 | 7.4653 | 7.3611 | 7.2189 | 7.0042 | 6.7611 | 6.5053 | 6.3516 | 6.2295 | 6.1642 | 6.1042 | 5.7811 | 5.4979 | 4.8579 | 7.2979 | 7.1042 | 6.9042 | 6.6842 | 6.3947 | 6.0947 | 5.8989 | 5.7295 | 5.5779 | 5.3747 | 4.7421 | 4.1263 | 2.5063
|  | STROMNESS | CF |  |  |  |  | 8.2737 | 8.2442 | 8.2147 | 8.1842 | 8.1526 | 8.1211 | 8.0895 | 8.0568 | 8.0253 | 7.9926 | 7.8484 | 7.6716 | 7.5116 | 7.5263 | 7.4621 | 7.3968 | 7.3274 | 7.2547 | 7.1916 | 7.1211 | 7.0537 | 6.9842 | 6.9021 | 6.4158 | 6.2095 | 6.0221 | 7.4326 | 7.4011 | 7.3695 | 7.3368 | 7.2958 | 7.2368 | 7.1716 | 7.1095 | 7.0453 | 6.9705 | 6.5347 | 6.3474 | 6.1832
| THURSO | STRONSAY | MINIMUM HEADROOM | HY 64548 27016 | YES | YES | 0 | 1.0905 | 1.0789 | 1.06 | 1.04 | 1.0221 | 0.86105 | 0.66316 | 0.46421 | 0.28316 | 0.010526 | -1.6137 | -3.4842 | -4.8547 | 0.97474 | 0.96211 | 0.94421 | 0.92526 | 0.90842 | 0.78 | 0.60316 | 0.42211 | 0.25158 | -0.011579 | -1.4968 | -3.3095 | -4.7947 | 0.97895 | 0.96842 | 0.94842 | 0.92842 | 0.90842 | 0.74842 | 0.54947 | 0.34947 | 0.17789 | -0.070526 | -1.8811 | -3.9137 | -5.4705
|  | STRONSAY | EE |  |  |  |  | 1.0968 | 1.0863 | 1.0653 | 1.0432 | 1.0221 | 0.86105 | 0.66316 | 0.46421 | 0.29368 | 0.069474 | -1.6137 | -3.4842 | -4.8547 | 0.98105 | 0.97053 | 0.95053 | 0.93053 | 0.91158 | 0.78 | 0.61895 | 0.45895 | 0.31895 | 0.12105 | -1.4968 | -3.3095 | -4.7947 | 0.98526 | 0.97579 | 0.95474 | 0.93263 | 0.91053 | 0.74842 | 0.54947 | 0.34947 | 0.17789 | -0.053684 | -1.8811 | -3.9137 | -5.4705
|  | STRONSAY | HT |  |  |  |  | 1.0905 | 1.0789 | 1.06 | 1.04 | 1.0221 | 0.88842 | 0.75474 | 0.60842 | 0.40632 | 0.086316 | -1.4042 | -3.0632 | -4.1779 | 0.97474 | 0.96211 | 0.94421 | 0.92526 | 0.90842 | 0.79684 | 0.68737 | 0.56526 | 0.38737 | 0.071579 | -1.4316 | -3.2211 | -4.4716 | 0.97895 | 0.96842 | 0.94842 | 0.92842 | 0.90842 | 0.77368 | 0.63895 | 0.49158 | 0.28211 | -0.070526 | -1.7137 | -3.5989 | -4.8832
|  | STRONSAY | HE |  |  |  |  | 1.1042 | 1.0979 | 1.0895 | 1.0811 | 1.0716 | 0.86737 | 0.67263 | 0.47368 | 0.28316 | 0.010526 | -1.1547 | -2.5842 | -4.1442 | 0.98842 | 0.98316 | 0.97474 | 0.96632 | 0.95579 | 0.78 | 0.60316 | 0.42211 | 0.25158 | -0.011579 | -1.1263 | -2.5705 | -4.1474 | 0.97895 | 0.96842 | 0.94842 | 0.92842 | 0.90842 | 0.77368 | 0.63895 | 0.49158 | 0.28211 | -0.070526 | -1.7137 | -3.5989 | -4.8832
|  | STRONSAY | CF |  |  |  |  | 1.1074 | 1.1042 | 1.0979 | 1.0937 | 1.0874 | 1.0221 | 0.96526 | 0.85368 | 0.73895 | 0.61053 | 0.017895 | -0.88105 | -1.8632 | 0.99263 | 0.98842 | 0.98421 | 0.97789 | 0.97263 | 0.91895 | 0.87158 | 0.76316 | 0.64842 | 0.51053 | -0.083158 | -0.99579 | -2.0442 | 0.99368 | 0.99158 | 0.98526 | 0.98 | 0.97579 | 0.90947 | 0.85158 | 0.73368 | 0.60632 | 0.46105 | -0.18947 | -1.1853 | -2.2947
| FORT WILLIAM | STRONTIAN | MINIMUM HEADROOM | NM 81521 61955 | YES | NO | 0 | 1.1147 | 1.1021 | 1.0895 | 1.0768 | 1.0653 | 1.0442 | 1.0232 | 1.0042 | 0.98632 | 0.96737 | 0.89368 | 0.83789 | 0.79053 | 1.0126 | 0.98842 | 0.96737 | 0.94526 | 0.92526 | 0.90316 | 0.88211 | 0.86211 | 0.84316 | 0.82421 | 0.74842 | 0.69053 | 0.64211 | 1.0505 | 1.0368 | 1.0179 | 0.99684 | 0.97789 | 0.95684 | 0.93474 | 0.91368 | 0.89474 | 0.87579 | 0.79579 | 0.73579 | 0.68526
|  | STRONTIAN | EE |  |  |  |  | 1.1189 | 1.1095 | 1.0989 | 1.0874 | 1.0758 | 1.0642 | 1.0526 | 1.0379 | 1.0221 | 1.0084 | 0.94526 | 0.9 | 0.86211 | 1.0221 | 1.0042 | 0.98737 | 0.96947 | 0.95053 | 0.93368 | 0.91684 | 0.90105 | 0.88632 | 0.87263 | 0.81053 | 0.76526 | 0.72947 | 1.0547 | 1.0442 | 1.0337 | 1.0158 | 0.99789 | 0.98211 | 0.96421 | 0.94947 | 0.93368 | 0.91895 | 0.85053 | 0.80211 | 0.76
|  | STRONTIAN | HT |  |  |  |  | 1.1147 | 1.1021 | 1.0895 | 1.0768 | 1.0653 | 1.0442 | 1.0232 | 1.0042 | 0.98632 | 0.96737 | 0.89368 | 0.83789 | 0.79053 | 1.0126 | 0.98842 | 0.96737 | 0.94526 | 0.92526 | 0.90316 | 0.88211 | 0.86211 | 0.84316 | 0.82421 | 0.74842 | 0.69053 | 0.64211 | 1.0505 | 1.0368 | 1.0179 | 0.99684 | 0.97789 | 0.95684 | 0.93474 | 0.91368 | 0.89474 | 0.87579 | 0.79579 | 0.73579 | 0.68526
|  | STRONTIAN | HE |  |  |  |  | 1.1263 | 1.12 | 1.1126 | 1.1063 | 1.0989 | 1.0895 | 1.0832 | 1.0758 | 1.0695 | 1.0621 | 1.0411 | 1.0232 | 1.0074 | 1.0326 | 1.0253 | 1.0137 | 1.0042 | 0.99263 | 0.98105 | 0.97053 | 0.95895 | 0.95053 | 0.94105 | 0.90632 | 0.88421 | 0.86842 | 1.0505 | 1.0368 | 1.0179 | 0.99684 | 0.97789 | 0.95684 | 0.93474 | 0.91368 | 0.89474 | 0.87579 | 0.79579 | 0.73579 | 0.68526
|  | STRONTIAN | CF |  |  |  |  | 1.1295 | 1.1263 | 1.1232 | 1.12 | 1.1168 | 1.1126 | 1.1095 | 1.1063 | 1.1021 | 1.0979 | 1.0832 | 1.0758 | 1.0674 | 1.0358 | 1.0326 | 1.0295 | 1.0242 | 1.0189 | 1.0116 | 1.0053 | 1 | 0.99263 | 0.98526 | 0.95789 | 0.94 | 0.92632 | 1.0653 | 1.0621 | 1.0589 | 1.0547 | 1.0516 | 1.0474 | 1.0442 | 1.0411 | 1.0368 | 1.0337 | 1.0095 | 0.99158 | 0.98
| SHETLAND | SUMBURGH | MINIMUM HEADROOM | HU3900512755 | YES | YES | 0 | 1.4642 | 1.4221 | 1.38 | 1.3389 | 1.2989 | 1.2568 | 1.2168 | 1.1779 | 1.1411 | 1.1053 | 0.96526 | 0.85158 | 0.75474 | 1.3021 | 1.2789 | 1.2537 | 1.2253 | 1.1895 | 1.1505 | 1.1105 | 1.0695 | 1.0305 | 0.99263 | 0.84211 | 0.71895 | 0.61263 | 1.3463 | 1.3242 | 1.3 | 1.2768 | 1.2526 | 1.2242 | 1.1832 | 1.1432 | 1.1042 | 1.0684 | 0.92105 | 0.79684 | 0.68947
|  | SUMBURGH | EE |  |  |  |  | 1.4821 | 1.4495 | 1.4158 | 1.3821 | 1.3484 | 1.3158 | 1.2832 | 1.2537 | 1.2242 | 1.1958 | 1.0758 | 0.99158 | 0.92211 | 1.3116 | 1.2926 | 1.2716 | 1.2505 | 1.2295 | 1.2021 | 1.1726 | 1.1453 | 1.1189 | 1.0895 | 0.96316 | 0.87053 | 0.79368 | 1.3547 | 1.3368 | 1.3168 | 1.2968 | 1.2758 | 1.2547 | 1.2337 | 1.2147 | 1.1916 | 1.1621 | 1.0389 | 0.94947 | 0.87263
|  | SUMBURGH | HT |  |  |  |  | 1.4642 | 1.4221 | 1.38 | 1.3389 | 1.2989 | 1.2568 | 1.2168 | 1.1779 | 1.1411 | 1.1053 | 0.96526 | 0.85158 | 0.75474 | 1.3021 | 1.2789 | 1.2537 | 1.2253 | 1.1895 | 1.1505 | 1.1105 | 1.0695 | 1.0305 | 0.99263 | 0.84211 | 0.71895 | 0.61263 | 1.3463 | 1.3242 | 1.3 | 1.2768 | 1.2526 | 1.2242 | 1.1832 | 1.1432 | 1.1042 | 1.0684 | 0.92105 | 0.79684 | 0.68947
|  | SUMBURGH | HE |  |  |  |  | 1.5095 | 1.4884 | 1.4663 | 1.4453 | 1.4221 | 1.3989 | 1.3779 | 1.3568 | 1.3368 | 1.3189 | 1.2505 | 1.2074 | 1.1758 | 1.3253 | 1.3126 | 1.2979 | 1.2832 | 1.2684 | 1.2505 | 1.2358 | 1.2211 | 1.2053 | 1.1926 | 1.1389 | 1.1011 | 1.0695 | 1.3463 | 1.3242 | 1.3 | 1.2768 | 1.2526 | 1.2242 | 1.1832 | 1.1432 | 1.1042 | 1.0684 | 0.92105 | 0.79684 | 0.68947
|  | SUMBURGH | CF |  |  |  |  | 1.5211 | 1.5095 | 1.4968 | 1.4832 | 1.4695 | 1.4568 | 1.4432 | 1.4295 | 1.4168 | 1.4042 | 1.3453 | 1.3063 | 1.2768 | 1.3316 | 1.3253 | 1.3179 | 1.3105 | 1.3011 | 1.2937 | 1.2863 | 1.2779 | 1.2695 | 1.2611 | 1.2274 | 1.1958 | 1.1716 | 1.3747 | 1.3684 | 1.3611 | 1.3537 | 1.3453 | 1.3379 | 1.3305 | 1.3221 | 1.3147 | 1.3063 | 1.2737 | 1.2568 | 1.2442
| ALNESS | TAIN | MINIMUM HEADROOM | NH 77578 81489 | NO | YES | 0 | 16.4079 | 16.3247 | 16.2311 | 16.1363 | 24.7716 | 24.0684 | 23.2653 | 22.46 | 21.7221 | 21.0621 | 19.8484 | 18.54 | 17.9411 | 14.9905 | 14.9074 | 14.8179 | 14.6905 | 22.7042 | 21.7253 | 20.8474 | 19.9663 | 19.1747 | 18.4726 | 17.3263 | 16.2905 | 15.7126 | 15.2655 | 15.1824 | 15.0897 | 14.995 | 23.4053 | 22.48 | 21.5821 | 20.6832 | 19.8621 | 19.1316 | 17.8495 | 16.4653 | 15.82
|  | TAIN | EE |  |  |  |  | 16.4405 | 16.3742 | 16.2942 | 16.2111 | 24.8547 | 24.6453 | 24.4095 | 23.6547 | 22.8547 | 22.0495 | 19.8484 | 18.54 | 17.9411 | 15.0232 | 14.9568 | 14.8832 | 14.8053 | 22.9011 | 22.5547 | 22.2853 | 21.3926 | 20.5284 | 19.6589 | 17.4537 | 16.2905 | 15.7126 | 15.2982 | 15.2318 | 15.1529 | 15.0697 | 23.4895 | 23.2716 | 22.96 | 22.0495 | 21.1558 | 20.2568 | 17.8526 | 16.4653 | 15.82
|  | TAIN | HT |  |  |  |  | 16.4079 | 16.3247 | 16.2311 | 16.1363 | 24.7716 | 24.0684 | 23.2653 | 22.46 | 21.7221 | 21.0621 | 19.86 | 19.0168 | 18.4684 | 14.9905 | 14.9074 | 14.8179 | 14.6905 | 22.7042 | 21.7253 | 20.8474 | 19.9663 | 19.1747 | 18.4726 | 17.3263 | 16.5042 | 15.9389 | 15.2655 | 15.1824 | 15.0897 | 14.995 | 23.4053 | 22.48 | 21.5821 | 20.6832 | 19.8621 | 19.1316 | 17.8495 | 16.9442 | 16.3484
|  | TAIN | HE |  |  |  |  | 16.4858 | 16.4405 | 16.39 | 16.3353 | 25.0063 | 24.8011 | 24.6253 | 24.3653 | 23.8611 | 23.3621 | 21.4379 | 20.2579 | 19.3853 | 15.0684 | 15.0232 | 14.9737 | 14.92 | 23.1421 | 22.8832 | 22.6895 | 22.1516 | 21.6211 | 21.0947 | 19.1 | 17.9463 | 17.1589 | 15.2655 | 15.1824 | 15.0897 | 14.995 | 23.4053 | 22.48 | 21.5821 | 20.6832 | 19.8621 | 19.1316 | 17.8495 | 16.9442 | 16.3484
|  | TAIN | CF |  |  |  |  | 16.51 | 16.4847 | 16.4553 | 16.4268 | 25.1263 | 25.0442 | 24.9674 | 24.8916 | 24.8221 | 24.7653 | 23.6053 | 22.7747 | 22.1147 | 15.0926 | 15.0674 | 15.0389 | 15.0116 | 23.2621 | 23.2063 | 23.1537 | 23.1021 | 22.8442 | 22.5642 | 21.2842 | 20.4495 | 19.7747 | 15.3676 | 15.3424 | 15.3139 | 15.2845 | 23.76 | 23.6789 | 23.6042 | 23.5316 | 23.4632 | 23.2737 | 21.9579 | 21.0463 | 20.3179
| ARDMORE / HARRIS GRID | TARBERT | MINIMUM HEADROOM | NB 15289 00157 | NO | YES | 0.999 | 0.17784 | 0.14521 | 0.10732 | -0.76532 | -0.81058 | -0.97374 | -1.1327 | -1.2927 | -1.4327 | -1.5758 | -2.9074 | -4.4727 | -5.7979 | 0.097842 | 0.038895 | -0.026368 | -0.74847 | -0.79795 | -0.94005 | -1.079 | -1.2158 | -1.3411 | -1.4643 | -2.8106 | -4.4116 | -5.8843 | 0.068368 | 0.0083684 | -0.055842 | -0.96742 | -1.0148 | -1.1801 | -1.3401 | -1.5011 | -1.6443 | -1.7885 | -3.2506 | -5.0011 | -6.5264
|  | TARBERT | EE |  |  |  |  | 0.18942 | 0.16311 | 0.12837 | -0.76532 | -0.81058 | -0.97374 | -1.1327 | -1.2927 | -1.4327 | -1.5758 | -2.9074 | -4.4727 | -5.7979 | 0.11047 | 0.079947 | 0.025211 | -0.74847 | -0.79795 | -0.94005 | -1.079 | -1.2158 | -1.3411 | -1.4643 | -2.8106 | -4.4116 | -5.8843 | 0.094684 | 0.047316 | -0.0074211 | -0.96742 | -1.0148 | -1.1801 | -1.3401 | -1.5011 | -1.6443 | -1.7885 | -3.2506 | -5.0011 | -6.5264
|  | TARBERT | HT |  |  |  |  | 0.17784 | 0.14521 | 0.10732 | 0.069421 | 0.023105 | -0.10953 | -0.24216 | -0.37479 | -0.519 | -0.68111 | -2.0327 | -3.6601 | -4.7979 | 0.097842 | 0.038895 | -0.026368 | -0.092684 | -0.15689 | -0.27795 | -0.39689 | -0.51689 | -0.64637 | -0.79374 | -2.2485 | -4.0464 | -5.3401 | 0.068368 | 0.0083684 | -0.055842 | -0.12005 | -0.18321 | -0.31689 | -0.45163 | -0.58637 | -0.73374 | -0.90005 | -2.4464 | -4.3064 | -5.6201
|  | TARBERT | HE |  |  |  |  | 0.20837 | 0.19047 | 0.17047 | 0.14837 | 0.12416 | 0.014684 | -0.080053 | -0.23479 | -0.39058 | -0.62321 | -1.5927 | -2.859 | -4.2306 | 0.13047 | 0.11153 | 0.092579 | 0.069421 | 0.037842 | -0.077947 | -0.20532 | -0.36321 | -0.51163 | -0.75268 | -1.7569 | -3.0895 | -4.5327 | 0.068368 | 0.0083684 | -0.055842 | -0.12005 | -0.18321 | -0.31689 | -0.45163 | -0.58637 | -0.73374 | -0.90005 | -2.4464 | -4.3064 | -5.6201
|  | TARBERT | CF |  |  |  |  | 0.21784 | 0.20837 | 0.19679 | 0.18521 | 0.17363 | 0.13047 | 0.090474 | 0.051526 | 0.0020526 | -0.12005 | -0.64532 | -1.4443 | -2.3695 | 0.13995 | 0.13047 | 0.11889 | 0.10732 | 0.096789 | 0.058895 | 0.011526 | -0.037947 | -0.15058 | -0.28637 | -0.859 | -1.7116 | -2.7274 | 0.15047 | 0.13363 | 0.11468 | 0.092579 | 0.074684 | 0.017842 | -0.036895 | -0.091632 | -0.20321 | -0.33479 | -0.94532 | -1.8506 | -2.9085
| PORT ANN | TARBERT JURA | MINIMUM HEADROOM | NR 60552 82166 | YES | YES | 0 | 0.20421 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.19895 | 0.19895 | 0.19789 | 0.19579 | 0.19474 | 0.19053 | 0.18632 | 0.18316 | 0.20211 | 0.20105 | 0.2 | 0.19895 | 0.19895 | 0.19684 | 0.19579 | 0.19474 | 0.19263 | 0.19158 | 0.18632 | 0.18211 | 0.17789 | 0.20316 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.19789 | 0.19684 | 0.19579 | 0.19368 | 0.19263 | 0.18737 | 0.18316 | 0.17895
|  | TARBERT JURA | EE |  |  |  |  | 0.20526 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.2 | 0.19895 | 0.19895 | 0.19789 | 0.19474 | 0.19158 | 0.18737 | 0.20316 | 0.20105 | 0.20105 | 0.2 | 0.19895 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19474 | 0.19053 | 0.18737 | 0.18316 | 0.20421 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.19579 | 0.19158 | 0.18842 | 0.18421
|  | TARBERT JURA | HT |  |  |  |  | 0.20421 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.19895 | 0.19895 | 0.19789 | 0.19579 | 0.19474 | 0.19053 | 0.18632 | 0.18316 | 0.20211 | 0.20105 | 0.2 | 0.19895 | 0.19895 | 0.19684 | 0.19579 | 0.19474 | 0.19263 | 0.19158 | 0.18632 | 0.18211 | 0.17789 | 0.20316 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.19789 | 0.19684 | 0.19579 | 0.19368 | 0.19263 | 0.18737 | 0.18316 | 0.17895
|  | TARBERT JURA | HE |  |  |  |  | 0.20526 | 0.20526 | 0.20526 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20105 | 0.19895 | 0.19789 | 0.19579 | 0.20316 | 0.20316 | 0.20316 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.2 | 0.2 | 0.19789 | 0.19684 | 0.19474 | 0.19263 | 0.20316 | 0.20211 | 0.20105 | 0.2 | 0.2 | 0.19789 | 0.19684 | 0.19579 | 0.19368 | 0.19263 | 0.18737 | 0.18316 | 0.17895
|  | TARBERT JURA | CF |  |  |  |  | 0.20526 | 0.20526 | 0.20526 | 0.20526 | 0.20526 | 0.20421 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.2 | 0.2 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20316 | 0.20211 | 0.20105 | 0.20105 | 0.20105 | 0.2 | 0.19895 | 0.19789 | 0.19684 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20421 | 0.20316 | 0.20211 | 0.20211 | 0.20211 | 0.20105 | 0.2 | 0.19895 | 0.19789
| PORT ANN | TARBERT LOCH FYNE | MINIMUM HEADROOM | NR 86003 68479 | NO | YES | 0 | 3.1547 | 3.1179 | 3.0663 | 3.0137 | 2.9568 | 2.6263 | 2.1232 | 1.6653 | 1.2684 | 0.86947 | -2.7063 | -6.8326 | -9.8484 | 2.9411 | 2.8326 | 2.7021 | 2.6179 | 2.4884 | 2.2168 | 1.8232 | 1.4568 | 1.1189 | 0.75684 | -2.5968 | -6.6 | -9.8495 | 2.9989 | 2.9 | 2.7768 | 2.6947 | 2.5684 | 2.2284 | 1.7042 | 1.2326 | 0.82211 | 0.40947 | -3.4232 | -7.8895 | -11.28
|  | TARBERT LOCH FYNE | EE |  |  |  |  | 3.1695 | 3.1389 | 3.0874 | 3.0337 | 2.9779 | 2.6453 | 2.1232 | 1.6653 | 1.2684 | 0.86947 | -2.7063 | -6.8326 | -9.8484 | 2.9737 | 2.8958 | 2.7968 | 2.7137 | 2.5989 | 2.2684 | 1.8232 | 1.4568 | 1.1189 | 0.78211 | -2.5968 | -6.6 | -9.8495 | 3.0295 | 2.9568 | 2.8568 | 2.7716 | 2.6579 | 2.2442 | 1.7042 | 1.2326 | 0.82211 | 0.40947 | -3.4232 | -7.8895 | -11.28
|  | TARBERT LOCH FYNE | HT |  |  |  |  | 3.1547 | 3.1179 | 3.0663 | 3.0137 | 2.9568 | 2.6263 | 2.2747 | 1.9368 | 1.5421 | 1.0189 | -2.3095 | -5.9632 | -8.4232 | 2.9411 | 2.8326 | 2.7021 | 2.6179 | 2.4884 | 2.2168 | 1.9189 | 1.6389 | 1.3137 | 0.84105 | -2.5232 | -6.4768 | -9.2284 | 2.9989 | 2.9 | 2.7768 | 2.6947 | 2.5684 | 2.2284 | 1.8632 | 1.5147 | 1.1053 | 0.55474 | -3.0842 | -7.2189 | -10.0442
|  | TARBERT LOCH FYNE | HE |  |  |  |  | 3.1874 | 3.1674 | 3.1411 | 3.1126 | 3.0832 | 2.7389 | 2.3947 | 1.9958 | 1.5663 | 0.95895 | -1.6274 | -4.7642 | -8.1705 | 3.0168 | 2.9568 | 2.8853 | 2.8358 | 2.7326 | 2.4147 | 2.0737 | 1.7274 | 1.3474 | 0.75684 | -1.7242 | -4.8842 | -8.3242 | 2.9989 | 2.9 | 2.7768 | 2.6947 | 2.5684 | 2.2284 | 1.8632 | 1.5147 | 1.1053 | 0.55474 | -3.0842 | -7.2189 | -10.0442
|  | TARBERT LOCH FYNE | CF |  |  |  |  | 3.1979 | 3.1863 | 3.1705 | 3.1547 | 3.1379 | 3.0074 | 2.8905 | 2.7758 | 2.6105 | 2.3232 | 0.99895 | -0.97579 | -3.1179 | 3.0368 | 3.0158 | 2.9842 | 2.9558 | 2.9147 | 2.7863 | 2.6474 | 2.5021 | 2.2389 | 1.9295 | 0.60526 | -1.3979 | -3.6884 | 3.0874 | 3.0674 | 3.0379 | 3.0084 | 2.9705 | 2.8074 | 2.6432 | 2.4737 | 2.2095 | 1.8905 | 0.44842 | -1.7295 | -4.1495
| TAYNUILT | TAYNUILT | MINIMUM HEADROOM | NN 01856 31079 | NO | YES | 0 | 2.6968 | 2.5863 | 2.4453 | 2.3 | 2.1505 | 1.9747 | 1.8179 | 1.6589 | 1.4979 | 1.3347 | 0.59579 | -0.02 | -0.62526 | 2.5474 | 2.4284 | 2.2737 | 2.1105 | 1.9453 | 1.7747 | 1.6232 | 1.4674 | 1.3105 | 1.1516 | 0.43474 | -0.16211 | -0.75158 | 2.5116 | 2.3853 | 2.24 | 2.0895 | 1.9368 | 1.7789 | 1.6326 | 1.4695 | 1.3063 | 1.1411 | 0.38947 | -0.23895 | -0.85474
|  | TAYNUILT | EE |  |  |  |  | 2.7126 | 2.5863 | 2.4453 | 2.3 | 2.1505 | 1.9747 | 1.8179 | 1.6589 | 1.4979 | 1.3347 | 0.59579 | -0.02 | -0.62526 | 2.5653 | 2.4284 | 2.2737 | 2.1105 | 1.9453 | 1.7747 | 1.6232 | 1.4674 | 1.3105 | 1.1516 | 0.43474 | -0.16211 | -0.75158 | 2.5284 | 2.3853 | 2.24 | 2.0895 | 1.9368 | 1.7789 | 1.6326 | 1.4695 | 1.3063 | 1.1411 | 0.38947 | -0.23895 | -0.85474
|  | TAYNUILT | HT |  |  |  |  | 2.6968 | 2.6316 | 2.5684 | 2.5032 | 2.4389 | 2.3726 | 2.3063 | 2.24 | 2.18 | 2.1179 | 1.8337 | 1.5747 | 1.3274 | 2.5474 | 2.4916 | 2.4263 | 2.3579 | 2.2905 | 2.2221 | 2.1526 | 2.0853 | 2.0221 | 1.9568 | 1.6621 | 1.3895 | 1.1284 | 2.5116 | 2.44 | 2.3695 | 2.2989 | 2.2284 | 2.1568 | 2.0842 | 2.0137 | 1.9474 | 1.88 | 1.5737 | 1.2895 | 1.0179
|  | TAYNUILT | HE |  |  |  |  | 2.7337 | 2.6884 | 2.64 | 2.5916 | 2.54 | 2.4874 | 2.4347 | 2.3821 | 2.3295 | 2.2789 | 2.0463 | 1.8021 | 1.5568 | 2.5874 | 2.5421 | 2.4884 | 2.4358 | 2.38 | 2.3232 | 2.2684 | 2.2105 | 2.1547 | 2.1011 | 1.8463 | 1.6042 | 1.3663 | 2.5116 | 2.44 | 2.3695 | 2.2989 | 2.2284 | 2.1568 | 2.0842 | 2.0137 | 1.9474 | 1.88 | 1.5737 | 1.2895 | 1.0179
|  | TAYNUILT | CF |  |  |  |  | 2.7453 | 2.7284 | 2.7095 | 2.6905 | 2.6726 | 2.6547 | 2.6368 | 2.6168 | 2.6021 | 2.5832 | 2.5021 | 2.4389 | 2.3895 | 2.5947 | 2.5853 | 2.5663 | 2.5484 | 2.5305 | 2.5126 | 2.4958 | 2.4768 | 2.46 | 2.4421 | 2.36 | 2.2968 | 2.2474 | 2.5621 | 2.5432 | 2.5232 | 2.5032 | 2.4832 | 2.4642 | 2.4432 | 2.4242 | 2.4053 | 2.3853 | 2.2989 | 2.2305 | 2.1747
| BURGHMUIR | THIMBLEROW | MINIMUM HEADROOM | NO 11356 23764 | NO | YES | 0 | 31.0505 | 30.78 | 30.4811 | 30.2263 | 29.9568 | 29.6684 | 29.4021 | 29.1337 | 28.8547 | 28.5832 | 27.4821 | 26.5526 | 25.7326 | 29.5558 | 29.2789 | 28.9737 | 28.7147 | 28.44 | 28.1484 | 27.88 | 27.6063 | 27.3221 | 27.0453 | 25.92 | 24.9653 | 24.1211 | 29.3032 | 29.1284 | 28.9358 | 28.7463 | 28.5442 | 28.3189 | 28.1147 | 27.9147 | 27.7158 | 27.5232 | 26.8211 | 26.2863 | 25.8547
|  | THIMBLEROW | EE |  |  |  |  | 31.1674 | 30.98 | 30.7747 | 30.5547 | 30.3432 | 30.1358 | 29.9358 | 29.7526 | 29.5747 | 29.3979 | 28.5937 | 27.9274 | 27.3579 | 29.6832 | 29.4821 | 29.2726 | 29.0474 | 28.8316 | 28.62 | 28.4179 | 28.2316 | 28.0505 | 27.8716 | 27.0516 | 26.3674 | 25.78 | 29.3884 | 29.2632 | 29.1316 | 28.9937 | 28.8505 | 28.7053 | 28.5632 | 28.4274 | 28.2947 | 28.1674 | 27.6137 | 27.2474 | 26.9737
|  | THIMBLEROW | HT |  |  |  |  | 31.0505 | 30.78 | 30.4811 | 30.2263 | 29.9568 | 29.6684 | 29.4021 | 29.1337 | 28.8547 | 28.5832 | 27.4821 | 26.5526 | 25.7326 | 29.5558 | 29.2789 | 28.9737 | 28.7147 | 28.44 | 28.1484 | 27.88 | 27.6063 | 27.3221 | 27.0453 | 25.92 | 24.9653 | 24.1211 | 29.3032 | 29.1284 | 28.9358 | 28.7463 | 28.5442 | 28.3189 | 28.1147 | 27.9147 | 27.7158 | 27.5232 | 26.8211 | 26.2863 | 25.8547
|  | THIMBLEROW | HE |  |  |  |  | 31.2632 | 31.1253 | 30.9611 | 30.7821 | 30.6189 | 30.4579 | 30.3074 | 30.1663 | 30.0326 | 29.9042 | 29.4295 | 29.1084 | 28.8705 | 29.7916 | 29.6389 | 29.4632 | 29.2811 | 29.1147 | 28.9516 | 28.8 | 28.6568 | 28.5211 | 28.3916 | 27.9084 | 27.58 | 27.3347 | 29.3032 | 29.1284 | 28.9358 | 28.7463 | 28.5442 | 28.3189 | 28.1147 | 27.9147 | 27.7158 | 27.5232 | 26.8211 | 26.2863 | 25.8547
|  | THIMBLEROW | CF |  |  |  |  | 31.2905 | 31.2221 | 31.1295 | 31.0316 | 30.9232 | 30.8168 | 30.7042 | 30.5895 | 30.4842 | 30.3768 | 29.9084 | 29.6147 | 29.4011 | 29.82 | 29.7484 | 29.6474 | 29.54 | 29.4274 | 29.3179 | 29.2042 | 29.0863 | 28.9789 | 28.8705 | 28.3937 | 28.0926 | 27.8726 | 29.4768 | 29.4147 | 29.3442 | 29.2716 | 29.1958 | 29.1211 | 29.0453 | 28.9663 | 28.8916 | 28.8158 | 28.4895 | 28.3137 | 28.2116
| TAYNUILT | TIRORAN BRIDGE | MINIMUM HEADROOM | NM 48666 28729 | YES | YES | 0 | 0.21368 | 0.21158 | 0.21053 | 0.20737 | 0.20632 | 0.20421 | 0.20211 | 0.2 | 0.19789 | 0.19684 | 0.18842 | 0.18211 | 0.17579 | 0.20737 | 0.20632 | 0.20526 | 0.20421 | 0.20316 | 0.20105 | 0.19789 | 0.19684 | 0.19368 | 0.19263 | 0.18316 | 0.17579 | 0.16842 | 0.20842 | 0.20632 | 0.20526 | 0.20316 | 0.20105 | 0.19895 | 0.19579 | 0.19368 | 0.19158 | 0.19053 | 0.18105 | 0.17368 | 0.16632
|  | TIRORAN BRIDGE | EE |  |  |  |  | 0.21368 | 0.21263 | 0.21158 | 0.21053 | 0.20842 | 0.20737 | 0.20526 | 0.20421 | 0.20316 | 0.20105 | 0.19474 | 0.18947 | 0.18421 | 0.20737 | 0.20632 | 0.20632 | 0.20526 | 0.20421 | 0.20421 | 0.20211 | 0.20105 | 0.19895 | 0.19684 | 0.19053 | 0.18421 | 0.17895 | 0.20947 | 0.20737 | 0.20632 | 0.20526 | 0.20421 | 0.20316 | 0.2 | 0.19895 | 0.19684 | 0.19474 | 0.18842 | 0.18211 | 0.17684
|  | TIRORAN BRIDGE | HT |  |  |  |  | 0.21368 | 0.21158 | 0.21053 | 0.20737 | 0.20632 | 0.20421 | 0.20211 | 0.2 | 0.19789 | 0.19684 | 0.18842 | 0.18211 | 0.17579 | 0.20737 | 0.20632 | 0.20526 | 0.20421 | 0.20316 | 0.20105 | 0.19789 | 0.19684 | 0.19368 | 0.19263 | 0.18316 | 0.17579 | 0.16842 | 0.20842 | 0.20632 | 0.20526 | 0.20316 | 0.20105 | 0.19895 | 0.19579 | 0.19368 | 0.19158 | 0.19053 | 0.18105 | 0.17368 | 0.16632
|  | TIRORAN BRIDGE | HE |  |  |  |  | 0.21368 | 0.21368 | 0.21368 | 0.21263 | 0.21263 | 0.21158 | 0.21053 | 0.20947 | 0.20842 | 0.20737 | 0.20421 | 0.20105 | 0.19895 | 0.20737 | 0.20737 | 0.20737 | 0.20632 | 0.20632 | 0.20526 | 0.20526 | 0.20421 | 0.20421 | 0.20316 | 0.20105 | 0.19684 | 0.19474 | 0.20842 | 0.20632 | 0.20526 | 0.20316 | 0.20105 | 0.19895 | 0.19579 | 0.19368 | 0.19158 | 0.19053 | 0.18105 | 0.17368 | 0.16632
|  | TIRORAN BRIDGE | CF |  |  |  |  | 0.21579 | 0.21368 | 0.21368 | 0.21368 | 0.21368 | 0.21263 | 0.21263 | 0.21263 | 0.21263 | 0.21053 | 0.20737 | 0.20632 | 0.20526 | 0.20842 | 0.20737 | 0.20737 | 0.20737 | 0.20737 | 0.20632 | 0.20632 | 0.20632 | 0.20632 | 0.20526 | 0.20421 | 0.20316 | 0.20105 | 0.21053 | 0.20947 | 0.20947 | 0.20947 | 0.20947 | 0.20737 | 0.20737 | 0.20737 | 0.20737 | 0.20526 | 0.20316 | 0.20105 | 0.19895
| BOAT OF GARTEN | TOMATIN | MINIMUM HEADROOM | NH 79106 29734 | YES | YES | 0 | 1.1674 | 1.1568 | 1.1326 | 1.1 | 1.0684 | 0.61263 | 0.15474 | -0.31368 | -0.67789 | -1.0684 | -3.3263 | -6.5284 | -8.9474 | 1.0674 | 1.0568 | 1.04 | 1.0232 | 1.0053 | 0.54947 | 0.087368 | -0.38632 | -0.72211 | -0.99053 | -3.0705 | -6.2168 | -8.8421 | 1.0411 | 1.02 | 0.98526 | 0.95263 | 0.91895 | 0.41158 | -0.094737 | -0.61579 | -1.0053 | -1.3905 | -3.7958 | -7.2926 | -10.0484
|  | TOMATIN | EE |  |  |  |  | 1.1737 | 1.1642 | 1.1368 | 1.1084 | 1.0737 | 0.82421 | 0.50842 | -0.028421 | -0.54105 | -1.0684 | -3.3263 | -6.5284 | -8.9474 | 1.0726 | 1.0642 | 1.0463 | 1.0284 | 1.0095 | 0.80842 | 0.55263 | 0.021053 | -0.47789 | -0.99053 | -3.0705 | -6.2168 | -8.8421 | 1.0526 | 1.0358 | 0.99895 | 0.96211 | 0.92632 | 0.66947 | 0.35579 | -0.24947 | -0.81158 | -1.3905 | -3.7958 | -7.2926 | -10.0484
|  | TOMATIN | HT |  |  |  |  | 1.1674 | 1.1568 | 1.1326 | 1.1 | 1.0684 | 0.61263 | 0.15474 | -0.31368 | -0.67789 | -0.93789 | -3.0347 | -5.9505 | -7.9263 | 1.0674 | 1.0568 | 1.04 | 1.0232 | 1.0053 | 0.54947 | 0.087368 | -0.38632 | -0.72211 | -0.93474 | -3.0305 | -6.1989 | -8.4253 | 1.0411 | 1.02 | 0.98526 | 0.95263 | 0.91895 | 0.41158 | -0.094737 | -0.61579 | -1.0053 | -1.2726 | -3.5895 | -6.9095 | -9.1884
|  | TOMATIN | HE |  |  |  |  | 1.18 | 1.1747 | 1.1653 | 1.1537 | 1.1432 | 0.82421 | 0.50211 | 0.17474 | -0.15053 | -0.60105 | -2.5737 | -5.0474 | -7.7495 | 1.0789 | 1.0737 | 1.0663 | 1.0579 | 1.0484 | 0.80211 | 0.50211 | 0.19684 | -0.10632 | -0.54632 | -2.4737 | -4.9916 | -7.7442 | 1.0411 | 1.02 | 0.98526 | 0.95263 | 0.91895 | 0.41158 | -0.094737 | -0.61579 | -1.0053 | -1.2726 | -3.5895 | -6.9095 | -9.1884
|  | TOMATIN | CF |  |  |  |  | 1.1832 | 1.1811 | 1.1758 | 1.1684 | 1.1632 | 1.0737 | 0.98842 | 0.79895 | 0.59895 | 0.37579 | -0.63368 | -2.1726 | -3.8842 | 1.0821 | 1.08 | 1.0758 | 1.0695 | 1.0653 | 1.02 | 0.96211 | 0.77053 | 0.56842 | 0.32632 | -0.70526 | -2.3 | -4.1558 | 1.0726 | 1.0674 | 1.0579 | 1.0474 | 1.04 | 0.93579 | 0.84421 | 0.62842 | 0.40526 | 0.15158 | -0.97579 | -2.7053 | -4.6579
| LAIRG | TORBOLL | MINIMUM HEADROOM | NC 75779 00296 | YES | YES | 0 | 0.10211 | 0.10211 | 0.1 | 0.098947 | 0.096842 | 0.075789 | 0.051579 | 0.026316 | 0.0021053 | -0.04 | -0.27053 | -0.59263 | -0.82316 | 0.10105 | 0.10105 | 0.098947 | 0.097895 | 0.095789 | 0.075789 | 0.051579 | 0.026316 | 0.0031579 | -0.042105 | -0.29158 | -0.65789 | -0.92526 | 0.10105 | 0.10105 | 0.098947 | 0.097895 | 0.094737 | 0.082105 | 0.066316 | 0.049474 | 0.027368 | -0.030526 | -0.31684 | -0.69053 | -0.95895
|  | TORBOLL | EE |  |  |  |  | 0.10211 | 0.10211 | 0.10105 | 0.1 | 0.096842 | 0.083158 | 0.067368 | 0.051579 | 0.037895 | 0.0031579 | -0.25158 | -0.54316 | -0.81263 | 0.10105 | 0.10105 | 0.1 | 0.1 | 0.095789 | 0.085263 | 0.073684 | 0.06 | 0.048421 | 0.014737 | -0.25263 | -0.56211 | -0.86737 | 0.10105 | 0.10105 | 0.1 | 0.098947 | 0.094737 | 0.082105 | 0.066316 | 0.049474 | 0.035789 | -0.0010526 | -0.28842 | -0.61684 | -0.92842
|  | TORBOLL | HT |  |  |  |  | 0.10211 | 0.10211 | 0.1 | 0.098947 | 0.097895 | 0.087368 | 0.076842 | 0.055789 | 0.031579 | -0.017895 | -0.27053 | -0.59263 | -0.82316 | 0.10105 | 0.10105 | 0.098947 | 0.097895 | 0.097895 | 0.088421 | 0.081053 | 0.058947 | 0.037895 | -0.016842 | -0.29158 | -0.65789 | -0.92526 | 0.10105 | 0.10105 | 0.098947 | 0.097895 | 0.096842 | 0.086316 | 0.075789 | 0.052632 | 0.027368 | -0.030526 | -0.31684 | -0.69053 | -0.95895
|  | TORBOLL | HE |  |  |  |  | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.075789 | 0.051579 | 0.026316 | 0.0021053 | -0.04 | -0.21474 | -0.45684 | -0.72211 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.075789 | 0.051579 | 0.026316 | 0.0031579 | -0.042105 | -0.22421 | -0.48842 | -0.77895 | 0.10105 | 0.10105 | 0.098947 | 0.097895 | 0.096842 | 0.086316 | 0.075789 | 0.052632 | 0.027368 | -0.030526 | -0.31684 | -0.69053 | -0.95895
|  | TORBOLL | CF |  |  |  |  | 0.10211 | 0.10211 | 0.10211 | 0.10211 | 0.10105 | 0.096842 | 0.091579 | 0.071579 | 0.051579 | 0.027368 | -0.069474 | -0.22526 | -0.41158 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.096842 | 0.092632 | 0.070526 | 0.049474 | 0.022105 | -0.084211 | -0.25368 | -0.46526 | 0.10105 | 0.10105 | 0.10105 | 0.10105 | 0.1 | 0.095789 | 0.090526 | 0.067368 | 0.045263 | 0.016842 | -0.093684 | -0.27053 | -0.48526
| KINTORE | TORRYBURN | MINIMUM HEADROOM | NJ 79129 15653 | NO | YES | 1.182 | 23.8548 | 23.5159 | 23.1064 | 22.6454 | 22.1275 | 21.0906 | 20.0696 | 19.0538 | 17.9759 | 16.9033 | 12.2064 | 9.2812 | 7.0169 | 20.7801 | 20.3896 | 19.9201 | 19.3864 | 18.7801 | 17.6696 | 16.5769 | 15.4896 | 14.3612 | 13.2391 | 8.7475 | 6.3096 | 3.9527 | 22.0454 | 21.7106 | 21.3043 | 20.8496 | 20.3243 | 19.2148 | 18.0612 | 16.9127 | 15.7054 | 14.5022 | 9.4096 | 6.4201 | 3.9117
|  | TORRYBURN | EE |  |  |  |  | 23.9243 | 23.6706 | 23.3148 | 22.9043 | 22.4443 | 21.3654 | 20.2275 | 19.1096 | 18.0685 | 17.0243 | 12.2064 | 9.2812 | 7.0169 | 20.8506 | 20.5601 | 20.1548 | 19.6822 | 19.1485 | 18.0117 | 16.8391 | 15.6969 | 14.6148 | 13.5338 | 8.7475 | 6.3096 | 3.9527 | 22.1148 | 21.8643 | 21.5117 | 21.1064 | 20.6517 | 19.5201 | 18.2622 | 17.0191 | 15.8527 | 14.6843 | 9.4096 | 6.4201 | 3.9117
|  | TORRYBURN | HT |  |  |  |  | 23.8548 | 23.5159 | 23.1064 | 22.6454 | 22.1275 | 21.0906 | 20.0696 | 19.0538 | 17.9759 | 16.9033 | 12.6896 | 11.0412 | 7.9601 | 20.7801 | 20.3896 | 19.9201 | 19.3864 | 18.7801 | 17.6696 | 16.5769 | 15.4896 | 14.3612 | 13.2391 | 8.9169 | 7.3875 | 3.9769 | 22.0454 | 21.7106 | 21.3043 | 20.8496 | 20.3243 | 19.2148 | 18.0612 | 16.9127 | 15.7054 | 14.5022 | 9.8412 | 8.1148 | 4.5948
|  | TORRYBURN | HE |  |  |  |  | 24.0096 | 23.8159 | 23.5727 | 23.2601 | 22.8759 | 21.9106 | 20.9622 | 20.0327 | 19.1096 | 18.1991 | 14.3875 | 12.638 | 9.5517 | 20.9359 | 20.7106 | 20.4264 | 20.0559 | 19.5969 | 18.6117 | 17.6096 | 16.6306 | 15.658 | 14.6991 | 10.7812 | 9.3327 | 6.3327 | 22.0454 | 21.7106 | 21.3043 | 20.8496 | 20.3243 | 19.2148 | 18.0612 | 16.9127 | 15.7054 | 14.5022 | 9.8412 | 8.1148 | 4.5948
|  | TORRYBURN | CF |  |  |  |  | 24.1096 | 24.0422 | 23.9612 | 23.8675 | 23.7643 | 23.4791 | 23.0412 | 22.5854 | 22.1412 | 21.7064 | 19.5822 | 18.4506 | 16.0991 | 21.0517 | 20.9769 | 20.8864 | 20.7833 | 20.6664 | 20.3948 | 19.9212 | 19.4243 | 18.9317 | 18.4338 | 16.1169 | 15.1633 | 12.5222 | 22.2991 | 22.2327 | 22.1517 | 22.0591 | 21.9569 | 21.6717 | 21.238 | 20.7864 | 20.3433 | 19.8769 | 17.4738 | 16.3169 | 13.558
| LAIRG | TRESSADY | MINIMUM HEADROOM | NC 70537 03678 | YES | YES | 0 | 0.56737 | 0.54947 | 0.52316 | 0.49789 | 0.47158 | 0.27789 | 0.023158 | -0.23895 | -0.49053 | -0.86 | -3.0316 | -5.64 | -7.6874 | 0.50421 | 0.48421 | 0.45895 | 0.43474 | 0.40842 | 0.25579 | 0.018947 | -0.22632 | -0.45789 | -0.83579 | -2.9116 | -5.6274 | -7.7042 | 0.50947 | 0.49263 | 0.46737 | 0.44211 | 0.41474 | 0.22105 | -0.016842 | -0.26526 | -0.47789 | -0.88632 | -3.3421 | -6.1937 | -8.5347
|  | TRESSADY | EE |  |  |  |  | 0.57368 | 0.56105 | 0.53368 | 0.50421 | 0.47579 | 0.27789 | 0.041053 | -0.20421 | -0.41579 | -0.72105 | -3.0316 | -5.64 | -7.6874 | 0.51158 | 0.49789 | 0.47263 | 0.44632 | 0.42105 | 0.26632 | 0.074737 | -0.12421 | -0.29579 | -0.57684 | -2.8632 | -5.4642 | -7.7042 | 0.51579 | 0.50421 | 0.47684 | 0.44842 | 0.42 | 0.22105 | -0.016842 | -0.26526 | -0.47789 | -0.78947 | -3.3421 | -6.1937 | -8.5347
|  | TRESSADY | HT |  |  |  |  | 0.56737 | 0.54947 | 0.52316 | 0.49789 | 0.47158 | 0.30526 | 0.13789 | -0.051579 | -0.31368 | -0.75684 | -2.8811 | -5.3495 | -7.0421 | 0.50421 | 0.48421 | 0.45895 | 0.43474 | 0.40842 | 0.28105 | 0.14211 | -0.02 | -0.25579 | -0.70632 | -2.9116 | -5.6274 | -7.5442 | 0.50947 | 0.49263 | 0.46737 | 0.44211 | 0.41474 | 0.24842 | 0.08 | -0.11263 | -0.38526 | -0.88632 | -3.2526 | -6.0716 | -8.0295
|  | TRESSADY | HE |  |  |  |  | 0.58211 | 0.57579 | 0.56632 | 0.55579 | 0.54316 | 0.27895 | 0.023158 | -0.23895 | -0.49053 | -0.86 | -2.4663 | -4.5084 | -6.7368 | 0.52421 | 0.51579 | 0.50421 | 0.49368 | 0.48211 | 0.25579 | 0.018947 | -0.22632 | -0.45789 | -0.83579 | -2.4179 | -4.5211 | -6.8221 | 0.50947 | 0.49263 | 0.46737 | 0.44211 | 0.41474 | 0.24842 | 0.08 | -0.11263 | -0.38526 | -0.88632 | -3.2526 | -6.0716 | -8.0295
|  | TRESSADY | CF |  |  |  |  | 0.58526 | 0.58211 | 0.57684 | 0.57158 | 0.56526 | 0.48526 | 0.41368 | 0.25895 | 0.1 | -0.078947 | -0.91789 | -2.2074 | -3.6568 | 0.53053 | 0.52526 | 0.51789 | 0.51158 | 0.50526 | 0.44421 | 0.38842 | 0.22632 | 0.054737 | -0.15263 | -1.0116 | -2.3516 | -3.9295 | 0.53053 | 0.52632 | 0.52 | 0.51368 | 0.50737 | 0.42632 | 0.35368 | 0.18947 | 0.0073684 | -0.20421 | -1.1295 | -2.5695 | -4.2189
| SHETLAND | TUMBLIN | MINIMUM HEADROOM | HU3334053363 | YES | YES | 0 | 6.7126 | 6.6421 | 6.5642 | 6.4863 | 6.4095 | 6.2295 | 6.0505 | 5.8442 | 5.6484 | 5.4516 | 4.1284 | 2.5505 | 1.4937 | 6.2221 | 6.1463 | 6.0653 | 5.9832 | 5.9042 | 5.7432 | 5.5842 | 5.4253 | 5.2505 | 5.0747 | 3.9011 | 2.4074 | 1.2905 | 6.2642 | 6.1884 | 6.1042 | 6.0211 | 5.94 | 5.7547 | 5.5716 | 5.3674 | 5.1653 | 4.9621 | 3.5653 | 1.8737 | 0.70316
|  | TUMBLIN | EE |  |  |  |  | 6.7432 | 6.6874 | 6.62 | 6.5495 | 6.4811 | 6.2916 | 6.0695 | 5.8442 | 5.6484 | 5.4516 | 4.1284 | 2.5505 | 1.4937 | 6.2558 | 6.1947 | 6.1263 | 6.0547 | 5.9863 | 5.8211 | 5.6326 | 5.4421 | 5.2747 | 5.1074 | 3.9011 | 2.4074 | 1.2905 | 6.2979 | 6.2368 | 6.1653 | 6.0905 | 6.0189 | 5.8253 | 5.5989 | 5.3674 | 5.1653 | 4.9621 | 3.5653 | 1.8737 | 0.70316
|  | TUMBLIN | HT |  |  |  |  | 6.7126 | 6.6421 | 6.5642 | 6.4863 | 6.4095 | 6.2295 | 6.0505 | 5.8705 | 5.6695 | 5.4684 | 4.3095 | 3.0053 | 2.1474 | 6.2221 | 6.1463 | 6.0653 | 5.9832 | 5.9042 | 5.7432 | 5.5842 | 5.4253 | 5.2505 | 5.0747 | 3.9558 | 2.58 | 1.6442 | 6.2642 | 6.1884 | 6.1042 | 6.0211 | 5.94 | 5.7547 | 5.5716 | 5.3874 | 5.1811 | 4.9716 | 3.7316 | 2.2726 | 1.3
|  | TUMBLIN | HE |  |  |  |  | 6.7726 | 6.7516 | 6.7147 | 6.6758 | 6.6326 | 6.4453 | 6.2832 | 6.1221 | 5.9368 | 5.6968 | 4.6779 | 3.5179 | 2.2747 | 6.3032 | 6.2663 | 6.2263 | 6.1863 | 6.1421 | 5.9842 | 5.8474 | 5.7116 | 5.5474 | 5.3179 | 4.3642 | 3.2263 | 2.0053 | 6.2642 | 6.1884 | 6.1042 | 6.0211 | 5.94 | 5.7547 | 5.5716 | 5.3874 | 5.1811 | 4.9716 | 3.7316 | 2.2726 | 1.3
|  | TUMBLIN | CF |  |  |  |  | 6.7842 | 6.7726 | 6.7589 | 6.74 | 6.7158 | 6.6379 | 6.5663 | 6.4937 | 6.4284 | 6.3211 | 5.8 | 5.0726 | 4.3221 | 6.3168 | 6.3042 | 6.2779 | 6.2526 | 6.2274 | 6.16 | 6.0968 | 6.0347 | 5.9747 | 5.8642 | 5.3558 | 4.6368 | 3.8558 | 6.3695 | 6.3463 | 6.3189 | 6.2947 | 6.2684 | 6.1895 | 6.1158 | 6.0421 | 5.9737 | 5.8547 | 5.2947 | 4.5011 | 3.6621
| TUMMEL BRIDGE | TUMMEL BRIDGE | MINIMUM HEADROOM | NN 75906 59080 | YES | YES | 6.46 | -5.3053 | -5.3211 | -5.3789 | -5.44 | -5.4968 | -6.1347 | -6.8832 | -7.6516 | -8.3863 | -9.4221 | -15.7747 | -23.0589 | -28.3547 | -5.4358 | -5.4484 | -5.4716 | -5.5 | -5.5295 | -6.1158 | -6.7905 | -7.4884 | -8.1495 | -9.1632 | -14.9147 | -21.9421 | -27.6779 | -5.3968 | -5.4116 | -5.4621 | -5.5158 | -5.5674 | -6.2158 | -6.9789 | -7.7611 | -8.4337 | -9.4021 | -16.4989 | -24.4126 | -30.4716
|  | TUMMEL BRIDGE | EE |  |  |  |  | -5.2989 | -5.3211 | -5.3789 | -5.44 | -5.4968 | -6.1253 | -6.8737 | -7.6411 | -8.3053 | -9.2558 | -15.7747 | -23.0589 | -28.3547 | -5.4305 | -5.4421 | -5.4705 | -5.5 | -5.5295 | -6.0516 | -6.6621 | -7.2853 | -7.8221 | -8.6737 | -14.9147 | -21.9421 | -27.6779 | -5.3916 | -5.4105 | -5.4621 | -5.5158 | -5.5674 | -6.2158 | -6.9789 | -7.7611 | -8.4337 | -9.4021 | -16.4989 | -24.4126 | -30.4716
|  | TUMMEL BRIDGE | HT |  |  |  |  | -5.3053 | -5.3211 | -5.3611 | -5.4021 | -5.4516 | -5.9726 | -6.4811 | -7.0937 | -7.8695 | -9.0958 | -14.8084 | -21.2 | -25.4958 | -5.4358 | -5.4484 | -5.4716 | -5.4947 | -5.52 | -5.9495 | -6.3674 | -6.9032 | -7.58 | -8.7895 | -14.5789 | -21.4705 | -26.2779 | -5.3968 | -5.4116 | -5.4463 | -5.4842 | -5.5274 | -6.0568 | -6.5737 | -7.2074 | -8.0032 | -9.36 | -15.7305 | -22.9937 | -27.9389
|  | TUMMEL BRIDGE | HE |  |  |  |  | -5.2937 | -5.3032 | -5.3189 | -5.3368 | -5.3547 | -6.1347 | -6.8832 | -7.6516 | -8.3863 | -9.4221 | -13.9432 | -19.4663 | -25.5305 | -5.4253 | -5.4316 | -5.4411 | -5.4505 | -5.4611 | -6.1158 | -6.7905 | -7.4884 | -8.1495 | -9.1632 | -13.4747 | -19.0632 | -25.1737 | -5.3968 | -5.4116 | -5.4463 | -5.4842 | -5.5274 | -6.0568 | -6.5737 | -7.2074 | -8.0032 | -9.36 | -15.7305 | -22.9937 | -27.9389
|  | TUMMEL BRIDGE | CF |  |  |  |  | -5.2884 | -5.2937 | -5.3032 | -5.3137 | -5.3232 | -5.5558 | -5.7642 | -6.1926 | -6.6221 | -7.0947 | -9.3568 | -12.8347 | -16.6337 | -5.4211 | -5.4242 | -5.4305 | -5.4368 | -5.4421 | -5.5768 | -5.7516 | -6.1905 | -6.6347 | -7.1589 | -9.4358 | -12.9653 | -17.0242 | -5.3821 | -5.3863 | -5.3947 | -5.4032 | -5.4126 | -5.6211 | -5.84 | -6.3253 | -6.8168 | -7.3726 | -9.8779 | -13.7316 | -18.0221
| MACDUFF | TURRIFF | MINIMUM HEADROOM | NJ 72407 50271 | NO | YES | 0.06 | 4.6068 | 4.4468 | 4.0605 | 3.5437 | 2.9058 | 1.6395 | 0.24368 | -1.2932 | -2.6805 | -6.0005 | -10.3626 | -17.9405 | -23.9058 | 6.5621 | 6.2 | 5.72 | 5.1537 | 4.4453 | 3.2737 | 2.1326 | 0.80737 | -0.42421 | -3.0432 | -6.7905 | -13.8895 | -20.1158 | 5.9192 | 5.6971 | 5.4066 | 5.0866 | 4.5634 | 3.2182 | 1.7297 | 0.096053 | -1.3776 | -4.8934 | -9.4724 | -17.4608 | -23.8461
|  | TURRIFF | EE |  |  |  |  | 4.6689 | 4.5426 | 4.2942 | 3.8426 | 3.27 | 1.8542 | 0.24368 | -1.2932 | -2.6805 | -6.0005 | -10.3626 | -17.9405 | -23.9058 | 6.6611 | 6.3916 | 5.9863 | 5.5021 | 4.8747 | 3.5916 | 2.1495 | 0.80737 | -0.42421 | -3.0432 | -6.7905 | -13.8895 | -20.1158 | 6.0003 | 5.8203 | 5.5561 | 5.2624 | 4.9182 | 3.4434 | 1.7297 | 0.096053 | -1.3776 | -4.8934 | -9.4724 | -17.4608 | -23.8461
|  | TURRIFF | HT |  |  |  |  | 4.6068 | 4.4468 | 4.0605 | 3.5437 | 2.9058 | 1.6395 | 0.40158 | -0.85632 | -2.2784 | -5.5858 | -8.9805 | -15.8553 | -20.5679 | 6.5621 | 6.2 | 5.72 | 5.1537 | 4.4453 | 3.2737 | 2.1326 | 0.97263 | -0.31474 | -2.94 | -6.0537 | -13.3589 | -18.5063 | 5.9192 | 5.6971 | 5.4066 | 5.0866 | 4.5634 | 3.2182 | 1.9034 | 0.56658 | -0.94395 | -4.4471 | -8.0492 | -15.4187 | -20.6976
|  | TURRIFF | HE |  |  |  |  | 4.7563 | 4.67 | 4.5626 | 4.3026 | 3.8258 | 2.3879 | 1.0963 | -0.11947 | -1.2932 | -3.3195 | -6.3879 | -12.4184 | -19.7026 | 6.7979 | 6.6284 | 6.3526 | 5.9674 | 5.4253 | 4.1379 | 2.9568 | 1.8621 | 0.81789 | -0.79474 | -3.46 | -9.3674 | -16.3537 | 5.9192 | 5.6971 | 5.4066 | 5.0866 | 4.5634 | 3.2182 | 1.9034 | 0.56658 | -0.94395 | -4.4471 | -8.0492 | -15.4187 | -20.6976
|  | TURRIFF | CF |  |  |  |  | 4.8047 | 4.7553 | 4.6953 | 4.6311 | 4.5637 | 4.0668 | 3.5363 | 2.9553 | 2.4553 | 2.0911 | -0.29632 | -4.4626 | -8.7089 | 6.8726 | 6.7758 | 6.6663 | 6.5263 | 6.3116 | 5.8253 | 5.3358 | 4.7853 | 4.3084 | 3.9632 | 1.7842 | -2.2768 | -6.6779 | 6.1718 | 6.1003 | 6.015 | 5.9203 | 5.8108 | 5.3582 | 4.9371 | 4.4971 | 4.0708 | 3.6834 | 1.1424 | -3.3355 | -7.925
| RANNOCH | TYNDRUM | MINIMUM HEADROOM | NN 32894 30860 | YES | YES | 0 | 0.66737 | 0.66105 | 0.65158 | 0.64105 | 0.63158 | 0.57368 | 0.50737 | 0.43684 | 0.37263 | 0.29053 | -0.16842 | -0.73895 | -1.0842 | 0.87368 | 0.86737 | 0.85895 | 0.85053 | 0.84211 | 0.81158 | 0.77684 | 0.73895 | 0.70632 | 0.65474 | 0.26105 | -0.26632 | -0.62632 | 0.93474 | 0.92737 | 0.91789 | 0.90842 | 0.89789 | 0.84421 | 0.77895 | 0.71053 | 0.65368 | 0.59263 | 0.13158 | -0.48 | -0.87053
|  | TYNDRUM | EE |  |  |  |  | 0.66947 | 0.66316 | 0.65263 | 0.64316 | 0.63158 | 0.57368 | 0.50737 | 0.43684 | 0.37263 | 0.29053 | -0.16842 | -0.73895 | -1.0842 | 0.87579 | 0.87053 | 0.86211 | 0.85579 | 0.84526 | 0.81368 | 0.77684 | 0.73895 | 0.70632 | 0.65474 | 0.26105 | -0.26632 | -0.62632 | 0.93684 | 0.93053 | 0.92 | 0.91053 | 0.89789 | 0.84421 | 0.77895 | 0.71053 | 0.65368 | 0.59263 | 0.13158 | -0.48 | -0.87053
|  | TYNDRUM | HT |  |  |  |  | 0.66737 | 0.66105 | 0.65158 | 0.64105 | 0.63158 | 0.58105 | 0.53474 | 0.48737 | 0.41579 | 0.33684 | -0.031579 | -0.45684 | -0.73158 | 0.87368 | 0.86737 | 0.85895 | 0.85053 | 0.84211 | 0.81158 | 0.78526 | 0.75789 | 0.72526 | 0.67579 | 0.33474 | -0.10421 | -0.39684 | 0.93474 | 0.92737 | 0.91789 | 0.90842 | 0.89895 | 0.85158 | 0.80737 | 0.76 | 0.70316 | 0.64737 | 0.25474 | -0.21684 | -0.52211
|  | TYNDRUM | HE |  |  |  |  | 0.67474 | 0.67053 | 0.66526 | 0.66 | 0.65474 | 0.59474 | 0.54526 | 0.49684 | 0.44632 | 0.39579 | 0.04 | -0.36316 | -0.80632 | 0.88105 | 0.87684 | 0.87263 | 0.86737 | 0.86211 | 0.82947 | 0.80211 | 0.77579 | 0.74947 | 0.72316 | 0.42421 | 0.033684 | -0.38947 | 0.93474 | 0.92737 | 0.91789 | 0.90842 | 0.89895 | 0.85158 | 0.80737 | 0.76 | 0.70316 | 0.64737 | 0.25474 | -0.21684 | -0.52211
|  | TYNDRUM | CF |  |  |  |  | 0.67579 | 0.67474 | 0.67158 | 0.66842 | 0.66632 | 0.64421 | 0.62421 | 0.60421 | 0.58737 | 0.57474 | 0.45789 | 0.20737 | -0.046316 | 0.88211 | 0.88105 | 0.87895 | 0.87579 | 0.87263 | 0.86105 | 0.84947 | 0.83789 | 0.82842 | 0.82105 | 0.76842 | 0.53684 | 0.28 | 0.94316 | 0.94211 | 0.93895 | 0.93474 | 0.93263 | 0.91158 | 0.89263 | 0.87368 | 0.85789 | 0.84632 | 0.75368 | 0.49684 | 0.21789
| DUNVEGAN | UIG | MINIMUM HEADROOM | NG 39131 64412 | YES | YES | 0 | 2.8568 | 2.8 | 2.7421 | 2.6853 | 2.6295 | 2.5642 | 2.5021 | 2.4379 | 2.38 | 2.3263 | 2.0895 | 1.9021 | 1.7463 | 2.6474 | 2.5811 | 2.5147 | 2.4484 | 2.3853 | 2.3116 | 2.2432 | 2.1737 | 2.1116 | 2.0547 | 1.7968 | 1.5863 | 1.4095 | 2.7411 | 2.7021 | 2.6347 | 2.5695 | 2.5053 | 2.4316 | 2.3611 | 2.2905 | 2.2263 | 2.1684 | 1.9042 | 1.6905 | 1.5116
|  | UIG | EE |  |  |  |  | 2.8811 | 2.8389 | 2.7926 | 2.7463 | 2.7011 | 2.6516 | 2.5989 | 2.5484 | 2.5 | 2.4568 | 2.2463 | 2.0758 | 1.9484 | 2.6779 | 2.6274 | 2.5758 | 2.5221 | 2.4705 | 2.4189 | 2.3632 | 2.3063 | 2.2547 | 2.2084 | 1.9884 | 1.8053 | 1.6632 | 2.7558 | 2.7284 | 2.6958 | 2.6421 | 2.5895 | 2.5347 | 2.4768 | 2.4179 | 2.3632 | 2.3158 | 2.0832 | 1.8905 | 1.7442
|  | UIG | HT |  |  |  |  | 2.8568 | 2.8 | 2.7421 | 2.6853 | 2.6295 | 2.5642 | 2.5021 | 2.4379 | 2.38 | 2.3263 | 2.0895 | 1.9021 | 1.7463 | 2.6474 | 2.5811 | 2.5147 | 2.4484 | 2.3853 | 2.3116 | 2.2432 | 2.1737 | 2.1116 | 2.0547 | 1.7968 | 1.5863 | 1.4095 | 2.7411 | 2.7021 | 2.6347 | 2.5695 | 2.5053 | 2.4316 | 2.3611 | 2.2905 | 2.2263 | 2.1684 | 1.9042 | 1.6905 | 1.5116
|  | UIG | HE |  |  |  |  | 2.9011 | 2.8842 | 2.8642 | 2.8347 | 2.8042 | 2.7684 | 2.7358 | 2.7021 | 2.6716 | 2.6432 | 2.5326 | 2.4558 | 2.3958 | 2.7211 | 2.6905 | 2.6589 | 2.6253 | 2.5916 | 2.5547 | 2.5189 | 2.4853 | 2.4516 | 2.4221 | 2.3074 | 2.2263 | 2.1621 | 2.7411 | 2.7021 | 2.6347 | 2.5695 | 2.5053 | 2.4316 | 2.3611 | 2.2905 | 2.2263 | 2.1684 | 1.9042 | 1.6905 | 1.5116
|  | UIG | CF |  |  |  |  | 2.9116 | 2.9032 | 2.8937 | 2.8832 | 2.8726 | 2.8537 | 2.8358 | 2.8179 | 2.7989 | 2.7821 | 2.7032 | 2.6432 | 2.6021 | 2.7421 | 2.7242 | 2.7063 | 2.6863 | 2.6684 | 2.6474 | 2.6263 | 2.6074 | 2.5863 | 2.5674 | 2.4768 | 2.4116 | 2.3632 | 2.7863 | 2.7779 | 2.7684 | 2.7568 | 2.7474 | 2.7358 | 2.7242 | 2.7116 | 2.7011 | 2.6853 | 2.5937 | 2.5242 | 2.4737
| GRUDIE BRIDGE | ULLAPOOL | MINIMUM HEADROOM | NH 13018 94588 | NO | NO | 0 | 0.88526 | 0.82737 | 0.76947 | 0.71263 | 3.6568 | 3.5947 | 3.5337 | 3.4758 | 3.4242 | 3.3747 | 3.1516 | 2.9684 | 2.8084 | 0.87579 | 0.81263 | 0.75053 | 0.68947 | 3.6295 | 3.5621 | 3.4979 | 3.4347 | 3.38 | 3.3274 | 3.0821 | 2.8789 | 2.7 | 0.87579 | 0.81263 | 0.75158 | 0.69053 | 3.6305 | 3.5632 | 3.4989 | 3.4358 | 3.3811 | 3.3284 | 3.0832 | 2.8811 | 2.7021
|  | ULLAPOOL | EE |  |  |  |  | 0.91158 | 0.86526 | 0.82 | 0.77474 | 3.7274 | 3.6821 | 3.6389 | 3.5916 | 3.5463 | 3.5084 | 3.3274 | 3.1863 | 3.0632 | 0.90421 | 0.85474 | 0.80632 | 0.75684 | 3.7074 | 3.6589 | 3.6126 | 3.5621 | 3.5126 | 3.4716 | 3.2768 | 3.1189 | 2.9811 | 0.90421 | 0.85474 | 0.80632 | 0.75684 | 3.7074 | 3.6589 | 3.6137 | 3.5621 | 3.5137 | 3.4726 | 3.2779 | 3.12 | 2.9832
|  | ULLAPOOL | HT |  |  |  |  | 0.88526 | 0.82737 | 0.76947 | 0.71263 | 3.6568 | 3.5947 | 3.5337 | 3.4758 | 3.4242 | 3.3747 | 3.1516 | 2.9684 | 2.8084 | 0.87579 | 0.81263 | 0.75053 | 0.68947 | 3.6295 | 3.5621 | 3.4979 | 3.4347 | 3.38 | 3.3274 | 3.0821 | 2.8789 | 2.7 | 0.87579 | 0.81263 | 0.75158 | 0.69053 | 3.6305 | 3.5632 | 3.4989 | 3.4358 | 3.3811 | 3.3284 | 3.0832 | 2.8811 | 2.7021
|  | ULLAPOOL | HE |  |  |  |  | 0.94737 | 0.91895 | 0.89053 | 0.86 | 3.8284 | 3.7968 | 3.7663 | 3.7379 | 3.7105 | 3.6863 | 3.5916 | 3.5316 | 3.4874 | 0.94316 | 0.91263 | 0.88316 | 0.85053 | 3.8168 | 3.7842 | 3.7516 | 3.7221 | 3.6926 | 3.6663 | 3.5663 | 3.5011 | 3.4516 | 0.87579 | 0.81263 | 0.75158 | 0.69053 | 3.6305 | 3.5632 | 3.4989 | 3.4358 | 3.3811 | 3.3284 | 3.0832 | 2.8811 | 2.7021
|  | ULLAPOOL | CF |  |  |  |  | 0.96526 | 0.94737 | 0.93053 | 0.91158 | 3.8947 | 3.8758 | 3.8568 | 3.8379 | 3.82 | 3.8011 | 3.72 | 3.6653 | 3.6263 | 0.96316 | 0.94316 | 0.92421 | 0.90526 | 3.8863 | 3.8663 | 3.8453 | 3.8263 | 3.8063 | 3.7863 | 3.6989 | 3.6389 | 3.5937 | 0.96316 | 0.94316 | 0.92421 | 0.90526 | 3.8863 | 3.8663 | 3.8463 | 3.8263 | 3.8063 | 3.7874 | 3.7 | 3.6389 | 3.5947
| SHETLAND | UNST | MINIMUM HEADROOM | HP6398113411 | YES | YES | 0 | 1.5126 | 1.48 | 1.4453 | 1.4126 | 1.38 | 1.3453 | 1.3116 | 1.28 | 1.2484 | 1.2189 | 1.0947 | 0.98316 | 0.88737 | 1.2684 | 1.2263 | 1.1842 | 1.1432 | 1.1011 | 1.0579 | 1.0158 | 0.97684 | 0.93684 | 0.9 | 0.75263 | 0.62842 | 0.52316 | 1.1737 | 1.1305 | 1.0863 | 1.0432 | 1.0011 | 0.95789 | 0.91579 | 0.87684 | 0.83684 | 0.80105 | 0.65368 | 0.53158 | 0.42632
|  | UNST | EE |  |  |  |  | 1.5263 | 1.5 | 1.4737 | 1.4463 | 1.4179 | 1.3895 | 1.3632 | 1.3379 | 1.3137 | 1.2905 | 1.1937 | 1.1189 | 1.0505 | 1.2863 | 1.2537 | 1.2211 | 1.1874 | 1.1537 | 1.12 | 1.0863 | 1.0547 | 1.0253 | 0.99579 | 0.86947 | 0.77789 | 0.70211 | 1.1937 | 1.1589 | 1.1253 | 1.0895 | 1.0547 | 1.02 | 0.98632 | 0.95474 | 0.92526 | 0.89579 | 0.77053 | 0.68 | 0.60421
|  | UNST | HT |  |  |  |  | 1.5126 | 1.48 | 1.4453 | 1.4126 | 1.38 | 1.3453 | 1.3116 | 1.28 | 1.2484 | 1.2189 | 1.0947 | 0.98316 | 0.88737 | 1.2684 | 1.2263 | 1.1842 | 1.1432 | 1.1011 | 1.0579 | 1.0158 | 0.97684 | 0.93684 | 0.9 | 0.75263 | 0.62842 | 0.52316 | 1.1737 | 1.1305 | 1.0863 | 1.0432 | 1.0011 | 0.95789 | 0.91579 | 0.87684 | 0.83684 | 0.80105 | 0.65368 | 0.53158 | 0.42632
|  | UNST | HE |  |  |  |  | 1.5474 | 1.5305 | 1.5126 | 1.4947 | 1.4747 | 1.4547 | 1.4368 | 1.4179 | 1.4011 | 1.3853 | 1.3305 | 1.2958 | 1.2737 | 1.3116 | 1.2926 | 1.2705 | 1.2505 | 1.2274 | 1.2042 | 1.1832 | 1.1621 | 1.1432 | 1.1242 | 1.0568 | 1.0095 | 0.97474 | 1.1737 | 1.1305 | 1.0863 | 1.0432 | 1.0011 | 0.95789 | 0.91579 | 0.87684 | 0.83684 | 0.80105 | 0.65368 | 0.53158 | 0.42632
|  | UNST | CF |  |  |  |  | 1.5579 | 1.5474 | 1.5379 | 1.5274 | 1.5158 | 1.5053 | 1.4947 | 1.4842 | 1.4726 | 1.4621 | 1.4147 | 1.3853 | 1.3653 | 1.3253 | 1.3126 | 1.3011 | 1.2884 | 1.2737 | 1.2611 | 1.2484 | 1.2347 | 1.2211 | 1.2084 | 1.1505 | 1.1084 | 1.0768 | 1.2253 | 1.2179 | 1.2095 | 1.1958 | 1.1811 | 1.1674 | 1.1537 | 1.14 | 1.1253 | 1.1116 | 1.0505 | 1.0074 | 0.97684
| SHETLAND | VOE | MINIMUM HEADROOM | HU4117663079 | YES | YES | 0 | 9.5179 | 9.4168 | 9.3042 | 9.1926 | 9.0589 | 8.7484 | 8.4263 | 8.0326 | 7.6874 | 7.3284 | 4.8737 | 1.9632 | 0.055789 | 8.4316 | 8.3768 | 8.2874 | 8.1737 | 8.0379 | 7.7811 | 7.5253 | 7.2232 | 6.9158 | 6.5926 | 4.3516 | 1.6189 | -0.40105 | 8.2958 | 8.1916 | 8.0726 | 7.9568 | 7.8168 | 7.4905 | 7.1495 | 6.7347 | 6.3705 | 5.9989 | 3.4274 | 0.35789 | -1.7137
|  | VOE | EE |  |  |  |  | 9.56 | 9.48 | 9.3789 | 9.2779 | 9.1632 | 8.8242 | 8.4263 | 8.0326 | 7.6874 | 7.3284 | 4.8737 | 1.9632 | 0.055789 | 8.4505 | 8.4053 | 8.3495 | 8.2716 | 8.1568 | 7.8874 | 7.5611 | 7.2232 | 6.9158 | 6.6032 | 4.3516 | 1.6189 | -0.40105 | 8.3411 | 8.2579 | 8.1516 | 8.0463 | 7.9263 | 7.5695 | 7.1495 | 6.7347 | 6.3705 | 5.9989 | 3.4274 | 0.35789 | -1.7137
|  | VOE | HT |  |  |  |  | 9.5179 | 9.4168 | 9.3042 | 9.1926 | 9.0589 | 8.7484 | 8.4379 | 8.1263 | 7.7684 | 7.3895 | 5.2895 | 2.9358 | 1.38 | 8.4316 | 8.3768 | 8.2874 | 8.1737 | 8.0379 | 7.7811 | 7.5253 | 7.2474 | 6.9316 | 6.5926 | 4.54 | 2.0389 | 0.34 | 8.2958 | 8.1916 | 8.0726 | 7.9568 | 7.8168 | 7.4905 | 7.1642 | 6.8358 | 6.4579 | 6.0579 | 3.8168 | 1.2768 | -0.39368
|  | VOE | HE |  |  |  |  | 9.6232 | 9.5747 | 9.5189 | 9.4621 | 9.3842 | 9.0411 | 8.74 | 8.4516 | 8.1337 | 7.7011 | 5.8484 | 3.7211 | 1.4316 | 8.4811 | 8.4516 | 8.4179 | 8.38 | 8.34 | 8.1084 | 7.8705 | 7.6221 | 7.3337 | 6.9189 | 5.1811 | 3.0926 | 0.83684 | 8.2958 | 8.1916 | 8.0726 | 7.9568 | 7.8168 | 7.4905 | 7.1642 | 6.8358 | 6.4579 | 6.0579 | 3.8168 | 1.2768 | -0.39368
|  | VOE | CF |  |  |  |  | 9.6558 | 9.6263 | 9.5905 | 9.5547 | 9.5189 | 9.3832 | 9.2568 | 9.1305 | 8.9916 | 8.8 | 7.8737 | 6.5495 | 5.1832 | 8.4989 | 8.4821 | 8.4632 | 8.4432 | 8.4232 | 8.3589 | 8.3011 | 8.2021 | 8.08 | 7.8895 | 6.9811 | 5.6579 | 4.2232 | 8.4411 | 8.4095 | 8.3726 | 8.3358 | 8.2979 | 8.1558 | 8.0221 | 7.8884 | 7.7411 | 7.5358 | 6.5453 | 5.1211 | 3.6432
| DUDHOPE | WALTON | MINIMUM HEADROOM | NO 38995 30333 | NO | YES | 0.088 | 24.6688 | 24.5636 | 24.452 | 24.3246 | 24.1541 | 23.8688 | 23.6467 | 23.4225 | 23.2057 | 22.9888 | 22.4067 | 21.5667 | 20.8109 | 22.9594 | 22.8573 | 22.7499 | 22.4383 | 22.1183 | 21.7909 | 21.5752 | 21.3636 | 21.1573 | 20.9541 | 20.6194 | 19.772 | 19.0373 | 23.6604 | 23.5478 | 23.4141 | 23.2236 | 22.9425 | 22.5994 | 22.3688 | 22.1415 | 21.9194 | 21.6815 | 21.2246 | 20.2678 | 19.4025
|  | WALTON | EE |  |  |  |  | 24.7183 | 24.6004 | 24.4773 | 24.3341 | 24.1836 | 23.8741 | 23.6467 | 23.4225 | 23.2057 | 22.9888 | 22.4067 | 21.5667 | 20.8109 | 23.0109 | 22.9194 | 22.8194 | 22.6309 | 22.3352 | 22.0257 | 21.8204 | 21.6204 | 21.3994 | 21.1773 | 20.7973 | 19.9425 | 19.1657 | 23.7099 | 23.5667 | 23.4141 | 23.2404 | 22.9446 | 22.6404 | 22.4036 | 22.1562 | 21.9194 | 21.6815 | 21.2246 | 20.2678 | 19.4025
|  | WALTON | HT |  |  |  |  | 24.6688 | 24.5636 | 24.452 | 24.3246 | 24.1541 | 23.8688 | 23.6636 | 23.4625 | 23.2583 | 23.0552 | 22.5667 | 21.7299 | 20.9973 | 22.9594 | 22.8573 | 22.7499 | 22.4383 | 22.1183 | 21.7909 | 21.5752 | 21.3636 | 21.1573 | 20.9541 | 20.6194 | 19.772 | 19.0373 | 23.6604 | 23.5478 | 23.4278 | 23.2236 | 22.9425 | 22.5994 | 22.3688 | 22.1415 | 21.9204 | 21.7025 | 21.3709 | 20.4394 | 19.6215
|  | WALTON | HE |  |  |  |  | 24.7404 | 24.6699 | 24.5941 | 24.5131 | 24.4183 | 24.3141 | 24.2204 | 24.1299 | 24.0099 | 23.9162 | 23.1025 | 22.6552 | 22.2867 | 23.0341 | 22.9699 | 22.8994 | 22.8204 | 22.6867 | 22.4415 | 22.3025 | 22.1731 | 22.052 | 21.9699 | 21.0678 | 20.6288 | 20.2783 | 23.6604 | 23.5478 | 23.4278 | 23.2236 | 22.9425 | 22.5994 | 22.3688 | 22.1415 | 21.9204 | 21.7025 | 21.3709 | 20.4394 | 19.6215
|  | WALTON | CF |  |  |  |  | 24.752 | 24.7067 | 24.6604 | 24.6131 | 24.5657 | 24.5141 | 24.4625 | 24.4131 | 24.3625 | 24.312 | 24.0741 | 23.9046 | 23.7099 | 23.0457 | 23.0025 | 22.9573 | 22.9109 | 22.8636 | 22.8152 | 22.7657 | 22.7162 | 22.6667 | 22.6162 | 22.1973 | 21.8794 | 21.6531 | 23.7436 | 23.6962 | 23.6478 | 23.5983 | 23.5499 | 23.4962 | 23.4436 | 23.392 | 23.3394 | 23.2878 | 22.9762 | 22.6983 | 22.4604
| INVERNESS | WATERLOO PLACE | MINIMUM HEADROOM | NH 66301 45800 | NO | YES | 0 | 22.4782 | 39.3661 | 39.315 | 39.2511 | 39.1836 | 38.9396 | 38.7268 | 38.4436 | 38.2482 | 38.0537 | 37.9778 | 37.8146 | 37.6589 | 22.7745 | 38.364 | 38.3149 | 38.2494 | 38.176 | 37.8997 | 37.6596 | 37.3819 | 37.1909 | 36.999 | 36.9196 | 36.813 | 36.6413 | 22.7754 | 39.3738 | 39.3326 | 39.2835 | 39.1873 | 38.7071 | 38.289 | 37.8758 | 37.6517 | 37.429 | 37.3476 | 37.2777 | 37.1041
|  | WATERLOO PLACE | EE |  |  |  |  | 22.4911 | 39.3875 | 39.3458 | 39.3002 | 39.2535 | 39.1474 | 39.0978 | 38.9058 | 38.7164 | 38.4535 | 37.9778 | 38.0016 | 37.893 | 22.784 | 38.3818 | 38.3411 | 38.2975 | 38.2504 | 38.1323 | 38.0817 | 37.8645 | 37.6502 | 37.3908 | 36.9196 | 37.0208 | 36.9013 | 22.7834 | 39.3891 | 39.3554 | 39.3182 | 39.281 | 39.1149 | 39.0434 | 38.665 | 38.2865 | 37.8882 | 37.3476 | 37.4855 | 37.3645
|  | WATERLOO PLACE | HT |  |  |  |  | 22.4782 | 39.3661 | 39.315 | 39.2511 | 39.1836 | 38.9396 | 38.7268 | 38.4436 | 38.2482 | 38.0537 | 37.9932 | 37.8146 | 37.6589 | 22.7745 | 38.364 | 38.3149 | 38.2494 | 38.176 | 37.8997 | 37.6596 | 37.3819 | 37.1909 | 36.999 | 37.0079 | 36.813 | 36.6413 | 22.7754 | 39.3738 | 39.3326 | 39.2835 | 39.1873 | 38.7071 | 38.289 | 37.8758 | 37.6517 | 37.429 | 37.4751 | 37.2777 | 37.1041
|  | WATERLOO PLACE | HE |  |  |  |  | 22.5035 | 39.4192 | 39.389 | 39.3562 | 39.3205 | 39.2243 | 39.1861 | 39.0849 | 38.9847 | 38.8875 | 38.6023 | 38.4917 | 38.021 | 22.7969 | 38.4071 | 38.3783 | 38.3466 | 38.3119 | 38.2097 | 38.17 | 38.0574 | 37.9453 | 37.8357 | 37.5213 | 37.5589 | 36.8973 | 22.7754 | 39.3738 | 39.3326 | 39.2835 | 39.1873 | 38.7071 | 38.289 | 37.8758 | 37.6517 | 37.429 | 37.4751 | 37.2777 | 37.1041
|  | WATERLOO PLACE | CF |  |  |  |  | 22.5095 | 39.44 | 39.4296 | 39.4118 | 39.3934 | 39.3518 | 39.3299 | 39.316 | 39.2615 | 39.2039 | 38.9807 | 38.8667 | 38.767 | 22.8093 | 38.4329 | 38.4155 | 38.3982 | 38.3803 | 38.3416 | 38.3213 | 38.3079 | 38.2474 | 38.1829 | 37.9329 | 37.8074 | 37.6958 | 22.8022 | 39.4303 | 39.4179 | 39.405 | 39.3906 | 39.3638 | 39.3475 | 39.3346 | 39.277 | 39.1664 | 38.7434 | 38.5271 | 38.3292
| LYNDHURST | WEST KIRKTON | MINIMUM HEADROOM | NO 39194 33796 | NO | YES | 0.336 | 17.0108 | 16.6003 | 16.1372 | 15.6803 | 15.2624 | 14.8835 | 14.5614 | 14.2529 | 13.9656 | 13.6856 | 12.2814 | 11.2824 | 10.5193 | 22.2714 | 21.9545 | 21.6008 | 21.2503 | 20.9251 | 20.6251 | 20.3619 | 20.1103 | 19.8766 | 19.6493 | 18.3366 | 17.2619 | 16.4293 | 16.5053 | 16.0579 | 15.5432 | 15.0379 | 14.5779 | 14.1727 | 13.8295 | 13.5032 | 13.2011 | 12.9085 | 11.3948 | 10.3232 | 9.4895
|  | WEST KIRKTON | EE |  |  |  |  | 17.1256 | 16.8035 | 16.4319 | 16.0087 | 15.6393 | 15.2466 | 14.9119 | 14.6361 | 14.3824 | 14.1551 | 12.9866 | 12.0751 | 11.4898 | 22.3682 | 22.1166 | 21.8335 | 21.5135 | 21.2293 | 20.9324 | 20.6766 | 20.4587 | 20.2577 | 20.0766 | 19.1429 | 18.2019 | 17.5735 | 16.5801 | 16.279 | 15.8685 | 15.3969 | 14.9906 | 14.5632 | 14.2053 | 13.9137 | 13.6453 | 13.4085 | 12.1685 | 11.2011 | 10.5727
|  | WEST KIRKTON | HT |  |  |  |  | 17.0108 | 16.6003 | 16.1372 | 15.6803 | 15.2624 | 14.8835 | 14.5614 | 14.2529 | 13.9656 | 13.6856 | 12.2814 | 11.2824 | 10.5193 | 22.2714 | 21.9545 | 21.6008 | 21.2503 | 20.9251 | 20.6251 | 20.3619 | 20.1103 | 19.8766 | 19.6493 | 18.3366 | 17.2619 | 16.4293 | 16.5053 | 16.0579 | 15.5432 | 15.0379 | 14.5779 | 14.1727 | 13.8295 | 13.5032 | 13.2011 | 12.9085 | 11.3948 | 10.3232 | 9.4895
|  | WEST KIRKTON | HE |  |  |  |  | 17.2803 | 17.0361 | 16.7193 | 16.3508 | 16.0435 | 15.7098 | 15.4929 | 15.3151 | 15.1372 | 14.9624 | 14.1414 | 13.5887 | 13.1845 | 22.4987 | 22.3072 | 22.0714 | 21.7998 | 21.5651 | 21.3166 | 21.1472 | 21.0029 | 20.8598 | 20.7208 | 20.1145 | 19.7261 | 19.3914 | 16.5053 | 16.0579 | 15.5432 | 15.0379 | 14.5779 | 14.1727 | 13.8295 | 13.5032 | 13.2011 | 12.9085 | 11.3948 | 10.3232 | 9.4895
|  | WEST KIRKTON | CF |  |  |  |  | 17.3329 | 17.2782 | 17.1614 | 17.0024 | 16.8519 | 16.7182 | 16.5635 | 16.4087 | 16.2866 | 16.1624 | 15.5519 | 15.1445 | 14.8656 | 22.6029 | 22.5082 | 22.3998 | 22.2777 | 22.1619 | 22.0587 | 21.9408 | 21.824 | 21.7282 | 21.6303 | 21.164 | 20.8714 | 20.6798 | 16.7516 | 16.6832 | 16.6074 | 16.4958 | 16.3295 | 16.1853 | 16.0169 | 15.8485 | 15.7169 | 15.5822 | 14.9232 | 14.4853 | 14.1811
| KILLIN | WESTER DRUMMOND | MINIMUM HEADROOM | NN 72155 44784 | YES | YES | 0 | 0.093684 | 0.092632 | 0.090526 | 0.088421 | 0.086316 | 0.066316 | 0.043158 | 0.017895 | -0.0021053 | -0.027368 | -0.19263 | -0.37368 | -0.48316 | 0.094737 | 0.092632 | 0.091579 | 0.089474 | 0.087368 | 0.072632 | 0.053684 | 0.032632 | 0.016842 | -0.0063158 | -0.15684 | -0.32316 | -0.43368 | 0.093684 | 0.091579 | 0.089474 | 0.087368 | 0.085263 | 0.066316 | 0.043158 | 0.016842 | -0.0031579 | -0.028421 | -0.20526 | -0.39684 | -0.52
|  | WESTER DRUMMOND | EE |  |  |  |  | 0.093684 | 0.093684 | 0.090526 | 0.089474 | 0.086316 | 0.066316 | 0.043158 | 0.017895 | -0.0021053 | -0.027368 | -0.19263 | -0.37368 | -0.48316 | 0.094737 | 0.094737 | 0.091579 | 0.090526 | 0.087368 | 0.072632 | 0.053684 | 0.032632 | 0.016842 | -0.0052632 | -0.15684 | -0.32316 | -0.43368 | 0.093684 | 0.093684 | 0.089474 | 0.088421 | 0.085263 | 0.066316 | 0.043158 | 0.016842 | -0.0031579 | -0.028421 | -0.20526 | -0.39684 | -0.52
|  | WESTER DRUMMOND | HT |  |  |  |  | 0.093684 | 0.092632 | 0.091579 | 0.088421 | 0.087368 | 0.070526 | 0.054737 | 0.037895 | 0.014737 | -0.016842 | -0.14947 | -0.28211 | -0.36632 | 0.094737 | 0.092632 | 0.091579 | 0.089474 | 0.088421 | 0.074737 | 0.062105 | 0.047368 | 0.028421 | -1.3878e-17 | -0.12842 | -0.26526 | -0.35684 | 0.093684 | 0.091579 | 0.090526 | 0.087368 | 0.086316 | 0.069474 | 0.054737 | 0.036842 | 0.012632 | -0.017895 | -0.16526 | -0.31158 | -0.40737
|  | WESTER DRUMMOND | HE |  |  |  |  | 0.094737 | 0.093684 | 0.093684 | 0.092632 | 0.091579 | 0.068421 | 0.048421 | 0.026316 | 0.0052632 | -0.021053 | -0.13474 | -0.26632 | -0.40632 | 0.095789 | 0.094737 | 0.094737 | 0.093684 | 0.092632 | 0.073684 | 0.056842 | 0.036842 | 0.018947 | -0.0063158 | -0.11053 | -0.23368 | -0.36737 | 0.093684 | 0.091579 | 0.090526 | 0.087368 | 0.086316 | 0.069474 | 0.054737 | 0.036842 | 0.012632 | -0.017895 | -0.16526 | -0.31158 | -0.40737
|  | WESTER DRUMMOND | CF |  |  |  |  | 0.095789 | 0.095789 | 0.093684 | 0.092632 | 0.092632 | 0.085263 | 0.077895 | 0.068421 | 0.058947 | 0.047368 | -0.0052632 | -0.087368 | -0.16842 | 0.096842 | 0.096842 | 0.094737 | 0.093684 | 0.093684 | 0.088421 | 0.082105 | 0.072632 | 0.063158 | 0.051579 | 0.0021053 | -0.077895 | -0.15895 | 0.094737 | 0.094737 | 0.093684 | 0.092632 | 0.092632 | 0.085263 | 0.077895 | 0.067368 | 0.056842 | 0.044211 | -0.012632 | -0.10211 | -0.19053
| THURSO | WESTRAY | MINIMUM HEADROOM | HY 50213 39413 | YES | YES | 0.05 | 1.4647 | 1.4511 | 1.4374 | 1.4237 | 1.4089 | 1.3932 | 1.3784 | 1.3647 | 1.3511 | 1.3374 | -0.31526 | -0.39842 | -0.47316 | 1.2784 | 1.2647 | 1.2511 | 1.2321 | 1.2058 | 1.1805 | 1.1563 | 1.1342 | 1.1111 | 1.0837 | -0.33737 | -0.43211 | -0.51632 | 1.4226 | 1.4079 | 1.3826 | 1.3563 | 1.3311 | 1.3058 | 1.2826 | 1.2616 | 1.2384 | 1.2132 | -0.54474 | -0.63316 | -0.71316
|  | WESTRAY | EE |  |  |  |  | 1.4689 | 1.4584 | 1.4468 | 1.4353 | 1.4226 | 1.41 | 1.3984 | 1.3868 | 1.3763 | 1.3658 | -0.24158 | -0.30368 | -0.36158 | 1.2826 | 1.2721 | 1.2605 | 1.2489 | 1.2363 | 1.2174 | 1.1921 | 1.1742 | 1.1563 | 1.1395 | -0.25526 | -0.32579 | -0.39211 | 1.4268 | 1.4163 | 1.4037 | 1.3805 | 1.3616 | 1.3416 | 1.3174 | 1.2995 | 1.2826 | 1.2658 | -0.46684 | -0.53316 | -0.59526
|  | WESTRAY | HT |  |  |  |  | 1.4647 | 1.4511 | 1.4374 | 1.4237 | 1.4089 | 1.3932 | 1.3784 | 1.3647 | 1.3511 | 1.3374 | -0.31526 | -0.39842 | -0.47316 | 1.2784 | 1.2647 | 1.2511 | 1.2321 | 1.2058 | 1.1805 | 1.1563 | 1.1342 | 1.1111 | 1.0837 | -0.33737 | -0.43211 | -0.51632 | 1.4226 | 1.4079 | 1.3826 | 1.3563 | 1.3311 | 1.3058 | 1.2826 | 1.2616 | 1.2384 | 1.2132 | -0.54474 | -0.63316 | -0.71316
|  | WESTRAY | HE |  |  |  |  | 1.4774 | 1.47 | 1.4616 | 1.4532 | 1.4437 | 1.4342 | 1.4258 | 1.4174 | 1.4089 | 1.4016 | 0.65 | 0.63842 | 0.61947 | 1.2911 | 1.2837 | 1.2753 | 1.2668 | 1.2574 | 1.2479 | 1.2395 | 1.2311 | 1.2226 | 1.2153 | 0.52053 | 0.48263 | 0.43632 | 1.4226 | 1.4079 | 1.3826 | 1.3563 | 1.3311 | 1.3058 | 1.2826 | 1.2616 | 1.2384 | 1.2132 | -0.54474 | -0.63316 | -0.71316
|  | WESTRAY | CF |  |  |  |  | 1.4816 | 1.4774 | 1.4732 | 1.4689 | 1.4637 | 1.4595 | 1.4553 | 1.45 | 1.4458 | 1.4405 | 1.4216 | 1.4111 | 1.4068 | 1.2953 | 1.2911 | 1.2868 | 1.2826 | 1.2774 | 1.2732 | 1.2689 | 1.2637 | 1.2595 | 1.2542 | 1.2342 | 1.2026 | 1.1679 | 1.4395 | 1.4353 | 1.4311 | 1.4268 | 1.4216 | 1.4174 | 1.4132 | 1.4079 | 1.3995 | 1.3911 | 1.3574 | 1.3279 | 1.2953
| TARLAND | WHITEHOUSE | MINIMUM HEADROOM | NJ 61658 15058 | NO | YES | 2.4 | 3.0589 | 2.9547 | 2.8347 | 2.7147 | 2.5937 | 2.2779 | 1.9453 | 1.5611 | 1.1337 | 0.70947 | -1.2947 | -4.1832 | -6.0895 | 3.5221 | 3.3558 | 3.1726 | 3.0063 | 2.8411 | 2.5168 | 2.2021 | 1.8884 | 1.5421 | 1.1705 | -0.53053 | -3.2684 | -5.2558 | 3.5821 | 3.4779 | 3.3579 | 3.2379 | 3.0853 | 2.7326 | 2.3421 | 1.9516 | 1.5189 | 1.0895 | -0.94632 | -4.0674 | -6.1863
|  | WHITEHOUSE | EE |  |  |  |  | 3.1021 | 3.02 | 2.9158 | 2.8084 | 2.6979 | 2.3611 | 1.98 | 1.5947 | 1.2379 | 0.83684 | -1.2947 | -4.1832 | -6.0895 | 3.5768 | 3.4579 | 3.3042 | 3.1611 | 3.0179 | 2.6884 | 2.3221 | 1.9579 | 1.6347 | 1.3095 | -0.53053 | -3.2684 | -5.2558 | 3.6253 | 3.5432 | 3.4379 | 3.3305 | 3.2189 | 2.8789 | 2.4937 | 2.0526 | 1.6505 | 1.2463 | -0.94632 | -4.0674 | -6.1863
|  | WHITEHOUSE | HT |  |  |  |  | 3.0589 | 2.9547 | 2.8347 | 2.7147 | 2.5937 | 2.2779 | 1.9453 | 1.5611 | 1.1337 | 0.70947 | -1.0674 | -3.4453 | -5.0042 | 3.5221 | 3.3558 | 3.1726 | 3.0063 | 2.8411 | 2.5168 | 2.2021 | 1.8884 | 1.5421 | 1.1705 | -0.48947 | -2.9789 | -4.6695 | 3.5821 | 3.4779 | 3.3579 | 3.2379 | 3.0853 | 2.7326 | 2.3421 | 1.9516 | 1.5189 | 1.0895 | -0.73579 | -3.3674 | -5.1411
|  | WHITEHOUSE | HE |  |  |  |  | 3.1611 | 3.1084 | 3.0474 | 2.9811 | 2.9116 | 2.5789 | 2.2968 | 2.0158 | 1.74 | 1.4705 | -0.16105 | -2.2579 | -4.4895 | 3.6463 | 3.5832 | 3.4979 | 3.4095 | 3.3189 | 3.0074 | 2.7411 | 2.4789 | 2.2232 | 1.9726 | 0.47895 | -1.5842 | -3.7842 | 3.5821 | 3.4779 | 3.3579 | 3.2379 | 3.0853 | 2.7326 | 2.3421 | 1.9516 | 1.5189 | 1.0895 | -0.73579 | -3.3674 | -5.1411
|  | WHITEHOUSE | CF |  |  |  |  | 3.1926 | 3.1642 | 3.1316 | 3.0968 | 3.0621 | 2.9326 | 2.8147 | 2.6968 | 2.5937 | 2.5095 | 1.9695 | 0.65895 | -0.67789 | 3.68 | 3.6495 | 3.6095 | 3.5705 | 3.5305 | 3.4032 | 3.2842 | 3.1663 | 3.0589 | 2.9695 | 2.2958 | 1.1074 | -0.27895 | 3.7158 | 3.6874 | 3.6547 | 3.6189 | 3.5853 | 3.4547 | 3.3347 | 3.2168 | 3.1116 | 3.0274 | 2.3874 | 0.98632 | -0.46421
| PERSLEY | WHITESTRIPES | MINIMUM HEADROOM | NJ 92850 11054 | NO | NO | 0 | 9.7616 | 9.3984 | 8.7332 | 8.0016 | 7.2037 | 8.8426 | 8.4311 | 7.9984 | 7.5468 | 7.0774 | 4.6353 | 2.2984 | 0.085789 | 9.6421 | 9.3042 | 8.5684 | 7.7547 | 6.8642 | 8.6937 | 8.2432 | 7.7674 | 7.2684 | 6.7474 | 4.0368 | 1.4484 | -1.0537 | 9.9697 | 9.5887 | 8.8582 | 8.0487 | 7.1624 | 8.975 | 8.5224 | 8.0434 | 7.5424 | 7.0213 | 4.2834 | 1.6455 | -0.96395
|  | WHITESTRIPES | EE |  |  |  |  | 9.8311 | 9.6132 | 9.0205 | 8.3489 | 7.61 | 16.8437 | 15.9689 | 15.1037 | 14.2595 | 13.4226 | 9.3511 | 5.5311 | 2.0121 | 9.7126 | 9.5032 | 8.88 | 8.1316 | 7.3053 | 16.4589 | 15.5074 | 14.5653 | 13.64 | 12.7263 | 8.2758 | 4.0821 | 0.097895 | 10.0403 | 9.8203 | 9.1666 | 8.4224 | 7.6003 | 16.7424 | 15.7739 | 14.8076 | 13.8613 | 12.9234 | 8.3508 | 4.0571 | 0.045526
|  | WHITESTRIPES | HT |  |  |  |  | 9.7616 | 9.3984 | 8.7332 | 8.0016 | 7.2037 | 16.3826 | 15.4668 | 14.5616 | 13.6563 | 12.7542 | 8.6711 | 4.8279 | 1.1216 | 9.6421 | 9.3042 | 8.5684 | 7.7547 | 6.8642 | 15.9558 | 14.9505 | 13.9579 | 12.9674 | 11.9821 | 7.4863 | 3.1621 | -1.0537 | 9.9697 | 9.5887 | 8.8582 | 8.0487 | 7.1624 | 16.2466 | 15.2287 | 14.2192 | 13.2076 | 12.2003 | 7.6192 | 3.2592 | -0.96395
|  | WHITESTRIPES | HE |  |  |  |  | 9.9584 | 9.8384 | 9.4868 | 8.9395 | 8.3142 | 17.6479 | 16.8984 | 16.1553 | 15.4216 | 14.6984 | 11.29 | 8.0658 | 4.9837 | 9.84 | 9.72 | 9.3758 | 8.76 | 8.0526 | 17.3116 | 16.4853 | 15.6653 | 14.8547 | 14.0558 | 10.2674 | 6.6274 | 3.1495 | 9.9697 | 9.5887 | 8.8582 | 8.0487 | 7.1624 | 16.2466 | 15.2287 | 14.2192 | 13.2076 | 12.2003 | 7.6192 | 3.2592 | -0.96395
|  | WHITESTRIPES | CF |  |  |  |  | 9.9721 | 9.8553 | 9.7342 | 9.5742 | 9.2321 | 8.8426 | 8.4311 | 7.9984 | 7.5468 | 7.0774 | 4.6353 | 2.2984 | 0.085789 | 9.8537 | 9.7368 | 9.6158 | 9.4726 | 9.1168 | 8.6937 | 8.2432 | 7.7674 | 7.2684 | 6.7474 | 4.0368 | 1.4484 | -1.0232 | 10.1813 | 10.0645 | 9.9434 | 9.7771 | 9.4013 | 8.975 | 8.5224 | 8.0434 | 7.5424 | 7.0213 | 4.2834 | 1.6455 | -0.865
| CARRADALE 1 | WHITING BAY | MINIMUM HEADROOM | NS 04169 26277 | YES | YES | 0.05 | 6.8732 | 6.8258 | 6.7774 | 6.7279 | 6.6774 | 6.6226 | 6.57 | 6.5205 | 6.4732 | 6.4268 | 6.2247 | 6.0247 | 5.8563 | 7.3321 | 7.2626 | 7.1932 | 7.1237 | 7.0542 | 6.9763 | 6.8974 | 6.8216 | 6.7479 | 6.6774 | 6.41 | 6.1868 | 5.9858 | 7.2111 | 7.1637 | 7.1142 | 7.0647 | 7.0005 | 6.9332 | 6.87 | 6.7995 | 6.7237 | 6.6532 | 6.3763 | 6.15 | 5.9447
|  | WHITING BAY | EE |  |  |  |  | 6.8932 | 6.8542 | 6.8132 | 6.7711 | 6.7279 | 6.6837 | 6.6416 | 6.6005 | 6.5626 | 6.5258 | 6.3816 | 6.2753 | 6.1574 | 7.3637 | 7.3079 | 7.2521 | 7.1953 | 7.1374 | 7.0795 | 7.0258 | 6.9721 | 6.9184 | 6.8647 | 6.6353 | 6.4753 | 6.3458 | 7.2311 | 7.1921 | 7.1511 | 7.1089 | 7.0658 | 7.0205 | 6.9689 | 6.9195 | 6.8721 | 6.8289 | 6.6005 | 6.4332 | 6.2963
|  | WHITING BAY | HT |  |  |  |  | 6.8732 | 6.8258 | 6.7774 | 6.7279 | 6.6774 | 6.6226 | 6.57 | 6.5205 | 6.4732 | 6.4268 | 6.2247 | 6.0247 | 5.8563 | 7.3321 | 7.2626 | 7.1932 | 7.1237 | 7.0542 | 6.9763 | 6.8974 | 6.8216 | 6.7479 | 6.6774 | 6.41 | 6.1868 | 5.9858 | 7.2111 | 7.1637 | 7.1142 | 7.0647 | 7.0005 | 6.9332 | 6.87 | 6.7995 | 6.7237 | 6.6532 | 6.3763 | 6.15 | 5.9447
|  | WHITING BAY | HE |  |  |  |  | 6.9195 | 6.8953 | 6.8689 | 6.8405 | 6.81 | 6.7774 | 6.7468 | 6.7184 | 6.6921 | 6.6658 | 6.5826 | 6.5395 | 6.5163 | 7.4058 | 7.3721 | 7.3363 | 7.2995 | 7.2605 | 7.2205 | 7.1837 | 7.1468 | 7.1142 | 7.0837 | 6.9721 | 6.9026 | 6.8426 | 7.2111 | 7.1637 | 7.1142 | 7.0647 | 7.0005 | 6.9332 | 6.87 | 6.7995 | 6.7237 | 6.6532 | 6.3763 | 6.15 | 5.9447
|  | WHITING BAY | CF |  |  |  |  | 6.9353 | 6.9216 | 6.9089 | 6.8942 | 6.8795 | 6.8658 | 6.8511 | 6.8363 | 6.8216 | 6.8079 | 6.7458 | 6.7153 | 6.6995 | 7.4279 | 7.4089 | 7.39 | 7.3689 | 7.3479 | 7.3279 | 7.3079 | 7.2868 | 7.2658 | 7.2458 | 7.1563 | 7.1016 | 7.0605 | 7.2732 | 7.2595 | 7.2468 | 7.2321 | 7.2174 | 7.2037 | 7.1889 | 7.1742 | 7.1595 | 7.1447 | 7.0826 | 7.0447 | 7.0132
| MYBSTER 1 | WICK | MINIMUM HEADROOM | ND 35583 50947 | NO | YES | 0 | 10.4147 | 10.2621 | 10.0242 | 9.72 | 9.4158 | 8.6063 | 7.8105 | 6.9979 | 3.8053 | 2.9989 | -1.6463 | -7.0074 | -10.9558 | 11.6442 | 11.3421 | 11.02 | 10.7042 | 10.3895 | 9.6611 | 8.9484 | 8.2189 | 5.7853 | 5.0726 | 0.54842 | -5.3358 | -9.7021 | 11.32 | 11.0379 | 10.7137 | 10.3905 | 10.0684 | 9.2274 | 8.4021 | 7.5579 | 4.3495 | 3.5179 | -1.5242 | -7.6274 | -12.1295
|  | WICK | EE |  |  |  |  | 10.4716 | 10.3432 | 10.1663 | 9.9621 | 9.6874 | 9.3189 | 8.6095 | 7.7253 | 7.4432 | 6.5558 | 1.7705 | -3.6221 | -8.4463 | 11.7779 | 11.5379 | 11.2663 | 10.9895 | 10.7147 | 10.3284 | 9.7326 | 9.0168 | 8.7105 | 7.9516 | 3.5716 | -1.8084 | -6.9547 | 11.4337 | 11.2147 | 10.9442 | 10.6568 | 10.3674 | 9.9684 | 9.2453 | 8.3495 | 8.04 | 7.1284 | 2.0347 | -3.8958 | -9.34
|  | WICK | HT |  |  |  |  | 10.4147 | 10.2621 | 10.0242 | 9.72 | 9.4158 | 8.6063 | 7.8105 | 6.9979 | 3.8053 | 2.9989 | -1.6463 | -7.0074 | -10.9558 | 11.6442 | 11.3421 | 11.02 | 10.7042 | 10.3895 | 9.6611 | 8.9484 | 8.2189 | 5.7853 | 5.0726 | 0.54842 | -5.3358 | -9.7021 | 11.32 | 11.0379 | 10.7137 | 10.3905 | 10.0684 | 9.2274 | 8.4021 | 7.5579 | 4.3495 | 3.5179 | -1.5242 | -7.6274 | -12.1295
|  | WICK | HE |  |  |  |  | 10.5537 | 10.4705 | 10.3705 | 10.2632 | 10.1474 | 9.3505 | 8.6947 | 8.0547 | 5.9389 | 4.92 | 1.0116 | -3.24 | -8.7221 | 11.9295 | 11.8053 | 11.6537 | 11.4874 | 11.2211 | 10.4968 | 9.9579 | 9.4379 | 7.82 | 6.8716 | 3.1368 | -1.2495 | -6.6821 | 11.32 | 11.0379 | 10.7137 | 10.3905 | 10.0684 | 9.2274 | 8.4021 | 7.5579 | 4.3495 | 3.5179 | -1.5242 | -7.6274 | -12.1295
|  | WICK | CF |  |  |  |  | 10.5989 | 10.5505 | 10.4947 | 10.4358 | 10.3789 | 10.1179 | 9.88 | 9.6474 | 7.9137 | 7.4358 | 5.4747 | 2.8158 | -0.56211 | 12.0032 | 11.9284 | 11.8453 | 11.76 | 11.66 | 11.4011 | 11.1611 | 10.9242 | 9.4737 | 9.0095 | 7.0242 | 4.2484 | 0.68421 | 11.5968 | 11.5379 | 11.4695 | 11.4021 | 11.3179 | 11.0232 | 10.7474 | 10.4621 | 8.62 | 8.0905 | 5.9526 | 2.9716 | -0.83579
| WOODHILL | WOODHILL | MINIMUM HEADROOM | NJ 91259 07053 | NO | NO | 0.2 | 17.0337 | 16.8242 | 16.5116 | 16.1158 | 15.7232 | 15.2989 | 14.8863 | 14.4832 | 14.0863 | 13.7253 | 11.6389 | 10.9695 | 9.7695 | 16.1158 | 15.6968 | 15.3758 | 14.9537 | 14.5358 | 14.0916 | 13.66 | 13.2379 | 12.8263 | 12.9453 | 11.1537 | 10.1484 | 8.8263 | 16.8684 | 16.64 | 16.3368 | 15.9137 | 15.4947 | 15.0453 | 14.6074 | 14.1821 | 13.7632 | 13.8989 | 12.8926 | 10.9137 | 9.5747
|  | WOODHILL | EE |  |  |  |  | 17.1189 | 16.9547 | 16.78 | 16.5432 | 16.2168 | 15.8737 | 15.5347 | 15.2042 | 14.8937 | 14.6095 | 13.8126 | 12.4137 | 11.5705 | 16.3042 | 15.9821 | 15.6495 | 15.4137 | 15.0663 | 14.7116 | 14.3611 | 14.0189 | 13.6958 | 13.3937 | 12.98 | 11.7116 | 10.7842 | 16.9632 | 16.7842 | 16.5958 | 16.3758 | 16.0263 | 15.6642 | 15.3063 | 14.9579 | 14.6295 | 14.3263 | 13.92 | 12.4916 | 11.5495
|  | WOODHILL | HT |  |  |  |  | 17.0337 | 16.8242 | 16.5116 | 16.1158 | 15.7232 | 15.2989 | 14.8863 | 14.4832 | 14.0863 | 14.0074 | 12.82 | 10.9695 | 9.7695 | 16.1158 | 15.6968 | 15.3758 | 14.9537 | 14.5358 | 14.0916 | 13.66 | 13.2379 | 12.8263 | 12.9453 | 11.9432 | 10.1484 | 8.8263 | 16.8684 | 16.64 | 16.3368 | 15.9137 | 15.4947 | 15.0453 | 14.6074 | 14.1821 | 13.7632 | 13.8989 | 12.8926 | 10.9137 | 9.5747
|  | WOODHILL | HE |  |  |  |  | 17.2126 | 17.0895 | 16.9547 | 16.8084 | 16.6537 | 16.4695 | 16.14 | 15.9379 | 15.7084 | 13.7253 | 11.6389 | 11.0895 | 10.8884 | 16.4958 | 16.3147 | 16.0905 | 15.8484 | 15.6032 | 15.3337 | 14.9779 | 14.7337 | 14.4989 | 13.0242 | 11.1537 | 10.4105 | 9.9137 | 16.8684 | 16.64 | 16.3368 | 15.9137 | 15.4947 | 15.0453 | 14.6074 | 14.1821 | 13.7632 | 13.8989 | 12.8926 | 10.9137 | 9.5747
|  | WOODHILL | CF |  |  |  |  | 17.2632 | 17.1811 | 17.0979 | 17.0105 | 16.9232 | 16.8263 | 16.7284 | 16.6316 | 16.5095 | 16.3547 | 15.6432 | 15.1274 | 14.7411 | 16.5621 | 16.4526 | 16.3274 | 16.1768 | 16.02 | 15.8558 | 15.6895 | 15.5211 | 15.3579 | 15.1947 | 14.4432 | 13.9 | 13.4832 | 17.1253 | 17.0368 | 16.9474 | 16.8537 | 16.7589 | 16.6558 | 16.5516 | 16.4484 | 16.3095 | 16.1442 | 15.3842 | 14.8284 | 14.4011

## Local Authority Reference
#VALUE! | Local Authority | Grid Supply Point | Primary Substation
| Aberdeen City | CLAYHILLS | BALNAGASK
| Aberdeen City | PERSLEY | BRIDGE OF DON
| Aberdeen City | CLAYHILLS | CLAYHILLS
| Aberdeen City | CLAYHILLS | COMMERCE STREET
| Aberdeen City | CRAIGIEBUCKLER | CRAIGIEBUCKLER
| Aberdeen City | REDMOSS | CRAIGINCHES
| Aberdeen City | CRAIGIEBUCKLER | CRAIGTON
| Aberdeen City | CRAIGIEBUCKLER | CULTER
| Aberdeen City | WILLOWDALE | DENBURN
| Aberdeen City | DYCE | DYCE NORTH
| Aberdeen City | WILLOWDALE | GREYFRIARS
| Aberdeen City | DYCE | HARVEST AVENUE
| Aberdeen City | PERSLEY | HAUDAGAIN
| Aberdeen City | WILLOWDALE | HAYTON
| Aberdeen City | REDMOSS | KINCORTH
| Aberdeen City | PERSLEY | NORTHFIELD
| Aberdeen City | KINTORE | PARK
| Aberdeen City | WOODHILL | QUEENS LANE NORTH
| Aberdeen City | REDMOSS | REDMOSS
| Aberdeen City | CRAIGIEBUCKLER | RUTHRIESTON
| Aberdeen City | KINTORE | SKENE
| Aberdeen City | WOODHILL | SPRINGHILL
| Aberdeen City | PERSLEY | ST MACHAR
| Aberdeen City | WILLOWDALE | ST NICHOLAS
| Aberdeen City | PERSLEY | STONEYWOOD T1&T2
| Aberdeen City | PERSLEY | STONEYWOOD T3
| Aberdeen City | KINTORE | TORRYBURN
| Aberdeen City | PERSLEY | WHITESTRIPES
| Aberdeen City | WOODHILL | WOODHILL
| Aberdeenshire | TARLAND | ABOYNE
| Aberdeenshire | BOAT OF GARTEN | AVIEMORE
| Aberdeenshire | TARLAND | BALLATER
| Aberdeenshire | BOAT OF GARTEN | BALLINDALLOCH
| Aberdeenshire | DYCE | BALMEDIE
| Aberdeenshire | KINTORE | BANCHORY
| Aberdeenshire | PETERHEAD SHELL | BODDAM
| Aberdeenshire | TUMMEL BRIDGE | BONSKEID
| Aberdeenshire | PERSLEY | BRIDGE OF DON
| Aberdeenshire | CRAIGIEBUCKLER | CRAIGTON
| Aberdeenshire | KEITH | CULLEN
| Aberdeenshire | CRAIGIEBUCKLER | CULTER
| Aberdeenshire | COUPAR ANGUS | DALRULZION
| Aberdeenshire | KEITH | DUFFTOWN
| Aberdeenshire | DYCE | DYCE NORTH
| Aberdeenshire | FIDDES | EDZELL
| Aberdeenshire | DYCE | ELLON
| Aberdeenshire | FRASERBURGH | FRASERBURGH
| Aberdeenshire | KINTORE | FYVIE
| Aberdeenshire | STRICHEN | HATTON
| Aberdeenshire | KEITH | HUNTLY
| Aberdeenshire | BRIDGE OF DUN | INCHBARE
| Aberdeenshire | KEITH | INSCH
| Aberdeenshire | FIDDES | INVERBERVIE
| Aberdeenshire | KINTORE | INVERURIE
| Aberdeenshire | KEITH | KEITH
| Aberdeenshire | KINTORE | KEMNAY
| Aberdeenshire | REDMOSS | KINCORTH
| Aberdeenshire | DYCE | KINGSEAT
| Aberdeenshire | FIDDES | LAURENCEKIRK
| Aberdeenshire | KEITH | LIMEHILLOCKS
| Aberdeenshire | BRIDGE OF DUN | LOGIE PERT
| Aberdeenshire | MACDUFF | MACDUFF
| Aberdeenshire | KEITH | MARNOCH
| Aberdeenshire | LUNANHEAD | MARYTON
| Aberdeenshire | STRICHEN | MAUD
| Aberdeenshire | KINTORE | METHLICK
| Aberdeenshire | KINTORE | MIDMAR
| Aberdeenshire | STRICHEN | MINTLAW
| Aberdeenshire | BRIDGE OF DUN | MONTROSE NORTH
| Aberdeenshire | TARLAND | MOSSAT
| Aberdeenshire | STRICHEN | NEW PITSLIGO
| Aberdeenshire | REDMOSS | NEWTONHILL
| Aberdeenshire | KINTORE | OLDMELDRUM
| Aberdeenshire | KINTORE | PARK
| Aberdeenshire | PETERHEAD GRANGE | PETERHEAD GRANGE
| Aberdeenshire | PETERHEAD GRANGE | PETERHEAD NORTH STREET
| Aberdeenshire | MACDUFF | PORTSOY
| Aberdeenshire | REDMOSS | REDMOSS
| Aberdeenshire | CRAIGIEBUCKLER | RUTHRIESTON
| Aberdeenshire | KINTORE | SKENE
| Aberdeenshire | WOODHILL | SPRINGHILL
| Aberdeenshire | BRIDGE OF DUN | ST CYRUS
| Aberdeenshire | ST FERGUS GAS | ST FERGUS GAS TERM
| Aberdeenshire | FIDDES | STONEHAVEN
| Aberdeenshire | STRICHEN | STONEYHILL
| Aberdeenshire | TARLAND | STRATHDON
| Aberdeenshire | STRICHEN | STRICHEN
| Aberdeenshire | KINTORE | TORRYBURN
| Aberdeenshire | MACDUFF | TURRIFF
| Aberdeenshire | TARLAND | WHITEHOUSE
| Aberdeenshire | PERSLEY | WHITESTRIPES
| Angus | COUPAR ANGUS | ALYTH
| Angus | MILTON OF CRAIGIE | ASHLUDIE
| Angus | ABERNETHY | BALBEGGIE
| Angus | MILTON OF CRAIGIE | BALDOVIE
| Angus | TARLAND | BALLATER
| Angus | KINTORE | BANCHORY
| Angus | BRIDGE OF DUN | BRECHIN
| Angus | BRIDGE OF DUN | BRIDGE OF DUN
| Angus | MILTON OF CRAIGIE | BROUGHTY FERRY
| Angus | ARBROATH | CARNOUSTIE
| Angus | ARBROATH | CHARLES AVENUE
| Angus | COUPAR ANGUS | COUPAR ANGUS
| Angus | COUPAR ANGUS | DALRULZION
| Angus | FIDDES | EDZELL
| Angus | MILTON OF CRAIGIE | EDZELL STREET
| Angus | ARBROATH | ELLIOT DEPOT
| Angus | LUNANHEAD | FRIOCKHEIM
| Angus | CHARLESTON | GOURDIE
| Angus | ARBROATH | HUME STREET
| Angus | BRIDGE OF DUN | INCHBARE
| Angus | LUNANHEAD | INVERARITY
| Angus | FIDDES | LAURENCEKIRK
| Angus | COUPAR ANGUS | LEOCH
| Angus | LUNANHEAD | LOCHSIDE
| Angus | BRIDGE OF DUN | LOGIE PERT
| Angus | MILTON OF CRAIGIE | LONGHAUGH
| Angus | LUNANHEAD | LUNANHEAD
| Angus | LYNDHURST | MACALPINE ROAD
| Angus | LUNANHEAD | MARYTON
| Angus | BRIDGE OF DUN | MILL ROAD MONTROSE
| Angus | BRIDGE OF DUN | MONTROSE NORTH
| Angus | ARBROATH | REDFORD
| Angus | BRIDGE OF DUN | ST CYRUS
| Angus | LYNDHURST | WEST KIRKTON
| Argyll and Bute | PORT ANN | AIRIGH-NA-BRODAIG
| Argyll and Bute | CARRADALE | BALLURE
| Argyll and Bute | TAYNUILT | BARCALDINE
| Argyll and Bute | RANNOCH | BLACKMOUNT
| Argyll and Bute | PORT ANN | BOWMORE
| Argyll and Bute | DUNOON | BRUCHAG
| Argyll and Bute | CLACHAN | BUTTERBRIDGE
| Argyll and Bute | CARRADALE | CAMPBELTOWN
| Argyll and Bute | KILLIN | CASHLIE
| Argyll and Bute | KILLIN | CHAORACH
| Argyll and Bute | CARRADALE | CLAONAIG
| Argyll and Bute | DUNOON | COLINTRAIVE
| Argyll and Bute | TAYNUILT | CONNEL
| Argyll and Bute | PORT ANN | CRINAN
| Argyll and Bute | PORT ANN | CROMALT
| Argyll and Bute | TAYNUILT | DALMALLY
| Argyll and Bute | TAYNUILT | DERVAIG
| Argyll and Bute | CARRADALE | DIPPEN
| Argyll and Bute | CLACHAN | DOUGLAS PIER
| Argyll and Bute | STRATHLEVEN | DRYMEN
| Argyll and Bute | DUNOON | DUNOON
| Argyll and Bute | TAYNUILT | EREDINE
| Argyll and Bute | DUNOON | GLENDARUEL
| Argyll and Bute | RANNOCH | GLENETIVE
| Argyll and Bute | DUNOON | INNELLAN
| Argyll and Bute | CLACHAN | INVERARAY
| Argyll and Bute | PORT ANN | INVERNEIL
| Argyll and Bute | DUNOON | KAMES
| Argyll and Bute | TAYNUILT | KENMORE
| Argyll and Bute | TAYNUILT | KERRERA
| Argyll and Bute | TAYNUILT | KILCHRENAN
| Argyll and Bute | TAYNUILT | KILMELFORD
| Argyll and Bute | TAYNUILT | KILNINVER
| Argyll and Bute | TAYNUILT | KINLOCH
| Argyll and Bute | TUMMEL BRIDGE | KINLOCH RANNOCH
| Argyll and Bute | TAYNUILT | LOCHDONHEAD
| Argyll and Bute | PORT ANN | LOCHGILPHEAD
| Argyll and Bute | CLACHAN | LOCHGOILHEAD
| Argyll and Bute | PORT ANN | LUSSAGIVEN
| Argyll and Bute | DUNOON | NEWTON
| Argyll and Bute | TAYNUILT | OBAN
| Argyll and Bute | DUNOON | OTTER FERRY
| Argyll and Bute | PORT ANN | PORT ASKAIG
| Argyll and Bute | PORT ANN | PORT ELLEN
| Argyll and Bute | DUNOON | ROTHESAY
| Argyll and Bute | FORT WILLIAM | SALEN 2
| Argyll and Bute | DUNOON | SANDBANK
| Argyll and Bute | TAYNUILT | SCAMMADALE
| Argyll and Bute | PORT ANN | STONEFIELD
| Argyll and Bute | CLACHAN | STRACHUR
| Argyll and Bute | PORT ANN | TARBERT JURA
| Argyll and Bute | PORT ANN | TARBERT LOCH FYNE
| Argyll and Bute | TAYNUILT | TAYNUILT
| Argyll and Bute | TAYNUILT | TIRORAN BRIDGE
| Argyll and Bute | RANNOCH | TYNDRUM
| Argyll and Bute | CARRADALE | WESTPARK FERGUS
| Clackmannanshire | ABERNETHY | GLENDEVON
| Clackmannanshire | BRACO | GLENEAGLES
| Clackmannanshire | ABERNETHY | MILNATHORT
| Dundee City | MILTON OF CRAIGIE | ASHLUDIE
| Dundee City | MILTON OF CRAIGIE | BALDOVIE
| Dundee City | MILTON OF CRAIGIE | BROUGHTY FERRY
| Dundee City | CHARLESTON | CHARLESTON
| Dundee City | DUDHOPE | CONSTABLE STREET
| Dundee City | MILTON OF CRAIGIE | EDZELL STREET
| Dundee City | CHARLESTON | GOURDIE
| Dundee City | COUPAR ANGUS | LEOCH
| Dundee City | LYNDHURST | LOCHEE
| Dundee City | MILTON OF CRAIGIE | LONGHAUGH
| Dundee City | LYNDHURST | LYNDHURST
| Dundee City | LYNDHURST | MACALPINE ROAD
| Dundee City | CHARLESTON | MENZIESHILL
| Dundee City | MILTON OF CRAIGIE | MILTON OF CRAIGIE
| Dundee City | CHARLESTON | NINEWELLS
| Dundee City | MILTON OF CRAIGIE | OLD CRAIGIE ROAD
| Dundee City | GLENAGNES | OVERGATE
| Dundee City | DUDHOPE | ROSEBANK STREET
| Dundee City | GLENAGNES | WALTON
| Dundee City | LYNDHURST | WEST KIRKTON
| East Dunbartonshire | STRATHLEVEN | KEPCULLOCH
| East Dunbartonshire | STRATHLEVEN | KILLEARN
| East Dunbartonshire | BRACO | KIPPEN
| Eilean Siar | ARDMORE | AIRD
| Eilean Siar | STORNOWAY | ARNISH
| Eilean Siar | STORNOWAY | BARVAS
| Eilean Siar | STORNOWAY | BATTERY POINT
| Eilean Siar | STORNOWAY | CALLANISH
| Eilean Siar | ARDMORE | CLACHAN
| Eilean Siar | STORNOWAY | COLL
| Eilean Siar | ARDMORE | DRIMORE
| Eilean Siar | STORNOWAY | GISLA
| Eilean Siar | ARDMORE | HARRIS GRID
| Eilean Siar | STORNOWAY | LAXAY
| Eilean Siar | ARDMORE | LOCH CARNAN
| Eilean Siar | STORNOWAY | MAARUIG
| Eilean Siar | ARDMORE | POLLACHAR
| Eilean Siar | ARDMORE / HARRIS GRID | STOCKINISH
| Eilean Siar | ARDMORE / HARRIS GRID | TARBERT
| Fife | ABERNETHY | ABERNETHY
| Fife | ABERNETHY | BRIDGE OF EARN
| Fife | ABERNETHY | GLENDEVON
| Fife | ABERNETHY | MILNATHORT
| Highland | FORT AUGUSTUS | ABERCHALDER
| Highland | KEITH | ABERLOUR
| Highland | GRUDIE BRIDGE | ACHILTIBUIE
| Highland | BROADFORD | ACHINTEE
| Highland | BEAULY | AIGAS
| Highland | FORT WILLIAM | ANNAT
| Highland | NAIRN | ARDERSIER
| Highland | FORT AUGUSTUS | ARDOCHY
| Highland | FORT WILLIAM | ARISAIG
| Highland | GRUDIE BRIDGE | AULTBEA
| Highland | BOAT OF GARTEN | AVIEMORE
| Highland | ALNESS | BALALDIE
| Highland | BOAT OF GARTEN | BALLINDALLOCH
| Highland | TAYNUILT | BARCALDINE
| Highland | DOUNREAY | BETTYHILL
| Highland | GRUDIE BRIDGE | BIDEN CLAN RAONAILD
| Highland | RANNOCH | BLACKMOUNT
| Highland | BEAULY | BLACKSTAND
| Highland | BOAT OF GARTEN | BOAT OF GARTEN
| Highland | TUMMEL BRIDGE | BONSKEID
| Highland | RANNOCH | BRIDGE OF GAUR
| Highland | BROADFORD | BROADFORD
| Highland | FORT AUGUSTUS | BUNOICH
| Highland | TUMMEL BRIDGE | CALVINE
| Highland | DOUNREAY | COLDBACKIE
| Highland | ST FILLANS | COMRIE
| Highland | BEAULY | CONON BRIDGE
| Highland | BEAULY | CONON FALLS
| Highland | ALNESS | CONTULLICH
| Highland | FORT WILLIAM | CORRAN
| Highland | ALNESS | CROSSHILLS
| Highland | INVERNESS | CULLODEN
| Highland | NAIRN | DALCROSS
| Highland | INVERNESS | DALNEIGH
| Highland | BOAT OF GARTEN | DALWHINNIE
| Highland | BEAULY | DINGWALL
| Highland | BRORA | DORNOCH
| Highland | DOUNREAY | DOUNREAY
| Highland | CEANNACROC | DRUMNADROCHIT
| Highland | GRUDIE BRIDGE | DRUMRUNIE
| Highland | DUNVEGAN | DRYNOCH
| Highland | DUNOON | DUNOON
| Highland | DUNVEGAN | DUNVEGAN GRID
| Highland | INVERNESS | ERROGIE
| Highland | FORT WILLIAM | FISHNISH
| Highland | NAIRN | FORRES
| Highland | DOUNREAY | FORSS
| Highland | INVERNESS | FOYERS
| Highland | GRUDIE BRIDGE | GARBAT FOREST
| Highland | ALNESS | GLASTULLICH
| Highland | SHIN | GLEDFIELD
| Highland | FORT AUGUSTUS | GLEN LAOGH
| Highland | KINLOCHLEVEN | GLENCOE
| Highland | FORT AUGUSTUS | GLENDOE PRIMARY
| Highland | RANNOCH | GLENETIVE
| Highland | FORT WILLIAM | GLENUIG
| Highland | BRORA | GOLSPIE
| Highland | BOAT OF GARTEN | GRANTOWN
| Highland | GRUDIE BRIDGE | GRUDIE BRIDGE
| Highland | THURSO | HALKIRK
| Highland | THURSO | HASTIGROW
| Highland | BRORA | HELMSDALE
| Highland | INVERNESS | HILTON
| Highland | INVERNESS | INVERARNIE
| Highland | GRUDIE BRIDGE | INVERBROOM
| Highland | FORT AUGUSTUS | INVERGARRY
| Highland | ALNESS | INVERGORDON
| Highland | FORT WILLIAM | INVERLOCHY
| Highland | INVERNESS | INVERNESS
| Highland | BROADFORD | KALNAKIL
| Highland | GRUDIE BRIDGE | KERRY FALLS
| Highland | BEAULY | KILTARLITY
| Highland | FORT WILLIAM | KINGAIRLOCH
| Highland | BOAT OF GARTEN | KINGUSSIE
| Highland | TUMMEL BRIDGE | KINLOCH RANNOCH
| Highland | GRUDIE BRIDGE | KINLOCHEWE
| Highland | KINLOCHLEVEN | KINLOCHLEVEN
| Highland | FORT WILLIAM | KINLOCHMOIDART
| Highland | BROADFORD | KISHORNHILL
| Highland | BROADFORD | KYLE
| Highland | LAIRG | LAIRG GRID
| Highland | MYBSTER | LATHERON
| Highland | NAIRN | LETHEN
| Highland | GRUDIE BRIDGE | LETTEREWE
| Highland | FORT WILLIAM | LIDDESDALE
| Highland | GRUDIE BRIDGE | LOCH GLASCARNOCH
| Highland | FORT WILLIAM | LOCHALINE
| Highland | GRUDIE BRIDGE | LOCHINVER
| Highland | BROADFORD | LOWER OLLACH
| Highland | FORT WILLIAM | MALLAIG
| Highland | BEAULY | MARYBANK
| Highland | MYBSTER | MELVICH
| Highland | THURSO | MOUNT PLEASANT
| Highland | BEAULY | MUIR OF ORD
| Highland | BEAULY | MUIREND
| Highland | NAIRN | NAIRN CENTRAL
| Highland | ALNESS | NIGG
| Highland | BROADFORD | NOSTIE BRIDGE
| Highland | THURSO | ORMLIE
| Highland | CASSLEY | OVERSCAIG
| Highland | ALNESS | PEDDIESTON
| Highland | FORT WILLIAM | PINEGROVE
| Highland | FORT WILLIAM | POOR HOUSE
| Highland | DUNVEGAN | PORTREE
| Highland | QUOICH | QUOICH PRIMARY
| Highland | FORT WILLIAM | RAHOY
| Highland | INVERNESS | RAIGMORE
| Highland | INVERNESS | LONGMAN DRIVE
| Highland | CASSLEY | RHICONICH
| Highland | TAYNUILT | SALEN
| Highland | BROADFORD | SHIELDAIG
| Highland | SHIN | SHIN
| Highland | FORT WILLIAM | SHONA BEAG
| Highland | BROADFORD | SKULAMUS
| Highland | FORT WILLIAM | STRONTIAN
| Highland | ALNESS | TAIN
| Highland | BOAT OF GARTEN | TOMATIN
| Highland | LAIRG | TORBOLL
| Highland | LAIRG | TRESSADY
| Highland | DUNVEGAN | UIG
| Highland | GRUDIE BRIDGE | ULLAPOOL
| Highland | INVERNESS | WATERLOO PLACE
| Highland | KILLIN | WESTER DRUMMOND
| Highland | MYBSTER | WICK
| Moray | KEITH | ABERLOUR
| Moray | ELGIN | ASHGROVE
| Moray | BOAT OF GARTEN | AVIEMORE
| Moray | TARLAND | BALLATER
| Moray | BOAT OF GARTEN | BALLINDALLOCH
| Moray | ELGIN | BILBOHALL
| Moray | KEITH | BUCKIE
| Moray | ELGIN | BURGHEAD
| Moray | KEITH | CULLEN
| Moray | ELGIN | CUMMING STREET
| Moray | KEITH | DUFFTOWN
| Moray | ELGIN | ELGIN
| Moray | ELGIN | FOCHABERS
| Moray | NAIRN | FORRES
| Moray | BOAT OF GARTEN | GRANTOWN
| Moray | KEITH | HUNTLY
| Moray | KEITH | KEITH
| Moray | ELGIN | KINLOSS
| Moray | NAIRN | LETHEN
| Moray | ELGIN | LHANBRYDE
| Moray | KEITH | LIMEHILLOCKS
| Moray | ELGIN | LOSSIEMOUTH
| Moray | KEITH | MARNOCH
| Moray | TARLAND | MOSSAT
| Moray | NAIRN | NAIRN CENTRAL
| Moray | MACDUFF | PORTSOY
| Moray | KEITH | ROTHES
| Moray | TARLAND | STRATHDON
| North Ayrshire | CARRADALE | BALLIEKINE
| North Ayrshire | CARRADALE | BRODICK
| North Ayrshire | DUNOON | BRUCHAG
| North Ayrshire | CARRADALE | MACHRIE
| North Ayrshire | CARRADALE | WHITING BAY
| North Lanarkshire | BRACO | KIPPEN
| Orkney Islands | THURSO | BURGARHILL
| Orkney Islands | THURSO | EDAY
| Orkney Islands | THURSO | EDAY TIDAL
| Orkney Islands | THURSO | FLOTTA
| Orkney Islands | THURSO | KIRKWALL
| Orkney Islands | THURSO | LYNESS
| Orkney Islands | THURSO | NORTH HOY
| Orkney Islands | THURSO | RACKWICK
| Orkney Islands | THURSO | ROUSAY
| Orkney Islands | THURSO | SANDAY
| Orkney Islands | THURSO | SHAPINSAY
| Orkney Islands | THURSO | ST MARYS
| Orkney Islands | THURSO | STROMNESS
| Orkney Islands | THURSO | STRONSAY
| Orkney Islands | THURSO | WESTRAY
| Perth and Kinross | TUMMEL BRIDGE | ABERFELDY
| Perth and Kinross | ABERNETHY | ABERNETHY
| Perth and Kinross | COUPAR ANGUS | ALYTH
| Perth and Kinross | BOAT OF GARTEN | AVIEMORE
| Perth and Kinross | ABERNETHY | BALBEGGIE
| Perth and Kinross | TARLAND | BALLATER
| Perth and Kinross | RANNOCH | BLACKMOUNT
| Perth and Kinross | COUPAR ANGUS | BLAIRGOWRIE
| Perth and Kinross | TUMMEL BRIDGE | BONSKEID
| Perth and Kinross | ABERNETHY | BRIDGE OF EARN
| Perth and Kinross | RANNOCH | BRIDGE OF GAUR
| Perth and Kinross | BURGHMUIR | BURGHMUIR
| Perth and Kinross | BRACO | CALLANDER
| Perth and Kinross | TUMMEL BRIDGE | CALVINE
| Perth and Kinross | COUPAR ANGUS | CAPUTH
| Perth and Kinross | KILLIN | CASHLIE
| Perth and Kinross | KILLIN | CHAORACH
| Perth and Kinross | KILLIN | COSHIEVILLE
| Perth and Kinross | COUPAR ANGUS | COUPAR ANGUS
| Perth and Kinross | BRACO | CRIEFF
| Perth and Kinross | ST FILLANS | DALCHONZIE
| Perth and Kinross | COUPAR ANGUS | DALRULZION
| Perth and Kinross | BOAT OF GARTEN | DALWHINNIE
| Perth and Kinross | BRACO | DUNBLANE
| Perth and Kinross | ABERNETHY | ERROL
| Perth and Kinross | TUMMEL BRIDGE | FINCASTLE
| Perth and Kinross | BRACO | FORTEVIOT
| Perth and Kinross | ABERNETHY | GLENDEVON
| Perth and Kinross | BRACO | GLENEAGLES
| Perth and Kinross | RANNOCH | GLENETIVE
| Perth and Kinross | BURGHMUIR | GOODLYBURN
| Perth and Kinross | CHARLESTON | GOURDIE
| Perth and Kinross | ABERNETHY | HARBOUR
| Perth and Kinross | BURGHMUIR | INVERALMOND
| Perth and Kinross | FORT WILLIAM | INVERLOCHY
| Perth and Kinross | KILLIN | KILLIN TOWN
| Perth and Kinross | BOAT OF GARTEN | KINGUSSIE
| Perth and Kinross | TUMMEL BRIDGE | KINLOCH RANNOCH
| Perth and Kinross | COUPAR ANGUS | LEOCH
| Perth and Kinross | KILLIN | LOCHEARNHEAD
| Perth and Kinross | LUNANHEAD | MARYTON
| Perth and Kinross | ABERNETHY | MILNATHORT
| Perth and Kinross | CHARLESTON | NINEWELLS
| Perth and Kinross | TUMMEL BRIDGE | PITLOCHRY
| Perth and Kinross | BURGHMUIR | REDGORTON
| Perth and Kinross | ABERNETHY | SCONE
| Perth and Kinross | ST FILLANS | ST FILLANS
| Perth and Kinross | BURGHMUIR | THIMBLEROW
| Perth and Kinross | RANNOCH | TYNDRUM
| Shetland Islands | WOODHILL | BRAE
| Shetland Islands | SHETLAND | FIRTH
| Shetland Islands | SHETLAND | GUTCHER
| Shetland Islands | SHETLAND | MID YELL
| Shetland Islands | SHETLAND | SANDWICK
| Shetland Islands | SHETLAND | SCALLOWAY
| Shetland Islands | SHETLAND | SUMBURGH
| Shetland Islands | SHETLAND | TUMBLIN
| Shetland Islands | SHETLAND | UNST
| Shetland Islands | SHETLAND | VOE
| Stirling | STRATHLEVEN | ABERFOYLE
| Stirling | KILLIN | ARCHYLE
| Stirling | BRACO | CALLANDER
| Stirling | KILLIN | CASHLIE
| Stirling | KILLIN | CHAORACH
| Stirling | KILLIN | COSHIEVILLE
| Stirling | ST FILLANS | DALCHONZIE
| Stirling | TAYNUILT | DALMALLY
| Stirling | STRATHLEVEN | DRYMEN
| Stirling | BRACO | DUNBLANE
| Stirling | BRACO | GLENEAGLES
| Stirling | STRATHLEVEN | KEPCULLOCH
| Stirling | STRATHLEVEN | KILLEARN
| Stirling | KILLIN | KILLIN TOWN
| Stirling | BRACO | KIPPEN
| Stirling | KILLIN | LOCHEARNHEAD
| Stirling | KILLIN | LUBNAIG
| Stirling | ST FILLANS | ST FILLANS
| Stirling | RANNOCH | TYNDRUM
| West Dunbartonshire | STRATHLEVEN | BLAIRLINNANS
| West Dunbartonshire | STRATHLEVEN | DRYMEN
| West Dunbartonshire | STRATHLEVEN | KILLEARN

## EISD
#VALUE! | GSPs in November 2024 LTDS | Demand |  | Generation |  | Comments (optional)
|  | EISD | Under review at freeze date? | EISD | Under review at freeze date?
| Abernethy | 2028 | Under active review | 2028 | Under active review
| Braco | 2025 | Under active review | 2035 | Under active review
| Burghmuir | 2028 | Under active review | 2028 | Under active review
| Coupar Angus | NA |  | 2029 | Under active review
| Killin | 2025 | Under active review | 2030 | Under active review
| Rannoch | 2025 | Under active review | 2025 | Under active review
| St Fillans | 2025 | Under active review | 2028 | Under active review
| Tummel Bridge | 2025 | Under active review | 2026 | Under active review
| Redmoss | NA |  | 2031
| Woodhill | NA |  | NA
| Ardkinglas | 2025 | Under active review | 2030 | Under active review
| Ardmore | 2028 | Under active review | 2028 | Under active review
| Cassley | NA | Under active review | 2028 | Under active review
| Charleston | 2030 | Under active review | 2028 | Under active review
| Clayhills | NA |  | 2025 | Under active review
| Lyndhurst | 2032 | Under active review | 2035 | Under active review
| Peterhead Grange | 2033 | Under active review | 2033 | Under active review
| Dunbeath | NA |  | NA | Under active review
| Alness | NA |  | 2030 | Under active review
| Beauly | NA |  | 2030 | Under active review
| Broadford | 2028 | Under active review | 2028 | Under active review
| Brora | NA |  | 2034 | Under active review
| Dunvegan | NA |  | 2028 | Under active review
| Fasnakyle | 2025 | Under active review | 2035 | Under active review
| Grudie Bridge | NA |  | NA
| Lairg | NA |  | 2033 | Under active review
| Shin | NA |  | NA | Under active review
| Orrin | NA |  | NA
| Dounreay | NA |  | 2033 | Under active review
| Fraserburgh | 2033 | Under active review | 2033 | Under active review
| Dallas | 2025 | Under active review | N/A
| Kinlochleven | 2025 | Under active review | N/A
| Glenfarclas | 2025 | Under active review | N/A
| Berryburn | 2024 | Under active review | 2030 | Under active review
| Fetteresso | NA |  | 2029 | Under active review
| Craigiebuckler | NA |  | 2032
| Kintore | 2032 | Under active review | 2032 | Under active review
| Tarland | NA |  | 2032 | Under active review
| Willowdale | NA |  | 2030
| Dyce | 2025 | Under active review | 2025 | Under active review
| Persley | NA |  | NA
| Peterhead Shell | NA |  | NA
| Strichen | 2033 | Under active review | 2033 | Under active review
| Arbroath | 2026 | Under active review | 2032 | Under active review
| Bridge of Dun | NA |  | 2032 | Under active review
| Fiddes | NA |  | 2032 | Under active review
| Lunanhead | 2028 | Under active review | 2028 | Under active review
| Milton of Craigie | NA |  | 2033 | Under active review
| Ceannacroc | NA |  | NA
| Fort Augustus | 2035 | Under active review | 2035 | Under active review
| Quoich | 2028 |  | 2028
| Boat of Garten | 2025 | Under active review | 2030 | Under active review
| Inverness | NA |  | 2030 | Under active review
| Nairn | 2027 | Under active review | 2027 | Under active review
| Rothienorman | 2033 | Under active review | 2033 | Under active review
| Cairnford | NA |  | NA
| Elgin | 2025 | Under active review | 2027 | Under active review
| Keith 1 | 2028 | Under active review | 2028 | Under active review
| Keith 2 | 2028 | Under active review | 2028 | Under active review
| MacDuff | NA |  | 2029 | Under active review
| Carradale 1 | 2025 | Under active review | 2034 | Under active review
| Carradale 2 | 2025 | Under active review | 2034 | Under active review
| Clachan | 2025 | Under active review | 2030 | Under active review
| Dunoon | 2025 | Under active review | 2028 | Under active review
| Fort William | NA | Under active review | NA | Under active review
| Port Ann | 2029 | Under active review | 2034 | Under active review
| Taynuilt | 2025 | Under active review | 2034 | Under active review
| Dudhope | NA |  | 2028 | Under active review
| Mybster 1 | NA |  | 2035
| Mybster 2 | NA |  | NA
| Thurso | NA |  | 2033
| Sloy | 2025 | Under active review | 2030 | Under active review
| St Fergus Gas | NA |  | 2033 | Under active review
Links to additional public-domain information related to the EISDs, provided by the Transmission Owner
https://www.ssen-transmission.co.uk/customer-connections/transmission-owner-reinforcement-instruction-tori-quarterly-update-reports/
2025-04-11 | Transmission Owner's freeze date
SHEPD | DNO Licence area
SSEN Transmisson | Transmision Owner providing
V1.1 11/04/2025 | Last update (version, date)
Notes
1 Earliest in service dates (EISDs) represent a snapshot of the Transmission Owner's view at the 'freeze date' of the earliest date for connection for NEW applications for demand and generation of significant size (>1MW)
For customers which already have accepted connections with a DNO, DNOs may already have agreed with transmission for earlier connection dates for demand and generation customers
2 The above EISD's are likely to be subject to change on completion of NESO's Connections Reform Project TMO4+, further information can be found at:
https://www.neso.energy/industry-information/connections-reform
3 For storage, both the demand and generation EISDs may be relevant.
4 Where an EISD has not been established for a GSP, this is shown as N/A.
There is likely to be some headroom for connection because there is no constraint yet defined with defined construction works affecting connnection, this is shown as "no date restriction identified".
5 Where the tranmission owner is actively reviewing construction works and earliest in service dates for new applications may be revised e.g. due to an application for capacity affecting that GSP, this is shown as "under active review"
6 The EISDs reflect both works at a Grid Supply Point and in wider tranmission network.
7 Unlike the rest of the DNO Network Scenario Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output.
8 The list of GSPs includes at a minimum the GSPs associated with the primary substations and Bulk Supply Points in the DNO's last Long Term Development Statement Table 3. Future new GSPs may not be included.