## Cover
Applies to: Third Party Designers | SSEPD STANDARD DESIGN MATRICES FOR POC ASSESSMENT |  | TG-PS-930
Classification: Public | Uncontrolled if printed |  | Rev:1.01
The author / owner of this document is: |  | This document has been approved for Issue by: | Date of Issue: | Review Date:
JB, Procedures and Investigations |  | DT, Engineering Projects | Oct 2015 | Oct 2020
Please read the supporting notes before using the matrices
Reference shall be made to the relevant documents on the SSEPD ICP website, ssepd.co.uk/competitioninconnections/

## Supporting Notes
Standard Design Matrices
The Standard Design Matrices shall be used as the guidance for determinining a point of connection. The matrices detail where generic design is acceptable and where more detailed analysis is required.
The matrices are designed to be a 'quick guide' to reference the process. Process maps have been included as tabs in this spreadsheet and these provided a more detailed view of the requirements for each design. Reference must me made to the Planning and Design Guidance documents. The process maps are shown on the following tabs;
(a) Streetlighting. ADMD limited to 8kVA and single customer load to 2kVA
(b) Domestic (excluding loads with motor starting). ADMD limited to 8kVA and single customer load to 23kVA per phase
(c) Light Industrial, commercial ( including domestic and all loads with motor starting). ADMD limited to 23kVA per phase and single customer load to 23kVA per phase
(d) Heavy industrial and commercial (includes domestic estates). Any ADMD not exceeding 1000kVA. Single customer loads up to 1500kVA.
The following notes refer to the standard design matrices
1 | Maximum Capacities | these may well be subject to other design constraints such a volt drop, earth fault loop impedance etc.
2 | New unloaded LV cables | winter cyclic ratings will be used unless load is predominantly in summer in which case the summer sustained rating shall be used
3 | Existing loaded LV cables | winter cyclic rating less ADMD applicable to existing installed load
4 | New transformers | nameplate rating
5 | Existing transformers | nameplate rating less ADMD applicable to existing installed load
6 | Volt Drop | Volt drop on distributor not to exceed 5% and that on service 2%
7 | Overhead Circuit | defined by any OH line section between the primary substation and the POC
8 | Windebut | an EA Technology design product - other software or a manual method of calculation can be used
9 | SinCal | a Siemens design product - other software or a manual method of calculation can be used

## Standard Design Matrices
Standard Design Matrix for Multiple Customer (2 or more) for Single POC Assessment - Applies ADMD (After Diversity Maximum Demand)
Please also refer to the 'Supporting Notes' tab
Number of Phases | Aggregated ADMD Limit | Demand Type | Method of Calculation and Output Requirements
|  |  | LV Service | LV Distributor |  | 6.6kV or 11kV Secondary Substation Transformer |  |  |  |  | 2kV up to 4kV Networks | 6.6 and 11kV Circuits |  | 22kV and 33kV Substations | 22kV and 33kV circuits |  | 66kV up to and incl. 400kV Substations | 66kV up to and incl. 400kV Circuits
|  |  |  | up to 10 metre branch ('T') on to existing Distributor | >10 metre branch and any extension to distributor | up to 50kVA | >50kVA to 100kVA | >100 kVA to 500kVA | >500kVA | Upgraded or New Tx |  | Overhead | Under- ground |  | Overhead | Under- ground |  | Overhead | Under- ground
Single phase | up to 8kVA | Street Lighting | Service 'T' + standard service (max service length 20m (35mm2 concentric), otherwise service design assessment required) | Use same LV Distributor cable CSA or equivalent |  | Transformer loading assessment only |  |  |  |  | SSEPD provide POC
Single phase | Max ADMD of 8kVA / phase | Domestic only (with no motor starting e.g. heat pumps) Maximum 9 properties (maximum 3 per phase) |  | Use same LV Distributor cable CSA or equivalent | Design assessment or use simplistic approach in TG-PS-886 (Appendix 1) for 'T'
Two phases
Three Phase
Single phase | Max ADMD of 23kVA / phase | Industrial/commercial or domestic including any load with motor starting (e.g. heat pumps) | Service 'T' + standard service (max service length 20m (35mm2 concentric), otherwise service design assessment required) | Design assessment using suitable analysis method / tool (e.g. Windebut). |  |  |  | Transformer loading assessment. Include design assessment for any non domestic load using suitable analysis method / tool (e.g. SinCal). |  |  | SSEPD will provide POC
Two phases
Three phase
Three phase | 69kVA and up to 150kVA | Any demand type | Design assessment using suitable analysis method / tool (e.g. Windebut).
Three phase | up to 250kVA
Three phase | up to 500kVA |  |  |  |  | Upgrade transformer capacity. Design assessment for any non domestic load using suitable analysis method / tool (e.g. SinCal). | [5 empty] | Design assessment using suitable analysis method / tool (e.g. Sincal)
Three phase | over 500kVA and up to 1000kVA | [12 empty] | SSEPD will provide POC
Key
| Design assessment not essential |  |  | Design assessment necessary |  |  | SSEPD will provide POC |  |  | Transformer upgrade essential |  |  |  | Awaiting requirements. SSEPD will provide POC meantime
The completed network must comply with the Supply Characteristics of the Design and Planning Guidance applicable to the voltage
Standard Design Matrix for Single Customer for Single POC Assessment - Single point demand (no diversity)
Please also refer to the 'Supporting Notes' tab
Number of Phases | Maximum Demand | Demand Type | Method of Calculation and Output Requirements
|  |  | LV Service | LV Distributor |  | 6.6kV or 11kV Secondary Substation Transformer |  |  |  |  | 2kV up to 4kV Networks | 6.6 and 11kV Circuits |  | 22kV and 33kV Substations | 22 and 33kV Circuits |  | 66kV up to and incl. 400kV Substations | 66kV up to and incl. 400kV Circuits
|  |  |  | up to 10 metre branch ('T') on to existing distributor | >10 metre branch and any extension to distributor | up to 50kVA | >50kVA to 100kVA | >100 kVA to 500kVA | >500 kVA | Upgraded or New Tx |  | Overhead | Under- ground |  | Overhead | Under- ground |  | Overhead | Under- ground
Single phase | up to 2kVA | Street Lighting | Service 'T' + standard service (max service length 20m (35mm2 concentric), otherwise service design assessment required) | Use same LV cable CSA or equivalent | [6 empty] | SSEPD will provide POC
Single phase | up to 8kVA
Single phase | up to 23kVA |  |  |  |  | Transformer loading assessment only
Two phases | up to 46kVA
Three phase | up to 69kVA
Single phase | up to 23kVA | Industrial and Commercial or Domestic including any load with motor starting (e.g. heat pumps) etc | Design assessment using a suitable analysis method / tool (e.g. Windebut). |  |  | Transformer loading assessment. Design assessment using suitable analysis method / tool (e.g. SinCal) |  |  |  |  | SSEPD will provide POC
Two phases | up to 46kVA
Three Phase | up to 69kVA
Three Phase | up to 250kVA | Commercial / Industrial (LV only)
Three Phase | up to 414kVA | [10 empty] | Design assessment using suitable analysis method / tool (e.g. SinCal)
Three Phase | up to and including 1,500kVA | Industrial / Commercial (LV from dedicated transformer) | Most likely singles | No distributer (dedicated feed from transformer)
Three Phase | up to 50,000kVA | Industrial / Commercial or Distributed Generation | SSEPD will provide POC